## DATA INPUT
ENTER THE AVERAGE MONTHLY INFLUENT FLOW
INTO THE CORROSPONDING BOXES BELOW:
JANUARY | 31.827 | DECEMBER | 33.035
ENTER THE PRESENT MONTH AND YEAR IN BOX BELOW (A5) | [5 empty] | FEBRUARY
2004-02-01 | [5 empty] | 2004
IW-1 | IW-2 | IW-3 | IW-4 | IW-5
35.5 | 36.5 | 37.3 | 36.3 | 35.1 | 2004-02-11
|  | ENTER INJECTION WELL SHUT-IN PRESSURE ABOVE |  |  | ENTER DATE OF SHUT-IN READINGS
ENTER SLUDGE DISPOSAL SITE FOR EACH WEEK BELOW
| WEEK 1 | WEEK 2 | WEEK 3 | WEEK 4
1 st | CSLOL Inc. | CSLOL Inc. | CSLOL Inc. | CSLOL Inc.
2 nd | Okeechobee, FL | Okeechobee, FL | Okeechobee, FL | Okeechobee, FL
RAW DATA REPORT ENTRY CATEGORIES
GTL PLANT DAILY PROCESS SUMMARY
[6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29
TOTAL RAW INFLUENT FLOW (MGD) | [5 empty] | 64.329 | 57.786 | 51.88 | 47.76 | 45.168 | 43.6 | 41.587 | 39.429 | 38.556 | 37.403 | 37.151 | 36.39 | 35.781 | 35.354 | 34.636 | 35.04 | 35.135 | 33.933 | 35.089 | 35.694 | 35.699 | 35.057 | 34.886 | 34.651 | 35.845 | 38.83 | 36.605 | 35.216 | 34.979
TOTAL EFFLUENT FLOW (MGD) | [5 empty] | 61.984 | 56.028 | 50.404 | 46.552 | 43.397 | 41.688 | 39.508 | 37.409 | 36.934 | 36.412 | 35.612 | 35.115 | 35.419 | 34.768 | 33.648 | 34.446 | 34.9 | 33.292 | 33.685 | 34.079 | 34.634 | 33.622 | 33.877 | 33.322 | 34.645 | 37.552 | 35.611 | 33.794 | 33.219
MAXIMUM HOURLY RAW INFLUENT FLOW (MGD) | [5 empty] | 2.896 | 2.643 | 2.402 | 2.243 | 2.168 | 2.066 | 2.034 | 1.951 | 1.958 | 1.831 | 1.807 | 1.743 | 1.808 | 1.822 | 1.706 | 1.783 | 1.804 | 1.811 | 1.896 | 1.789 | 1.914 | 1.804 | 1.72 | 1.704 | 1.787 | 1.85 | 1.807 | 1.742 | 1.733
MAXIMUM INSTANANEOUS PEAK RAW INFUENT FLOW (MGD) | [5 empty] | 77.282 | 71.034 | 65.588 | 61.935 | 61.006 | 60.653 | 58.442 | 56.84 | 56.327 | 53.571 | 53.828 | 52.482 | 51.969 | 53.283 | 51.072 | 52.963 | 57.16 | 50.88 | 54.308 | 51.873 | 55.366 | 52.706 | 51.296 | 52.995 | 51.296 | 51.905 | 52.77 | 51.36 | 51.713
MINIMUM INSTANANEOUS PEAK RAW INFUENT FLOW (MGD) | [5 empty] | 43.992 | 42.069 | 30.407 | 26.145 | 21.242 | 20.056 | 18.454 | 17.942 | 13.681 | 15.027 | 13.938 | 13.777 | 16.501 | 13.489 | 14.711 | 14.162 | 12.111 | 12.464 | 8.875 | 12.079 | 13.393 | 13.136 | 11.855 | 14.034 | 14.034 | 17.91 | 14.771 | 16.085 | 14.546
TOTAL RETURN ACTIVATED SLUDGE FLOW (MGD) | [5 empty] | 10.589 | 10.118 | 10.207 | 10.618 | 11.487 | 11.516 | 10.964 | 8.528 | 10.993 | 10.836 | 11.753 | 11.517 | 10.831 | 11.894 | 11.422 | 9.404 | 9.988 | 8.355 | 9.195 | 11.512 | 11.417 | 11.097 | 11.832 | 11.52 | 11.737 | 11.064 | 9.55 | 8.487 | 10.032
TOTAL WASTE FLOW TO DEWATERING PROCESS (MG) | [5 empty] | 0.163 | 0.325 | 0.27 | 0.294 | 0.36 | 0.171 | 0 | 0.083 | 0.47 | 0.471 | 0.379 | 0.424 | 0.174 | 0 | 0.123 | 0.521 | 0.509 | 0.351 | 0.522 | 0.192 | 0 | 0.181 | 0.536 | 0.504 | 0.394 | 0.587 | 0.274 | 0 | 0.247
TOTAL DAILY RAINFALL | [5 empty] | 3.69 | 0 | 0 | 0 | 0 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85 | 0.18 | 0 | 0 | 0
RAW INFLUENT pH | [5 empty] | 7.2 | 7 | 7 | 7 | 7 | 7 | 7.1 | 7 | 6.8 | 7.1 | 7 | 7 | 7.1 | 7 | 7.1 | 7 | 7 | 7.1 | 7.2 | 7.1 | 7.1 | 7.2 | 7.1 | 7.1 | 7.1 | 7 | 7 | 7 | 7
RAW INFLUENT HYDROGEN SULFIDE (PPM) | [5 empty] | 3 | 2 | 3 | 4 | 4 | 0 | 0 | 5 | 4 | 3 | 5 | 6 | 0 | 0 | 5 | 5 | 5 | 4 | 6 | 6 | 5 | 5 | 6 | 5 | 6 | 7 | 5 | 5 | 6
RAW INFLUENT TEMPERATURE (F ) | [5 empty] | 75 | 75.2 | 76 | 76.2 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 78 | 78 | 78 | 78 | 78 | 77 | 77 | 77 | 77 | 77 | 77 | 76 | 78 | 76 | 77 | 77 | 77
TOTAL DAILY KILOWATTS (FPL POWER CONSUMPTION) | [5 empty] | 31251 | 31427 | 31403 | 31462 | 31579 | 31336 | 31172 | 31804 | 31475 | 31287 | 31176 | 30913 | 30678 | 31005 | 30909 | 31401 | 30573 | 31501 | 31518 | 31189 | 31260 | 31884 | 31679 | 30374 | 29256 | 28249 | 28700 | 28962 | 28486
GTL PLANT DAILY PROCESS SUMMARY
(CONTINUED)
[6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29
FINAL EFFLUENT FREE CHLORINE RESIDUAL (PPM) | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1
FINAL EFFLUENT TOTAL CHLORINE RESIDUAL (PPM) | [5 empty] | 0.4 | 0.3 | 0.4 | 0.4 | 0.9 | 0.6 | 0.6 | 0.6 | 0.8 | 0.6 | 0.4 | 0.6 | 0.6 | 7 | 0.9 | 0.6 | 0.3 | 0.5 | 0.4 | 0.6 | 0.5 | 0.6 | 0.4 | 0.6 | 0.5 | 0.6 | 0.7 | 0.7 | 0.8
FINAL EFFLUENT pH (daily average) | [5 empty] | 6.6 | 6.7 | 6.6 | 6.7 | 6.6 | 6.8 | 6.6 | 6.6 | 6.6 | 6.5 | 6.4 | 6.5 | 6.4 | 6.3 | 6.3 | 6.6 | 6.6 | 6.6 | 6.5 | 6.5 | 6.4 | 6.4 | 6.4 | 6.4 | 6.5 | 6.5 | 6.4 | 6.4 | 6.4
FINAL EFFLUENT pH (daily minimum) | [5 empty] | 6.5 | 6.6 | 6.5 | 6.6 | 6.5 | 6.4 | 6.4 | 6.4 | 6.4 | 6.3 | 6.5 | 6.3 | 6.3 | 6.2 | 6.2 | 6.4 | 6.3 | 6.4 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.4 | 6.4 | 6.4 | 6.3 | 6.3
FINAL EFFLUENT pH (daily maximum) | [5 empty] | 6.7 | 6.8 | 6.8 | 6.7 | 6.8 | 7 | 6.8 | 6.7 | 6.7 | 6.7 | 6.8 | 6.8 | 6.6 | 6.3 | 6.5 | 7 | 6.7 | 6.8 | 6.5 | 6.9 | 6.4 | 6.4 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.4 | 6.4
FINAL EFFLUENT TEMPARTURE (F ) | [5 empty] | 77 | 79 | 78 | 78 | 79 | 79 | 79 | 78 | 77 | 79 | 80 | 79 | 80 | 80 | 80 | 80 | 80 | 79 | 78 | 79 | 79 | 80 | 80 | 80 | 80 | 80 | 79 | 79 | 79
AVERAGE CLARIFIER BLANKET DEPTH (INCHES) | [5 empty] | 51 | 50 | 52 | 48 | 43 | 48 | 56 | 45 | 37 | 49 | 56 | 50 | 63 | 67 | 58 | 52 | 53 | 52 | 53 | 52 | 64 | 52 | 51 | 47 | 51 | 51 | 51 | 58 | 49
FINAL EFFLUENT SAMPLE TEMPARTURE (C ) | [5 empty] | 4 | 4 | 4 | 8 | 5 | 0 | 0 | 4 | 2 | 3 | 5 | 4 | 0 | 0 | 2 | 2 | 3 | 3 | 3 | 0 | 3 | 1 | 2 | 3 | 4 | 4 | 1 | 1 | 2
TOTAL RETURN ACTIVATED SLUDGE FLOW TO REACTOR ONE (MGD) | [5 empty] | 3.198 | 2.69 | 3.125 | 3.21 | 4.003 | 4.051 | 3.617 | 1.097 | 3.838 | 3.532 | 4.667 | 4.671 | 3.823 | 4.451 | 4.017 | 2.266 | 2.806 | 1.27 | 1.979 | 4.16 | 3.905 | 3.508 | 4.578 | 4.727 | 4.72 | 4.082 | 2.825 | 2.04 | 4.181
TOTAL RETURN ACTIVATED SLUDGE FLOW TO REACTOR TWO (MGD) | [5 empty] | 7.391 | 7.428 | 7.081 | 7.408 | 7.184 | 7.465 | 7.347 | 7.431 | 7.155 | 7.304 | 7.086 | 6.845 | 7.008 | 7.443 | 7.405 | 7.138 | 7.182 | 7.085 | 7.216 | 7.352 | 7.512 | 7.589 | 7.253 | 6.793 | 7.017 | 6.982 | 6.725 | 6.447 | 5.851
GTL PLANT DAILY PROCESS SUMMARY
CONTINUED
[6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29
TOTAL DAILY TRUCKING LOAD OF DEWATERED SLUDGE REMOVED | [5 empty] | 1 | 6 | 3 | 4 | 4 | 4 | 1 | 1 | 4 | 6 | 5 | 6 | 5 | 0 | 1 | 6 | 6 | 4 | 6 | 6 | 1 | 0 | 6 | 6 | 4 | 7 | 7 | 0 | 0
TOTAL DAILY HYDROGEN PEROXIDE CONSUMED (LBS) | [5 empty] | 758 | 200 | 359 | 110 | 170 | 210 | 519 | 140 | 1657 | 1458 | 1367 | 4698 | 1407 | 1517 | 1587 | 1448 | 1627 | 1757 | 1188 | 1716 | 1637 | 1557 | 1647 | 1597 | 1148 | 1148 | 1527 | 978 | 1278
TOTAL DAILY CHLORINE CONSUMED (LBS) | [5 empty] | 1360 | 1240 | 1260 | 980 | 1360 | 1000 | 1400 | 1240 | 1160 | 920 | 1040 | 1200 | 0 | 0 | 1280 | 1200 | 620 | 1240 | 1300 | 1220 | 1080 | 1020 | 1020 | 1140 | 1100 | 1220 | 1600 | 1380 | 1220
TOTAL DAILY POLYMER CONSUMED (GALS) | [5 empty] | 28 | 0 | 66 | 30 | 56 | 32 | 0 | 0 | 41 | 81 | 68 | 103 | 38 | 9 | 10 | 58 | 64 | 59 | 75 | 0 | 0 | 45 | 143 | 121 | 54 | 117 | 66 | 0 | 36
TOTAL TONS OF LIME DELIVERED DAILY | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTAL DAILY GASIOUS OXYGEN PRODUCED (TONS) | [5 empty] | 17.1 | 17.9 | 18.4 | 20 | 17.7 | 22 | 21.9 | 18.8 | 20.3 | 20.9 | 25.3 | 21.8 | 27.6 | 24.8 | 26 | 21.6 | 25.4 | 21.1 | 24.6 | 22.8 | 23.3 | 25.4 | 22.2 | 24.8 | 25.9 | 25.5 | 28.2 | 29.8 | 27.8
AVERAGE PERCENT OXYGEN PRODUCT PURITY | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 97 | 100 | 100 | 100 | 100 | 100 | 97 | 99 | 100 | 99 | 100 | 100 | 100 | 100 | 99 | 100 | 99 | 98 | 99 | 99 | 97 | 94 | 100
TOTAL DAILY LIQUID OXYGEN IN STORAGE (TONS) | [5 empty] | 183 | 184 | 185 | 185 | 184 | 185 | 186 | 186 | 186 | 187 | 187 | 188 | 188 | 188 | 189 | 186 | 187 | 187 | 189 | 189 | 191 | 191 | 191 | 191 | 191 | 191 | 190 | 192 | 193
MONITORING WELL PRESSURE DATA
MONITORING WELL ONE UPPER/LOWER LEVEL
| MW-1 |  | UPPER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29
MINIMUM | [5 empty] | 48.28 | 45.71 | 46.04 | 48.23 | 48.25 | 48.28 | 48.38 | 48.22 | 46.46 | 46.8 | 48.36 | 48.36 | 48.34 | 48.46 | 48.37 | 46.88 | 47.16 | 48.14 | 48.13 | 48.27 | 48.35 | 48.31 | 46.09 | 46.47 | 48.51 | 48.63 | 48.43 | 48.36 | 48.31
MAXIMUM | [5 empty] | 48.61 | 48.55 | 48.76 | 48.51 | 48.54 | 48.66 | 48.64 | 48.44 | 48.47 | 48.58 | 48.58 | 48.61 | 48.59 | 48.7 | 48.76 | 48.62 | 48.56 | 48.46 | 48.55 | 48.66 | 48.65 | 48.58 | 48.56 | 48.74 | 48.83 | 48.86 | 48.77 | 48.58 | 48.55
AVERAGE | [5 empty] | 48.5 | 46.86 | 47.69 | 48.44 | 48.45 | 48.46 | 48.51 | 48.38 | 47.44 | 47.95 | 48.48 | 48.51 | 48.51 | 48.52 | 48.57 | 47.69 | 48.01 | 48.31 | 48.42 | 48.47 | 48.49 | 48.48 | 47.37 | 47.84 | 48.67 | 48.72 | 48.57 | 48.52 | 48.47
| MW-1 |  | LOWER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29
MINIMUM | [5 empty] | 41.59 | 33.99 | 33.98 | 41.36 | 41.44 | 41.47 | 41.51 | 41.42 | 36.72 | 36.71 | 41.52 | 41.54 | 41.56 | 41.62 | 41.62 | 36.4 | 36.22 | 41.27 | 41.33 | 41.55 | 41.65 | 41.63 | 29.21 | 29.82 | 41.57 | 41.71 | 41.56 | 41.48 | 41.56
MAXIMUM | [5 empty] | 42.07 | 41.69 | 41.62 | 41.66 | 41.66 | 41.75 | 41.87 | 41.64 | 41.77 | 41.69 | 41.77 | 41.8 | 41.87 | 41.93 | 41.96 | 41.7 | 41.48 | 41.55 | 41.69 | 41.83 | 42.12 | 42.03 | 41.93 | 41.61 | 41.88 | 42.04 | 41.85 | 41.78 | 41.74
AVERAGE | [5 empty] | 41.76 | 36.86 | 38.89 | 41.52 | 41.5 | 41.57 | 41.64 | 41.48 | 39.01 | 39.88 | 41.57 | 41.6 | 41.65 | 41.73 | 41.79 | 38.52 | 39.59 | 41.44 | 41.5 | 41.61 | 41.85 | 41.73 | 35.59 | 37.48 | 41.64 | 41.83 | 41.68 | 41.59 | 41.59
MONITORING WELL TWO UPPER/LOWER LEVEL
| MW-2 |  | UPPER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29
MINIMUM | [5 empty] | 48.28 | 45.71 | 46.04 | 48.23 | 48.25 | 48.28 | 48.38 | 48.22 | 46.46 | 46.8 | 48.36 | 48.36 | 48.34 | 48.46 | 48.37 | 46.88 | 47.16 | 48.14 | 48.13 | 48.27 | 48.35 | 48.31 | 46.09 | 46.47 | 48.51 | 48.63 | 48.43 | 48.36 | 48.31
MAXIMUM | [5 empty] | 48.61 | 48.55 | 48.76 | 48.51 | 48.54 | 48.66 | 48.64 | 48.44 | 48.47 | 48.58 | 48.58 | 48.61 | 48.59 | 48.7 | 48.76 | 48.62 | 48.56 | 48.46 | 48.55 | 48.66 | 48.65 | 48.58 | 48.56 | 48.74 | 48.83 | 48.86 | 48.77 | 48.58 | 48.55
AVERAGE | [5 empty] | 48.5 | 46.86 | 47.69 | 48.44 | 48.45 | 48.46 | 48.51 | 48.38 | 47.44 | 47.95 | 48.48 | 48.51 | 48.51 | 48.52 | 48.57 | 47.69 | 48.01 | 48.31 | 48.42 | 48.47 | 48.49 | 48.48 | 47.37 | 47.84 | 48.67 | 48.72 | 48.57 | 48.52 | 48.47
| MW-2 |  | LOWER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29
MINIMUM | [5 empty] | 41.59 | 33.99 | 33.98 | 41.36 | 41.44 | 41.47 | 41.51 | 41.42 | 36.72 | 36.71 | 41.52 | 41.54 | 41.56 | 41.62 | 41.62 | 36.4 | 36.22 | 41.27 | 41.33 | 41.55 | 41.65 | 41.63 | 29.21 | 29.82 | 41.57 | 41.71 | 41.56 | 41.48 | 41.56
MAXIMUM | [5 empty] | 42.07 | 41.69 | 41.62 | 41.66 | 41.66 | 41.75 | 41.87 | 41.64 | 41.77 | 41.69 | 41.77 | 41.8 | 41.87 | 41.93 | 41.96 | 41.7 | 41.48 | 41.55 | 41.69 | 41.83 | 42.12 | 42.03 | 41.93 | 41.61 | 41.88 | 42.04 | 41.85 | 41.78 | 41.74
AVERAGE | [5 empty] | 41.76 | 36.86 | 38.89 | 41.52 | 41.5 | 41.57 | 41.64 | 41.48 | 39.01 | 39.88 | 41.57 | 41.6 | 41.65 | 41.73 | 41.79 | 38.52 | 39.59 | 41.44 | 41.5 | 41.61 | 41.85 | 41.73 | 35.59 | 37.48 | 41.64 | 41.83 | 41.68 | 41.59 | 41.59
MONITORING WELL THREE UPPER/LOWER LEVEL
| MW-3 |  | UPPER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29
MINIMUM | [5 empty] | 31.49 | 17.64 | 17.63 | 30.98 | 31.17 | 31.25 | 31.39 | 31.21 | 20.87 | 20.69 | 31.33 | 31.51 | 31.55 | 31.66 | 31.61 | 20.79 | 20.58 | 31.1 | 31.24 | 31.49 | 31.61 | 31.63 | 19.44 | 19.26 | 31.49 | 31.78 | 31.58 | 31.56 | 31.52
MAXIMUM | [5 empty] | 31.87 | 31.79 | 31.1 | 31.32 | 31.44 | 31.6 | 31.6 | 31.43 | 31.46 | 31.43 | 31.61 | 31.72 | 31.76 | 31.95 | 31.97 | 31.78 | 31.3 | 31.48 | 31.67 | 31.85 | 31.87 | 31.83 | 31.83 | 31.62 | 31.85 | 31.95 | 31.88 | 31.75 | 31.7
AVERAGE | [5 empty] | 31.72 | 22.77 | 26.34 | 31.23 | 31.33 | 31.44 | 31.48 | 31.34 | 25.64 | 27.55 | 31.46 | 31.6 | 31.63 | 31.82 | 31.85 | 24.88 | 27.31 | 31.31 | 31.45 | 31.75 | 31.78 | 31.75 | 25.5 | 27.24 | 31.68 | 31.91 | 31.72 | 31.62 | 31.6
| MW-3 |  | LOWER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29
MINIMUM | [5 empty] | 45.49 | 37.42 | 37.42 | 45.06 | 45.25 | 45.35 | 45.46 | 45.38 | 39.64 | 39.61 | 45.25 | 45.4 | 45.43 | 45.51 | 45.59 | 37.94 | 37.94 | 45.05 | 45.18 | 45.42 | 45.58 | 45.6 | 37.38 | 37.36 | 45.37 | 45.64 | 45.51 | 45.52 | 45.53
MAXIMUM | [5 empty] | 45.7 | 45.62 | 45.15 | 45.32 | 45.43 | 45.59 | 45.6 | 45.46 | 45.51 | 45.25 | 45.41 | 45.52 | 45.57 | 45.75 | 45.83 | 45.7 | 45.14 | 45.31 | 45.48 | 45.66 | 45.7 | 45.66 | 45.69 | 45.45 | 45.67 | 45.76 | 45.7 | 45.65 | 45.64
AVERAGE | [5 empty] | 45.55 | 40.43 | 42.4 | 45.32 | 45.38 | 45.47 | 45.5 | 45.47 | 42.28 | 43.12 | 45.37 | 45.49 | 45.5 | 45.54 | 45.74 | 40.83 | 42.41 | 45.2 | 45.36 | 45.49 | 45.59 | 45.59 | 41.52 | 42.64 | 45.51 | 45.66 | 45.57 | 45.52 | 45.53
MONITORING WELL RMW-1 UPPER/LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29
[5 empty] | JULIAN DATE | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60
| RMW-1 |  | UPPER LEVEL
MINIMUM | [5 empty] | 44.65 | 36.24 | 26.22 | 43.79 | 43.97 | 44.05 | 44.13 | 44.06 | 44.07 | 44.19 | 0.25 | 44.31 | 44.3 | 44.36 | 44.38 | 44.25 | 44.25 | 44.24 | 44.25 | 44.36 | 44.45 | 44.41 | 44.42 | 44.5 | 44.66 | -6999 | 44.52 | 44.45 | 44.43
MAXIMUM | [5 empty] | 44.82 | 44.72 | 43.8 | 44.02 | 44.14 | 44.29 | 44.3 | 44.14 | 44.22 | 44.33 | 44.36 | 44.39 | 44.37 | 44.5 | 44.55 | 44.42 | 44.36 | 44.36 | 44.43 | 44.53 | 44.56 | 44.49 | 44.55 | 44.69 | 44.74 | 62.89 | 44.68 | 44.54 | 44.51
AVERAGE | [5 empty] | 44.75 | 39.55 | 41.13 | 43.93 | 44.06 | 44.2 | 44.24 | 44.1 | 44.15 | 44.25 | 43.78 | 44.36 | 44.34 | 44.44 | 44.49 | 44.34 | 44.31 | 44.29 | 44.35 | 44.46 | 44.5 | 44.46 | 44.48 | 44.6 | 44.7 | -6999 | 44.61 | 44.5 | 44.47
| RMW-1 |  | LOWER LEVEL
MINIMUM | [5 empty] | 22.36 | 20.07 | 19.9 | 22.43 | 22.64 | 22.75 | 22.84 | 22.73 | 22.78 | 22.89 | 0.25 | 22.97 | 22.97 | 23 | 23.02 | 22.89 | 22.89 | 22.9 | 22.9 | 23.03 | 23.12 | 23.07 | 23.05 | 23.18 | 23.33 | -6999 | 23.12 | 23.05 | 23.02
MAXIMUM | [5 empty] | 22.55 | 22.44 | 22.44 | 22.67 | 22.81 | 22.96 | 22.98 | 22.84 | 22.92 | 23.01 | 23.08 | 23.1 | 23.07 | 23.21 | 23.25 | 23.08 | 23.04 | 23 | 23.07 | 23.18 | 23.17 | 23.15 | 23.18 | 23.36 | 23.43 | 62.97 | 23.38 | 23.18 | 23.13
AVERAGE | [5 empty] | 22.47 | 21.24 | 21.81 | 22.58 | 22.73 | 22.88 | 22.93 | 22.77 | 22.83 | 22.94 | 22.73 | 23.03 | 23.02 | 23.12 | 23.17 | 23 | 22.97 | 22.94 | 23 | 23.11 | 23.14 | 23.1 | 23.12 | 23.26 | 23.38 | -6999 | 23.27 | 23.13 | 23.08
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
| INJECTION WELL ONE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 16.78 | 13.5 | 12.13 | 11.69 | 13.93 | 14.05 | 14.37 | 13.15 | 13.26 | 12.66 | 12.58 | 13.26 | 11.81 | 14.41 | 9.6 | 12.8 | 12.64 | 12.76 | 15.1 | 12.22 | 16.02 | 13.43 | 15.37 | 13.5 | 12.6 | 11.96 | 12.54 | 15.59 | 11.85
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 11.23 | 8.93 | 7.44 | 0 | 0 | 6.79 | 6.87 | 5.99 | 5.98 | 5.28 | 4.76 | 6.88 | 5.54 | 0.01 | 0 | 0.01 | 0 | 0 | 5.23 | 0 | 6.61 | 4.82 | 0.01 | 5.85 | ER | 0 | 5.57 | 0 | 0
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 13.46 | 11.39 | 10.22 | 6.65 | 7.34 | 10.95 | 10.38 | 9.82 | 9.78 | 9.54 | 9.39 | 9.42 | 8.88 | 8.98 | 4.66 | 8.4 | 7.69 | 7.7 | 9.18 | 8.19 | 11.74 | 9.43 | 9.65 | 9.17 | ER | 6.31 | 9.34 | 9.48 | 5.61
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 76.1 | 62.61 | 57.02 | 55.98 | 63.13 | 64.2 | 65.28 | 60.55 | 61.45 | 60.16 | 58.56 | 62.84 | 56.9 | 65.62 | 50.06 | 59.19 | 58.94 | 59.18 | 69.08 | 58.67 | 70.8 | 61.45 | 69.1 | 62.79 | 59.21 | 58.37 | 59.82 | 69.53 | 56.73
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 54.5 | 48.07 | 44.75 | 35.23 | 34.83 | 42.91 | 43.11 | 41.18 | 41.32 | 40.33 | 40.4 | 43.59 | 40.98 | 35.46 | 35.03 | 35.14 | 34.16 | 34.13 | 39.79 | 34.27 | 42.02 | 38.82 | 35.26 | 41.1 | 34.71 | 34.94 | 40.56 | 34.94 | 34.59
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 62.51 | 55.17 | 51.61 | 45.32 | 48.63 | 54.1 | 52.41 | 50.59 | 50.72 | 50.09 | 49.81 | 49.71 | 48.34 | 48.83 | 41.38 | 47.13 | 46.47 | 46.39 | 48.56 | 47.39 | 56.45 | 49.14 | 50.63 | 48.71 | 47.4 | 45.76 | 49.67 | 50.19 | 44.14
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
| INJECTION WELL TWO |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 17.11 | 13.68 | 12.26 | 13.82 | 14.34 | 14.25 | 14.54 | 13.37 | 13.62 | 12.93 | 12.49 | 13.54 | 12.09 | 14.8 | 13.57 | 12.57 | 12.65 | 13.01 | 15.45 | 12.49 | 16.38 | 13.73 | 15.58 | 13.8 | 12.85 | 18.79 | 12.85 | 15.84 | 16.57
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 11.37 | 9.12 | 7.53 | 5.63 | 7.6 | 6.84 | 6.94 | 6.03 | 0.02 | 5.18 | 5.05 | 6.99 | 5.56 | 5.62 | 0.02 | 0.02 | 0.02 | 5.06 | 5.2 | 4.58 | 6.83 | 4.78 | 0.02 | 5.87 | 6.18 | 7.42 | 5.45 | 5.5 | 7.19
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 13.62 | 11.57 | 10.39 | 10.36 | 11.57 | 11.14 | 10.54 | 9.97 | 9.52 | 9.69 | 9.52 | 9.57 | 9.01 | 9.15 | 7.93 | 2.12 | 3.91 | 9.25 | 9.38 | 9.36 | 12.09 | 9.66 | 8.45 | 9.34 | 9.74 | 11.24 | 9.45 | 9.82 | 10.03
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 74.6 | 61.53 | 56.11 | 60.25 | 62.02 | 63.04 | 64.15 | 59.41 | 60.23 | 59.04 | 57.73 | 61.63 | 55.79 | 59.19 | 60.48 | 56.73 | 57.77 | 58.02 | 67.78 | 57.52 | 69.58 | 60.49 | 67.93 | 61.62 | 58.12 | 79.4 | 58.62 | 68.14 | 69.31
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 53.46 | 47.14 | 43.87 | 40.55 | 43.07 | 42.04 | 42.26 | 40.32 | 35.42 | 39.52 | 39.63 | 42.76 | 40.18 | 40.18 | 35.42 | 34.96 | 34.21 | 38.6 | 38.95 | 38.16 | 41.17 | 38.04 | 34.86 | 40.29 | 40.76 | 43.84 | 39.74 | 40.08 | 41.89
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 61.36 | 54.16 | 50.68 | 50.71 | 53.78 | 53.09 | 51.42 | 49.56 | 49 | 49.17 | 48.88 | 48.78 | 47.45 | 47.97 | 45.13 | 38.74 | 40.45 | 47.22 | 47.6 | 47.66 | 55.37 | 48.21 | 48.09 | 47.8 | 49.1 | 53.53 | 48.67 | 49.56 | 49.82
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
| INJECTION WELL THREE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 15.03 | 11.58 | 10.29 | 11.42 | 12.37 | 12.44 | 12.67 | 11.66 | 11.94 | 11.34 | 11.03 | 11.92 | 10.44 | 9.87 | 11.44 | 11 | 11.18 | 11.46 | 13.7 | 10.94 | 8.94 | 12.08 | 15.38 | 12.19 | 11.38 | 16.11 | 11.36 | 14.05 | 14.19
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 9.62 | 7.71 | 6.41 | 4.74 | 6.22 | 5.96 | 6.06 | 5.25 | 5.3 | 4.57 | ER | 6.14 | ER | ER | 4.75 | 3.66 | ER | 4.46 | ER | 4.01 | ER | ER | ER | 5.26 | ER | 6.34 | 4.84 | 4.88 | 6.12
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 11.7 | 9.81 | 8.76 | 8.66 | 9.9 | 9.73 | 9.23 | 8.73 | 8.73 | 8.5 | 8.01 | 8.4 | 6.14 | 5.1 | 7.02 | 7.55 | 7.12 | 8.06 | 6.89 | 8.18 | 0.23 | 5.99 | 8.54 | 8.27 | ER | 9.79 | 8.35 | 8.7 | 8.75
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 76.6 | 62.9 | 57.25 | 61.57 | 63.54 | 64.62 | 65.74 | 60.95 | 61.81 | 60.56 | 58.9 | 63.21 | 57.14 | 54.84 | 61.87 | 59.33 | 59.3 | 59.62 | 69.6 | 59.01 | 50.89 | 61.83 | 75.9 | 63.14 | 59.55 | 81.5 | 60.19 | 70.1 | 71
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 54.69 | 48.25 | 44.93 | 41.46 | 44.03 | 43.06 | 43.29 | 41.33 | 41.46 | 40.46 | 35.51 | 43.77 | 35.71 | 36.03 | 41.9 | 38.83 | 36.57 | 39.53 | 34.79 | 39.07 | 35.06 | 34.64 | 36.14 | 41.25 | 41.71 | 44.77 | 40.71 | 41.06 | 42.87
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 62.82 | 55.39 | 51.81 | 51.82 | 55.04 | 54.39 | 52.67 | 50.84 | 50.94 | 50.35 | 49.49 | 49.91 | 46.22 | 44.49 | 46.61 | 48 | 47.6 | 48.29 | 46.94 | 48.81 | 36.21 | 45.45 | 50.58 | 48.98 | 50.27 | 54.84 | 49.9 | 50.85 | 51.02
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
FUTURE
| INJECTION WELL FOUR |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 18.94 | 16.02 | 14.44 | 15.88 | 16.39 | 0.15 | 0.15 | 0.13 | 0.16 | 0.16 | 15.06 | 13.58 | 14.83 | 18.14 | 16.21 | 15.15 | 14.96 | 5.6 | 0.14 | 0.14 | 0.15 | 0.15 | 4.96 | 0.14 | 0.38 | 11.19 | 0.13 | 0.14 | 0.14
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 0.12 | 10.9 | 9.3 | 7.37 | 0.12 | 0.12 | 0.11 | 0.11 | 0.12 | 0.12 | 0.13 | 0.13 | 7.73 | 7.67 | 7.35 | 0.12 | 0.12 | 0.11 | 0.11 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.11 | 0.1 | 0.12
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 11.99 | 13.65 | 12.38 | 12.32 | 4.84 | 0.13 | 0.13 | 0.12 | 0.13 | 0.13 | 0.31 | 4.94 | 11.43 | 11.6 | 10.21 | 8.9 | 8.28 | 0.19 | 0.12 | 0.12 | 0.13 | 0.13 | 0.16 | 0.13 | 0.13 | 0.57 | 0.12 | 0.12 | 0.12
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 74.5 | 62.5 | 57.17 | 61.07 | 62.78 | 37.6 | 37.78 | 37.2 | 37.15 | 37.15 | 62.78 | 58.43 | 56.99 | 60.16 | 61.57 | 59.24 | 58.13 | 43.13 | 37.96 | 37.13 | 36.54 | 37.47 | 42.61 | 37.47 | 37.38 | 49.86 | 37.32 | 36.99 | 37.71
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 35.7 | 48.47 | 45.27 | 41.93 | 36.39 | 35.76 | 35.77 | 35.43 | 35.33 | 35.23 | 35.3 | 35.31 | 41.61 | 41.59 | 42.37 | 36.44 | 35.83 | 35.5 | 34.44 | 35.1 | 34.94 | 34.81 | 35.17 | 34.96 | 35.58 | 35.94 | 35.72 | 35.11 | 35.63
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 55.58 | 55.35 | 51.91 | 51.83 | 42.59 | 36.78 | 36.63 | 36.3 | 36.3 | 36.33 | 36.71 | 41.58 | 48.75 | 49.25 | 46.92 | 45.98 | 45.58 | 36.26 | 36.02 | 36.13 | 35.82 | 36.05 | 36.22 | 36.18 | 36.49 | 37.41 | 36.5 | 36.05 | 36.37
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
| INJECTION WELL FIVE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 14.8 | 11.45 | 10.24 | 11.2 | 12.23 | 12.38 | 12.68 | 11.64 | 11.85 | 11.31 | 11.87 | 11.81 | ER | ER | 8.06 | 10.65 | 11.02 | 11.3 | 13.39 | 10.81 | 14.09 | 11.88 | 14.84 | 11.96 | 11.16 | 15.73 | 11.18 | 10.98 | 13.88
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | ER | 7.71 | 6.44 | 4.96 | 4.54 | 6.26 | 6.38 | 5.64 | 5.62 | 4.96 | 0.28 | ER | ER | ER | ER | 3.94 | 4.39 | 4.79 | ER | 4.4 | 6.14 | 4.54 | ER | ER | 5.46 | 6.34 | 5.15 | ER | 6.28
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 11.07 | 9.71 | 8.74 | 8.63 | 9.83 | 9.78 | 9.3 | 8.83 | 8.82 | 8.6 | 8.42 | 2.88 | ER | ER | 3.87 | 7.51 | 7.88 | 8.15 | 8.17 | 8.23 | 10.49 | 8.49 | 7.08 | 6.49 | 8.55 | 9.7 | 8.38 | 5.72 | 8.74
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 76 | 62.59 | 57.05 | 61.24 | 62.97 | 63.99 | 65.08 | 60.44 | 61.33 | 60.1 | 64.55 | 62.72 | 36.31 | 36.05 | 49.42 | 59.01 | 58.91 | 59.19 | 69.14 | 58.62 | 70.6 | 61.27 | 75.2 | 62.59 | 59.04 | 80.8 | 59.75 | 57.7 | 70.4
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 34.14 | 48.2 | 25.67 | 41.25 | 42.48 | 42.79 | 43.01 | 41.16 | 41.17 | 40.22 | 35.08 | 34.02 | 34.68 | 34.72 | 34.94 | 38.73 | 39.48 | 39.41 | 33.74 | 38.87 | 41.98 | 38.82 | 33.88 | 33.5 | 41.46 | 44.43 | 40.52 | 33.59 | 42.56
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 61.45 | 55.18 | 51.35 | 51.5 | 54.58 | 53.96 | 52.27 | 50.49 | 50.52 | 49.95 | 49.55 | 40.47 | 35.53 | 35.43 | 41.11 | 47.72 | 48.5 | 48.12 | 48.29 | 48.49 | 56.34 | 48.99 | 46.83 | 45.61 | 49.93 | 54.38 | 49.61 | 44.66 | 50.62
GTL DAILY LABORATORY ANALYSIS REPORT DATA
| RAW INFLUENT DATA |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29
RAW TOTAL SUSPENDED SOLIDS | [5 empty] | 30 | 84 | 108 | 126 | 84 | 60 | 62 | 80 | 102 | 230 | 166 | 68 | 124 | 124 | 122 | 144 | 84 | 100 | 120 | 102 | 136 | 96 | 124 | 104 | 140 | 76 | 134 | 144 | 100
RAW FIXED SUSPENDED SOLIDS | [5 empty] | 4 | 8 | 40 | 18 | 12 | 6 | 8 | 12 | 14 | 26 | 22 | 12 | 10 | 8 | 10 | 22 | 16 | 14 | 22 | 4 | 8 | 10 | 14 | 20 | 24 | 10 | 14 | 8 | 8
RAW ALKILINITY | [5 empty] | 206 | 184 | 188 | 194 | 190 | 184 | 200 | 194 | 198 | 212 | 204 | 212 | 210 | 210 | 190 | 212 | 208 | 210 | 206 | 194 | 204 | 204 | 216 | 218 | 216 | 208 | 202 | 210 | 204
RAW CHLORIDES | [5 empty] | 650 | 520 | 490 | 470 | 470 | 460 | 470 | 510 | 480 | 540 | 540 | 600 | 580 | 570 | 620 | 610 | 630 | 620 | 540 | 620 | 610 | 550 | 620 | 640 | 640 | 640 | 650 | 640 | 640
RAW COD | [5 empty] | 224 |  |  | 260 | 260 | 342 | 312 | 299 |  |  | 331 | 308 | 244 | 365 | 255 |  |  | 369 | 343 | 351 | 381 | 347 |  |  | 640 | 281 | 344 | 298 | 362
RAW CBOD | [5 empty] | 30 | 60 | 49 | 69 | 84 | 82 | 100.2 | 91 | 84 | 115 | 90.5 | 106 | 78 | 89 | 103 | 134 | 83 | 93 | 91 | 86 | 98 | 78 | 82 | 105 | 82 | 42 | 76 | 99 | 71
RAW SUFATES
| EFFLUENT DATA |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29
EFFLUENT TOTAL DISSOLVED SOLIDS | [5 empty] | 1030 | 943 | 891 | 970 | 1046 | 1009 | 1010 | 1052 | 1078 | 1127 | 877 | 1140 | 1109 | 1068 | 1171 | 1129 | 1169 | 1231 | 1223 | 1332 | 1360 | 1335 | 1323 | 1345 | 1335 | 1263 | 1270 | 1158 | 1266
EFFLUENT TOTAL SUSPENDED SOLIDS | [5 empty] | 22 | 44 | 29 | 15 | 14 | 30 | 19 | 14 | 20 | 18 | 19 | 13 | 17 | 13 | 9 | 18 | 21 | 24 | 15 | 15 | 12 | 14 | 15 | 18 | 12 | 22 | 15 | 20 | 12
EFFLUENT FIXED SUSPENDED SOLIDS | [5 empty] | 4 | 13 | 7 | 4 | 4 | 1 | 5 | 2 | 4 | 4 | 4 | 3 | 3 | 2 | 1 | 6 | 4 | 5 | 3 | 1 | 2 | 2 | 1 | 6 | 2 | 5 | 2 | 4 | 1
EFFLUENT ALKILINITY | [5 empty] | 184 | 188 | 184 | 188 | 188 | 192 | 194 | 196 | 192 | 190 | 190 | 184 | 180 | 182 | 184 | 192 | 192 | 192 | 190 | 182 | 196 | 194 | 192 | 198 | 192 | 196 | 186 | 190 | 198
EFFLUENT TURBIDITY | [5 empty] | 14 | 21.7 | 10.5 | 7.82 | 7.75 | 6.46 | 8.14 | 9.94 | 8.62 | 8.66 | 11.5 | 5.62 | 6.12 | 7.17 | 7.58 | 7.45 | 8.6 | 14.7 | 7.87 | 10.4 | 6.71 | 6.63 | 7.46 | 5.7 | 7.54 | 13.3 | 12.4 | 7.3 | 5.33
EFFLUENT CHLORIDES | [5 empty] | 630 | 440 | 480 | 480 | 480 | 480 | 490 | 500 | 470 | 520 | 520 | 540 | 580 | 560 | 610 | 600 | 620 | 620 | 630 | 640 | 650 | 620 | 670 | 680 | 670 | 660 | 620 | 620 | 620
EFFLUENT CONDUCTIVITY | [5 empty] | 2060 | 1926 | 2090 | 2100 | 2180 | 2210 | 2260 | 2300 | 2320 | 2360 | 2390 | 2350 | 2360 | 2360 | 2500 | 2510 | 2630 | 2350 | 2410 | 2510 | 2580 | 2610 | 2460 | 2590 | 2520 | 2360 | 2290 | 2260 | 2350
EFFLUENT TOTAL BACTERIA COUNT | [5 empty] | TNCT | TNTC | TNTC | TNTC | 780 | 380 | TNTC | TNTC | 36 | 27 | 3400 | 27 | 232 | 116 | TNTC | TNTC | 6900 | 37500 | 46000 | 39500 | 420 | 25000 | 161 | 36 | 0 | 1083 | TNTC | 3600 | 600
EFFLUENT FECAL BACTERIA COUNT | [5 empty] | 6400 | 27 | 18 | 18 | 27 | 0 | TNTC | TNTC | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 143 | 9 | 9 | 89 | 152 | 0 | 9 | 18 | 0 | 0 | 18 | 0 | 0 | 0
EFFLUENT COD | [5 empty] | 64 |  |  |  | 53 | 50 | 57 | 52 | 41 |  |  | 49 | 46 | 52 | 54 | 41 |  | 42 | 55 | 58 | 58 | 54 |  |  | 61 | 63 | 52 | 43 | 48
EFFLUENT CBOD | [5 empty] | 25: 3; 26: 5; 27: 2; 28: 3; 29: 2
EFFLUENT SULFATES
LABORATORY NUTRIENT DATA
RAW INFLUENT | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29
RAW AMMONIA (PPM) | [5 empty] | 7.9 |  |  | 13.27 | 13.27 | 14.58 | 15.17 | 15.5 |  |  | 16.8 | 16.54 | 16.71 | 17.08 | 13.08 |  |  | 18.54 | 18.05 | 16.71 | 16.42 | 17.13 |  |  | 16.97 | 16.02 | 16.86 | 17.35 | 16.51
RAW NITRATES (PPM) | [5 empty] | 0.02 |  |  | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 |  |  | 0.02 | 0.02 | 0.058 | 0.081 | 0.02 |  |  | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 |  |  | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
RAW TOTAL KNEDJAHL NITRIGEN | [5 empty] | 0.05 |  |  | 18.04 | 18.04 | 18.95 | 19.73 | 20.51 |  |  | 21.87 | 21.87 | 22.04 | 21.84 | 19.98 |  |  | 22.99 | 22.65 | 21.69 | 21.64 | 22.24 |  |  | 21.74 | 21 | 21.07 | 22.2 | 21.02
RAW TOTAL PHOSPHORUS | [5 empty] | 2 |  |  | 2.23 | 2.23 | 2.44 | 2.5 | 2.62 |  |  | 2.79 | 2.77 | 2.81 | 2.79 | 1.83 |  |  | 2.91 | 3.02 | 2.68 | 2.86 | 2.78 |  |  | 2.68 | 2.69 | 2.9 | 2.94 | 2.72
EFFLUENT | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29
EFFLUENT AMMONIA (PPM) | [5 empty] | 7.3 |  |  | 9.56 | 9.56 | 11.35 | 8.47 | 11.04 |  |  | 11.62 | 13.68 | 13.29 | 13.09 | 11.67 |  |  | 14.34 | 13.87 | 13.9 | 12.37 | 12.27 |  |  | 13.75 | 12.32 | 13.22 | 11.57 | 12.77
EFFLUENT NITRATES (PPM) | [5 empty] | 0.3 |  |  | 0.115 | 0.115 | 0.077 | 0.861 | 0.213 |  |  | 0.19 | 0.202 | 0.165 | 0.144 | 0.87 |  |  | 0.163 | 0.242 | 0.09 | 0.108 | 0.318 |  |  | 0.28 | 0.275 | 0.133 | 0.206 | 0.198
EFFLUENT TOTAL KNEDJAHL NITRIGEN | [5 empty] | 12 |  |  | 13.06 | 13.06 | 14.95 | 13.89 | 14.44 |  |  | 15.18 | 17.21 | 17.06 | 16.9 | 16.64 |  |  | 18.12 | 18.11 | 17.65 | 16.15 | 15.94 |  |  | 17.23 | 15.6 | 16.42 | 15.03 | 16.33
EFFLUENT TOTAL PHOSPHORUS | [5 empty] | 1.1 |  |  | 0.892 | 0.892 | 0.9 | 0.835 | 0.957 |  |  | 0.879 | 0.85 | 1.39 | 1.43 | 0.836 |  |  | 1.59 | 0.963 | 0.927 | 0.874 | 0.851 |  |  | 0.834 | 0.867 | 0.865 | 1.02 | 0.739
LABORATORY REACTOR PROCESSES DATA
| REACTOR ONE TRAIN A |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29
MIXED-LIQUIR SUSPENDED SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
AVERAGE SETTLABLE SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
MIXED LIQUIR VOLITLE SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
| REACTOR ONE TRAIN B |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29
MIXED-LIQUIR SUSPENDED SOLIDS | [5 empty] | 2500 | 2390 | 3200 | 2460 | 1970 | 2030 | 2120 | 1980 | 3400 | 4300 | 2550 | 1600 | 2810 | 3010 | 3230 | 3600 | 3500 | 4430 | 3880 | 2090 | 2610 | 4070 | 3920 | 3740 | 3660 | 3800 | 2520 | 2940 | 3540
AVERAGE SETTLABLE SOLIDS | [5 empty] | 23 | 21 | 22 | 26 | 24 | 25 | 27 | 25 | 22 | 26 | 32 | 31 | 33 | 31 | 36 | 37 | 30 | 31 | 37 | 33 | 33 | 38 | 34 | 31 | 32 | 27 | 33 | 36 | 32
MIXED LIQUIR VOLITLE SOLIDS | [5 empty] | 2250 | 1940 | 2610 | 2070 | 1650 | 1710 | 1780 | 1680 | 2860 | 3610 | 2120 | 1350 | 2310 | 2480 | 2720 | 2920 | 2840 | 3720 | 3260 | 1810 | 2220 | 3400 | 3240 | 3090 | 3070 | 3190 | 2080 | 2390 | 2990
LABORATORY REACTOR PROCESSES DATA
CONTINUED
| REACTOR TWO TRAIN C |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29
MIXED-LIQUIR SUSPENDED SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
AVERAGE SETTLABLE SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
MIXED LIQUIR VOLITLE SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
| REACTOR TWO TRAIN D |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29
MIXED-LIQUIR SUSPENDED SOLIDS | [5 empty] | 2610 | 2340 | 3230 | 2340 | 1980 | 2620 | 2100 | 2280 | 3200 | 3200 | 2630 | 1950 | 3000 | 3090 | 2680 | 3170 | 3430 | 3620 | 3720 | 2400 | 2690 | 3940 | 3720 | 3730 | 3620 | 3250 | 3210 | 3280 | 3210
AVERAGE SETTLABLE SOLIDS | [5 empty] | 22 | 18 | 21 | 26 | 23 | 26 | 28 | 18 | 24 | 26 | 29 | 29 | 32 | 34 | 37 | 34 | 27 | 30 | 32 | 33 | 33 | 35 | 34 | 32 | 34 | 29 | 35 | 36 | 32
MIXED LIQUIR VOLITLE SOLIDS | [5 empty] | 2360 | 1900 | 2670 | 1970 | 1660 | 2280 | 1730 | 1940 | 2700 | 2690 | 2200 | 1650 | 2470 | 2550 | 2210 | 2570 | 2800 | 3040 | 3120 | 2030 | 2250 | 3240 | 3080 | 3080 | 3040 | 2730 | 2660 | 2780 | 2700
LABORATORY RETURN ACTIVATED SLUDGE AND WASTE SLUDGE DATA
| RETURN ACTIVATED SLUDGE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29
PERCENT RETURN SLUDGE TOTAL SUSPENDED SOLIDS | [5 empty] | 0.95 | 1.02 | 1.05 | 1.01 | 1.14 | 0.99 | 1.03 | 0.89 | 0.88 | 1.02 | 1.09 | 1.07 | 1.1 | 1.1 | 0.65 | 1.21 | 0.87 | 0.89 | 1.05 | 0.98 | 0.97 | 1.14 | 1.17 | 1.11 | 1.04 | 1.15 | 1.18 | 0.88 | 1.1
PERCENT RETURN SLUDGE FIXED SUSPENDED SOLIDS | [5 empty] | 22 | 20.4 | 20.7 | 21.2 | 19.3 | 21.8 | 20 | 21.6 | 21 | 19.8 | 20 | 20.1 | 19.9 | 23.6 | 18.9 | 11.5 | 22.3 | 20.4 | 21.5 | 20.9 | 21.5 | 20.1 | 19.2 | 20.6 | 21.4 | 21.5 | 21.1 | 21.4 | 20.8
|  | WASTE SLUDGE |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29
PERCENT WASTE FEED TOTAL SUSPENDED SOLDS | [5 empty] | 1.59 | 1.53 | 1.54 |  | 1.57 |  |  | 1.65 | 1.49 | 1.58 | 1.54 | 1.53 |  |  | 1.52 | 1.48 | 1.17 | 1.47 | 1.27 |  |  |  | 1.57 | 1.33 | 1.48 | 1.48 |  |  | 1.45
PERCENT WASTE FEED FIXED SUSPENDED SOLIDS | [5 empty] | 21.4 | 21.6 | 21.4 |  | 19.7 |  |  | 21.2 | 20.8 | 20.9 | 12.6 | 18.3 |  |  | 21.1 | 20.3 | 20.5 | 19.7 | 22.8 |  |  |  | 20.4 | 20.3 | 21.6 | 20.9 |  |  | 21.4
WASTE FEED SLUDGE pH | [5 empty] | 6.7 | 6.61 | 6.72 |  | 6.8 |  |  | 6.52 | 6.69 | 6.74 | 6.74 | 6.44 |  |  | 6.62 | 6.66 | 6.7 | 6.64 | 6.68 |  |  |  | 6.77 | 6.53 | 6.69 | 6.68 |  |  | 6.26
DEWATERING FILTRATE TOTAL SUSPENDED SOLIDS | [5 empty] | 0.28 | 0.18 | 0.26 |  | 0.22 |  |  | 0.19 | 0.19 | 0.19 | 0.24 | 0.22 |  |  | 0.2 | 0.22 | 0.16 | 0.21 | 0.21 |  |  |  | 0.35 | 0.26 | 0.21 | 0.22 |  |  | 0.18
DEWATERING FILTRATE FIXED SUSPENDED SOLIDS | [5 empty] | 57.1 | 61.1 | 53.8 |  | 50 |  |  | 52.6 | 52.6 | 57.9 | 50 | 50 |  |  | 65 | 54.5 | 62.5 | 52.4 | 66.7 |  |  |  | 40 | 50 | 66.7 | 63.6 |  |  | 55.6
DEWATERING FILTRATE pH | [5 empty] | 7.11 | 7.21 | 7.15 |  | 7.19 |  |  | 7.14 | 7.11 | 7.19 | 7.11 | 6.98 |  |  | 7.05 | 7.09 | 7.14 | 7.18 | 7.1 |  |  |  | 7.52 | 6.83 | 7.12 | 7.18 |  |  | 6.79
| DEWATERED CAKE SLUDGE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29
PERCENT TOTAL SOLIDS PRESS CAKE | [5 empty] | 16.66 | 17.85 | 16.31 |  | 17.67 |  |  | 17.68 | 18.78 | 17.87 | 18.19 | 18.96 |  |  | 17.49 | 16.73 | 17.49 | 17.62 | 17.46 |  |  |  | 17.44 | 17.47 | 17.66 | 17.36 |  |  | 16.44
PERCENT FIXED SOLIDS PRESS CAKE | [5 empty] | 14.8 | 15.6 | 14.7 |  | 20.9 |  |  | 16.5 | 15.2 | 14 | 19.4 | 18.96 |  |  | 15.6 | 13.7 | 15.1 | 15 | 13.5 |  |  |  | 14.1 | 14.1 | 13.4 | 13.4 |  |  | 14.3
PERCENT TOTAL SOLIDS LIME CAKE
OTHER SLUDGE REMOVAL
[6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29
GRIT (CU.YDS.) | [5 empty] | 1: 10; 5: 10; 9: 10; 12: 10; 19: 10; 26: 10
RAGS (CU.YDS.) | [5 empty] | 9: 10; 13: 10; 20: 10; 26: 10
VACUUM DEBRIS (EST. GAL)
MONITORING WELLS LABORATORY DATA
| MONITOR WELL ONE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
UPPER LEVEL
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
MONITORING WELLS LABORATORY DATA
| MONITOR WELL TWO |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
UPPER LEVEL
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
MONITORING WELLS LABORATORY DATA
| MONITOR WELL THREE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
FUTURE
UPPER LEVEL
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
MONITORING WELLS LABORATORY DATA
| REGIONAL MONITOR WELL ONE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
UPPER LEVEL
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
FEBRUARY |  | 0 |  | 0
|  | 0 |  | 0
1
1
|  | 2 |  | 1
1
[5 empty] | 1st WEEK | 1: 2nd WEEK; 2: 3rd WEEK; 3: 4th WEEK
| 1 |  | 1 |  | 1 | 1: 8; 2: 15; 3: 23
| 2 |  | 2 |  | 2 | 1: 9; 2: 16; 3: 24
| 3 |  | 3 |  | 3 | 1: 10; 2: 17; 3: 25
| 4 |  | 4 |  | 4 | 1: 11; 2: 18; 3: 26
| 5 |  | 5 |  | 5 | 1: 12; 2: 19; 3: 27
| 6 |  | 6 |  | 6 | 1: 13; 2: 20; 3: 28
| 7 |  | 7 |  | 7 | 1: 14; 2: 21; 3: 29
| 8 |  | 8 |  |  | 2: 22
| 9 |  | 9
| 10 |  | 10
| 11 |  | 11
| 12 |  | 12
| 13 |  | 13
| 14 |  | 14
| 15 |  | 15
| 16 |  | 16
| 17 |  | 17
| 18 |  | 18
| 19 |  | 19
| 20 |  | 20
| 21 |  | 21
| 22 |  | 22
| 23 |  | 23
| 24 |  | 24
| 25 |  | 25
| 26 |  | 26
| 27 |  | 27
| 28 |  | 28
29
| APRIL | MARCH | FEBRUARY
| AUGUST | JULY | JUNE
| DECEMBER | NOVEMBER | OCTOBER
| FEBRUARY | JANUARY | DECEMBER
| JANUARY | DECEMBER | NOVEMBER
| JUNE | MAY | APRIL
| JULY | JUNE | MAY | JANUARY
| MARCH | FEBRUARY | JANUARY | DECEMBER
| MAY | APRIL | MARCH
| NOVEMBER | OCTOBER | SEPTEMBER
| OCTOBER | SEPTEMBER | AUGUST
| SEPTEMBER | AUGUST | JULY
| HYDROGEN PEROXIDE |  | 0.1395
| CHLORINE |  | 0.1475
| POLYMER |  | 0.61
| FPL |  | 0.055
[6 empty] | 1st WEEK |  |  | 2nd WEEK |  |  | 3rd WEEK |  |  | 4th WEEK
[7 empty] | G | H | I | J
[5 empty] | MW1 UP | 1: 311
312
313
314
315
316
317
318

## MONITOR DATA
UNDERGROUND INJECTION CONTROL SECTION
MONTHLY OPERATING REPORT DATA SUMMARY
FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT MONTH/YEAR |  |  | FEBRUARY |  | 2004
I.D. NUMBER: 5006M02066 | [5 empty] | LEAD OPERATOR: |  |  |  | MIKE JUST
TELEPHONE NUMBER: (954) 523-1002
MONITORING WELL 1 DATA | [6 empty] | I.D. # 5006A11311
MW-1
PERMIT/CERTIFICATION NUMBER | [6 empty] | 0054569-142-UO
PERMIT EXPIRATION DATE |  | 2009-01-06
UPPER MONITORING INTERVAL | [6 empty] | 1,288' - 1,320' |  |  |  | Ft. bls.
Sample Date |  | 2004-02-03 |  | 2004-02-10 |  | 2004-02-17 |  | 2004-02-24
Submittal Date |  | 2004-02-04 |  | 2004-02-11 |  | 2004-02-18 |  | 2004-02-25
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 48.86 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 45.71 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 72 |  | 74 |  | 74 |  | 74 |  |  | degrees (F) |  | 73.5
TDS |  | 7205 |  | 7288 |  | 7239 |  | 7560 |  |  | mg/l |  | 7323
CHLORIDE |  | 4050 |  | 4050 |  | 4050 |  | 4000 |  |  | mg/l |  | 4037.5
AMMONIA-N |  | 0.849 |  | 0.883 |  | 0.868 |  | 0.876 |  |  | mg/l |  | 0.869
TKN |  | 1.71 |  | 1.6 |  | 1.29 |  | 1.65 |  |  | mg/l |  | 1.5625
pH |  | 8 |  | 8.18 |  | 7.99 |  | 8.01 |  |  | Std units |  | 8.045
CONDUCTIVITY |  | 12860 |  | 11060 |  | 12870 |  | 12880 |  |  | umho/cm |  | 12417.5
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.05 | < | 0.05 | < | 0.05 | < | 0.05 |  |  | mg/l |  | 0.05
SULFATE |  | 800 |  | 950 |  | 850 |  | 950 |  |  | mg/l |  | 887.5
C.O.D. 'S |  | 150 |  | 150 |  | 140 |  | 140 |  |  | mg/l |  | 145
IRON |  | 0.61 |  | 1.04 |  | 1.35 |  | 0.47 |  |  | mg/l |  | 0.8675
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
LOWER MONITORING INTERVAL | [6 empty] | 1,449' - 1,557' |  |  |  | Ft. bls
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 42.12 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 29.21 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 73 |  | 75 |  | 73 |  | 73 |  |  | degrees (F) |  | 73.5
TDS |  | 9190 |  | 9373 |  | 8967 |  | 9490 |  |  | mg/l |  | 9255
CHLORIDE |  | 5500 |  | 5700 |  | 5500 |  | 5600 |  |  | mg/l |  | 5575
AMMONIA-N |  | 9.6 |  | 9.56 |  | 9.57 |  | 9.59 |  |  | mg/l |  | 9.58
TKN |  | 11.58 |  | 11.76 |  | 11.11 |  | 11.57 |  |  | mg/l |  | 11.505
pH |  | 7.51 |  | 7.47 |  | 7.36 |  | 7.34 |  |  | Std units |  | 7.42
CONDUCTIVITY |  | 16730 |  | 14380 |  | 16800 |  | 16720 |  |  | umho/cm |  | 16157.5
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.05 | < | 0.05 | < | 0.05 | < | 0.05 |  |  | mg/l |  | 0.05
SULFATE |  | 850 |  | 750 |  | 750 |  | 850 |  |  | mg/l |  | 800
C.O.D. 'S |  | 250 |  | 240 |  | 220 |  | 210 |  |  | mg/l |  | 230
IRON |  | 0.03 |  | 0.02 |  | 0.02 |  | 0.02 |  |  | mg/l |  | 0.0225
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
PAGE 24
UNDERGROUND INJECTION CONTROL SECTION
MONTHLY OPERATING REPORT DATA SUMMARY
FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT MONTH/YEAR |  |  | FEBRUARY |  | 2004
I.D. NUMBER: 5006M02066 | [5 empty] | LEAD OPERATOR: |  |  |  | MIKE JUST
TELEPHONE NUMBER: (954) 523-1002
MONITORING WELL 2 DATA | [6 empty] | I.D. # 5006A11308 & 309
MW-2
PERMIT/CERTIFICATION NUMBER | [6 empty] | 0054569-142-UO
PERMIT EXPIRATION DATE |  | 2009-01-06
UPPER MONITORING INTERVAL | [6 empty] | 1,300' - 1,344' |  |  |  | Ft. bls.
Sample Date |  | 2004-02-03 |  | 2004-02-10 |  | 2004-02-17 |  | 2004-02-24
Submittal Date |  | 2004-02-04 |  | 2004-02-11 |  | 2004-02-18 |  | 2004-02-25
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 48.86 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 45.71 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 71 |  | 75 |  | 71 |  | 70 |  |  | degrees (F) |  | 71.75
TDS |  | 7110 |  | 7208 |  | 7069 |  | 7280 |  |  | mg/l |  | 7166.75
CHLORIDE |  | 4050 |  | 3800 |  | 4050 |  | 3900 |  |  | mg/l |  | 3950
AMMONIA-N |  | 0.9 |  | 0.814 |  | 8.48 |  | 0.86 |  |  | mg/l |  | 2.7635
TKN |  | 1.29 |  | 1.92 |  | 1.5 |  | 1.77 |  |  | mg/l |  | 1.62
pH |  | 8.06 |  | 8.14 |  | 7.89 |  | 7.92 |  |  | Std units |  | 8.0025
CONDUCTIVITY |  | 12610 |  | 10850 |  | 12600 |  | 12540 |  |  | umho/cm |  | 12150
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.05 | < | 0.05 | < | 0.05 | < | 0.05 |  |  | mg/l |  | 0.05
SULFATE |  | 850 |  | 850 |  | 850 |  | 900 |  |  | mg/l |  | 862.5
C.O.D. 'S |  | 160 |  | 140 |  | 130 |  | 140 |  |  | mg/l |  | 142.5
IRON |  | 1.31 |  | 1.55 |  | 1.13 |  | 1.16 |  |  | mg/l |  | 1.2875
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
LOWER MONITORING INTERVAL | [6 empty] | 1,970' - 2,025' |  |  |  | Ft. bls
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 42.12 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 29.21 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 70 |  | 71 |  | 70 |  | 70 |  |  | degrees (F) |  | 70.25
TDS |  | 31030 |  | 31554 |  | 30408 |  | 31790 |  |  | mg/l |  | 31195.5
CHLORIDE |  | 18800 |  | 18000 |  | 18400 |  | 18800 |  |  | mg/l |  | 18500
AMMONIA-N |  | 1.38 |  | 1.37 |  | 1.36 |  | 1.37 |  |  | mg/l |  | 1.37
TKN |  | 2.06 |  | 2.13 |  | 2.08 |  | 2.15 |  |  | mg/l |  | 2.105
pH |  | 7.54 |  | 7.6 |  | 7.39 |  | 7.41 |  |  | Std units |  | 7.485
CONDUCTIVITY |  | 51100 |  | 43000 |  | 49800 |  | 51100 |  |  | umho/cm |  | 48750
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.05 | < | 0.05 | < | 0.05 | < | 0.05 |  |  | mg/l |  | 0.05
SULFATE |  | 2300 |  | 2400 |  | 2700 |  | 2600 |  |  | mg/l |  | 2500
C.O.D. 'S |  | 780 |  | 770 |  | 890 |  | 760 |  |  | mg/l |  | 800
IRON |  | 0.06 |  | 0.04 |  | 0.06 |  | 0.04 |  |  | mg/l |  | 0.05
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
PAGE 25
UNDERGROUND INJECTION CONTROL SECTION
MONTHLY OPERATING REPORT DATA SUMMARY
FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT MONTH/YEAR |  |  | FEBRUARY |  | 2004
I.D. NUMBER: 5006M02066 | [5 empty] | LEAD OPERATOR: |  |  |  | MIKE JUST
TELEPHONE NUMBER: (954) 523-1002
MONITORING WELL 2 DATA | [6 empty] | I.D. # 5006A11310
MW-3
PERMIT/CERTIFICATION NUMBER | [6 empty] | 0054569-142-UO
PERMIT EXPIRATION DATE |  | 2009-01-06
UPPER MONITORING INTERVAL | [6 empty] | 1,300' - 1,349' |  |  |  | Ft. bls.
Sample Date |  | 2004-02-03 |  | 2004-02-10 |  | 2004-02-17 |  | 2004-02-24
Submittal Date |  | 2004-02-04 |  | 2004-02-11 |  | 2004-02-18 |  | 2004-02-25
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 31.97 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 17.63 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 70 |  | 71 |  | 70 |  | 70 |  |  | degrees (F) |  | 70.25
TDS |  | 31030 |  | 31554 |  | 30408 |  | 31790 |  |  | mg/l |  | 31195.5
CHLORIDE |  | 18800 |  | 18000 |  | 18400 |  | 18800 |  |  | mg/l |  | 18500
AMMONIA-N |  | 1.38 |  | 1.37 |  | 1.36 |  | 1.37 |  |  | mg/l |  | 1.37
TKN |  | 2.06 |  | 2.13 |  | 2.08 |  | 2.15 |  |  | mg/l |  | 2.105
pH |  | 7.54 |  | 7.6 |  | 7.39 |  | 7.41 |  |  | Std units |  | 7.485
CONDUCTIVITY |  | 51100 |  | 43000 |  | 49800 |  | 51100 |  |  | umho/cm |  | 48750
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.05 | < | 0.05 | < | 0.05 | < | 0.05 |  |  | mg/l |  | 0.05
SULFATE |  | 2300 |  | 2400 |  | 2700 |  | 2600 |  |  | mg/l |  | 2500
C.O.D. 'S |  | 780 |  | 770 |  | 890 |  | 760 |  |  | mg/l |  | 800
IRON |  | 0.06 |  | 0.04 |  | 0.06 |  | 0.04 |  |  | mg/l |  | 0.05
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
LOWER MONITORING INTERVAL | [6 empty] | 1,970' - 2,027' |  |  |  | Ft. bls
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 45.83 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 37.36 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 69 |  | 68 |  | 69 |  | 70 |  |  | degrees (F) |  | 69
TDS |  | 28230 |  | 28721 |  | 26967 |  | 28873 |  |  | mg/l |  | 28197.75
CHLORIDE |  | 16800 |  | 16800 |  | 17400 |  | 17200 |  |  | mg/l |  | 17050
AMMONIA-N |  | 2.29 |  | 2.34 |  | 2.37 |  | 2.33 |  |  | mg/l |  | 2.3325
TKN |  | 3.09 |  | 3.15 |  | 3.2 |  | 3.11 |  |  | mg/l |  | 3.1375
pH |  | 7.62 |  | 7.45 |  | 7.4 |  | 7.43 |  |  | Std units |  | 7.475
CONDUCTIVITY |  | 47200 |  | 39800 |  | 48000 |  | 47000 |  |  | umho/cm |  | 45500
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.05 | < | 0.05 | < | 0.05 | < | 0.05 |  |  | mg/l |  | 0.05
SULFATE |  | 1450 |  | 2300 |  | 2300 |  | 2500 |  |  | mg/l |  | 2137.5
C.O.D. 'S |  | 770 |  | 740 |  | 780 |  | 700 |  |  | mg/l |  | 747.5
IRON |  | 0.04 |  | 0.03 |  | 0.05 |  | 0.04 |  |  | mg/l |  | 0.04
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
PAGE 26
UNDERGROUND INJECTION CONTROL SECTION
MONTHLY OPERATING REPORT DATA SUMMARY
FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT MONTH/YEAR |  |  | FEBRUARY |  | 2004
I.D. NUMBER: 5006M02066 | [5 empty] | LEAD OPERATOR: |  |  |  | MIKE JUST
TELEPHONE NUMBER: (954) 523-1002
REGIONAL MONITORING WELL DATA
RMW-1
PERMIT NUMBER | [6 empty] | 0054569-142-UO
PERMIT EXPIRATION DATE |  | 2009-01-06
UPPER MONITORING INTERVAL | [6 empty] | 1300' - 1339' |  |  |  | Ft. bls.
Sample Date |  | 2004-02-03
Submittal Date |  | 2004-02-04
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 62.89 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | -6999 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 69 | [8 empty] | degrees (F) |  | 69
TDS |  | 5520 | [8 empty] | mg/l |  | 5520
CHLORIDE |  | 3150 | [8 empty] | mg/l |  | 3150
AMMONIA-N |  | 0.627 | [8 empty] | mg/l |  | 0.627
TKN |  | 1.21 | [8 empty] | mg/l |  | 1.21
pH |  | 8.34 | [8 empty] | Std units |  | 8.34
CONDUCTIVITY |  | 9870 | [8 empty] | umho/cm |  | 9870
FECAL COLIFORM |  | 0 | [8 empty] | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.05 | [8 empty] | mg/l |  | 0.05
SULFATE |  | 900 | [8 empty] | mg/l |  | 900
C.O.D. 'S |  | 130 | [8 empty] | mg/l |  | 130
IRON |  | 0.33 | [8 empty] | mg/l |  | 0.33
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
LOWER MONITORING INTERVAL | [6 empty] | 1500' - 1600' |  |  |  | Ft. bls
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 62.97 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | -6999 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 67 | [8 empty] | degrees (F) |  | 67
TDS |  | 25760 | [8 empty] | mg/l |  | 25760
CHLORIDE |  | 17200 | [8 empty] | mg/l |  | 17200
AMMONIA-N |  | 0.294 | [8 empty] | mg/l |  | 0.294
TKN |  | 1.01 | [8 empty] | mg/l |  | 1.01
pH |  | 7.63 | [8 empty] | Std units |  | 7.63
CONDUCTIVITY |  | 44100 | [8 empty] | umho/cm |  | 44100
FECAL COLIFORM |  | 0 | [8 empty] | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.05 | [8 empty] | mg/l |  | 0.05
SULFATE |  | 2100 | [8 empty] | mg/l |  | 2100
C.O.D. 'S |  | 650 | [8 empty] | mg/l |  | 650
IRON |  | 0.06 | [8 empty] | mg/l |  | 0.06
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
PAGE 27
Formulas:
LEAD OPERATOR: = [LEAD OPERATOR:, row above]+1

## WELL PRN DATA
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 1 |  |  | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60
32 | 16.78 | 11.23 | 13.46 | 76.1 | 54.5 | 62.51
33 | 13.5 | 8.93 | 11.39 | 62.61 | 48.07 | 55.17 |  |  | FLOW
34 | 12.13 | 7.44 | 10.22 | 57.02 | 44.75 | 51.61 | I |  | MAX | 16.78 | 13.5 | 12.13 | 11.69 | 13.93 | 14.05 | 14.37 | 13.15 | 13.26 | 12.66 | 12.58 | 13.26 | 11.81 | 14.41 | 9.6 | 12.8 | 12.64 | 12.76 | 15.1 | 12.22 | 16.02 | 13.43 | 15.37 | 13.5 | 12.6 | 11.96 | 12.54 | 15.59 | 11.85
35 | 11.69 | 0 | 6.65 | 55.98 | 35.23 | 45.32 | N |  | MIN | 11.23 | 8.93 | 7.44 | 0 | 0 | 6.79 | 6.87 | 5.99 | 5.98 | 5.28 | 4.76 | 6.88 | 5.54 | 0.01 | 0 | 0.01 | 0 | 0 | 5.23 | 0 | 6.61 | 4.82 | 0.01 | 5.85 | ER | 0 | 5.57 | 0 | 0
36 | 13.93 | 0 | 7.34 | 63.13 | 34.83 | 48.63 | J |  | TOT | 13.46 | 11.39 | 10.22 | 6.65 | 7.34 | 10.95 | 10.38 | 9.82 | 9.78 | 9.54 | 9.39 | 9.42 | 8.88 | 8.98 | 4.66 | 8.4 | 7.69 | 7.7 | 9.18 | 8.19 | 11.74 | 9.43 | 9.65 | 9.17 | ER | 6.31 | 9.34 | 9.48 | 5.61
37 | 14.05 | 6.79 | 10.95 | 64.2 | 42.91 | 54.1 | E | INJECTION WELL ONE
38 | 14.37 | 6.87 | 10.38 | 65.28 | 43.11 | 52.41 | C |  | PSI
39 | 13.15 | 5.99 | 9.82 | 60.55 | 41.18 | 50.59 | T |  | MAX | 76.1 | 62.61 | 57.02 | 55.98 | 63.13 | 64.2 | 65.28 | 60.55 | 61.45 | 60.16 | 58.56 | 62.84 | 56.9 | 65.62 | 50.06 | 59.19 | 58.94 | 59.18 | 69.08 | 58.67 | 70.8 | 61.45 | 69.1 | 62.79 | 59.21 | 58.37 | 59.82 | 69.53 | 56.73
40 | 13.26 | 5.98 | 9.78 | 61.45 | 41.32 | 50.72 | O |  | MIN | 54.5 | 48.07 | 44.75 | 35.23 | 34.83 | 42.91 | 43.11 | 41.18 | 41.32 | 40.33 | 40.4 | 43.59 | 40.98 | 35.46 | 35.03 | 35.14 | 34.16 | 34.13 | 39.79 | 34.27 | 42.02 | 38.82 | 35.26 | 41.1 | 34.71 | 34.94 | 40.56 | 34.94 | 34.59
41 | 12.66 | 5.28 | 9.54 | 60.16 | 40.33 | 50.09 | N |  | AVG | 62.51 | 55.17 | 51.61 | 45.32 | 48.63 | 54.1 | 52.41 | 50.59 | 50.72 | 50.09 | 49.81 | 49.71 | 48.34 | 48.83 | 41.38 | 47.13 | 46.47 | 46.39 | 48.56 | 47.39 | 56.45 | 49.14 | 50.63 | 48.71 | 47.4 | 45.76 | 49.67 | 50.19 | 44.14
42 | 12.58 | 4.76 | 9.39 | 58.56 | 40.4 | 49.81
43 | 13.26 | 6.88 | 9.42 | 62.84 | 43.59 | 49.71 | W
44 | 11.81 | 5.54 | 8.88 | 56.9 | 40.98 | 48.34 | E
45 | 14.41 | 0.01 | 8.98 | 65.62 | 35.46 | 48.83 | L
46 | 9.6 | 0 | 4.66 | 50.06 | 35.03 | 41.38 | L
47 | 12.8 | 0.01 | 8.4 | 59.19 | 35.14 | 47.13 | O
48 | 12.64 | 0 | 7.69 | 58.94 | 34.16 | 46.47 | N
49 | 12.76 | 0 | 7.7 | 59.18 | 34.13 | 46.39 | E
50 | 15.1 | 5.23 | 9.18 | 69.08 | 39.79 | 48.56
51 | 12.22 | 0 | 8.19 | 58.67 | 34.27 | 47.39 | D
52 | 16.02 | 6.61 | 11.74 | 70.8 | 42.02 | 56.45 | A
53 | 13.43 | 4.82 | 9.43 | 61.45 | 38.82 | 49.14 | T
54 | 15.37 | 0.01 | 9.65 | 69.1 | 35.26 | 50.63 | A
55 | 13.5 | 5.85 | 9.17 | 62.79 | 41.1 | 48.71
56 | 12.6 | ER | ER | 59.21 | 34.71 | 47.4
57 | 11.96 | 0 | 6.31 | 58.37 | 34.94 | 45.76
58 | 12.54 | 5.57 | 9.34 | 59.82 | 40.56 | 49.67
59 | 15.59 | 0 | 9.48 | 69.53 | 34.94 | 50.19
60 | 11.85 | 0 | 5.61 | 56.73 | 34.59 | 44.14
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 2 |  |  | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60
32 | 17.11 | 11.37 | 13.62 | 74.6 | 53.46 | 61.36
33 | 13.68 | 9.12 | 11.57 | 61.53 | 47.14 | 54.16 |  |  | FLOW
34 | 12.26 | 7.53 | 10.39 | 56.11 | 43.87 | 50.68 | I |  | MAX | 17.11 | 13.68 | 12.26 | 13.82 | 14.34 | 14.25 | 14.54 | 13.37 | 13.62 | 12.93 | 12.49 | 13.54 | 12.09 | 14.8 | 13.57 | 12.57 | 12.65 | 13.01 | 15.45 | 12.49 | 16.38 | 13.73 | 15.58 | 13.8 | 12.85 | 18.79 | 12.85 | 15.84 | 16.57
35 | 13.82 | 5.63 | 10.36 | 60.25 | 40.55 | 50.71 | N |  | MIN | 11.37 | 9.12 | 7.53 | 5.63 | 7.6 | 6.84 | 6.94 | 6.03 | 0.02 | 5.18 | 5.05 | 6.99 | 5.56 | 5.62 | 0.02 | 0.02 | 0.02 | 5.06 | 5.2 | 4.58 | 6.83 | 4.78 | 0.02 | 5.87 | 6.18 | 7.42 | 5.45 | 5.5 | 7.19
36 | 14.34 | 7.6 | 11.57 | 62.02 | 43.07 | 53.78 | J |  | TOT | 13.62 | 11.57 | 10.39 | 10.36 | 11.57 | 11.14 | 10.54 | 9.97 | 9.52 | 9.69 | 9.52 | 9.57 | 9.01 | 9.15 | 7.93 | 2.12 | 3.91 | 9.25 | 9.38 | 9.36 | 12.09 | 9.66 | 8.45 | 9.34 | 9.74 | 11.24 | 9.45 | 9.82 | 10.03
37 | 14.25 | 6.84 | 11.14 | 63.04 | 42.04 | 53.09 | E | INJECTION WELL TWO
38 | 14.54 | 6.94 | 10.54 | 64.15 | 42.26 | 51.42 | C |  | PSI
39 | 13.37 | 6.03 | 9.97 | 59.41 | 40.32 | 49.56 | T |  | MAX | 74.6 | 61.53 | 56.11 | 60.25 | 62.02 | 63.04 | 64.15 | 59.41 | 60.23 | 59.04 | 57.73 | 61.63 | 55.79 | 59.19 | 60.48 | 56.73 | 57.77 | 58.02 | 67.78 | 57.52 | 69.58 | 60.49 | 67.93 | 61.62 | 58.12 | 79.4 | 58.62 | 68.14 | 69.31
40 | 13.62 | 0.02 | 9.52 | 60.23 | 35.42 | 49 | I |  | MIN | 53.46 | 47.14 | 43.87 | 40.55 | 43.07 | 42.04 | 42.26 | 40.32 | 35.42 | 39.52 | 39.63 | 42.76 | 40.18 | 40.18 | 35.42 | 34.96 | 34.21 | 38.6 | 38.95 | 38.16 | 41.17 | 38.04 | 34.86 | 40.29 | 40.76 | 43.84 | 39.74 | 40.08 | 41.89
41 | 12.93 | 5.18 | 9.69 | 59.04 | 39.52 | 49.17 | O |  | AVG | 61.36 | 54.16 | 50.68 | 50.71 | 53.78 | 53.09 | 51.42 | 49.56 | 49 | 49.17 | 48.88 | 48.78 | 47.45 | 47.97 | 45.13 | 38.74 | 40.45 | 47.22 | 47.6 | 47.66 | 55.37 | 48.21 | 48.09 | 47.8 | 49.1 | 53.53 | 48.67 | 49.56 | 49.82
42 | 12.49 | 5.05 | 9.52 | 57.73 | 39.63 | 48.88 | N
43 | 13.54 | 6.99 | 9.57 | 61.63 | 42.76 | 48.78
44 | 12.09 | 5.56 | 9.01 | 55.79 | 40.18 | 47.45 | W
45 | 14.8 | 5.62 | 9.15 | 64.48 | 40.18 | 47.97 | E
46 | 13.57 | 0.02 | 7.93 | 60.48 | 35.42 | 45.13 | L
47 | 12.57 | 0.02 | 2.12 | 56.73 | 34.96 | 38.74 | L
48 | 12.65 | 0.02 | 3.91 | 57.77 | 34.21 | 40.45
49 | 13.01 | 5.06 | 9.25 | 58.02 | 38.6 | 47.22 | T
50 | 15.45 | 5.2 | 9.38 | 67.78 | 38.95 | 47.6 | W
51 | 12.49 | 4.58 | 9.36 | 57.52 | 38.16 | 47.66 | O
52 | 16.38 | 6.83 | 12.09 | 69.58 | 41.17 | 55.37
53 | 13.73 | 4.78 | 9.66 | 60.49 | 38.04 | 48.21 | D
54 | 15.58 | 0.02 | 8.45 | 67.93 | 34.86 | 48.09 | A
55 | 13.8 | 5.87 | 9.34 | 61.62 | 40.29 | 47.8 | T
56 | 12.85 | 6.18 | 9.74 | 58.12 | 40.76 | 49.1 | A
57 | 18.79 | 7.42 | 11.24 | 79.4 | 43.84 | 53.53
58 | 12.85 | 5.45 | 9.45 | 58.62 | 39.74 | 48.67
59 | 15.84 | 5.5 | 9.82 | 68.14 | 40.08 | 49.56
60 | 16.57 | 7.19 | 10.03 | 69.31 | 41.89 | 49.82
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 3 |  |  | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60
32 | 15.03 | 9.62 | 11.7 | 76.6 | 54.69 | 62.82
33 | 11.58 | 7.71 | 9.81 | 62.9 | 48.25 | 55.39 |  |  | FLOW
34 | 10.29 | 6.41 | 8.76 | 57.25 | 44.93 | 51.81 | I |  | MAX | 15.03 | 11.58 | 10.29 | 11.42 | 12.37 | 12.44 | 12.67 | 11.66 | 11.94 | 11.34 | 11.03 | 11.92 | 10.44 | 9.87 | 11.44 | 11 | 11.18 | 11.46 | 13.7 | 10.94 | 8.94 | 12.08 | 15.38 | 12.19 | 11.38 | 16.11 | 11.36 | 14.05 | 14.19
35 | 11.42 | 4.74 | 8.66 | 61.57 | 41.46 | 51.82 | N |  | MIN | 9.62 | 7.71 | 6.41 | 4.74 | 6.22 | 5.96 | 6.06 | 5.25 | 5.3 | 4.57 | ER | 6.14 | ER | ER | 4.75 | 3.66 | ER | 4.46 | ER | 4.01 | ER | ER | ER | 5.26 | ER | 6.34 | 4.84 | 4.88 | 6.12
36 | 12.37 | 6.22 | 9.9 | 63.54 | 44.03 | 55.04 | J |  | TOT | 11.7 | 9.81 | 8.76 | 8.66 | 9.9 | 9.73 | 9.23 | 8.73 | 8.73 | 8.5 | 8.01 | 8.4 | 6.14 | 5.1 | 7.02 | 7.55 | 7.12 | 8.06 | 6.89 | 8.18 | 0.23 | 5.99 | 8.54 | 8.27 | ER | 9.79 | 8.35 | 8.7 | 8.75
37 | 12.44 | 5.96 | 9.73 | 64.62 | 43.06 | 54.39 | E | INJECTION WELL THREE
38 | 12.67 | 6.06 | 9.23 | 65.74 | 43.29 | 52.67 | C |  | PSI
39 | 11.66 | 5.25 | 8.73 | 60.95 | 41.33 | 50.84 | T |  | MAX | 76.6 | 62.9 | 57.25 | 61.57 | 63.54 | 64.62 | 65.74 | 60.95 | 61.81 | 60.56 | 58.9 | 63.21 | 57.14 | 54.84 | 61.87 | 59.33 | 59.3 | 59.62 | 69.6 | 59.01 | 50.89 | 61.83 | 75.9 | 63.14 | 59.55 | 81.5 | 60.19 | 70.1 | 71
40 | 11.94 | 5.3 | 8.73 | 61.81 | 41.46 | 50.94 | I |  | MIN | 54.69 | 48.25 | 44.93 | 41.46 | 44.03 | 43.06 | 43.29 | 41.33 | 41.46 | 40.46 | 35.51 | 43.77 | 35.71 | 36.03 | 41.9 | 38.83 | 36.57 | 39.53 | 34.79 | 39.07 | 35.06 | 34.64 | 36.14 | 41.25 | 41.71 | 44.77 | 40.71 | 41.06 | 42.87
41 | 11.34 | 4.57 | 8.5 | 60.56 | 40.46 | 50.35 | O |  | AVG | 62.82 | 55.39 | 51.81 | 51.82 | 55.04 | 54.39 | 52.67 | 50.84 | 50.94 | 50.35 | 49.49 | 49.91 | 46.22 | 44.49 | 46.61 | 48 | 47.6 | 48.29 | 46.94 | 48.81 | 36.21 | 45.45 | 50.58 | 48.98 | 50.27 | 54.84 | 49.9 | 50.85 | 51.02
42 | 11.03 | ER | 8.01 | 58.9 | 35.51 | 49.49 | N
43 | 11.92 | 6.14 | 8.4 | 63.21 | 43.77 | 49.91
44 | 10.44 | ER | 6.14 | 57.14 | 35.71 | 46.22 | W
45 | 9.87 | ER | 5.1 | 54.84 | 36.03 | 44.49 | E
46 | 11.44 | 4.75 | 7.02 | 61.87 | 41.9 | 46.61 | L
47 | 11 | 3.66 | 7.55 | 59.33 | 38.83 | 48 | L
48 | 11.18 | ER | 7.12 | 59.3 | 36.57 | 47.6
49 | 11.46 | 4.46 | 8.06 | 59.62 | 39.53 | 48.29 | T
50 | 13.7 | ER | 6.89 | 69.6 | 34.79 | 46.94 | H
51 | 10.94 | 4.01 | 8.18 | 59.01 | 39.07 | 48.81 | R
52 | 8.94 | ER | 0.23 | 50.89 | 35.06 | 36.21 | E
53 | 12.08 | ER | 5.99 | 61.83 | 34.64 | 45.45 | E
54 | 15.38 | ER | 8.54 | 75.9 | 36.14 | 50.58
55 | 12.19 | 5.26 | 8.27 | 63.14 | 41.25 | 48.98 | D
56 | 11.38 | ER | ER | 59.55 | 41.71 | 50.27 | A
57 | 16.11 | 6.34 | 9.79 | 81.5 | 44.77 | 54.84 | T
58 | 11.36 | 4.84 | 8.35 | 60.19 | 40.71 | 49.9 | A
59 | 14.05 | 4.88 | 8.7 | 70.1 | 41.06 | 50.85
60 | 14.19 | 6.12 | 8.75 | 71 | 42.87 | 51.02
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 4 |  |  | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60
32 | 18.94 | 0.12 | 11.99 | 74.5 | 35.7 | 55.58
33 | 16.02 | 10.9 | 13.65 | 62.5 | 48.47 | 55.35 |  |  | FLOW
34 | 14.44 | 9.3 | 12.38 | 57.17 | 45.27 | 51.91 | I |  | MAX | 18.94 | 16.02 | 14.44 | 15.88 | 16.39 | 0.15 | 0.15 | 0.13 | 0.16 | 0.16 | 15.06 | 13.58 | 14.83 | 18.14 | 16.21 | 15.15 | 14.96 | 5.6 | 0.14 | 0.14 | 0.15 | 0.15 | 4.96 | 0.14 | 0.38 | 11.19 | 0.13 | 0.14 | 0.14
35 | 15.88 | 7.37 | 12.32 | 61.07 | 41.93 | 51.83 | N |  | MIN | 0.12 | 10.9 | 9.3 | 7.37 | 0.12 | 0.12 | 0.11 | 0.11 | 0.12 | 0.12 | 0.13 | 0.13 | 7.73 | 7.67 | 7.35 | 0.12 | 0.12 | 0.11 | 0.11 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.11 | 0.1 | 0.12
36 | 16.39 | 0.12 | 4.84 | 62.78 | 36.39 | 42.59 | J |  | TOT | 11.99 | 13.65 | 12.38 | 12.32 | 4.84 | 0.13 | 0.13 | 0.12 | 0.13 | 0.13 | 0.31 | 4.94 | 11.43 | 11.6 | 10.21 | 8.9 | 8.28 | 0.19 | 0.12 | 0.12 | 0.13 | 0.13 | 0.16 | 0.13 | 0.13 | 0.57 | 0.12 | 0.12 | 0.12
37 | 0.15 | 0.12 | 0.13 | 37.6 | 35.76 | 36.78 | E | INJECTION WELL FOUR
38 | 0.15 | 0.11 | 0.13 | 37.78 | 35.77 | 36.63 | C |  | PSI
39 | 0.13 | 0.11 | 0.12 | 37.2 | 35.43 | 36.3 | T |  | MAX | 74.5 | 62.5 | 57.17 | 61.07 | 62.78 | 37.6 | 37.78 | 37.2 | 37.15 | 37.15 | 62.78 | 58.43 | 56.99 | 60.16 | 61.57 | 59.24 | 58.13 | 43.13 | 37.96 | 37.13 | 36.54 | 37.47 | 42.61 | 37.47 | 37.38 | 49.86 | 37.32 | 36.99 | 37.71
40 | 0.16 | 0.12 | 0.13 | 37.15 | 35.33 | 36.3 | I |  | MIN | 35.7 | 48.47 | 45.27 | 41.93 | 36.39 | 35.76 | 35.77 | 35.43 | 35.33 | 35.23 | 35.3 | 35.31 | 41.61 | 41.59 | 42.37 | 36.44 | 35.83 | 35.5 | 34.44 | 35.1 | 34.94 | 34.81 | 35.17 | 34.96 | 35.58 | 35.94 | 35.72 | 35.11 | 35.63
41 | 0.16 | 0.12 | 0.13 | 37.15 | 35.23 | 36.33 | O |  | AVG | 55.58 | 55.35 | 51.91 | 51.83 | 42.59 | 36.78 | 36.63 | 36.3 | 36.3 | 36.33 | 36.71 | 41.58 | 48.75 | 49.25 | 46.92 | 45.98 | 45.58 | 36.26 | 36.02 | 36.13 | 35.82 | 36.05 | 36.22 | 36.18 | 36.49 | 37.41 | 36.5 | 36.05 | 36.37
42 | 15.06 | 0.13 | 0.31 | 62.78 | 35.3 | 36.71 | N
43 | 13.58 | 0.13 | 4.94 | 58.43 | 35.31 | 41.58
44 | 14.83 | 7.73 | 11.43 | 56.99 | 41.61 | 48.75 | W
45 | 18.14 | 7.67 | 11.6 | 65.57 | 41.59 | 49.25 | E
46 | 16.21 | 7.35 | 10.21 | 61.57 | 42.37 | 46.92 | L
47 | 15.15 | 0.12 | 8.9 | 59.24 | 36.44 | 45.98 | L
48 | 14.96 | 0.12 | 8.28 | 58.13 | 35.83 | 45.58
49 | 5.6 | 0.11 | 0.19 | 43.13 | 35.5 | 36.26 | F
50 | 0.14 | 0.11 | 0.12 | 37.96 | 34.44 | 36.02 | O
51 | 0.14 | 0.12 | 0.12 | 37.13 | 35.1 | 36.13 | U
52 | 0.15 | 0.12 | 0.13 | 36.54 | 34.94 | 35.82 | R
53 | 0.15 | 0.12 | 0.13 | 37.47 | 34.81 | 36.05
54 | 4.96 | 0.12 | 0.16 | 42.61 | 35.17 | 36.22 | D
55 | 0.14 | 0.12 | 0.13 | 37.47 | 34.96 | 36.18 | A
56 | 0.38 | 0.12 | 0.13 | 37.38 | 35.58 | 36.49 | T
57 | 11.19 | 0.12 | 0.57 | 49.86 | 35.94 | 37.41 | A
58 | 0.13 | 0.11 | 0.12 | 37.32 | 35.72 | 36.5
59 | 0.14 | 0.1 | 0.12 | 36.99 | 35.11 | 36.05
60 | 0.14 | 0.12 | 0.12 | 37.71 | 35.63 | 36.37
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 5 |  |  | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60
32 | 14.8 | ER | 11.07 | 76 | 34.14 | 61.45
33 | 11.45 | 7.71 | 9.71 | 62.59 | 48.2 | 55.18 |  |  | FLOW
34 | 10.24 | 6.44 | 8.74 | 57.05 | 25.67 | 51.35 | I |  | MAX | 14.8 | 11.45 | 10.24 | 11.2 | 12.23 | 12.38 | 12.68 | 11.64 | 11.85 | 11.31 | 11.87 | 11.81 | ER | ER | 8.06 | 10.65 | 11.02 | 11.3 | 13.39 | 10.81 | 14.09 | 11.88 | 14.84 | 11.96 | 11.16 | 15.73 | 11.18 | 10.98 | 13.88
35 | 11.2 | 4.96 | 8.63 | 61.24 | 41.25 | 51.5 | N |  | MIN | ER | 7.71 | 6.44 | 4.96 | 4.54 | 6.26 | 6.38 | 5.64 | 5.62 | 4.96 | 0.28 | ER | ER | ER | ER | 3.94 | 4.39 | 4.79 | ER | 4.4 | 6.14 | 4.54 | ER | ER | 5.46 | 6.34 | 5.15 | ER | 6.28
36 | 12.23 | 4.54 | 9.83 | 62.97 | 42.48 | 54.58 | J |  | TOT | 11.07 | 9.71 | 8.74 | 8.63 | 9.83 | 9.78 | 9.3 | 8.83 | 8.82 | 8.6 | 8.42 | 2.88 | ER | ER | 3.87 | 7.51 | 7.88 | 8.15 | 8.17 | 8.23 | 10.49 | 8.49 | 7.08 | 6.49 | 8.55 | 9.7 | 8.38 | 5.72 | 8.74
37 | 12.38 | 6.26 | 9.78 | 63.99 | 42.79 | 53.96 | E | INJECTION WELL FIVE
38 | 12.68 | 6.38 | 9.3 | 65.08 | 43.01 | 52.27 | C |  | PSI
39 | 11.64 | 5.64 | 8.83 | 60.44 | 41.16 | 50.49 | T |  | MAX | 76 | 62.59 | 57.05 | 61.24 | 62.97 | 63.99 | 65.08 | 60.44 | 61.33 | 60.1 | 64.55 | 62.72 | 36.31 | 36.05 | 49.42 | 59.01 | 58.91 | 59.19 | 69.14 | 58.62 | 70.6 | 61.27 | 75.2 | 62.59 | 59.04 | 80.8 | 59.75 | 57.7 | 70.4
40 | 11.85 | 5.62 | 8.82 | 61.33 | 41.17 | 50.52 | I |  | MIN | 34.14 | 48.2 | 25.67 | 41.25 | 42.48 | 42.79 | 43.01 | 41.16 | 41.17 | 40.22 | 35.08 | 34.02 | 34.68 | 34.72 | 34.94 | 38.73 | 39.48 | 39.41 | 33.74 | 38.87 | 41.98 | 38.82 | 33.88 | 33.5 | 41.46 | 44.43 | 40.52 | 33.59 | 42.56
41 | 11.31 | 4.96 | 8.6 | 60.1 | 40.22 | 49.95 | O |  | AVG | 61.45 | 55.18 | 51.35 | 51.5 | 54.58 | 53.96 | 52.27 | 50.49 | 50.52 | 49.95 | 49.55 | 40.47 | 35.53 | 35.43 | 41.11 | 47.72 | 48.5 | 48.12 | 48.29 | 48.49 | 56.34 | 48.99 | 46.83 | 45.61 | 49.93 | 54.38 | 49.61 | 44.66 | 50.62
42 | 11.87 | 0.28 | 8.42 | 64.55 | 35.08 | 49.55 | N
43 | 11.81 | ER | 2.88 | 62.72 | 34.02 | 40.47
44 | ER | ER | ER | 36.31 | 34.68 | 35.53 | W
45 | ER | ER | ER | 36.05 | 34.72 | 35.43 | E
46 | 8.06 | ER | 3.87 | 49.42 | 34.94 | 41.11 | L
47 | 10.65 | 3.94 | 7.51 | 59.01 | 38.73 | 47.72 | L
48 | 11.02 | 4.39 | 7.88 | 58.91 | 39.48 | 48.5
49 | 11.3 | 4.79 | 8.15 | 59.19 | 39.41 | 48.12 | F
50 | 13.39 | ER | 8.17 | 69.14 | 33.74 | 48.29 | I
51 | 10.81 | 4.4 | 8.23 | 58.62 | 38.87 | 48.49 | V
52 | 14.09 | 6.14 | 10.49 | 70.6 | 41.98 | 56.34 | E
53 | 11.88 | 4.54 | 8.49 | 61.27 | 38.82 | 48.99
54 | 14.84 | ER | 7.08 | 75.2 | 33.88 | 46.83 | D
55 | 11.96 | ER | 6.49 | 62.59 | 33.5 | 45.61 | A
56 | 11.16 | 5.46 | 8.55 | 59.04 | 41.46 | 49.93 | T
57 | 15.73 | 6.34 | 9.7 | 80.8 | 44.43 | 54.38 | A
58 | 11.18 | 5.15 | 8.38 | 59.75 | 40.52 | 49.61
59 | 10.98 | ER | 5.72 | 57.7 | 33.59 | 44.66
60 | 13.88 | 6.28 | 8.74 | 70.4 | 42.56 | 50.62

## RMW PRN DATA
julian | u-avg | u-min | u-max | l-avg | l-min | l-max
32 | 22.47 | 22.36 | 22.55 | 44.75 | 44.65 | 44.82 | R |  |  | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60
33 | 21.24 | 20.07 | 22.44 | 39.55 | 36.24 | 44.72 | E
34 | 21.81 | 19.9 | 22.44 | 41.13 | 26.22 | 43.8 | G |  | LOW
35 | 22.58 | 22.43 | 22.67 | 43.93 | 43.79 | 44.02 | I |  | MIN | 22.36 | 20.07 | 19.9 | 22.43 | 22.64 | 22.75 | 22.84 | 22.73 | 22.78 | 22.89 | 0.25 | 22.97 | 22.97 | 23 | 23.02 | 22.89 | 22.89 | 22.9 | 22.9 | 23.03 | 23.12 | 23.07 | 23.05 | 23.18 | 23.33 | -6999 | 23.12 | 23.05 | 23.02
36 | 22.73 | 22.64 | 22.81 | 44.06 | 43.97 | 44.14 | O |  | MAX | 22.55 | 22.44 | 22.44 | 22.67 | 22.81 | 22.96 | 22.98 | 22.84 | 22.92 | 23.01 | 23.08 | 23.1 | 23.07 | 23.21 | 23.25 | 23.08 | 23.04 | 23 | 23.07 | 23.18 | 23.17 | 23.15 | 23.18 | 23.36 | 23.43 | 62.97 | 23.38 | 23.18 | 23.13
37 | 22.88 | 22.75 | 22.96 | 44.2 | 44.05 | 44.29 | N |  | AVG | 22.47 | 21.24 | 21.81 | 22.58 | 22.73 | 22.88 | 22.93 | 22.77 | 22.83 | 22.94 | 22.73 | 23.03 | 23.02 | 23.12 | 23.17 | 23 | 22.97 | 22.94 | 23 | 23.11 | 23.14 | 23.1 | 23.12 | 23.26 | 23.38 | -6999 | 23.27 | 23.13 | 23.08
38 | 22.93 | 22.84 | 22.98 | 44.24 | 44.13 | 44.3 | A | RMW
39 | 22.77 | 22.73 | 22.84 | 44.1 | 44.06 | 44.14 | L |  | UP
40 | 22.83 | 22.78 | 22.92 | 44.15 | 44.07 | 44.22 |  |  | MIN | 44.65 | 36.24 | 26.22 | 43.79 | 43.97 | 44.05 | 44.13 | 44.06 | 44.07 | 44.19 | 0.25 | 44.31 | 44.3 | 44.36 | 44.38 | 44.25 | 44.25 | 44.24 | 44.25 | 44.36 | 44.45 | 44.41 | 44.42 | 44.5 | 44.66 | -6999 | 44.52 | 44.45 | 44.43
41 | 22.94 | 22.89 | 23.01 | 44.25 | 44.19 | 44.33 | M |  | MAX | 44.82 | 44.72 | 43.8 | 44.02 | 44.14 | 44.29 | 44.3 | 44.14 | 44.22 | 44.33 | 44.36 | 44.39 | 44.37 | 44.5 | 44.55 | 44.42 | 44.36 | 44.36 | 44.43 | 44.53 | 44.56 | 44.49 | 44.55 | 44.69 | 44.74 | 62.89 | 44.68 | 44.54 | 44.51
42 | 22.73 | 0.25 | 23.08 | 43.78 | 0.25 | 44.36 | O |  | AVG | 44.75 | 39.55 | 41.13 | 43.93 | 44.06 | 44.2 | 44.24 | 44.1 | 44.15 | 44.25 | 43.78 | 44.36 | 44.34 | 44.44 | 44.49 | 44.34 | 44.31 | 44.29 | 44.35 | 44.46 | 44.5 | 44.46 | 44.48 | 44.6 | 44.7 | -6999 | 44.61 | 44.5 | 44.47
43 | 23.03 | 22.97 | 23.1 | 44.36 | 44.31 | 44.39 | N
44 | 23.02 | 22.97 | 23.07 | 44.34 | 44.3 | 44.37 | I
45 | 23.12 | 23 | 23.21 | 44.44 | 44.36 | 44.5 | T
46 | 23.17 | 23.02 | 23.25 | 44.49 | 44.38 | 44.55 | O
47 | 23 | 22.89 | 23.08 | 44.34 | 44.25 | 44.42 | R
48 | 22.97 | 22.89 | 23.04 | 44.31 | 44.25 | 44.36
49 | 22.94 | 22.9 | 23 | 44.29 | 44.24 | 44.36 | W
50 | 23 | 22.9 | 23.07 | 44.35 | 44.25 | 44.43 | E
51 | 23.11 | 23.03 | 23.18 | 44.46 | 44.36 | 44.53 | L
52 | 23.14 | 23.12 | 23.17 | 44.5 | 44.45 | 44.56 | L
53 | 23.1 | 23.07 | 23.15 | 44.46 | 44.41 | 44.49
54 | 23.12 | 23.05 | 23.18 | 44.48 | 44.42 | 44.55
55 | 23.26 | 23.18 | 23.36 | 44.6 | 44.5 | 44.69 | R
56 | 23.38 | 23.33 | 23.43 | 44.7 | 44.66 | 44.74 | M
57 | -6999 | -6999 | 62.97 | -6999 | -6999 | 62.89 | W
58 | 23.27 | 23.12 | 23.38 | 44.61 | 44.52 | 44.68
59 | 23.13 | 23.05 | 23.18 | 44.5 | 44.45 | 44.54 | O
60 | 23.08 | 23.02 | 23.13 | 44.47 | 44.43 | 44.51 | N
E
32 | 41.76 | 41.59 | 42.07 | 48.5 | 48.28 | 48.61 | M |  |  | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60
33 | 36.86 | 33.99 | 41.69 | 46.86 | 45.71 | 48.55 | O
34 | 38.89 | 33.98 | 41.62 | 47.69 | 46.04 | 48.76 | N |  | LOW
35 | 41.52 | 41.36 | 41.66 | 48.44 | 48.23 | 48.51 | I |  | MIN | 41.59 | 33.99 | 33.98 | 41.36 | 41.44 | 41.47 | 41.51 | 41.42 | 36.72 | 36.71 | 41.52 | 41.54 | 41.56 | 41.62 | 41.62 | 36.4 | 36.22 | 41.27 | 41.33 | 41.55 | 41.65 | 41.63 | 29.21 | 29.82 | 41.57 | 41.71 | 41.56 | 41.48 | 41.56
36 | 41.5 | 41.44 | 41.66 | 48.45 | 48.25 | 48.54 | T |  | MAX | 42.07 | 41.69 | 41.62 | 41.66 | 41.66 | 41.75 | 41.87 | 41.64 | 41.77 | 41.69 | 41.77 | 41.8 | 41.87 | 41.93 | 41.96 | 41.7 | 41.48 | 41.55 | 41.69 | 41.83 | 42.12 | 42.03 | 41.93 | 41.61 | 41.88 | 42.04 | 41.85 | 41.78 | 41.74
37 | 41.57 | 41.47 | 41.75 | 48.46 | 48.28 | 48.66 | O |  | AVG | 41.76 | 36.86 | 38.89 | 41.52 | 41.5 | 41.57 | 41.64 | 41.48 | 39.01 | 39.88 | 41.57 | 41.6 | 41.65 | 41.73 | 41.79 | 38.52 | 39.59 | 41.44 | 41.5 | 41.61 | 41.85 | 41.73 | 35.59 | 37.48 | 41.64 | 41.83 | 41.68 | 41.59 | 41.59
38 | 41.64 | 41.51 | 41.87 | 48.51 | 48.38 | 48.64 | R | MW-1
39 | 41.48 | 41.42 | 41.64 | 48.38 | 48.22 | 48.44 |  |  | UP
40 | 39.01 | 36.72 | 41.77 | 47.44 | 46.46 | 48.47 | W |  | MIN | 48.28 | 45.71 | 46.04 | 48.23 | 48.25 | 48.28 | 48.38 | 48.22 | 46.46 | 46.8 | 48.36 | 48.36 | 48.34 | 48.46 | 48.37 | 46.88 | 47.16 | 48.14 | 48.13 | 48.27 | 48.35 | 48.31 | 46.09 | 46.47 | 48.51 | 48.63 | 48.43 | 48.36 | 48.31
41 | 39.88 | 36.71 | 41.69 | 47.95 | 46.8 | 48.58 | E |  | MAX | 48.61 | 48.55 | 48.76 | 48.51 | 48.54 | 48.66 | 48.64 | 48.44 | 48.47 | 48.58 | 48.58 | 48.61 | 48.59 | 48.7 | 48.76 | 48.62 | 48.56 | 48.46 | 48.55 | 48.66 | 48.65 | 48.58 | 48.56 | 48.74 | 48.83 | 48.86 | 48.77 | 48.58 | 48.55
42 | 41.57 | 41.52 | 41.77 | 48.48 | 48.36 | 48.58 | L |  | AVG | 48.5 | 46.86 | 47.69 | 48.44 | 48.45 | 48.46 | 48.51 | 48.38 | 47.44 | 47.95 | 48.48 | 48.51 | 48.51 | 48.52 | 48.57 | 47.69 | 48.01 | 48.31 | 48.42 | 48.47 | 48.49 | 48.48 | 47.37 | 47.84 | 48.67 | 48.72 | 48.57 | 48.52 | 48.47
43 | 41.6 | 41.54 | 41.8 | 48.51 | 48.36 | 48.61 | L
44 | 41.65 | 41.56 | 41.87 | 48.51 | 48.34 | 48.59
45 | 41.73 | 41.62 | 41.93 | 48.52 | 48.46 | 48.7 | O
46 | 41.79 | 41.62 | 41.96 | 48.57 | 48.37 | 48.76 | N
47 | 38.52 | 36.4 | 41.7 | 47.69 | 46.88 | 48.62 | E
48 | 39.59 | 36.22 | 41.48 | 48.01 | 47.16 | 48.56
49 | 41.44 | 41.27 | 41.55 | 48.31 | 48.14 | 48.46 | I
50 | 41.5 | 41.33 | 41.69 | 48.42 | 48.13 | 48.55 | N
51 | 41.61 | 41.55 | 41.83 | 48.47 | 48.27 | 48.66 | J
52 | 41.85 | 41.65 | 42.12 | 48.49 | 48.35 | 48.65 | E
53 | 41.73 | 41.63 | 42.03 | 48.48 | 48.31 | 48.58 | C
54 | 35.59 | 29.21 | 41.93 | 47.37 | 46.09 | 48.56 | T
55 | 37.48 | 29.82 | 41.61 | 47.84 | 46.47 | 48.74 | I
56 | 41.64 | 41.57 | 41.88 | 48.67 | 48.51 | 48.83 | O
57 | 41.83 | 41.71 | 42.04 | 48.72 | 48.63 | 48.86 | N
58 | 41.68 | 41.56 | 41.85 | 48.57 | 48.43 | 48.77
59 | 41.59 | 41.48 | 41.78 | 48.52 | 48.36 | 48.58 | W
60 | 41.59 | 41.56 | 41.74 | 48.47 | 48.31 | 48.55 | E
L
L
32 | 41.76 | 41.59 | 42.07 | 48.5 | 48.28 | 48.61 | M |  |  | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60
33 | 36.86 | 33.99 | 41.69 | 46.86 | 45.71 | 48.55 | O
34 | 38.89 | 33.98 | 41.62 | 47.69 | 46.04 | 48.76 | N |  | LOW
35 | 41.52 | 41.36 | 41.66 | 48.44 | 48.23 | 48.51 | I |  | MIN | 41.59 | 33.99 | 33.98 | 41.36 | 41.44 | 41.47 | 41.51 | 41.42 | 36.72 | 36.71 | 41.52 | 41.54 | 41.56 | 41.62 | 41.62 | 36.4 | 36.22 | 41.27 | 41.33 | 41.55 | 41.65 | 41.63 | 29.21 | 29.82 | 41.57 | 41.71 | 41.56 | 41.48 | 41.56
36 | 41.5 | 41.44 | 41.66 | 48.45 | 48.25 | 48.54 | T |  | MAX | 42.07 | 41.69 | 41.62 | 41.66 | 41.66 | 41.75 | 41.87 | 41.64 | 41.77 | 41.69 | 41.77 | 41.8 | 41.87 | 41.93 | 41.96 | 41.7 | 41.48 | 41.55 | 41.69 | 41.83 | 42.12 | 42.03 | 41.93 | 41.61 | 41.88 | 42.04 | 41.85 | 41.78 | 41.74
37 | 41.57 | 41.47 | 41.75 | 48.46 | 48.28 | 48.66 | O |  | AVG | 41.76 | 36.86 | 38.89 | 41.52 | 41.5 | 41.57 | 41.64 | 41.48 | 39.01 | 39.88 | 41.57 | 41.6 | 41.65 | 41.73 | 41.79 | 38.52 | 39.59 | 41.44 | 41.5 | 41.61 | 41.85 | 41.73 | 35.59 | 37.48 | 41.64 | 41.83 | 41.68 | 41.59 | 41.59
38 | 41.64 | 41.51 | 41.87 | 48.51 | 48.38 | 48.64 | R | MW-2
39 | 41.48 | 41.42 | 41.64 | 48.38 | 48.22 | 48.44 |  |  | UP
40 | 39.01 | 36.72 | 41.77 | 47.44 | 46.46 | 48.47 | W |  | MIN | 48.28 | 45.71 | 46.04 | 48.23 | 48.25 | 48.28 | 48.38 | 48.22 | 46.46 | 46.8 | 48.36 | 48.36 | 48.34 | 48.46 | 48.37 | 46.88 | 47.16 | 48.14 | 48.13 | 48.27 | 48.35 | 48.31 | 46.09 | 46.47 | 48.51 | 48.63 | 48.43 | 48.36 | 48.31
41 | 39.88 | 36.71 | 41.69 | 47.95 | 46.8 | 48.58 | E |  | MAX | 48.61 | 48.55 | 48.76 | 48.51 | 48.54 | 48.66 | 48.64 | 48.44 | 48.47 | 48.58 | 48.58 | 48.61 | 48.59 | 48.7 | 48.76 | 48.62 | 48.56 | 48.46 | 48.55 | 48.66 | 48.65 | 48.58 | 48.56 | 48.74 | 48.83 | 48.86 | 48.77 | 48.58 | 48.55
42 | 41.57 | 41.52 | 41.77 | 48.48 | 48.36 | 48.58 | L |  | AVG | 48.5 | 46.86 | 47.69 | 48.44 | 48.45 | 48.46 | 48.51 | 48.38 | 47.44 | 47.95 | 48.48 | 48.51 | 48.51 | 48.52 | 48.57 | 47.69 | 48.01 | 48.31 | 48.42 | 48.47 | 48.49 | 48.48 | 47.37 | 47.84 | 48.67 | 48.72 | 48.57 | 48.52 | 48.47
43 | 41.6 | 41.54 | 41.8 | 48.51 | 48.36 | 48.61 | L
44 | 41.65 | 41.56 | 41.87 | 48.51 | 48.34 | 48.59
45 | 41.73 | 41.62 | 41.93 | 48.52 | 48.46 | 48.7 | T
46 | 41.79 | 41.62 | 41.96 | 48.57 | 48.37 | 48.76 | W
47 | 38.52 | 36.4 | 41.7 | 47.69 | 46.88 | 48.62 | O
48 | 39.59 | 36.22 | 41.48 | 48.01 | 47.16 | 48.56
49 | 41.44 | 41.27 | 41.55 | 48.31 | 48.14 | 48.46 | I
50 | 41.5 | 41.33 | 41.69 | 48.42 | 48.13 | 48.55 | N
51 | 41.61 | 41.55 | 41.83 | 48.47 | 48.27 | 48.66 | J
52 | 41.85 | 41.65 | 42.12 | 48.49 | 48.35 | 48.65 | E
53 | 41.73 | 41.63 | 42.03 | 48.48 | 48.31 | 48.58 | C
54 | 35.59 | 29.21 | 41.93 | 47.37 | 46.09 | 48.56 | T
55 | 37.48 | 29.82 | 41.61 | 47.84 | 46.47 | 48.74 | I
56 | 41.64 | 41.57 | 41.88 | 48.67 | 48.51 | 48.83 | O
57 | 41.83 | 41.71 | 42.04 | 48.72 | 48.63 | 48.86 | N
58 | 41.68 | 41.56 | 41.85 | 48.57 | 48.43 | 48.77
59 | 41.59 | 41.48 | 41.78 | 48.52 | 48.36 | 48.58 | W
60 | 41.59 | 41.56 | 41.74 | 48.47 | 48.31 | 48.55 | E
L
L
32 | 45.55 | 45.49 | 45.7 | 31.72 | 31.49 | 31.87 | M |  |  | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60
33 | 40.43 | 37.42 | 45.62 | 22.77 | 17.64 | 31.79 | O
34 | 42.4 | 37.42 | 45.15 | 26.34 | 17.63 | 31.1 | N |  | LOW
35 | 45.32 | 45.06 | 45.32 | 31.23 | 30.98 | 31.32 | I |  | MIN | 45.49 | 37.42 | 37.42 | 45.06 | 45.25 | 45.35 | 45.46 | 45.38 | 39.64 | 39.61 | 45.25 | 45.4 | 45.43 | 45.51 | 45.59 | 37.94 | 37.94 | 45.05 | 45.18 | 45.42 | 45.58 | 45.6 | 37.38 | 37.36 | 45.37 | 45.64 | 45.51 | 45.52 | 45.53
36 | 45.38 | 45.25 | 45.43 | 31.33 | 31.17 | 31.44 | T |  | MAX | 45.7 | 45.62 | 45.15 | 45.32 | 45.43 | 45.59 | 45.6 | 45.46 | 45.51 | 45.25 | 45.41 | 45.52 | 45.57 | 45.75 | 45.83 | 45.7 | 45.14 | 45.31 | 45.48 | 45.66 | 45.7 | 45.66 | 45.69 | 45.45 | 45.67 | 45.76 | 45.7 | 45.65 | 45.64
37 | 45.47 | 45.35 | 45.59 | 31.44 | 31.25 | 31.6 | O |  | AVG | 45.55 | 40.43 | 42.4 | 45.32 | 45.38 | 45.47 | 45.5 | 45.47 | 42.28 | 43.12 | 45.37 | 45.49 | 45.5 | 45.54 | 45.74 | 40.83 | 42.41 | 45.2 | 45.36 | 45.49 | 45.59 | 45.59 | 41.52 | 42.64 | 45.51 | 45.66 | 45.57 | 45.52 | 45.53
38 | 45.5 | 45.46 | 45.6 | 31.48 | 31.39 | 31.6 | R | MW-3
39 | 45.47 | 45.38 | 45.46 | 31.34 | 31.21 | 31.43 |  |  | UP
40 | 42.28 | 39.64 | 45.51 | 25.64 | 20.87 | 31.46 | W |  | MIN | 31.49 | 17.64 | 17.63 | 30.98 | 31.17 | 31.25 | 31.39 | 31.21 | 20.87 | 20.69 | 31.33 | 31.51 | 31.55 | 31.66 | 31.61 | 20.79 | 20.58 | 31.1 | 31.24 | 31.49 | 31.61 | 31.63 | 19.44 | 19.26 | 31.49 | 31.78 | 31.58 | 31.56 | 31.52
41 | 43.12 | 39.61 | 45.25 | 27.55 | 20.69 | 31.43 | E |  | MAX | 31.87 | 31.79 | 31.1 | 31.32 | 31.44 | 31.6 | 31.6 | 31.43 | 31.46 | 31.43 | 31.61 | 31.72 | 31.76 | 31.95 | 31.97 | 31.78 | 31.3 | 31.48 | 31.67 | 31.85 | 31.87 | 31.83 | 31.83 | 31.62 | 31.85 | 31.95 | 31.88 | 31.75 | 31.7
42 | 45.37 | 45.25 | 45.41 | 31.46 | 31.33 | 31.61 | L |  | AVG | 31.72 | 22.77 | 26.34 | 31.23 | 31.33 | 31.44 | 31.48 | 31.34 | 25.64 | 27.55 | 31.46 | 31.6 | 31.63 | 31.82 | 31.85 | 24.88 | 27.31 | 31.31 | 31.45 | 31.75 | 31.78 | 31.75 | 25.5 | 27.24 | 31.68 | 31.91 | 31.72 | 31.62 | 31.6
43 | 45.49 | 45.4 | 45.52 | 31.6 | 31.51 | 31.72 | L
44 | 45.5 | 45.43 | 45.57 | 31.63 | 31.55 | 31.76
45 | 45.54 | 45.51 | 45.75 | 31.82 | 31.66 | 31.95 | T
46 | 45.74 | 45.59 | 45.83 | 31.85 | 31.61 | 31.97 | H
47 | 40.83 | 37.94 | 45.7 | 24.88 | 20.79 | 31.78 | R
48 | 42.41 | 37.94 | 45.14 | 27.31 | 20.58 | 31.3 | E
49 | 45.2 | 45.05 | 45.31 | 31.31 | 31.1 | 31.48 | E
50 | 45.36 | 45.18 | 45.48 | 31.45 | 31.24 | 31.67
51 | 45.49 | 45.42 | 45.66 | 31.75 | 31.49 | 31.85 | I
52 | 45.59 | 45.58 | 45.7 | 31.78 | 31.61 | 31.87 | N
53 | 45.59 | 45.6 | 45.66 | 31.75 | 31.63 | 31.83 | J
54 | 41.52 | 37.38 | 45.69 | 25.5 | 19.44 | 31.83 | E
55 | 42.64 | 37.36 | 45.45 | 27.24 | 19.26 | 31.62 | C
56 | 45.51 | 45.37 | 45.67 | 31.68 | 31.49 | 31.85 | T
57 | 45.66 | 45.64 | 45.76 | 31.91 | 31.78 | 31.95 | I
58 | 45.57 | 45.51 | 45.7 | 31.72 | 31.58 | 31.88 | O
59 | 45.52 | 45.52 | 45.65 | 31.62 | 31.56 | 31.75 | N
60 | 45.53 | 45.53 | 45.64 | 31.6 | 31.52 | 31.7
W
E
L
L

## SHIFT DATA
PERSONNEL LIST
|  | SHIFT CODE |  | OPERATOR NAME |  | CERTIFICATION NUMBER |  | SOCIAL SECURITY NUMBER
CHIEF OPERATORS
HOSTNICK, N. | CO# 3207-A | 3 |  | BAYLER, J. | 3 | CO# 4474-A | "A" |  | "A" | 4474 | 3207 | 2D | J. BAROFSKY | 5096-C
McGEARY, J. | CO# 4545-A | 1 |  | HOSTNICK, N. | 1 | CO# 3207-A | "A" |  | "A" | 3207 | 4545 | 5 | S. HULL | 5613-C
BAYLER, J. | CO# 4474-A | 2 |  | McGEARY, J. | 2 | CO# 4545-A | "A" |  | "A" | 4545 | 4474 | 4 | VACANT | X
POMEROY, D. | CO# 421-B | 5 |  | POMEROY, D. | 5 | CO# 421-B | "B" |  | "B" | 421 | 421 | 3 | J. TINKER | 3291-C
[12 empty] | 1 | G. SLAYTON | 2606-B
[12 empty] | 2 | H. WALKER | 4700-A
OPERATOR II' S
THOMAS, P. | CO# 12833 C | 2D |  | BAROFSKY, J. | 2D | CO# 5096-C | [5 empty] | 5 | J. BENTLEY | X
HULL, S. | CO# 5613-C | 4 |  | BENTLEY, J. | 4 | CO# 9366-C | [5 empty] | 1D | S. CURMODE | X
JONES, K. | CO# 2466-B | 5 |  | CURMODE, S. | 5 | CO# 9379-A | [5 empty] | 4 | K. HENDERSON | 5087-B
BENTLEY, J. | CO# 9366-C | 2 |  | HULL, S. | 2 | CO# 5613-C | [5 empty] | 3D | K. JONES | 2466-C
CURMODE, S. | CO# 9379-A | 3 |  | JONES, K. | 3 | CO# 2466-B | [5 empty] | 3 | G. KLEYNHANS | 7367-C
BAROFSKY, J. | CO# 5096-C | 1 |  | THOMAS, P. | 1 | CO# 12833 C | [5 empty] | 2 | A. MORROW | 9164-C
[12 empty] | 1 | J. RAINFORTH | 2718-C
OPERATOR I' S
HENDERSON, K. | CO# 13437-C | 3D |  | FREIDLAND, M. | 3D | CO# XXXX-X
SANDERS, C. | CO# 12817-C | 1 |  | HENDERSON, K. | 1 | CO# 13437-C
PEUGEOT, P. | CO# 9661-C | 3 |  | KOKLAS, D. | 3 | CO# 5087-B
KOKLAS, D. | CO# 5087-B | 5 |  | NOBERT, B. | 5 | CO# 13506-C
FREIDLAND, M. | CO# XXXX-X | 2 |  | PEUGEOT, P. | 2 | CO# 9661-C
VERBOSH, R. | CO# 13500-C | 1D |  | SANDERS, C. | 1D | CO# 12817-C
NOBERT, B. | CO# 13506-C | 4 |  | VERBOSH, R. | 4 | CO# 13500-C
|  | 4 | 1 | BERNARDI, J | 4 | CO# XXXX-X
|  | 3 | 2 | FREIDLAND, M. | 3 | CO# 13437-C
|  | 5A | 3 | FUTURE, 5A | 5A | CO# XXXX-X
|  | 1 | 4 | HENDERSON, K. | 1 | CO# 5087-B
|  | 2 | 5 | KOKLAS, D. | 2 | CO# 13506-C
|  | 5 | 6 | NOBERT, B. | 5 | CO# 9661-C
|  | 4A | 7 | PEUGEOT, P. | 4A | CO# 12817-C
|  | 1D | 8 | SANDERS, C. | 1D | CO# 13500-C
|  | 3D | 9 | VERBOSH, R. | 3D | CO# 12667-C

## COVER PAGE
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
|  | FEBRUARY |  | 2004
| OPERATOR | TITLE | CERTIFICATE # | TOTAL COST |  |  | 66057.05
1 ST SHIFT | HOSTNICK, N. | CHIEF | CO# 3207-A | PEAK TO FLOW RATIO |  |  | 1.6315
2230-0630 | THOMAS, P. | OP. II | CO# 12833 C
| HENDERSON, K. | OP. I | CO# 13437-C |  | TOTAL SUSPENDED SOLIDS
| SANDERS, C. | OP. I DEWAT | CO# 12817-C |  |  |  | LBS/DAY
|  |  |  | RAW INFLUENT |  |  | 35991.6181
2 ND SHIFT |  |  |  | FINAL EFFLUENT |  |  | 5998.603
0630-1430 | McGEARY, J. | CHIEF | CO# 4545-A |  | TOTAL CBOD
| HULL, S. | OP. II RELIEF | CO# 5613-C |  |  |  | LBS/DAY
| BAROFSKY, J. | OP. II DEWAT | CO# 5096-C | RAW INFLUENT |  |  | 27789.7475
| PEUGEOT, P. | OP. I RELIEF | CO# 9661-C | FINAL EFFLUENT |  |  | 986.5377
CHEMICALS
3 RD SHIFT | BAYLER, J. | CHIEF | CO# 4474-A |  |  | COST | POUNDS
1430-2230 | JONES, K. | OP. II | CO# 2466-B | HYDROGEN PEROXIDE |  | 5079.195 | 36410
| KOKLAS, D. | OP. I | CO# 5087-B | CHLORINE |  | 4690.5 | 31800
| FREIDLAND, M. | OP. I DEWAT | CO# XXXX-X | POLYMER |  | 7122.36 | 11676
SLUDGE REMOVED
4 TH SHIFT | [6 empty] | TONS
WEEKEND | BENTLEY, J. | OP. II | CO# 9366-C | DRY TONS |  |  | 442.2527
2230-1030 | VERBOSH, R. | OP. I | CO# 13500-C |  | ENERGY
| 0 | OPI | 0 |  |  | COST | KILOWATTS
5 TH SHIFT | POMEROY, D. | CHIEF | CO# 421-B | FPL CONSUMPTION |  | 49164.995 | 893909
WEEKEND | CURMODE, S. | OP. II | CO# 9379-A
1030-2230 | NOBERT, B. | OP. I | CO# 13506-C | POPULATION EQUIVALENCE |  |  | 163469.103
This Monthly Operation Report prepared by: |  |  | BAYLER, J. | CO# 4474-A
State DEP Plant Classification: Class "A" Level "II"
I certify that I am familiar with the information contained in this report and that to the best of my knowledge and
belief, such information is true, complete and accurate.
Facilitiy Manager's Signature: ____________________________________ CO# __________________
Division Manager's Signature: ____________________________________ CO# __________________
Please direct all inquiries reguarding this report to the City Official Mailing Address:
Director of Public Services |  |  | Phone (954) 776-5151
City of Fort Lauderdale
P.O. Drawer 14250 |  |  | Copies mailed: Date ________________ To: DEP _____
Fort Lauderdale, Florida | [5 empty] | DNRP _____
33302
PAGE 1

## PRINT PAGES
UNDERGROUND INJECTION CONTROL SECTION
[29 empty] | MONTHLY OPERATING REPORT DATA SUMMARY | [13 empty] | DEP From # 17-801.900 (1) | [11 empty] | DEP From # 17-801.900 (1) | [19 empty] | DAILY SAMPLE RESULTS - PART B
[25 empty] | FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT DATE: |  | FEBRUARY | 2004 | [8 empty] | Form Title:Domestic Wastewater Treatment | [11 empty] | Form Title:Domestic Wastewater Treatment
[25 empty] | I.D. NUMBER: 5006M02066 |  |  |  |  | CHIEF OPERATOR: |  |  | BAYLER, J. | CO# 4474-A | [8 empty] | Plant Monthly Operating Report | [11 empty] | Plant Monthly Operating Report | [15 empty] | Permit Number: |  | FLA041378 |  |  |  |  | Three-month Average Daily Flow: | [5 empty] | 34.764
[25 empty] | TELEPHONE NUMBER: (954) 523-1002 | [17 empty] | Effective Date: July 1, 1991 | [11 empty] | Effective Date: July 1, 1991 | [15 empty] | Monitoring Period |  | From: | 2004-02-01 | To: | 2004-03-02 |  | (TMADF):/Permitted Capacity)x100: | [5 empty] | 62.41%
[19 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [9 empty] | INJECTION WELL DATA | [13 empty] | DEP Application No. __________________ | [11 empty] | DEP Application No. __________________ | [11 empty] | Department of Natural Resource Protection
[5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [13 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [6 empty] | IW-1 | IW-2 |  | IW-3 |  | IW-4 | IW-5 | [35 empty] | Laboratory/Licensing/Enforcement |  |  |  | Flow | Flow | Flow | Flow | Flow | Flow | CBOD5 | CBOD5 | TSS | TSS | pH | pH | TDS | NH-3 | TKN | pH | cond. | temp. | TP
[5 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [13 empty] | MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING | [5 empty] | PERMIT/CERTIFICATION NUMBER: | 0054569-142-UO | 0054569-142-UO |  | 0054569-142-UO |  | 0054569-142-UO | 0054569-142-UO | [19 empty] | DOMESTIC WASTEWATER TREATMENT PLANT | [11 empty] | BROWARD COUNTY DEPARTMENT OF NATURAL RESOURCE PROTECTION | [5 empty] | 218 S. W. 1st Avenue |  |  | (MGD) | (MGD) | (MGD) | (MGD) | (MGD) | (mg/l) | (mg/l) | (mg/l) | (mg/l) | (Min) | (Max) | mg/L | mg/L | mg/L | units | umho/ | F | mg/L
[5 empty] | MONTHLY OPERATIONAL REPORT | [13 empty] | MONITORING WELL ONE |  |  |  | 1/07/04 thru 1/06/09 |  | PERMIT EXPIRATION DATE: | 2009-01-06 | 2009-01-06 |  | 2009-01-06 |  | 2009-01-06 | 2009-01-06 | [19 empty] | MONTHLY OPERATING REPORT | [11 empty] | WASTEWATER TREATMENT PLANT | [5 empty] | Fort Lauderdale, FL 33301 | [17 empty] | cm
[5 empty] | PROCESS DATA | [11 empty] | MW-1 | I.D. #: 5066A11311 |  |  | PERMIT # 0054569-142-UO |  |  |  | CASING DEPTH | 2799' | 2798' |  | 2800' |  | 2804' | 2818' | [8 empty] | DOMESTIC WASTEWATER TREATMENT PLANT |  |  |  |  | (34) | [8 empty] | MONTH: | FEBRUARY |  | YEAR: | 2004 |  |  |  |  | MONTHLY SLUDGE REPORTS | [5 empty] | Tel. No. (954) 765-4804 | Code | 50050 | 50050 | 50050 | 50050 | 50050 | 50050 | 80082 | 80082 | 00530 | 00530 | 00400 | 00400
| RUN DATE | [14 empty] | RUN DATE | [8 empty] | TOTAL DEPTH | 3513' | 3518' |  | 3977' |  | 3305' | 3462' | [8 empty] | MONTHLY OPERATING REPORT |  |  |  |  | DAY OF | FLOW | CHLORINE | CHLORINE | CBOD5 | TSS | CBOD5 | TSS | PH |  |  | EFFLUENT NUTRIENTS (MG/L) |  |  | I. | [10 empty] | Mon. Site | INF-001 | EFF-002 | EFF-003 | EFF-004 | EFF-005 | EFF-006 | INF-002 | EFF-001 | INF-002 | EFF-001 | EFF-001 | EFF-001
| 2026-07-30 | [14 empty] | 2026-07-30 |  | UPPER MONITOR ZONE |  |  |  |  | LOWER MONITOR ZONE |  | AVERAGE DAILY FLOW: | 9.0268 | 9.5652 |  | 8.03 |  | 3.9148 | 8.2244 | MGD | [7 empty] | Part II - General Information |  |  |  |  | THE |  | RESIDUAL | RESIDUAL | INFLUENT | INFLUENT | EFFLUENT | EFFLUENT | EFFLUENT | TKN | NH3-N | NITRATE | TOTAL | FECAL | Plant Name: | GEORGE T. LOHMEYER WASTEWATER TREATMENT FACILITY | [6 empty] | MONTH: | FEBRUARY |  | 1 | 64.329 | 13.46 | 13.62 | 11.7 | 11.99 | 11.07 | 30 |  | 30 | 22 | 6.6 | 6.6 | 1030 | 7.3 | 12 | 6.6 | 2060 | 77 | 1.1
[17 empty] | MIN | MAX | AVG |  |  | MIN | MAX | AVG | **MAX DAILY FLOW PER MO (mg): | 13.46 | 13.62 |  | 11.7 |  | 13.65 | 11.07 | MG | [12 empty] | MONTH | (MGD) | AFTER | AFTER DE- | [8 empty] | P | COLIFORM | II. | [7 empty] | YEAR: | 2004 |  | 2 | 57.786 | 11.39 | 11.57 | 9.81 | 13.65 | 9.71 | 60 |  | 84 | 44 | 6.6 | 6.6 | 943 |  |  | 6.7 | 1926 | 79
| FEBRUARY | INFLUENT | HOURLY | INFLUENT | INFLUENT | RAS | PERCENT | WAS | RAIN | Sufates | [5 empty] | FEBRUARY | FT HEAD | FT HEAD | FT HEAD |  |  | FT HEAD | FT HEAD | FT HEAD | ** PEAK HR FLOW (MGD) ON MAX DAY: | 16.0724 | 17.0087 |  | 14.2124 |  | 6.4109 | 14.5521 | MGD |  | (1) Month: |  | FEBRUARY |  | Year: | 2004 |  | Parameter | Units | STORET | Value |  |  | CONTACT | CHLORINATION | MG/L | MG/L | MG/L | MG/L | [6 empty] | A) | Sludge Treatment Provided: |  |  |  |  | B) | Sludge Dewater Processes |  |  |  | 3 | 51.88 | 10.22 | 10.39 | 8.76 | 12.38 | 8.74 | 49 |  | 108 | 29 | 6.5 | 6.8 | 891 |  |  | 6.6 | 2090 | 78
| 2004 | FLOW | MAXIMUM | MAXIMUM | MINIMUM | FLOW | RAS | FLOW | INCHES | [6 empty] | 2004 | ABOVE | ABOVE | ABOVE |  |  | ABOVE | ABOVE | ABOVE | MAX SUSTAINED INJECTION PRESSURE: | 76.1 | 79.4 |  | 81.5 |  | 74.5 | 80.8 | PSIG |  | (2) Plant's DEP Identification Number: |  |  |  |  | 5006M02066 |  |  |  | Code |  | 1 | 64.329 | 0.4 |  | 30 | 30 |  | 22 | 6.6 | 12 | 7.3 | 0.3 | 1.1 | 6400 |  |  | Aerobic Digestion | [5 empty] | Thickner |  |  | 4 | 47.76 | 6.65 | 10.36 | 8.66 | 12.32 | 8.63 | 69 |  | 126 | 15 | 6.6 | 6.7 | 970 | 9.56 | 13.06 | 6.7 | 2100 | 78 | 0.892
|  | MGD | MGD | MGD | MGD | MGD |  | MGD | [8 empty] | NGVD | NGVD | NGVD |  |  | NGVD | NGVD | NGVD | MONTHLY AVG. INJECTION PRESSURE: | 49.5603 | 49.4124 |  | 50.0183 |  | 41.03 | 49.0148 | PSIG |  | (3) Plant Name: |  |  |  | George T. Lohmeyer Regional Wastewater |  |  | (16) Monthly average daily flow | mgd | 050053 | 39.43 | 2 | 57.786 | 0.3 |  | 60 | 84 |  | 44 | 6.7 |  |  |  |  | 27 |  |  | Anaerobic Digestion | [5 empty] | DGA___X___Filter Press |  |  | 5 | 45.168 | 7.34 | 11.57 | 9.9 | 4.84 | 9.83 | 84 |  | 84 | 14 | 6.5 | 6.8 | 1046 | 9.56 | 13.06 | 6.6 | 2180 | 79 | 0.892
| 1 | 64.329 | 2.896 | 77.282 | 43.992 | 10.589 | 16.46% | 0.163 | 3.69 |  |  | 1 |  |  |  | 1 | 48.28 | 48.61 | 48.55 |  |  | 41.59 | 42.07 | 41.76 | *** MAX INJECTION PRESSURE PERMITTED: | 99 | 99 |  | 99 |  | 99 | 99 | PSIG |  |  |  |  | Treatment Facility |  |  |  | (17) Permitted capacity | mgd | - | 55.7 | 3 | 51.88 | 0.4 |  | 49 | 108 |  | 29 | 6.6 |  |  |  |  | 18 |  |  | Other | [5 empty] | Centrifuge Drying Beds, Bed #______ |  |  | 6 | 43.6 | 10.95 | 11.14 | 9.73 | 0.13 | 9.78 | 82 |  | 60 | 30 | 6.4 | 7 | 1009 | 11.35 | 14.95 | 6.8 | 2210 | 79 | 0.9
| 2 | 57.786 | 2.643 | 71.034 | 42.069 | 10.118 | 17.51% | 0.325 | 0 |  |  | 2 |  |  |  | 2 | 45.71 | 48.55 | 48.5 |  |  | 33.99 | 41.69 | 36.86 | ***NOTE: (INJECTION PRESSURE NOT TO EXCEED 66% TESTED PRESSURE | [9 empty] | (4) Plant Address: |  |  | 1765 S.E. 18th Street at |  |  |  | (18) Three-month average daily flow | mgd | - | 34.764 | 4 | 47.76 | 0.4 |  | 69 | 126 |  | 15 | 6.7 | 13.06 | 9.56 | 0.115 | 0.892 | 18 | [8 empty] | Heat Treatment____No Treatment |  |  | 7 | 41.587 | 10.38 | 10.54 | 9.23 | 0.13 | 9.3 | 100.2 |  | 62 | 19 | 6.4 | 6.8 | 1010 | 8.47 | 13.89 | 6.6 | 2260 | 79 | 0.835
| 3 | 51.88 | 2.402 | 65.588 | 30.407 | 10.207 | 19.67% | 0.27 | 0 |  |  | 3 |  |  |  | 3 | 46.04 | 48.76 | 47.69 |  |  | 33.98 | 41.62 | 38.89 | TESTED CASING PRESSURE DURING MIT | 150 | 150 |  | 150 |  | 150 | 150 | PSIG |  |  |  |  | Eisenhower Boulevard |  |  |  | (19) Percent of permitted capacity | % | - | 62.41% | 5 | 45.168 | 0.9 |  | 84 | 84 |  | 14 | 6.6 | 13.06 | 9.56 | 0.115 | 0.892 | 27 | [7 empty] | x | Other: | LIME STABILIZATION |  | 8 | 39.429 | 9.82 | 9.97 | 8.73 | 0.12 | 8.83 | 91 |  | 80 | 14 | 6.4 | 6.7 | 1052 | 11.04 | 14.44 | 6.6 | 2300 | 78 | 0.957
| 4 | 47.76 | 2.243 | 61.935 | 26.145 | 10.618 | 22.23% | 0.294 | 0 |  |  | 4 |  |  |  | 4 | 48.23 | 48.51 | 48.44 |  |  | 41.36 | 41.66 | 41.52 | [10 empty] | (5) City: |  | Fort Lauderdale |  |  |  |  | (20) CBOD5 Effluent | mg/L | 080082 | 3 | 6 | 43.6 | 0.6 |  | 82 | 60 |  | 30 | 6.8 | 14.95 | 11.35 | 0.077 | 0.9 | 0 | [9 empty] | CLASS "AA" |  | 9 | 38.556 | 9.78 | 9.52 | 8.73 | 0.13 | 8.82 | 84 |  | 102 | 20 | 6.4 | 6.7 | 1078 |  |  | 6.6 | 2320 | 77
| 5 | 45.168 | 2.168 | 61.006 | 21.242 | 11.487 | 25.43% | 0.36 | 0 |  |  | 5 |  |  |  | 5 | 48.25 | 48.54 | 48.45 |  |  | 41.44 | 41.66 | 41.5 |  |  | MONITORING WELL DATA | [7 empty] | (6) County: |  | Broward |  |  |  |  | (21) CBOD5 Effluent | lbs/day | - | 986.5377 | 7 | 41.587 | 0.6 |  | 100.2 | 62 |  | 19 | 6.6 | 13.89 | 8.47 | 0.861 | 0.835 | TNTC | III. | Final Sludge Disposal: | [7 empty] | RMF-Azurix (Nutri-Cycle) |  | 10 | 37.403 | 9.54 | 9.69 | 8.5 | 0.13 | 8.6 | 115 |  | 230 | 18 | 6.3 | 6.7 | 1127 |  |  | 6.5 | 2360 | 79
| 6 | 43.6 | 2.066 | 60.653 | 20.056 | 11.516 | 26.41% | 0.171 | 0.21 |  |  | 6 |  |  |  | 6 | 48.28 | 48.66 | 48.46 |  |  | 41.47 | 41.75 | 41.57 |  | MW-1 | MW-2 |  | MW-3 |  | RMW-1 |  |  |  | (7) Phone Number: |  |  | (954) 523-1002 |  |  |  | (22) TSS Effluent | mg/L | 900201 | 18.2414 | 8 | 39.429 | 0.6 |  | 91 | 80 |  | 14 | 6.6 | 14.44 | 11.04 | 0.213 | 0.957 | TNTC | A) | Liquid Sludge Disposal: | [9 empty] | 11 | 37.151 | 9.39 | 9.52 | 8.01 | 0.31 | 8.42 | 90.5 |  | 166 | 19 | 6.5 | 6.8 | 877 | 11.62 | 15.18 | 6.4 | 2390 | 80 | 0.879
| 7 | 41.587 | 2.034 | 58.442 | 18.454 | 10.964 | 26.36% | 0 | 0 |  |  | 7 |  |  |  | 7 | 48.38 | 48.64 | 48.51 |  |  | 41.51 | 41.87 | 41.64 | PERMIT NUMBER | 0054569-142-UO | 0054569-142-UO |  | 0054569-142-UO |  | 0054569-142-UO |  |  |  | (8) Permit Number: |  |  | FLA041378 |  |  |  | (23) TSS Effluent | lbs/day | - | 5998.603 | 9 | 38.556 | 0.8 |  | 84 | 102 |  | 20 | 6.6 |  |  |  |  | 0 |  | WEEK OF | FEBRUARY | GALLONS | % SOLIDS |  |  | HAULERS |  |  | DISPOSAL SITE | 12 | 36.39 | 9.42 | 9.57 | 8.4 | 4.94 | 2.88 | 106 |  | 68 | 13 | 6.3 | 6.8 | 1140 | 13.68 | 17.21 | 6.5 | 2350 | 79 | 0.85
| 8 | 39.429 | 1.951 | 56.84 | 17.942 | 8.528 | 21.63% | 0.083 | 0 |  |  | 8 |  |  |  | 8 | 48.22 | 48.44 | 48.38 |  |  | 41.42 | 41.64 | 41.48 | UPPER MONITORING INTERVAL | 1288'-1320' | 1300'-1344' |  | 1300'-1349' |  | 1300'-1339' |  | Ft. bls. |  | (9) Plant Type: |  |  | Oxygen Activated Sludge |  |  |  | (24) Minimum pH |  | - | 6.2 | 10 | 37.403 | 0.6 |  | 115 | 230 |  | 18 | 6.5 |  |  |  |  | 0 | [11 empty] | 13 | 35.781 | 8.88 | 9.01 | 6.14 | 11.43 | ER | 78 |  | 124 | 17 | 6.3 | 6.6 | 1109 | 13.29 | 17.06 | 6.4 | 2360 | 80 | 1.39
| 9 | 38.556 | 1.958 | 56.327 | 13.681 | 10.993 | 28.51% | 0.47 | 0 |  |  | 9 |  |  |  | 9 | 46.46 | 48.47 | 47.44 |  |  | 36.72 | 41.77 | 39.01 | MONTHLY MAX DAILY PRESSURE | 48.86 | 48.86 |  | 31.97 |  | 62.89 |  | FT. HEAD |  | (10) Test Site Identification Number: |  |  |  |  | 5006X10744 |  | (25) Maximum pH |  | - | 7 | 11 | 37.151 | 0.4 |  | 90.5 | 166 |  | 19 | 6.4 | 15.18 | 11.62 | 0.19 | 0.879 | 0 |  | FIRST THRU SEVENTH | [9 empty] | 14 | 35.354 | 8.98 | 9.15 | 5.1 | 11.6 | ER | 89 |  | 124 | 13 | 6.2 | 6.3 | 1109 | 13.09 | 16.9 | 6.3 | 2360 | 80 | 1.43
| 10 | 37.403 | 1.831 | 53.571 | 15.027 | 10.836 | 28.97% | 0.471 | 0 |  |  | 10 |  |  |  | 10 | 46.8 | 48.58 | 47.95 |  |  | 36.71 | 41.69 | 39.88 | MONTHLY MIN DAILY PRESSURE | 45.71 | 45.71 |  | 17.63 |  | -6999 |  | FT. HEAD |  | (11) Fecal Coliform Method | [6 empty] | (26) Total N | mg/L | 000600 | 16.0112 | 12 | 36.39 | 0.6 |  | 106 | 68 |  | 13 | 6.5 | 17.21 | 13.68 | 0.202 | 0.85 | 0 | [11 empty] | 15 | 34.636 | 4.66 | 7.93 | 7.02 | 10.21 | 3.87 | 103 |  | 122 | 9 | 6.2 | 6.5 | 1171 | 11.67 | 16.64 | 6.3 | 2500 | 80 | 0.836
| 11 | 37.151 | 1.807 | 53.828 | 13.938 | 11.753 | 31.64% | 0.379 | 0 |  |  | 11 |  |  |  | 11 | 48.36 | 48.58 | 48.48 |  |  | 41.52 | 41.77 | 41.57 | TDS (MONTHLY AVERAGE) | 7323 | 7166.75 |  | 31195.5 |  | 5520 |  | mg/l |  |  | XX | Membrane Filter |  |  |  |  | (27) TKN | mg/L | 000625 | 15.7605 | 13 | 35.781 | 0.6 |  | 78 | 124 |  | 17 | 6.4 | 17.06 | 13.29 | 0.165 | 1.39 | 0 |  | EIGHT THRU FORTEENTH | [9 empty] | 16 | 35.04 | 8.4 | 2.12 | 7.55 | 8.9 | 7.51 | 134 |  | 144 | 18 | 6.4 | 7 | 1129 |  |  | 6.6 | 2510 | 80
| 12 | 36.39 | 1.743 | 52.482 | 13.777 | 11.517 | 31.65% | 0.424 | 0 |  |  | 12 |  |  |  | 12 | 48.36 | 48.61 | 48.51 |  |  | 41.54 | 41.8 | 41.6 | CHLORIDE (MONTHLY AVERAGE) | 4037.5 | 3950 |  | 18500 |  | 3150 |  | mg/l |  |  |  | Most Probable Number |  |  |  |  | (28) Ammonia (NH3 - N) | mg/L | 000610 | 11.9529 | 14 | 35.354 | 7 |  | 89 | 124 |  | 13 | 6.3 | 16.9 | 13.09 | 0.144 | 1.43 | 0 |  | FIFTHTEENTH THRU | [9 empty] | 17 | 35.135 | 7.69 | 3.91 | 7.12 | 8.28 | 7.88 | 83 |  | 84 | 21 | 6.3 | 6.7 | 1169 |  |  | 6.6 | 2630 | 80
| 13 | 35.781 | 1.808 | 51.969 | 16.501 | 10.831 | 30.27% | 0.174 | 0 |  |  | 13 |  |  |  | 13 | 48.34 | 48.59 | 48.51 |  |  | 41.56 | 41.87 | 41.65 | AMMONIA-N (MONTHLY AVERAGE) | 0.869 | 2.7635 |  | 1.37 |  | 0.627 |  | mg/l |  | (12) Type of Effluent Disposal or Reclaimed Water Reuse | [6 empty] | (29) Nitrate | mg/L | 071850 | 0.25071 | 15 | 34.636 | 0.9 |  | 103 | 122 |  | 9 | 6.3 | 16.64 | 11.67 | 0.87 | 0.836 | 179 |  | TWENTY SECOND | [9 empty] | 18 | 33.933 | 7.7 | 9.25 | 8.06 | 0.19 | 8.15 | 93 |  | 100 | 24 | 6.4 | 6.8 | 1231 | 14.34 | 18.12 | 6.6 | 2350 | 79 | 1.59
| 14 | 35.354 | 1.822 | 53.283 | 13.489 | 11.894 | 33.64% | 0 | 0 |  |  | 14 |  |  |  | 14 | 48.46 | 48.7 | 48.52 |  |  | 41.62 | 41.93 | 41.73 | TKN (MONTHLY AVERAGE) | 1.5625 | 1.62 |  | 2.105 |  | 1.21 |  | mg/l |  |  |  | Deep Well Injection |  |  |  |  | (30) Total Phosphorus | mg/L | 000665 | 0.97576 | 16 | 35.04 | 0.6 |  | 134 | 144 |  | 18 | 6.6 |  |  |  |  | 143 |  | TWENTY THIRD THRU | [9 empty] | 19 | 35.089 | 9.18 | 9.38 | 6.89 | 0.12 | 8.17 | 91 |  | 120 | 15 | 6.3 | 6.5 | 1223 | 13.87 | 18.11 | 6.5 | 2410 | 78 | 0.963
| 15 | 34.636 | 1.706 | 51.072 | 14.711 | 11.422 | 32.98% | 0.123 | 0 |  |  | 15 |  |  |  | 15 | 48.37 | 48.76 | 48.57 |  |  | 41.62 | 41.96 | 41.79 | pH (MONTHLY AVERAGE) | 8.045 | 8.0025 |  | 7.485 |  | 8.34 |  | Std units |  | (13) Limited Wet Wheather Discharge Activated | [6 empty] | (31) Minimum Chlorine Residual | mg/L | - | 0.3 | 17 | 35.135 | 0.3 |  | 83 | 84 |  | 21 | 6.6 |  |  |  |  | 9 |  | THIRTY FIRST | [9 empty] | 20 | 35.694 | 8.19 | 9.36 | 8.18 | 0.12 | 8.23 | 86 |  | 102 | 15 | 6.3 | 6.9 | 1332 | 13.9 | 17.65 | 6.5 | 2510 | 79 | 0.927
| 16 | 35.04 | 1.783 | 52.963 | 14.162 | 9.404 | 26.84% | 0.521 | 0 |  |  | 16 |  |  |  | 16 | 46.88 | 48.62 | 47.69 |  |  | 36.4 | 41.7 | 38.52 | CONDUCTIVITY (MONTHLY AVERAGE) | 12417.5 | 12150 |  | 48750 |  | 9870 |  | umho/cm |  |  |  | YES |  | XX | Not Applicable |  | (32) Maximum Chlorine Residual | mg/L | - | 7 | 18 | 33.933 | 0.5 |  | 93 | 100 |  | 24 | 6.6 | 18.12 | 14.34 | 0.163 | 1.59 | 9 | [11 empty] | 21 | 35.699 | 11.74 | 12.09 | 0.23 | 0.13 | 10.49 | 98 |  | 136 | 12 | 6.3 | 6.4 | 1360 | 12.37 | 16.15 | 6.4 | 2580 | 79 | 0.874
| 17 | 35.135 | 1.804 | 57.16 | 12.111 | 9.988 | 28.43% | 0.509 | 0 |  |  | 17 |  |  |  | 17 | 47.16 | 48.56 | 48.01 |  |  | 36.22 | 41.48 | 39.59 | FECAL COLIFORM (MONTHLY AVERAGE) | 0 | 0 |  | 0 |  | 0 |  | # col/100ml |  |  |  | NO |  |  |  |  | (33) Other Effluent Parameters |  |  |  | 19 | 35.089 | 0.4 |  | 91 | 120 |  | 15 | 6.5 | 18.11 | 13.87 | 0.242 | 0.963 | 89 | B) | Solid Sludge Hauled from Plant: | [9 empty] | 22 | 35.057 | 9.43 | 9.66 | 5.99 | 0.13 | 8.49 | 78 |  | 96 | 14 | 6.3 | 6.4 | 1335 | 12.27 | 15.94 | 6.4 | 2610 | 80 | 0.851
| 18 | 33.933 | 1.811 | 50.88 | 12.464 | 8.355 | 24.62% | 0.351 | 0 |  |  | 18 |  |  |  | 18 | 48.14 | 48.46 | 48.31 |  |  | 41.27 | 41.55 | 41.44 | TEMPERATURE (MONTHLY AVERAGE) | 73.5 | 71.75 |  | 70.25 |  | 69 |  | deg. F | [12 empty] | 20 | 35.694 | 0.6 |  | 86 | 102 |  | 15 | 6.5 | 17.65 | 13.9 | 0.09 | 0.927 | 152 |  | WEEK OF | FEBRUARY | TONS |  | % SOLIDS |  | HAULERS |  |  | DISPOSAL SITE | 23 | 34.886 | 9.65 | 8.45 | 8.54 | 0.16 | 7.08 | 82 |  | 124 | 15 | 6.3 | 6.5 | 1323 |  |  | 6.4 | 2460 | 80
| 19 | 35.089 | 1.896 | 54.308 | 8.875 | 9.195 | 26.2% | 0.522 | 0 |  |  | 19 |  |  |  | 19 | 48.13 | 48.55 | 48.42 |  |  | 41.33 | 41.69 | 41.5 | TOTAL PHOSPHOROUS (MONTHLY AVG.) | 0.05 | 0.05 |  | 0.05 |  | 0.05 |  | mg/l |  | (14) Cumulative Days of Wet Wheather Discharge | [10 empty] | 21 | 35.699 | 0.5 |  | 98 | 136 |  | 12 | 6.4 | 16.15 | 12.37 | 0.108 | 0.874 | 0 | [10 empty] | CSLOL Inc. | 24 | 34.651 | 9.17 | 9.34 | 8.27 | 0.13 | 6.49 | 105 |  | 104 | 18 | 6.3 | 6.5 | 1345 |  |  | 6.4 | 2590 | 80
| 20 | 35.694 | 1.789 | 51.873 | 12.079 | 11.512 | 32.25% | 0.192 | 0 |  |  | 20 |  |  |  | 20 | 48.27 | 48.66 | 48.47 |  |  | 41.55 | 41.83 | 41.61 | SULFATE (MONTHLY AVERAGE) | 887.5 | 862.5 |  | 2500 |  | 900 |  | mg/l |  |  |  | N/A | [8 empty] | 22 | 35.057 | 0.6 |  | 78 | 96 |  | 14 | 6.4 | 15.94 | 12.27 | 0.318 | 0.851 | 9 |  | FIRST THRU SEVENTH |  | 575 |  | 17.1225 |  | AZURIX |  |  | Okeechobee, FL | 25 | 35.845 | ER | 9.74 | ER | 0.13 | 8.55 | 82 | 3 | 140 | 12 | 6.4 | 6.5 | 1335 | 13.75 | 17.23 | 6.5 | 2520 | 80 | 0.834
| 21 | 35.699 | 1.914 | 55.366 | 13.393 | 11.417 | 31.98% | 0 | 0 |  |  | 21 |  |  |  | 21 | 48.35 | 48.65 | 48.49 |  |  | 41.65 | 42.12 | 41.85 | C.O.D. (MONTHLY AVERAGE) | 145 | 142.5 |  | 800 |  | 130 |  | mg/l |  | (15) Plant Staffing: | [10 empty] | 23 | 34.886 | 0.4 |  | 82 | 124 |  | 15 | 6.4 |  |  |  |  | 18 | [10 empty] | CSLOL Inc. | 26 | 38.83 | 6.31 | 11.24 | 9.79 | 0.57 | 9.7 | 42 | 5 | 76 | 22 | 6.4 | 6.5 | 1263 | 12.32 | 15.6 | 6.5 | 2360 | 80 | 0.867
| 22 | 35.057 | 1.804 | 52.706 | 13.136 | 11.097 | 31.65% | 0.181 | 0 |  |  | 22 |  |  |  | 22 | 48.31 | 48.58 | 48.48 |  |  | 41.63 | 42.03 | 41.73 | IRON (MONTHLY AVERAGE) | 0.8675 | 1.2875 |  | 0.05 |  | 0.33 |  | mg/l | [12 empty] | 24 | 34.651 | 0.6 |  | 105 | 104 |  | 18 | 6.4 |  |  |  |  | 0 |  | EIGHT THRU FORTEENTH |  | 675 |  | 18.296 |  | AZURIX |  |  | Okeechobee, FL | 27 | 36.605 | 9.34 | 9.45 | 8.35 | 0.12 | 8.38 | 76 | 2 | 134 | 15 | 6.4 | 6.5 | 1270 | 13.22 | 16.42 | 6.4 | 2290 | 79 | 0.865
| 23 | 34.886 | 1.72 | 51.296 | 11.855 | 11.832 | 33.92% | 0.536 | 0 |  |  | 23 |  |  |  | 23 | 46.09 | 48.56 | 47.37 |  |  | 29.21 | 41.93 | 35.59 | SULFIDE (MONTHLY AVERAGE) | #DIV/0! | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | mg/l |  |  | Day Shift Operator: |  |  | Class | "A" | Cert. No. | 4545 |  |  |  | 25 | 35.845 | 0.5 |  | 82 | 140 | 3 | 12 | 6.5 | 17.23 | 13.75 | 0.28 | 0.834 | 0 |  | FIFTHTEENTH THRU | [8 empty] | CSLOL Inc. | 28 | 35.216 | 9.48 | 9.82 | 8.7 | 0.12 | 5.72 | 99 | 3 | 144 | 20 | 6.3 | 6.4 | 1158 | 11.57 | 15.03 | 6.4 | 2260 | 79 | 1.02
| 24 | 34.651 | 1.704 | 52.995 | 14.034 | 11.52 | 33.25% | 0.504 | 0 |  |  | 24 |  |  |  | 24 | 46.47 | 48.74 | 47.84 |  |  | 29.82 | 41.61 | 37.48 | LOWER MONITORING INTERVAL | 1449'-1557' | 1970'-2025' |  | 1970'-2027' |  | 1500'-1600' |  | Ft. bls | [12 empty] | 26 | 38.83 | 0.6 |  | 42 | 76 | 5 | 22 | 6.5 | 15.6 | 12.32 | 0.275 | 0.867 | 18 |  | TWENTY SECOND |  | 750 |  | 18.296 |  | AZURIX |  |  | Okeechobee, FL | 29 | 34.979 | 5.61 | 10.03 | 8.75 | 0.12 | 8.74 | 71 | 2 | 100 | 12 | 6.3 | 6.4 | 1266 | 12.77 | 16.33 | 6.4 | 2350 | 79 | 0.739
| 25 | 35.845 | 1.787 | 51.296 | 14.034 | 11.737 | 32.74% | 0.394 | 0.85 |  |  | 25 |  |  |  | 25 | 48.51 | 48.83 | 48.67 |  |  | 41.57 | 41.88 | 41.64 | MONTHLY MAX DAILY PRESSURE | 42.12 | 42.12 |  | 45.83 |  | 62.97 |  | FT. HEAD |  |  | Evening Shift Operator: |  |  | Class | "A" | Cert. No. | 4474 |  |  |  | 27 | 36.605 | 0.7 |  | 76 | 134 | 2 | 15 | 6.4 | 16.42 | 13.22 | 0.133 | 0.865 | 0 |  | TWENTY THIRD THRU | [8 empty] | CSLOL Inc. | 30
| 26 | 38.83 | 1.85 | 51.905 | 17.91 | 11.064 | 28.49% | 0.587 | 0.18 |  |  | 26 |  |  |  | 26 | 48.63 | 48.86 | 48.72 |  |  | 41.71 | 42.04 | 41.83 | MONTHLY MIN DAILY PRESSURE | 29.21 | 29.21 |  | 37.36 |  | -6999 |  | FT. HEAD | [12 empty] | 28 | 35.216 | 0.7 |  | 99 | 144 | 3 | 20 | 6.4 | 15.03 | 11.57 | 0.206 | 1.02 | 0 |  | THIRTY FIRST |  | 750 |  | 17.274 |  | AZURIX |  |  | Okeechobee, FL | 31
| 27 | 36.605 | 1.807 | 52.77 | 14.771 | 9.55 | 26.09% | 0.274 | 0 |  |  | 27 |  |  |  | 27 | 48.43 | 48.77 | 48.57 |  |  | 41.56 | 41.85 | 41.68 | TDS (MONTHLY AVERAGE) | 9255 | 31195.5 |  | 28197.75 |  | 25760 |  | mg/l |  |  | Night Shift Operator: |  |  | Class | "A" | Cert. No. | 3207 |  |  |  | 29 | 34.979 | 0.8 |  | 71 | 100 | 2 | 12 | 6.4 | 16.33 | 12.77 | 0.198 | 0.739 | 0 | C) | Monthly quantities of solid sludge stockpiled at plant.Solid Sludge Hauled from Plant: | [9 empty] | TOT | 1143.469 | 252.75 | 277.39 | 224.84 | 113.53 | 222.06 | 2450.7 | 15 | 3174 | 529 | 184.9 | 192.4 | 33301 | 251.01 | 330.97 | 188.8 | 68196 | 2294 | 20.491
| 28 | 35.216 | 1.742 | 51.36 | 16.085 | 8.487 | 24.1% | 0 | 0 |  |  | 28 |  |  |  | 28 | 48.36 | 48.58 | 48.52 |  |  | 41.48 | 41.78 | 41.59 | CHLORIDE (MONTHLY AVERAGE) | 5575 | 18500 |  | 17050 |  | 17200 |  | mg/l | [27 empty] | 1) | Additions |  |  | Cubic Yards | [5 empty] | AVG | 39.43 | 9.0268 | 9.5652 | 8.03 | 3.9148 | 8.2244 | 84.5069 | 3 | 109.4483 | 18.2414 | 6.3759 | 6.6345 | 1148.3103 | 11.9529 | 15.7605 | 6.5103 | 2351.5862 | 79.1034 | 0.97576
| 29 | 34.979 | 1.733 | 51.713 | 14.546 | 10.032 | 28.68% | 0.247 | 0 |  |  | 29 |  |  |  | 29 | 48.31 | 48.55 | 48.47 |  |  | 41.56 | 41.74 | 41.59 | AMMONIA-N (MONTHLY AVERAGE) | 9.58 | 1.37 |  | 2.3325 |  | 0.294 |  | mg/l |  |  | Lead Operator:_________________________________ | [28 empty] | Tons | [5 empty] | MAX | 64.329 | 13.46 | 13.62 | 11.7 | 13.65 | 11.07 | 134 | 5 | 230 | 44 | 6.6 | 7 | 1360 | 14.34 | 18.12 | 6.8 | 2630 | 80 | 1.59
[25 empty] | TKN (MONTHLY AVERAGE) | 11.505 | 2.105 |  | 3.1375 |  | 1.01 |  | mg/l | [5 empty] | Signature |  | Cert. No. |  |  |  |  | Lead Operator : This is to certify that I am familar with the information contained on this report and that to the best of | [14 empty] | 2) | Removals |  |  | Cubic Yards | [5 empty] | MIN | 33.933 | 4.66 | 2.12 | 0.23 | 0.12 | 2.88 | 30 | 2 | 30 | 9 | 6.2 | 6.3 | 877 | 7.3 | 12 | 6.3 | 1926 | 77 | 0.739
[25 empty] | pH (MONTHLY AVERAGE) | 7.42 | 7.485 |  | 7.475 |  | 7.63 |  | Std units | [12 empty] | my knowledge and belief, this information is true, complete and accuate. | [16 empty] | X |  | Tons | [6 empty] | item #1 | 16.0724 | 17.0087 | 14.2124 | 6.4109 | 14.5521 | MAX HOURLY FLOW (MG) = |  |  |  | 2.896 | ON THE | 1 | DAY OF THIS MONTH
| TOTAL | 1143.469 | 56.222 | 1623.903 | 510.886 | 308.463 |  | 8.525 | 4.93 | 0 | [5 empty] | TOTAL | 1386.58 | 1409.97 | 1400.99 |  |  | 1145.01 | 1211.98 | 1180.09 | CONDUCTIVITY (MONTHLY AVERAGE) | 16157.5 | 48750 |  | 45500 |  | 44100 |  | umho/cm | [33 empty] | Signature |  |  |  |  | item #2 | 49.5603 | 49.4124 | 50.0183 | 41.03 | 49.0148
| AVERAGE | 39.43 | 1.9387 | 55.9967 | 17.6168 | 10.6367 | 26.98% | 0.341 | 0.17 | #DIV/0! | [5 empty] | AVERAGE | 47.8131 | 48.6197 | 48.31 |  |  | 39.4831 | 41.7924 | 40.6928 | FECAL COLIFORM (MONTHLY AVERAGE) | 0 | 0 |  | 0 |  | 0 |  | # col/100ml | [12 empty] | Signed: ____________________________ Date: ___________________ | [20 empty] | Title |  |  |  |  | item #3 | 35.5 | 36.5 | 37.3 | 36.3 | 35.1
[16 empty] | MAXIMUM | 48.63 | 48.86 | 48.72 |  |  | 41.71 | 42.12 | 41.85 | TEMPERATURE (MONTHLY AVERAGE) | 73.5 | 70.25 |  | 69 |  | 67 |  | deg. F | [33 empty] | Date |  |  |  | item #1 | =monthly maximum of the daily flows (MG), with peakhour flow (MGD) on the day of the month with maximum flow = | [14 empty] | 2.896 | MG/hour multiplied by
[16 empty] | MINIMUM | 45.71 | 48.44 | 47.37 |  |  | 29.21 | 41.48 | 35.59 | TOTAL PHOSPHOROUS (MONTHLY AVG.) | 0.05 | 0.05 |  | 0.05 |  | 0.05 |  | mg/l | [12 empty] | Name: Michael A. Just | [14 empty] | * Sludge Reports should be submitted along with the monthly operating reports to Broward County Department | [10 empty] | the % of average % of TOTAL RAW FLOW to each Injection well.
[25 empty] | SULFATE (MONTHLY AVERAGE) | 800 | 2500 |  | 2137.5 |  | 2100 |  | mg/l | [27 empty] | of Natural Resource Protection, 218 S. W. 1st Avenue, Fort Lauderdale, Florida 33301 | [9 empty] | item #2 | =monthly average injection well pressure at injection well (psig)
[25 empty] | C.O.D. (MONTHLY AVERAGE) | 230 | 800 |  | 747.5 |  | 650 |  | mg/l | [12 empty] | Company Name: City of Fort Lauderdale Telephone No. (954) 523-1002 | [24 empty] | item #3 | =monthly wellhead pressure with no flow (shut-in pressure,psig)
[25 empty] | IRON (MONTHLY AVERAGE) | 0.0225 | 0.05 |  | 0.04 |  | 0.06 |  | mg/l | [37 empty] | PLANT STAFFING
[5 empty] | PAGE 2 | [19 empty] | SULFIDE (MONTHLY AVERAGE) | #DIV/0! | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | mg/l | [37 empty] | Day Shift Operator |  |  | Class: | "A" | Certificate No. | 4545 | Name: |  | McGEARY, J.
[71 empty] | Evening Shift Operator |  |  | Class: | "A" | Certificate No. | 4474 | Name: |  | BAYLER, J.
[20 empty] | PAGE 20 | [50 empty] | Night Shift Operator |  |  | Class: | "A" | Certificate No. | 3207 | Name: |  | HOSTNICK, N.
[71 empty] | Lead Operator |  |  | Class: | "A" | Certificate No. | 2769 | Name: |  | JUST, M.
[71 empty] | Type of Effluent Disposal or Reclaimed Water Reuse: |  |  |  |  | DEEPWELL INJECTION
[71 empty] | Permited Wet Weather Discharge Activated: |  |  |  | YES: |  | NO: |  |  | Not Applicable |  | X
[28 empty] | Page 28 | [42 empty] | If Yes, cumulative days of wet weather:
Attach additional sheets if necessary to list all certified operators. See page 1 "COVER PAGE" of supplental attachements.
DEP form 62-620.910(10), effective November 29, 1994
[19 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [47 empty] | Department of Natural Resource Protection
[5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [13 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [47 empty] | Division of Pollution Prevention and Remediation Programs
[5 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [13 empty] | MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING | [50 empty] | 218 S. W. 1st Avenue
[5 empty] | MONTHLY OPERATIONAL REPORT | [13 empty] | MONITORING WELL TWO |  |  |  | 1/07/04 thru 1/06/09 | [39 empty] | SLUDGE HAULERS MONTHLY REPORT | [6 empty] | Fort Lauderdale, FL 33301
[5 empty] | INFLUENT DATA | [11 empty] | MW-2 | I.D. #: 5066A11308 & 09 |  |  | PERMIT # 0054569-142-UO | [41 empty] | BROWARD COUNTY CODE SECTION 27-356 (d)(4)(1) | [5 empty] | Tel. No. (954) 523-1002
| RUN DATE | [14 empty] | RUN DATE | [52 empty] | *FAX (954) 519-1245
| 2026-07-30 | [14 empty] | 2026-07-30 |  | UPPER MONITOR ZONE |  |  |  |  | LOWER MONITOR ZONE
[17 empty] | MIN | MAX | AVG |  |  | MIN | MAX | AVG | [35 empty] | Plant Name: | GEORGE T. LOHMEYER WASTEWATER TREATMENT FACILITY
| FEBRUARY | RAW | RAW TSS | RAW SS | RAW | RAW | RAW | RAW | RAW | RAW | [5 empty] | FEBRUARY | FT HEAD | FT HEAD | FT HEAD |  |  | FT HEAD | FT HEAD | FT HEAD | [35 empty] | Address: | 1765 S.E. 18th Street at Eisenhower Boulevard | [6 empty] | MONTH: | FEBRUARY
| 2004 | CBOD | TOTAL | FIXED | COD | pH | CL_ | ALK. | H2S | TEMP.(F) | [5 empty] | 2004 | ABOVE | ABOVE | ABOVE |  |  | ABOVE | ABOVE | ABOVE | [35 empty] | Phone: | (954) 523-1002 * FAX (954) 468-1577 | [6 empty] | YEAR: | 2004
[17 empty] | NGVD | NGVD | NGVD |  |  | NGVD | NGVD | NGVD
| 1 | 30 | 30 | 4 | 224 | 7.2 | 650 | 206 | 3 | 75 | [5 empty] | 1 | 48.28 | 48.61 | 48.5 |  |  | 41.59 | 42.07 | 41.76 | [35 empty] | a) | WEEK OF | FEBRUARY |  | Type of Sludge |  |  | Disopsal Site |  |  | Cubic Yards
| 2 | 60 | 84 | 8 |  | 7 | 520 | 184 | 2 | 75.2 | [5 empty] | 2 | 45.71 | 48.55 | 46.86 |  |  | 33.99 | 41.69 | 36.86
| 3 | 49 | 108 | 40 |  | 7 | 490 | 188 | 3 | 76 | [5 empty] | 3 | 46.04 | 48.76 | 47.69 |  |  | 33.98 | 41.62 | 38.89 | [36 empty] | FIRST THRU SEVENTH |  |  | GRIT |  |  | Central Landfill |  |  | 20
| 4 | 69 | 126 | 18 | 260 | 7 | 470 | 194 | 4 | 76.2 | [5 empty] | 4 | 48.23 | 48.51 | 48.44 |  |  | 41.36 | 41.66 | 41.52
| 5 | 84 | 84 | 12 | 260 | 7 | 470 | 190 | 4 | 77 | [5 empty] | 5 | 48.25 | 48.54 | 48.45 |  |  | 41.44 | 41.66 | 41.5 | [36 empty] | EIGHT THRU FORTEENTH |  |  | GRIT |  |  | Central Landfill |  |  | 20
| 6 | 82 | 60 | 6 | 342 | 7 | 460 | 184 | 0 | 77 | [5 empty] | 6 | 48.28 | 48.66 | 48.46 |  |  | 41.47 | 41.75 | 41.57 | [36 empty] | FIFTHTEENTH THRU
| 7 | 100.2 | 62 | 8 | 312 | 7.1 | 470 | 200 | 0 | 77 | [5 empty] | 7 | 48.38 | 48.64 | 48.51 |  |  | 41.51 | 41.87 | 41.64 | [36 empty] | TWENTY SECOND |  |  | GRIT |  |  | Central Landfill |  |  | 10
| 8 | 91 | 80 | 12 | 299 | 7 | 510 | 194 | 5 | 77 | [5 empty] | 8 | 48.22 | 48.44 | 48.38 |  |  | 41.42 | 41.64 | 41.48 | [36 empty] | TWENTY THIRD THRU
| 9 | 84 | 102 | 14 |  | 6.8 | 480 | 198 | 4 | 77 | [5 empty] | 9 | 46.46 | 48.47 | 47.44 |  |  | 36.72 | 41.77 | 39.01 | [36 empty] | THIRTY FIRST |  |  | GRIT |  |  | Central Landfill |  |  | 10
| 10 | 115 | 230 | 26 |  | 7.1 | 540 | 212 | 3 | 77 | [5 empty] | 10 | 46.8 | 48.58 | 47.95 |  |  | 36.71 | 41.69 | 39.88
| 11 | 90.5 | 166 | 22 | 331 | 7 | 540 | 204 | 5 | 77 | [5 empty] | 11 | 48.36 | 48.58 | 48.48 |  |  | 41.52 | 41.77 | 41.57 | [35 empty] | b) | WEEK OF | FEBRUARY |  | Type of Sludge |  |  | Disopsal Site |  |  | Cubic Yards
| 12 | 106 | 68 | 12 | 308 | 7 | 600 | 212 | 6 | 77 | [5 empty] | 12 | 48.36 | 48.61 | 48.51 |  |  | 41.54 | 41.8 | 41.6
| 13 | 78 | 124 | 10 | 244 | 7.1 | 580 | 210 | 0 | 78 | [5 empty] | 13 | 48.34 | 48.59 | 48.51 |  |  | 41.56 | 41.87 | 41.65 | [36 empty] | FIRST THRU SEVENTH |  |  | RAGS |  |  | Central Landfill |  |  | 0
| 14 | 89 | 124 | 8 | 365 | 7 | 570 | 210 | 0 | 78 | [5 empty] | 14 | 48.46 | 48.7 | 48.52 |  |  | 41.62 | 41.93 | 41.73
| 15 | 103 | 122 | 10 | 255 | 7.1 | 620 | 190 | 5 | 78 | [5 empty] | 15 | 48.37 | 48.76 | 48.57 |  |  | 41.62 | 41.96 | 41.79 | [36 empty] | EIGHT THRU FORTEENTH |  |  | RAGS |  |  | Central Landfill |  |  | 20
| 16 | 134 | 144 | 22 |  | 7 | 610 | 212 | 5 | 78 | [5 empty] | 16 | 46.88 | 48.62 | 47.69 |  |  | 36.4 | 41.7 | 38.52 | [36 empty] | FIFTHTEENTH THRU
| 17 | 83 | 84 | 16 |  | 7 | 630 | 208 | 5 | 78 | [5 empty] | 17 | 47.16 | 48.56 | 48.01 |  |  | 36.22 | 41.48 | 39.59 | [36 empty] | TWENTY SECOND |  |  | RAGS |  |  | Central Landfill |  |  | 10
| 18 | 93 | 100 | 14 | 369 | 7.1 | 620 | 210 | 4 | 77 | [5 empty] | 18 | 48.14 | 48.46 | 48.31 |  |  | 41.27 | 41.55 | 41.44 | [36 empty] | TWENTY THIRD THRU
| 19 | 91 | 120 | 22 | 343 | 7.2 | 540 | 206 | 6 | 77 | [5 empty] | 19 | 48.13 | 48.55 | 48.42 |  |  | 41.33 | 41.69 | 41.5 | [36 empty] | THIRTY FIRST |  |  | RAGS |  |  | Central Landfill |  |  | 10
| 20 | 86 | 102 | 4 | 351 | 7.1 | 620 | 194 | 6 | 77 | [5 empty] | 20 | 48.27 | 48.66 | 48.47 |  |  | 41.55 | 41.83 | 41.61 | [36 empty] | BCSR = Broward County Septage Receiving
| 21 | 98 | 136 | 8 | 381 | 7.1 | 610 | 204 | 5 | 77 | [5 empty] | 21 | 48.35 | 48.65 | 48.49 |  |  | 41.65 | 42.12 | 41.85 | [35 empty] | c) | WEEK OF | FEBRUARY |  | Type of Sludge |  |  | Disopsal Site |  |  | Gallons
| 22 | 78 | 96 | 10 | 347 | 7.2 | 550 | 204 | 5 | 77 | [5 empty] | 22 | 48.31 | 48.58 | 48.48 |  |  | 41.63 | 42.03 | 41.73
| 23 | 82 | 124 | 14 |  | 7.1 | 620 | 216 | 6 | 77 | [5 empty] | 23 | 46.09 | 48.56 | 47.37 |  |  | 29.21 | 41.93 | 35.59 | [36 empty] | FIRST THRU SEVENTH |  |  | VAC/Plastic & Rags |  |  | BCSR |  |  | 0
| 24 | 105 | 104 | 20 |  | 7.1 | 640 | 218 | 5 | 76 | [5 empty] | 24 | 46.47 | 48.74 | 47.84 |  |  | 29.82 | 41.61 | 37.48
| 25 | 82 | 140 | 24 | 640 | 7.1 | 640 | 216 | 6 | 78 | [5 empty] | 25 | 48.51 | 48.83 | 48.67 |  |  | 41.57 | 41.88 | 41.64 | [36 empty] | EIGHT THRU FORTEENTH |  |  | VAC/Plastic & Rags |  |  | BCSR |  |  | 0
| 26 | 42 | 76 | 10 | 281 | 7 | 640 | 208 | 7 | 76 | [5 empty] | 26 | 48.63 | 48.86 | 48.72 |  |  | 41.71 | 42.04 | 41.83 | [36 empty] | FIFTHTEENTH THRU
| 27 | 76 | 134 | 14 | 344 | 7 | 650 | 202 | 5 | 77 | [5 empty] | 27 | 48.43 | 48.77 | 48.57 |  |  | 41.56 | 41.85 | 41.68 | [36 empty] | TWENTY SECOND |  |  | VAC/Plastic & Rags |  |  | BSCR |  |  | 0
| 28 | 99 | 144 | 8 | 298 | 7 | 640 | 210 | 5 | 77 | [5 empty] | 28 | 48.36 | 48.58 | 48.52 |  |  | 41.48 | 41.78 | 41.59 | [36 empty] | TWENTY THIRD THRU
| 29 | 71 | 100 | 8 | 362 | 7 | 640 | 204 | 6 | 77 | [5 empty] | 29 | 48.31 | 48.55 | 48.47 |  |  | 41.56 | 41.74 | 41.59 | [36 empty] | THIRTY FIRST |  |  | VAC/Plastic & Rags |  |  | BSCR |  |  | 0
TOTALS
[61 empty] | a) | 60 | cu.yds |  | GRIT |  | Signature
| TOTAL | 2450.7 | 3174 | 404 | 6916 | 204.4 | 16620 | 5888 | 120 | 2231.4 | [5 empty] | TOTAL | 1386.58 | 1409.97 | 1399.3 |  |  | 1145.01 | 1211.98 | 1180.09 | [36 empty] | b) | 40 | cu.yds |  | RAGS |  | Title
| AVERAGE | 84.5069 | 109.4483 | 13.931 | 329.3333 | 7.0483 | 573.1034 | 203.0345 | 4.8 | 76.9448 | [5 empty] | AVERAGE | 47.8131 | 48.6197 | 48.2517 |  |  | 39.4831 | 41.7924 | 40.6928 | [36 empty] | c) | 0 | gal. |  | VAC/Plastic & Rags |  | Date
[16 empty] | MAXIMUM | 48.63 | 48.86 | 48.72 |  |  | 41.71 | 42.12 | 41.85
[16 empty] | MINIMUM | 45.71 | 48.44 | 46.86 |  |  | 29.21 | 41.48 | 35.59 | [36 empty] | * Sludge Reports should be submitted along with the monthly operating reports to Broward County Department
of Natural Resource Protection, 218 S. W. 1st Avenue, Fort Lauderdale, Florida 33301
PAGE 3
PAGE 21
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
[5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [13 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
[5 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [13 empty] | MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
[5 empty] | MONTHLY OPERATIONAL REPORT | [13 empty] | MONITORING WELL THREE |  |  |  | 1/07/04 thru 1/06/09
[5 empty] | EFFLUENT DATA PART 1 | [11 empty] | MW-3 | I.D. #: 5066A11310 |  |  | PERMIT # 0054569-142-UO
RUN DATE
[16 empty] | 2026-07-30 |  | UPPER MONITOR ZONE |  |  |  |  | LOWER MONITOR ZONE
| RUN DATE | [15 empty] | MIN | MAX | AVG |  |  | MIN | MAX | AVG
| 2026-07-30 | [14 empty] | FEBRUARY | FT HEAD | FT HEAD | FT HEAD |  |  | FT HEAD | FT HEAD | FT HEAD
[14 empty] | BOD | TSS | 2004 | ABOVE | ABOVE | ABOVE |  |  | ABOVE | ABOVE | ABOVE
| FEBRUARY | EFFLUENT | EFFL. TSS | EFFL. SS | EFFLUENT | EFFL. | EFFL. | EFFL. | EFFL. | EFFL. | TDS |  |  | MONTHLY AVG OVER 30 | MONTHLY AVG OVER 30 |  | NGVD | NGVD | NGVD |  |  | NGVD | NGVD | NGVD
| 2004 | CBOD | TOTAL | FIXED | COD | CL_ | ALK. | TURB. | COND. | TEMP.(F) |  |  |  | 0 | 0 | 1 | 31.49 | 31.87 | 31.72 |  |  | 45.49 | 45.7 | 45.55
[14 empty] | WEKKLY OVER 45 | WEKKLY OVER 45 | 2 | 17.64 | 31.79 | 22.77 |  |  | 37.42 | 45.62 | 40.43
| 1 |  | 22 | 4 | 64 | 630 | 184 | 14 | 2060 | 77 | 1030 | 0 |  | 0 | 0 | 3 | 17.63 | 31.1 | 26.34 |  |  | 37.42 | 45.15 | 42.4
| 2 |  | 44 | 13 |  | 440 | 188 | 21.7 | 1926 | 79 | 943 | 0 |  | SINGLE DAY OVER 60 | SINGLE DAY OVER 60 | 4 | 30.98 | 31.32 | 31.23 |  |  | 45.06 | 45.32 | 45.32
| 3 |  | 29 | 7 |  | 480 | 184 | 10.5 | 2090 | 78 | 891 | 0 |  | 0 | 0 | 5 | 31.17 | 31.44 | 31.33 |  |  | 45.25 | 45.43 | 45.38
| 4 |  | 15 | 4 |  | 480 | 188 | 7.82 | 2100 | 78 | 970 | 0 |  | 0 | 0 | 6 | 31.25 | 31.6 | 31.44 |  |  | 45.35 | 45.59 | 45.47
| 5 |  | 14 | 4 | 53 | 480 | 188 | 7.75 | 2180 | 79 | 1046 | 0 |  |  |  | 7 | 31.39 | 31.6 | 31.48 |  |  | 45.46 | 45.6 | 45.5
| 6 |  | 30 | 1 | 50 | 480 | 192 | 6.46 | 2210 | 79 | 1009 | 0 |  |  |  | 8 | 31.21 | 31.43 | 31.34 |  |  | 45.38 | 45.46 | 45.47
| 7 |  | 19 | 5 | 57 | 490 | 194 | 8.14 | 2260 | 79 | 1010 | 0 | #DIV/0! | #DIV/0! | 24.7143 | 9 | 20.87 | 31.46 | 25.64 |  |  | 39.64 | 45.51 | 42.28
| 8 |  | 14 | 2 | 52 | 500 | 196 | 9.94 | 2300 | 78 | 1052 | 0 |  | #DIV/0! | 23.5714 | 10 | 20.69 | 31.43 | 27.55 |  |  | 39.61 | 45.25 | 43.12
| 9 |  | 20 | 4 | 41 | 470 | 192 | 8.62 | 2320 | 77 | 1078 | 0 |  | #DIV/0! | 20.1429 | 11 | 31.33 | 31.61 | 31.46 |  |  | 45.25 | 45.41 | 45.37
| 10 |  | 18 | 4 |  | 520 | 190 | 8.66 | 2360 | 79 | 1127 | 0 |  | #DIV/0! | 18.5714 | 12 | 31.51 | 31.72 | 31.6 |  |  | 45.4 | 45.52 | 45.49
| 11 |  | 19 | 4 |  | 520 | 190 | 11.5 | 2390 | 80 | 877 | 0 |  | #DIV/0! | 19.1429 | 13 | 31.55 | 31.76 | 31.63 |  |  | 45.43 | 45.57 | 45.5
| 12 |  | 13 | 3 | 49 | 540 | 184 | 5.62 | 2350 | 79 | 1140 | 0 |  | #DIV/0! | 19 | 14 | 31.66 | 31.95 | 31.82 |  |  | 45.51 | 45.75 | 45.54
| 13 |  | 17 | 3 | 46 | 580 | 180 | 6.12 | 2360 | 80 | 1109 | 0 |  | #DIV/0! | 17.1429 | 15 | 31.61 | 31.97 | 31.85 |  |  | 45.59 | 45.83 | 45.74
| 14 |  | 13 | 2 | 52 | 560 | 182 | 7.17 | 2360 | 80 | 1109 | 0 | #DIV/0! | #DIV/0! | 16.2857 | 16 | 20.79 | 31.78 | 24.88 |  |  | 37.94 | 45.7 | 40.83
| 15 |  | 9 | 1 | 54 | 610 | 184 | 7.58 | 2500 | 80 | 1171 | 0 |  | #DIV/0! | 15.5714 | 17 | 20.58 | 31.3 | 27.31 |  |  | 37.94 | 45.14 | 42.41
| 16 |  | 18 | 6 | 41 | 600 | 192 | 7.45 | 2510 | 80 | 1129 | 0 |  | #DIV/0! | 15.2857 | 18 | 31.1 | 31.48 | 31.31 |  |  | 45.05 | 45.31 | 45.2
| 17 |  | 21 | 4 |  | 620 | 192 | 8.6 | 2630 | 80 | 1169 | 0 |  | #DIV/0! | 15.7143 | 19 | 31.24 | 31.67 | 31.45 |  |  | 45.18 | 45.48 | 45.36
| 18 |  | 24 | 5 | 42 | 620 | 192 | 14.7 | 2350 | 79 | 1231 | 0 |  | #DIV/0! | 16.4286 | 20 | 31.49 | 31.85 | 31.75 |  |  | 45.42 | 45.66 | 45.49
| 19 |  | 15 | 3 | 55 | 630 | 190 | 7.87 | 2410 | 78 | 1223 | 0 |  | #DIV/0! | 16.7143 | 21 | 31.61 | 31.87 | 31.78 |  |  | 45.58 | 45.7 | 45.59
| 20 |  | 15 | 1 | 58 | 640 | 182 | 10.4 | 2510 | 79 | 1332 | 0 |  | #DIV/0! | 16.4286 | 22 | 31.63 | 31.83 | 31.75 |  |  | 45.6 | 45.66 | 45.59
| 21 |  | 12 | 2 | 58 | 650 | 196 | 6.71 | 2580 | 79 | 1360 | 0 | #DIV/0! | #DIV/0! | 16.2857 | 23 | 19.44 | 31.83 | 25.5 |  |  | 37.38 | 45.69 | 41.52
| 22 |  | 14 | 2 | 54 | 620 | 194 | 6.63 | 2610 | 80 | 1335 | 0 |  | #DIV/0! | 17 | 24 | 19.26 | 31.62 | 27.24 |  |  | 37.36 | 45.45 | 42.64
| 23 |  | 15 | 1 |  | 670 | 192 | 7.46 | 2460 | 80 | 1323 | 0 |  | #DIV/0! | 16.5714 | 25 | 31.49 | 31.85 | 31.68 |  |  | 45.37 | 45.67 | 45.51
| 24 |  | 18 | 6 |  | 680 | 198 | 5.7 | 2590 | 80 | 1345 | 0 |  | #DIV/0! | 16.1429 | 26 | 31.78 | 31.95 | 31.91 |  |  | 45.64 | 45.76 | 45.66
| 25 | 3 | 12 | 2 | 61 | 670 | 192 | 7.54 | 2520 | 80 | 1335 | 1 |  | 3 | 14.4286 | 27 | 31.58 | 31.88 | 31.72 |  |  | 45.51 | 45.7 | 45.57
| 26 | 5 | 22 | 5 | 63 | 660 | 196 | 13.3 | 2360 | 80 | 1263 | 1 |  | 4 | 15.4286 | 28 | 31.56 | 31.75 | 31.62 |  |  | 45.52 | 45.65 | 45.52
| 27 | 2 | 15 | 2 | 52 | 620 | 186 | 12.4 | 2290 | 79 | 1270 | 1 |  | 3.3333 | 15.4286 | 29 | 31.52 | 31.7 | 31.6 |  |  | 45.53 | 45.64 | 45.53
| 28 | 3 | 20 | 4 | 43 | 620 | 190 | 7.3 | 2260 | 79 | 1158 | 1 |  | 3.25 | 16.5714
| 29 | 2 | 12 | 1 | 48 | 620 | 198 | 5.33 | 2350 | 79 | 1266 | 1 |  | 3 | 16.2857
[12 empty] | 0 |  | 3 | 16.5 | TOTAL | 817.05 | 918.41 | 870.7 |  |  | 1258.28 | 1320.92 | 1290.98
[12 empty] | 0 | 3 | 3 | 16.2 | AVERAGE | 28.1741 | 31.6693 | 30.0241 |  |  | 43.389 | 45.549 | 44.5166
| TOTAL | 15 | 529 | 105 | 1093 | 16700 | 5506 | 262.97 | 68196 | 2294 | 33301 |  |  |  |  | MAXIMUM | 31.78 | 31.97 | 31.91 |  |  | 45.64 | 45.83 | 45.74
| AVERAGE | 3 | 18.2414 | 3.6207 | 52.0476 | 575.8621 | 189.8621 | 9.0679 | 2351.5862 | 79.1034 | 1148.3103 |  |  | #DIV/0! | 17.2623 | MINIMUM | 17.63 | 31.1 | 22.77 |  |  | 37.36 | 45.14 | 40.43
| MAXIMUM | 5 | 44
[5 empty] | PAGE 4 | [14 empty] | PAGE 22
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
[5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [13 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
[5 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [13 empty] | MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
[5 empty] | MONTHLY OPERATIONAL REPORT | [13 empty] | REGIONAL MONITORING WELL ONE
[5 empty] | EFFLUENT DATA PART 2 | [13 empty] | RMW-1 |  |  |  | 1/07/04 thru 1/06/09
[16 empty] | RUN DATE |  |  |  |  | PERMIT # 0054569-142-UO
[16 empty] | 2026-07-30 |  | UPPER MONITOR ZONE |  |  |  |  | LOWER MONITOR ZONE
RUN DATE | [16 empty] | MIN | MAX | AVG |  |  | MIN | MAX | AVG
2026-07-30 | [15 empty] | FEBRUARY | FT HEAD | FT HEAD | FT HEAD |  |  | FT HEAD | FT HEAD | FT HEAD
[16 empty] | 2004 | ABOVE | ABOVE | ABOVE |  |  | ABOVE | ABOVE | ABOVE
| FEBRUARY | EFF. BACT. | EFF. BACT. | FREE | TOTAL | EFFL. | EFF PH | EFF PH | EFF. SAP | AVG. | Sufates | [5 empty] | NGVD | NGVD | NGVD |  |  | NGVD | NGVD | NGVD
| 2004 | TOTAL | FECAL | CL2 | CL2 | pH | MIN | MAX | TEMP.(C) | BLK. | [5 empty] | 1 | 44.65 | 44.82 | 44.75 |  |  | 22.36 | 22.55 | 22.47
[16 empty] | 2 | 36.24 | 44.72 | 39.55 |  |  | 20.07 | 22.44 | 21.24
| 1 | TNCT | 6400 | 0 | 0.4 | 6.6 | 6.6 | 6.6 | 4 | 51 | [5 empty] | 3 | 26.22 | 43.8 | 41.13 |  |  | 19.9 | 22.44 | 21.81
| 2 | TNTC | 27 | 0 | 0.3 | 6.7 | 6.6 | 6.6 | 4 | 50 | [5 empty] | 4 | 43.79 | 44.02 | 43.93 |  |  | 22.43 | 22.67 | 22.58
| 3 | TNTC | 18 | 0 | 0.4 | 6.6 | 6.5 | 6.8 | 4 | 52 | [5 empty] | 5 | 43.97 | 44.14 | 44.06 |  |  | 22.64 | 22.81 | 22.73
| 4 | TNTC | 18 | 0 | 0.4 | 6.7 | 6.6 | 6.7 | 8 | 48 | [5 empty] | 6 | 44.05 | 44.29 | 44.2 |  |  | 22.75 | 22.96 | 22.88
| 5 | 780 | 27 | 0 | 0.9 | 6.6 | 6.5 | 6.8 | 5 | 43 | [5 empty] | 7 | 44.13 | 44.3 | 44.24 |  |  | 22.84 | 22.98 | 22.93
| 6 | 380 | 0 | 0 | 0.6 | 6.8 | 6.4 | 7 | 0 | 48 | [5 empty] | 8 | 44.06 | 44.14 | 44.1 |  |  | 22.73 | 22.84 | 22.77
| 7 | TNTC | TNTC | 0.1 | 0.6 | 6.6 | 6.4 | 6.8 | 0 | 56 | [5 empty] | 9 | 44.07 | 44.22 | 44.15 |  |  | 22.78 | 22.92 | 22.83
| 8 | TNTC | TNTC | 0 | 0.6 | 6.6 | 6.4 | 6.7 | 4 | 45 | [5 empty] | 10 | 44.19 | 44.33 | 44.25 |  |  | 22.89 | 23.01 | 22.94
| 9 | 36 | 0 | 0 | 0.8 | 6.6 | 6.4 | 6.7 | 2 | 37 | [5 empty] | 11 | 0.25 | 44.36 | 43.78 |  |  | 0.25 | 23.08 | 22.73
| 10 | 27 | 0 | 0 | 0.6 | 6.5 | 6.3 | 6.7 | 3 | 49 | [5 empty] | 12 | 44.31 | 44.39 | 44.36 |  |  | 22.97 | 23.1 | 23.03
| 11 | 3400 | 0 | 0 | 0.4 | 6.4 | 6.5 | 6.8 | 5 | 56 | [5 empty] | 13 | 44.3 | 44.37 | 44.34 |  |  | 22.97 | 23.07 | 23.02
| 12 | 27 | 0 | 0 | 0.6 | 6.5 | 6.3 | 6.8 | 4 | 50 | [5 empty] | 14 | 44.36 | 44.5 | 44.44 |  |  | 23 | 23.21 | 23.12
| 13 | 232 | 0 | 0 | 0.6 | 6.4 | 6.3 | 6.6 | 0 | 63 | [5 empty] | 15 | 44.38 | 44.55 | 44.49 |  |  | 23.02 | 23.25 | 23.17
| 14 | 116 | 0 | 0 | 7 | 6.3 | 6.2 | 6.3 | 0 | 67 | [5 empty] | 16 | 44.25 | 44.42 | 44.34 |  |  | 22.89 | 23.08 | 23
| 15 | TNTC | 179 | 0 | 0.9 | 6.3 | 6.2 | 6.5 | 2 | 58 | [5 empty] | 17 | 44.25 | 44.36 | 44.31 |  |  | 22.89 | 23.04 | 22.97
| 16 | TNTC | 143 | 0 | 0.6 | 6.6 | 6.4 | 7 | 2 | 52 | [5 empty] | 18 | 44.24 | 44.36 | 44.29 |  |  | 22.9 | 23 | 22.94
| 17 | 6900 | 9 | 0 | 0.3 | 6.6 | 6.3 | 6.7 | 3 | 53 | [5 empty] | 19 | 44.25 | 44.43 | 44.35 |  |  | 22.9 | 23.07 | 23
| 18 | 37500 | 9 | 0 | 0.5 | 6.6 | 6.4 | 6.8 | 3 | 52 | [5 empty] | 20 | 44.36 | 44.53 | 44.46 |  |  | 23.03 | 23.18 | 23.11
| 19 | 46000 | 89 | 0 | 0.4 | 6.5 | 6.3 | 6.5 | 3 | 53 | [5 empty] | 21 | 44.45 | 44.56 | 44.5 |  |  | 23.12 | 23.17 | 23.14
| 20 | 39500 | 152 | 0 | 0.6 | 6.5 | 6.3 | 6.9 | 0 | 52 | [5 empty] | 22 | 44.41 | 44.49 | 44.46 |  |  | 23.07 | 23.15 | 23.1
| 21 | 420 | 0 | 0 | 0.5 | 6.4 | 6.3 | 6.4 | 3 | 64 | [5 empty] | 23 | 44.42 | 44.55 | 44.48 |  |  | 23.05 | 23.18 | 23.12
| 22 | 25000 | 9 | 0 | 0.6 | 6.4 | 6.3 | 6.4 | 1 | 52 | [5 empty] | 24 | 44.5 | 44.69 | 44.6 |  |  | 23.18 | 23.36 | 23.26
| 23 | 161 | 18 | 0 | 0.4 | 6.4 | 6.3 | 6.5 | 2 | 51 | [5 empty] | 25 | 44.66 | 44.74 | 44.7 |  |  | 23.33 | 23.43 | 23.38
| 24 | 36 | 0 | 0 | 0.6 | 6.4 | 6.3 | 6.5 | 3 | 47 | [5 empty] | 26 | -6999 | 62.89 | -6999 |  |  | -6999 | 62.97 | -6999
| 25 | 0 | 0 | 0 | 0.5 | 6.5 | 6.4 | 6.5 | 4 | 51 | [5 empty] | 27 | 44.52 | 44.68 | 44.61 |  |  | 23.12 | 23.38 | 23.27
| 26 | 1083 | 18 | 0 | 0.6 | 6.5 | 6.4 | 6.5 | 4 | 51 | [5 empty] | 28 | 44.45 | 44.54 | 44.5 |  |  | 23.05 | 23.18 | 23.13
| 27 | TNTC | 0 | 0.1 | 0.7 | 6.4 | 6.4 | 6.5 | 1 | 51 | [5 empty] | 29 | 44.43 | 44.51 | 44.47 |  |  | 23.02 | 23.13 | 23.08
| 28 | 3600 | 0 | 0.1 | 0.7 | 6.4 | 6.3 | 6.4 | 1 | 58
| 29 | 600 | 0 | 0.1 | 0.8 | 6.4 | 6.3 | 6.4 | 2 | 49
[16 empty] | TOTAL | -5828.84 | 1306.7 | -5765.16 |  |  | -6385.85 | 707.65 | -6358.25
[16 empty] | AVERAGE | -208.1729 | 45.0586 | -205.8986 |  |  | -228.0661 | 24.4017 | -227.0804
| TOTAL | 165798 | 7116 | 0.4 | 22.9 | 188.8 | 184.9 | 192.4 | 77 | 1509 | 0 |  |  |  |  | MAXIMUM | 44.66 | 62.89 | 44.75 |  |  | 23.33 | 62.97 | 23.38
| AVERAGE | 8289.9 | 263.5556 | 0.013793 | 0.78966 | 6.5103 | 6.3759 | 6.6345 | 2.4839 | 52.0345 | #DIV/0! |  |  |  |  | MINIMUM | -6999 | 43.8 | -6999 |  |  | -6999 | 22.44 | -6999
[7 empty] | 6.2 | 7
[7 empty] | MIN | MAX
PAGE 5
PAGE 23
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
NUTRIENTS
RUN DATE
| 2026-07-30 |  | INFLUENT | [5 empty] | EFFLUENT
| FEBRUARY | INFLUENT | INFLUENT | INFLUENT | INFLUENT |  | EFFL. | EFFL. | EFFL. | EFFL.
| 2004 | NH-3 | N03-N | TKN | TOT P |  | NH-3 | N03-N | TKN | TOT P
| 1 | 7.9 | 0.02 | 0.05 | 2 |  | 7.3 | 0.3 | 12 | 1.1
2
3
| 4 | 13.27 | 0.02 | 18.04 | 2.23 |  | 9.56 | 0.115 | 13.06 | 0.892
| 5 | 13.27 | 0.02 | 18.04 | 2.23 |  | 9.56 | 0.115 | 13.06 | 0.892
| 6 | 14.58 | 0.02 | 18.95 | 2.44 |  | 11.35 | 0.077 | 14.95 | 0.9
| 7 | 15.17 | 0.02 | 19.73 | 2.5 |  | 8.47 | 0.861 | 13.89 | 0.835
| 8 | 15.5 | 0.02 | 20.51 | 2.62 |  | 11.04 | 0.213 | 14.44 | 0.957
9
10
| 11 | 16.8 | 0.02 | 21.87 | 2.79 |  | 11.62 | 0.19 | 15.18 | 0.879
| 12 | 16.54 | 0.02 | 21.87 | 2.77 |  | 13.68 | 0.202 | 17.21 | 0.85
| 13 | 16.71 | 0.058 | 22.04 | 2.81 |  | 13.29 | 0.165 | 17.06 | 1.39
| 14 | 17.08 | 0.081 | 21.84 | 2.79 |  | 13.09 | 0.144 | 16.9 | 1.43
| 15 | 13.08 | 0.02 | 19.98 | 1.83 |  | 11.67 | 0.87 | 16.64 | 0.836
16
17
| 18 | 18.54 | 0.02 | 22.99 | 2.91 |  | 14.34 | 0.163 | 18.12 | 1.59
| 19 | 18.05 | 0.02 | 22.65 | 3.02 |  | 13.87 | 0.242 | 18.11 | 0.963
| 20 | 16.71 | 0.02 | 21.69 | 2.68 |  | 13.9 | 0.09 | 17.65 | 0.927
| 21 | 16.42 | 0.02 | 21.64 | 2.86 |  | 12.37 | 0.108 | 16.15 | 0.874
| 22 | 17.13 | 0.02 | 22.24 | 2.78 |  | 12.27 | 0.318 | 15.94 | 0.851
23
24
| 25 | 16.97 | 0.02 | 21.74 | 2.68 |  | 13.75 | 0.28 | 17.23 | 0.834
| 26 | 16.02 | 0.02 | 21 | 2.69 |  | 12.32 | 0.275 | 15.6 | 0.867
| 27 | 16.86 | 0.02 | 21.07 | 2.9 |  | 13.22 | 0.133 | 16.42 | 0.865
| 28 | 17.35 | 0.02 | 22.2 | 2.94 |  | 11.57 | 0.206 | 15.03 | 1.02
| 29 | 16.51 | 0.02 | 21.02 | 2.72 |  | 12.77 | 0.198 | 16.33 | 0.739
| TOTAL | 330.46 | 0.519 | 421.16 | 55.19 | TOT. | 251.01 | 5.265 | 330.97 | 20.491
| AVERAGE | 15.7362 | 0.024714 | 20.0552 | 2.6281 | AVG. | 11.9529 | 0.25071 | 15.7605 | 0.97576
PAGE 6
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
REACTOR ONE PROCESS
RUN DATE
| 2026-07-30 |  | TRAIN "A" | [5 empty] | TRAIN "B"
| FEBRUARY | MLSS | MLVSS | SS | SVI |  | MLSS | MLVSS | SS | SVI
| 2004 | "A" | "A" | "A" | "A" |  | "B" | "B" | "B" | "B"
| 1 | O/S | O/S | O/S |  |  | 2500 | 2250 | 23 | 92
| 2 | O/S | O/S | O/S |  |  | 2390 | 1940 | 21 | 87.8661
| 3 | O/S | O/S | O/S |  |  | 3200 | 2610 | 22 | 68.75
| 4 | O/S | O/S | O/S |  |  | 2460 | 2070 | 26 | 105.6911
| 5 | O/S | O/S | O/S |  |  | 1970 | 1650 | 24 | 121.8274
| 6 | O/S | O/S | O/S |  |  | 2030 | 1710 | 25 | 123.1527
| 7 | O/S | O/S | O/S |  |  | 2120 | 1780 | 27 | 127.3585
| 8 | O/S | O/S | O/S |  |  | 1980 | 1680 | 25 | 126.2626
| 9 | O/S | O/S | O/S |  |  | 3400 | 2860 | 22 | 64.7059
| 10 | O/S | O/S | O/S |  |  | 4300 | 3610 | 26 | 60.4651
| 11 | O/S | O/S | O/S |  |  | 2550 | 2120 | 32 | 125.4902
| 12 | O/S | O/S | O/S |  |  | 1600 | 1350 | 31 | 193.75
| 13 | O/S | O/S | O/S |  |  | 2810 | 2310 | 33 | 117.4377
| 14 | O/S | O/S | O/S |  |  | 3010 | 2480 | 31 | 102.99
| 15 | O/S | O/S | O/S |  |  | 3230 | 2720 | 36 | 111.4551
| 16 | O/S | O/S | O/S |  |  | 3600 | 2920 | 37 | 102.7778
| 17 | O/S | O/S | O/S |  |  | 3500 | 2840 | 30 | 85.7143
| 18 | O/S | O/S | O/S |  |  | 4430 | 3720 | 31 | 69.9774
| 19 | O/S | O/S | O/S |  |  | 3880 | 3260 | 37 | 95.3608
| 20 | O/S | O/S | O/S |  |  | 2090 | 1810 | 33 | 157.8947
| 21 | O/S | O/S | O/S |  |  | 2610 | 2220 | 33 | 126.4368
| 22 | O/S | O/S | O/S |  |  | 4070 | 3400 | 38 | 93.3661
| 23 | O/S | O/S | O/S |  |  | 3920 | 3240 | 34 | 86.7347
| 24 | O/S | O/S | O/S |  |  | 3740 | 3090 | 31 | 82.8877
| 25 | O/S | O/S | O/S |  |  | 3660 | 3070 | 32 | 87.4317
| 26 | O/S | O/S | O/S |  |  | 3800 | 3190 | 27 | 71.0526
| 27 | O/S | O/S | O/S |  |  | 2520 | 2080 | 33 | 130.9524
| 28 | O/S | O/S | O/S |  |  | 2940 | 2390 | 36 | 122.449
| 29 | O/S | O/S | O/S |  |  | 3540 | 2990 | 32 | 90.3955
|  | O/S | O/S | O/S
|  | O/S | O/S | O/S
| TOTAL | 0 | 0 | 0 |  |  | 87850 | 73360 | 868
| AVERAGE | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 3029.3103 | 2529.6552 | 29.931 | 98.8048
PAGE 7
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
REACTOR TWO PROCESS
RUN DATE
| 2026-07-30 |  | TRAIN "C" | [5 empty] | TRAIN "D"
| FEBRUARY | MLSS | MLVSS | SS | SVI |  | MLSS | MLVSS | SS | SVI
| 2004 | "C" | "C" | "C" | "C" |  | "D" | "D" | "D" | "D"
| 1 | O/S | O/S | O/S |  |  | 2610 | 2360 | 22 | 84.2912
| 2 | O/S | O/S | O/S |  |  | 2340 | 1900 | 18 | 76.9231
| 3 | O/S | O/S | O/S |  |  | 3230 | 2670 | 21 | 65.0155
| 4 | O/S | O/S | O/S |  |  | 2340 | 1970 | 26 | 111.1111
| 5 | O/S | O/S | O/S |  |  | 1980 | 1660 | 23 | 116.1616
| 6 | O/S | O/S | O/S |  |  | 2620 | 2280 | 26 | 99.2366
| 7 | O/S | O/S | O/S |  |  | 2100 | 1730 | 28 | 133.3333
| 8 | O/S | O/S | O/S |  |  | 2280 | 1940 | 18 | 78.9474
| 9 | O/S | O/S | O/S |  |  | 3200 | 2700 | 24 | 75
| 10 | O/S | O/S | O/S |  |  | 3200 | 2690 | 26 | 81.25
| 11 | O/S | O/S | O/S |  |  | 2630 | 2200 | 29 | 110.2662
| 12 | O/S | O/S | O/S |  |  | 1950 | 1650 | 29 | 148.7179
| 13 | O/S | O/S | O/S |  |  | 3000 | 2470 | 32 | 106.6667
| 14 | O/S | O/S | O/S |  |  | 3090 | 2550 | 34 | 110.0324
| 15 | O/S | O/S | O/S |  |  | 2680 | 2210 | 37 | 138.0597
| 16 | O/S | O/S | O/S |  |  | 3170 | 2570 | 34 | 107.2555
| 17 | O/S | O/S | O/S |  |  | 3430 | 2800 | 27 | 78.7172
| 18 | O/S | O/S | O/S |  |  | 3620 | 3040 | 30 | 82.8729
| 19 | O/S | O/S | O/S |  |  | 3720 | 3120 | 32 | 86.0215
| 20 | O/S | O/S | O/S |  |  | 2400 | 2030 | 33 | 137.5
| 21 | O/S | O/S | O/S |  |  | 2690 | 2250 | 33 | 122.6766
| 22 | O/S | O/S | O/S |  |  | 3940 | 3240 | 35 | 88.8325
| 23 | O/S | O/S | O/S |  |  | 3720 | 3080 | 34 | 91.3978
| 24 | O/S | O/S | O/S |  |  | 3730 | 3080 | 32 | 85.7909
| 25 | O/S | O/S | O/S |  |  | 3620 | 3040 | 34 | 93.9227
| 26 | O/S | O/S | O/S |  |  | 3250 | 2730 | 29 | 89.2308
| 27 | O/S | O/S | O/S |  |  | 3210 | 2660 | 35 | 109.0343
| 28 | O/S | O/S | O/S |  |  | 3280 | 2780 | 36 | 109.7561
| 29 | O/S | O/S | O/S |  |  | 3210 | 2700 | 32 | 99.6885
|  | O/S | O/S | O/S
|  | O/S | O/S | O/S
| TOTAL | 0 | 0 | 0 |  |  | 86240 | 72100 | 849
| AVERAGE | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 2973.7931 | 2486.2069 | 29.2759 | 98.4462
PAGE 8
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
RAS SUMMARY
RUN DATE
2026-07-30
| FEBRUARY | R-1 | R-2 | TOTAL | F/M | TOTAL | SLUDGE | % TOT | % FIX | % VOL.
| 2004 | TOT. RAS | TOT. RAS | MLVSS | RATIO | MLSS | AGE | RAS | RAS | RAS
|  | MGD | MGD
| 1 | 3.198 | 7.391 | 4610 | 0.4925 | 5110 | 2.2507 | 0.95 | 22 | 78
| 2 | 2.69 | 7.428 | 3840 | 1.0622 | 4730 | 0.82828 | 1.02 | 20.4 | 79.6
| 3 | 3.125 | 7.081 | 5280 | 0.56643 | 6430 | 0.97545 | 1.05 | 20.7 | 79.3
| 4 | 3.21 | 7.408 | 4040 | 0.95965 | 4800 | 0.67799 | 1.01 | 21.2 | 78.8
| 5 | 4.003 | 7.184 | 3310 | 1.3485 | 3950 | 0.88492 | 1.14 | 19.3 | 80.7
| 6 | 4.051 | 7.465 | 3990 | 1.0542 | 4650 | 1.5109 | 0.99 | 21.8 | 78.2
| 7 | 3.617 | 7.347 | 3510 | 1.3967 | 4220 | 1.3912 | 1.03 | 20 | 80
| 8 | 1.097 | 7.431 | 3620 | 1.1661 | 4260 | 1.1479 | 0.89 | 21.6 | 78.4
| 9 | 3.838 | 7.155 | 5560 | 0.68529 | 6600 | 1.4265 | 0.88 | 21 | 79
| 10 | 3.532 | 7.304 | 6300 | 0.80324 | 7500 | 0.74105 | 1.02 | 19.8 | 80.2
| 11 | 4.667 | 7.086 | 4320 | 0.91562 | 5180 | 0.71395 | 1.09 | 20 | 80
| 12 | 4.671 | 6.845 | 3000 | 1.5127 | 3550 | 1.2194 | 1.07 | 20.1 | 79.9
| 13 | 3.823 | 7.008 | 4780 | 0.68691 | 5810 | 1.1131 | 1.1 | 19.9 | 80.1
| 14 | 4.451 | 7.443 | 5030 | 0.73594 | 6100 | 1.1827 | 1.1 | 23.6 | 76.4
| 15 | 4.017 | 7.405 | 4930 | 0.85133 | 5910 | 1.1888 | 0.65 | 18.9 | 81.1
| 16 | 2.266 | 7.138 | 5490 | 1.0062 | 6770 | 1.1405 | 1.21 | 11.5 | 88.5
| 17 | 2.806 | 7.182 | 5640 | 0.6083 | 6930 | 1.9959 | 0.87 | 22.3 | 77.7
| 18 | 1.27 | 7.085 | 6760 | 0.54921 | 8050 | 2.0165 | 0.89 | 20.4 | 79.6
| 19 | 1.979 | 7.216 | 6380 | 0.58881 | 7600 | 1.5342 | 1.05 | 21.5 | 78.5
| 20 | 4.16 | 7.352 | 3840 | 0.94047 | 4490 | 1.0483 | 0.98 | 20.9 | 79.1
| 21 | 3.905 | 7.512 | 4470 | 0.92078 | 5300 | 0.9279 | 0.97 | 21.5 | 78.5
| 22 | 3.508 | 7.589 | 6640 | 0.48449 | 8010 | 2.023 | 1.14 | 20.1 | 79.9
| 23 | 4.578 | 7.253 | 6320 | 0.53251 | 7640 | 1.5012 | 1.17 | 19.2 | 80.8
| 24 | 4.727 | 6.793 | 6170 | 0.69375 | 7470 | 1.7619 | 1.11 | 20.6 | 79.4
| 25 | 4.72 | 7.017 | 6110 | 0.56596 | 7280 | 1.2331 | 1.04 | 21.4 | 78.6
| 26 | 4.082 | 6.982 | 5920 | 0.3241 | 7050 | 2.0306 | 1.15 | 21.5 | 78.5
| 27 | 2.825 | 6.725 | 4740 | 0.69049 | 5730 | 0.99295 | 1.18 | 21.1 | 78.9
| 28 | 2.04 | 6.447 | 5170 | 0.79335 | 6220 | 1.0426 | 0.88 | 21.4 | 78.6
| 29 | 4.181 | 5.851 | 5690 | 0.51349 | 6750 | 1.6403 | 1.1 | 20.8 | 79.2
| TOTAL | 101.037 | 207.123 | 145460 |  | 174090 |  | 29.73 | 594.5 | 2305.5
| AVERAGE | 3.484 | 7.1422 | 5015.8621 | 0.78155 | 6003.1034 | 1.1824 | 1.0252 | 20.5 | 79.5
PAGE 9
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
DEWATERING DATA
RUN DATE
| 2026-07-30 |  | FEED SLUDGE |  |  |  |  | FILTRATE RETURN
| FEBRUARY | % TOT. | % FIX. | % VOL. | pH |  | % TOT. | % FIX. | % VOL. | pH
| 2004 | FEED | FEED | FEED |  |  | FILT. | FILT. | FILT.
| 1 | 1.59 | 21.4 | 78.6 | 6.7 |  | 0.28 | 57.1 | 42.9 | 7.11
| 2 | 1.53 | 21.6 | 78.4 | 6.61 |  | 0.18 | 61.1 | 38.9 | 7.21
| 3 | 1.54 | 21.4 | 78.6 | 6.72 |  | 0.26 | 53.8 | 46.2 | 7.15
4
| 5 | 1.57 | 19.7 | 80.3 | 6.8 |  | 0.22 | 50 | 50 | 7.19
6
7
| 8 | 1.65 | 21.2 | 78.8 | 6.52 |  | 0.19 | 52.6 | 47.4 | 7.14
| 9 | 1.49 | 20.8 | 79.2 | 6.69 |  | 0.19 | 52.6 | 47.4 | 7.11
| 10 | 1.58 | 20.9 | 79.1 | 6.74 |  | 0.19 | 57.9 | 42.1 | 7.19
| 11 | 1.54 | 12.6 | 87.4 | 6.74 |  | 0.24 | 50 | 50 | 7.11
| 12 | 1.53 | 18.3 | 81.7 | 6.44 |  | 0.22 | 50 | 50 | 6.98
13
14
| 15 | 1.52 | 21.1 | 78.9 | 6.62 |  | 0.2 | 65 | 35 | 7.05
| 16 | 1.48 | 20.3 | 79.7 | 6.66 |  | 0.22 | 54.5 | 45.5 | 7.09
| 17 | 1.17 | 20.5 | 79.5 | 6.7 |  | 0.16 | 62.5 | 37.5 | 7.14
| 18 | 1.47 | 19.7 | 80.3 | 6.64 |  | 0.21 | 52.4 | 47.6 | 7.18
| 19 | 1.27 | 22.8 | 77.2 | 6.68 |  | 0.21 | 66.7 | 33.3 | 7.1
20
21
22
| 23 | 1.57 | 20.4 | 79.6 | 6.77 |  | 0.35 | 40 | 60 | 7.52
| 24 | 1.33 | 20.3 | 79.7 | 6.53 |  | 0.26 | 50 | 50 | 6.83
| 25 | 1.48 | 21.6 | 78.4 | 6.69 |  | 0.21 | 66.7 | 33.3 | 7.12
| 26 | 1.48 | 20.9 | 79.1 | 6.68 |  | 0.22 | 63.6 | 36.4 | 7.18
27
28
| 29 | 1.45 | 21.4 | 78.6 | 6.26 |  | 0.18 | 55.6 | 44.4 | 6.79
| TOTAL | 28.24 | 386.9 | 1513.1 | 126.19 |  | 4.19 | 1062.1 | 837.9 | 135.19
| AVERAGE | 1.4863 | 20.3632 | 79.6368 | 6.6416 |  | 0.22053 | 55.9 | 44.1 | 7.1153
PAGE 10
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
SLUDGE VOLUME REMOVED
RUN DATE
2026-07-30
|  | FEBRUARY | TRAILERS | TONS | DRY TONS | % LIME | % TOT. | % FIX. | % VOL.
|  | 2004 | REMOVED | SLUDGE | REMOVED | CAKE | CAKE | CAKE | CAKE
|  | 1 | 1 | 25 | 10.8074 |  | 16.66 | 14.8 | 85.2
|  | 2 | 6 | 150 | 20.7353 |  | 17.85 | 15.6 | 84.4
|  | 3 | 3 | 75 | 17.3389 |  | 16.31 | 14.7 | 85.3
|  | 4 | 4 | 100
|  | 5 | 4 | 100 | 23.5688 |  | 17.67 | 20.9 | 79.1
|  | 6 | 4 | 100
|  | 7 | 1 | 25
|  | 8 | 1 | 25 | 5.7108 |  | 17.68 | 16.5 | 83.5
|  | 9 | 4 | 100 | 29.2025 |  | 18.78 | 15.2 | 84.8
|  | 10 | 6 | 150 | 31.0323 |  | 17.87 | 14 | 86
|  | 11 | 5 | 125 | 24.3386 |  | 18.19 | 19.4 | 80.6
|  | 12 | 6 | 150 | 27.0516 |  | 18.96 | 18.96 | 81.04
|  | 13 | 5 | 125
|  | 14 | 0 | 0
|  | 15 | 1 | 25 | 7.7962 |  | 17.49 | 15.6 | 84.4
|  | 16 | 6 | 150 | 32.154 |  | 16.73 | 13.7 | 86.3
|  | 17 | 6 | 150 | 24.8336 |  | 17.49 | 15.1 | 84.9
|  | 18 | 4 | 100 | 21.5159 |  | 17.62 | 15 | 85
|  | 19 | 6 | 150 | 27.6446 |  | 17.46 | 13.5 | 86.5
|  | 20 | 6 | 150
|  | 21 | 1 | 25
|  | 22 | 0 | 0
|  | 23 | 6 | 150 | 35.0914 |  | 17.44 | 14.1 | 85.9
|  | 24 | 6 | 150 | 27.9523 |  | 17.47 | 14.1 | 85.9
|  | 25 | 4 | 100 | 24.3161 |  | 17.66 | 13.4 | 86.6
|  | 26 | 7 | 175 | 36.2273 |  | 17.36 | 13.4 | 86.6
|  | 27 | 7 | 175
|  | 28 | 0 | 0
|  | 29 | 0 | 0 | 14.9349 |  | 16.44 | 14.3 | 85.7
|  | TOTAL | 110 | 2750 | 442.2527 | 0 | 333.13 | 292.26 | 1607.74
|  | AVERAGE | 3.7931 | 94.8276 | 23.2765 | #DIV/0! | 17.5332 | 15.3821 | 84.6179
PAGE 11
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
CHEMICAL USEAGE
RUN DATE
2026-07-30
| FEBRUARY | H2O2 | CL2 | POLYMER | POLYMER | LIME | GOX | O2 % | LOX | FPL
| 2004 | POUNDS | POUNDS | GALLONS | POUNDS | DELV. | TONS | PURITY | TONS | KW
| 1 | 758 | 1360 | 28 | 233.52 | 0 | 17.1 | 100% | 183 | 31251
| 2 | 200 | 1240 | 0 | 0 | 0 | 17.9 | 100% | 184 | 31427
| 3 | 359 | 1260 | 66 | 550.44 | 0 | 18.4 | 100% | 185 | 31403
| 4 | 110 | 980 | 30 | 250.2 | 0 | 20 | 100% | 185 | 31462
| 5 | 170 | 1360 | 56 | 467.04 | 0 | 17.7 | 100% | 184 | 31579
| 6 | 210 | 1000 | 32 | 266.88 | 0 | 22 | 100% | 185 | 31336
| 7 | 519 | 1400 | 0 | 0 | 0 | 21.9 | 97% | 186 | 31172
| 8 | 140 | 1240 | 0 | 0 | 0 | 18.8 | 100% | 186 | 31804
| 9 | 1657 | 1160 | 41 | 341.94 | 0 | 20.3 | 100% | 186 | 31475
| 10 | 1458 | 920 | 81 | 675.54 | 0 | 20.9 | 100% | 187 | 31287
| 11 | 1367 | 1040 | 68 | 567.12 | 0 | 25.3 | 100% | 187 | 31176
| 12 | 4698 | 1200 | 103 | 859.02 | 0 | 21.8 | 100% | 188 | 30913
| 13 | 1407 | 0 | 38 | 316.92 | 0 | 27.6 | 97% | 188 | 30678
| 14 | 1517 | 0 | 9 | 75.06 | 0 | 24.8 | 99% | 188 | 31005
| 15 | 1587 | 1280 | 10 | 83.4 | 0 | 26 | 100% | 189 | 30909
| 16 | 1448 | 1200 | 58 | 483.72 | 0 | 21.6 | 99% | 186 | 31401
| 17 | 1627 | 620 | 64 | 533.76 | 0 | 25.4 | 100% | 187 | 30573
| 18 | 1757 | 1240 | 59 | 492.06 | 0 | 21.1 | 100% | 187 | 31501
| 19 | 1188 | 1300 | 75 | 625.5 | 0 | 24.6 | 100% | 189 | 31518
| 20 | 1716 | 1220 | 0 | 0 | 0 | 22.8 | 100% | 189 | 31189
| 21 | 1637 | 1080 | 0 | 0 | 0 | 23.3 | 99% | 191 | 31260
| 22 | 1557 | 1020 | 45 | 375.3 | 0 | 25.4 | 100% | 191 | 31884
| 23 | 1647 | 1020 | 143 | 1192.62 | 0 | 22.2 | 99% | 191 | 31679
| 24 | 1597 | 1140 | 121 | 1009.14 | 0 | 24.8 | 98% | 191 | 30374
| 25 | 1148 | 1100 | 54 | 450.36 | 0 | 25.9 | 99% | 191 | 29256
| 26 | 1148 | 1220 | 117 | 975.78 | 0 | 25.5 | 99% | 191 | 28249
| 27 | 1527 | 1600 | 66 | 550.44 | 0 | 28.2 | 97% | 190 | 28700
| 28 | 978 | 1380 | 0 | 0 | 0 | 29.8 | 94% | 192 | 28962
| 29 | 1278 | 1220 | 36 | 300.24 | 0 | 27.8 | 100% | 193 | 28486
| TOTAL | 36410 | 31800 | 1400 | 11676 | 0 | 668.9 |  | 5450 | 893909
| AVERAGE | 1255.5172 | 1096.5517 | 48.2759 | 402.6207 | 0 | 23.0655 | 99.21% | 187.931 | 30824.4483
PAGE 12
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL ONE
|  | RUN DATE |  |  | PERMIT NUMBER 0054569-142-UO
|  | 2026-07-30 |  |  | 1/07/04 thru 1/06/09 |  |  | I.D. #:5006A11308
|  | FEBRUARY | % INFL. | MAX | MIN | WELL 1 | MAX | MIN | AVG
|  | 2004 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 20.92% | 16.78 | 11.23 | 13.46 | 76.1 | 54.5 | 62.51
|  | 2 | 19.71% | 13.5 | 8.93 | 11.39 | 62.61 | 48.07 | 55.17
|  | 3 | 19.7% | 12.13 | 7.44 | 10.22 | 57.02 | 44.75 | 51.61
|  | 4 | 13.92% | 11.69 | 0 | 6.65 | 55.98 | 35.23 | 45.32
|  | 5 | 16.25% | 13.93 | 0 | 7.34 | 63.13 | 34.83 | 48.63
|  | 6 | 25.11% | 14.05 | 6.79 | 10.95 | 64.2 | 42.91 | 54.1
|  | 7 | 24.96% | 14.37 | 6.87 | 10.38 | 65.28 | 43.11 | 52.41
|  | 8 | 24.91% | 13.15 | 5.99 | 9.82 | 60.55 | 41.18 | 50.59
|  | 9 | 25.37% | 13.26 | 5.98 | 9.78 | 61.45 | 41.32 | 50.72
|  | 10 | 25.51% | 12.66 | 5.28 | 9.54 | 60.16 | 40.33 | 50.09
|  | 11 | 25.28% | 12.58 | 4.76 | 9.39 | 58.56 | 40.4 | 49.81
|  | 12 | 25.89% | 13.26 | 6.88 | 9.42 | 62.84 | 43.59 | 49.71
|  | 13 | 24.82% | 11.81 | 5.54 | 8.88 | 56.9 | 40.98 | 48.34
|  | 14 | 25.4% | 14.41 | 0.01 | 8.98 | 65.62 | 35.46 | 48.83
|  | 15 | 13.45% | 9.6 | 0 | 4.66 | 50.06 | 35.03 | 41.38
|  | 16 | 23.97% | 12.8 | 0.01 | 8.4 | 59.19 | 35.14 | 47.13
|  | 17 | 21.89% | 12.64 | 0 | 7.69 | 58.94 | 34.16 | 46.47
|  | 18 | 22.69% | 12.76 | 0 | 7.7 | 59.18 | 34.13 | 46.39
|  | 19 | 26.16% | 15.1 | 5.23 | 9.18 | 69.08 | 39.79 | 48.56
|  | 20 | 22.95% | 12.22 | 0 | 8.19 | 58.67 | 34.27 | 47.39
|  | 21 | 32.89% | 16.02 | 6.61 | 11.74 | 70.8 | 42.02 | 56.45
|  | 22 | 26.9% | 13.43 | 4.82 | 9.43 | 61.45 | 38.82 | 49.14
|  | 23 | 27.66% | 15.37 | 0.01 | 9.65 | 69.1 | 35.26 | 50.63
|  | 24 | 26.46% | 13.5 | 5.85 | 9.17 | 62.79 | 41.1 | 48.71
|  | 25 |  | 12.6 | ER | ER | 59.21 | 34.71 | 47.4
|  | 26 | 16.25% | 11.96 | 0 | 6.31 | 58.37 | 34.94 | 45.76
|  | 27 | 25.52% | 12.54 | 5.57 | 9.34 | 59.82 | 40.56 | 49.67
|  | 28 | 26.92% | 15.59 | 0 | 9.48 | 69.53 | 34.94 | 50.19
|  | 29 | 16.04% | 11.85 | 0 | 5.61 | 56.73 | 34.59 | 44.14
|  | TOTAL | 647.5% | 385.56 | 103.8 | 252.75 | 1793.32 | 1136.12 | 1437.25
|  | AVERAGE | 23.12% | 13.2952 | 3.7071 | 9.0268 | 61.8386 | 39.1766 | 49.5603
|  | MAXIMUM | 32.89% | 16.78 | 11.23 | 13.46 | 76.1 | 54.5 | 62.51
|  | MINIMUM | 13.45% | 9.6 | 0 | 4.66 | 50.06 | 34.13 | 41.38
PAGE 13
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL TWO
|  | RUN DATE |  |  | PERMIT NUMBER 0054569-142-UO
|  | 2026-07-30 |  |  | 1/07/04 thru 1/06/09 |  |  | I.D. #:5006A11309
|  | FEBRUARY | % INFL. | MAX | MIN | WELL 2 | MAX | MIN | AVG
|  | 2004 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 21.17% | 17.11 | 11.37 | 13.62 | 74.6 | 53.46 | 61.36
|  | 2 | 20.02% | 13.68 | 9.12 | 11.57 | 61.53 | 47.14 | 54.16
|  | 3 | 20.03% | 12.26 | 7.53 | 10.39 | 56.11 | 43.87 | 50.68
|  | 4 | 21.69% | 13.82 | 5.63 | 10.36 | 60.25 | 40.55 | 50.71
|  | 5 | 25.62% | 14.34 | 7.6 | 11.57 | 62.02 | 43.07 | 53.78
|  | 6 | 25.55% | 14.25 | 6.84 | 11.14 | 63.04 | 42.04 | 53.09
|  | 7 | 25.34% | 14.54 | 6.94 | 10.54 | 64.15 | 42.26 | 51.42
|  | 8 | 25.29% | 13.37 | 6.03 | 9.97 | 59.41 | 40.32 | 49.56
|  | 9 | 24.69% | 13.62 | 0.02 | 9.52 | 60.23 | 35.42 | 49
|  | 10 | 25.91% | 12.93 | 5.18 | 9.69 | 59.04 | 39.52 | 49.17
|  | 11 | 25.63% | 12.49 | 5.05 | 9.52 | 57.73 | 39.63 | 48.88
|  | 12 | 26.3% | 13.54 | 6.99 | 9.57 | 61.63 | 42.76 | 48.78
|  | 13 | 25.18% | 12.09 | 5.56 | 9.01 | 55.79 | 40.18 | 47.45
|  | 14 | 25.88% | 14.8 | 5.62 | 9.15 | 59.19 | 40.18 | 47.97
|  | 15 | 22.9% | 13.57 | 0.02 | 7.93 | 60.48 | 35.42 | 45.13
|  | 16 | 6.05% | 12.57 | 0.02 | 2.12 | 56.73 | 34.96 | 38.74
|  | 17 | 11.13% | 12.65 | 0.02 | 3.91 | 57.77 | 34.21 | 40.45
|  | 18 | 27.26% | 13.01 | 5.06 | 9.25 | 58.02 | 38.6 | 47.22
|  | 19 | 26.73% | 15.45 | 5.2 | 9.38 | 67.78 | 38.95 | 47.6
|  | 20 | 26.22% | 12.49 | 4.58 | 9.36 | 57.52 | 38.16 | 47.66
|  | 21 | 33.87% | 16.38 | 6.83 | 12.09 | 69.58 | 41.17 | 55.37
|  | 22 | 27.56% | 13.73 | 4.78 | 9.66 | 60.49 | 38.04 | 48.21
|  | 23 | 24.22% | 15.58 | 0.02 | 8.45 | 67.93 | 34.86 | 48.09
|  | 24 | 26.95% | 13.8 | 5.87 | 9.34 | 61.62 | 40.29 | 47.8
|  | 25 | 27.17% | 12.85 | 6.18 | 9.74 | 58.12 | 40.76 | 49.1
|  | 26 | 28.95% | 18.79 | 7.42 | 11.24 | 79.4 | 43.84 | 53.53
|  | 27 | 25.82% | 12.85 | 5.45 | 9.45 | 58.62 | 39.74 | 48.67
|  | 28 | 27.89% | 15.84 | 5.5 | 9.82 | 68.14 | 40.08 | 49.56
|  | 29 | 28.67% | 16.57 | 7.19 | 10.03 | 69.31 | 41.89 | 49.82
|  | TOTAL | 709.7% | 408.97 | 153.62 | 277.39 | 1806.23 | 1171.37 | 1432.96
|  | AVERAGE | 24.47% | 14.1024 | 5.2972 | 9.5652 | 62.2838 | 40.3921 | 49.4124
|  | MAXIMUM | 33.87% | 18.79 | 11.37 | 13.62 | 79.4 | 53.46 | 61.36
|  | MINIMUM | 6.05% | 12.09 | 0.02 | 2.12 | 55.79 | 34.21 | 38.74
PAGE 14
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL THREE
|  | RUN DATE |  |  | PERMIT NUMBER 0054569-142-UO
|  | 2026-07-30 |  |  | 1/07/04 thru 1/06/09 |  |  | I.D. #:5006A11310
|  | FEBRUARY | % INFL. | MAX | MIN | WELL 3 | MAX | MIN | AVG
|  | 2004 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 18.19% | 15.03 | 9.62 | 11.7 | 76.6 | 54.69 | 62.82
|  | 2 | 16.98% | 11.58 | 7.71 | 9.81 | 62.9 | 48.25 | 55.39
|  | 3 | 16.89% | 10.29 | 6.41 | 8.76 | 57.25 | 44.93 | 51.81
|  | 4 | 18.13% | 11.42 | 4.74 | 8.66 | 61.57 | 41.46 | 51.82
|  | 5 | 21.92% | 12.37 | 6.22 | 9.9 | 63.54 | 44.03 | 55.04
|  | 6 | 22.32% | 12.44 | 5.96 | 9.73 | 64.62 | 43.06 | 54.39
|  | 7 | 22.19% | 12.67 | 6.06 | 9.23 | 65.74 | 43.29 | 52.67
|  | 8 | 22.14% | 11.66 | 5.25 | 8.73 | 60.95 | 41.33 | 50.84
|  | 9 | 22.64% | 11.94 | 5.3 | 8.73 | 61.81 | 41.46 | 50.94
|  | 10 | 22.73% | 11.34 | 4.57 | 8.5 | 60.56 | 40.46 | 50.35
|  | 11 | 21.56% | 11.03 | ER | 8.01 | 58.9 | 35.51 | 49.49
|  | 12 | 23.08% | 11.92 | 6.14 | 8.4 | 63.21 | 43.77 | 49.91
|  | 13 | 17.16% | 10.44 | ER | 6.14 | 57.14 | 35.71 | 46.22
|  | 14 | 14.43% | 9.87 | ER | 5.1 | 54.84 | 36.03 | 44.49
|  | 15 | 20.27% | 11.44 | 4.75 | 7.02 | 61.87 | 41.9 | 46.61
|  | 16 | 21.55% | 11 | 3.66 | 7.55 | 59.33 | 38.83 | 48
|  | 17 | 20.26% | 11.18 | ER | 7.12 | 59.3 | 36.57 | 47.6
|  | 18 | 23.75% | 11.46 | 4.46 | 8.06 | 59.62 | 39.53 | 48.29
|  | 19 | 19.64% | 13.7 | ER | 6.89 | 69.6 | 34.79 | 46.94
|  | 20 | 22.92% | 10.94 | 4.01 | 8.18 | 59.01 | 39.07 | 48.81
|  | 21 | 0.6443% | 8.94 | ER | 0.23 | 50.89 | 35.06 | 36.21
|  | 22 | 17.09% | 12.08 | ER | 5.99 | 61.83 | 34.64 | 45.45
|  | 23 | 24.48% | 15.38 | ER | 8.54 | 75.9 | 36.14 | 50.58
|  | 24 | 23.87% | 12.19 | 5.26 | 8.27 | 63.14 | 41.25 | 48.98
|  | 25 |  | 11.38 | ER | ER | 59.55 | 41.71 | 50.27
|  | 26 | 25.21% | 16.11 | 6.34 | 9.79 | 81.5 | 44.77 | 54.84
|  | 27 | 22.81% | 11.36 | 4.84 | 8.35 | 60.19 | 40.71 | 49.9
|  | 28 | 24.7% | 14.05 | 4.88 | 8.7 | 70.1 | 41.06 | 50.85
|  | 29 | 25.02% | 14.19 | 6.12 | 8.75 | 71 | 42.87 | 51.02
|  | TOTAL | 572.6% | 349.4 | 112.3 | 224.84 | 1832.46 | 1182.88 | 1450.53
|  | AVERAGE | 20.45% | 12.0483 | 5.615 | 8.03 | 63.1883 | 40.789 | 50.0183
|  | MAXIMUM | 25.21% | 16.11 | 9.62 | 11.7 | 81.5 | 54.69 | 62.82
|  | MINIMUM | 0.6443% | 8.94 | 3.66 | 0.23 | 50.89 | 34.64 | 36.21
PAGE 15
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL FOUR
|  | RUN DATE |  |  | PERMIT NUMBER 0054569-142-UO
|  | 2026-07-30 |  |  | 1/07/04 thru 1/06/09
|  | FEBRUARY | % INFL. | MAX | MIN | WELL 4 | MAX | MIN | AVG
|  | 2004 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 18.64% | 18.94 | 0.12 | 11.99 | 74.5 | 35.7 | 55.58
|  | 2 | 23.62% | 16.02 | 10.9 | 13.65 | 62.5 | 48.47 | 55.35
|  | 3 | 23.86% | 14.44 | 9.3 | 12.38 | 57.17 | 45.27 | 51.91
|  | 4 | 25.8% | 15.88 | 7.37 | 12.32 | 61.07 | 41.93 | 51.83
|  | 5 | 10.72% | 16.39 | 0.12 | 4.84 | 62.78 | 36.39 | 42.59
|  | 6 | 0.2982% | 0.15 | 0.12 | 0.13 | 37.6 | 35.76 | 36.78
|  | 7 | 0.3126% | 0.15 | 0.11 | 0.13 | 37.78 | 35.77 | 36.63
|  | 8 | 0.3043% | 0.13 | 0.11 | 0.12 | 37.2 | 35.43 | 36.3
|  | 9 | 0.3372% | 0.16 | 0.12 | 0.13 | 37.15 | 35.33 | 36.3
|  | 10 | 0.3476% | 0.16 | 0.12 | 0.13 | 37.15 | 35.23 | 36.33
|  | 11 | 0.8344% | 15.06 | 0.13 | 0.31 | 62.78 | 35.3 | 36.71
|  | 12 | 13.58% | 13.58 | 0.13 | 4.94 | 58.43 | 35.31 | 41.58
|  | 13 | 31.94% | 14.83 | 7.73 | 11.43 | 56.99 | 41.61 | 48.75
|  | 14 | 32.81% | 18.14 | 7.67 | 11.6 | 60.16 | 41.59 | 49.25
|  | 15 | 29.48% | 16.21 | 7.35 | 10.21 | 61.57 | 42.37 | 46.92
|  | 16 | 25.4% | 15.15 | 0.12 | 8.9 | 59.24 | 36.44 | 45.98
|  | 17 | 23.57% | 14.96 | 0.12 | 8.28 | 58.13 | 35.83 | 45.58
|  | 18 | 0.5599% | 5.6 | 0.11 | 0.19 | 43.13 | 35.5 | 36.26
|  | 19 | 0.342% | 0.14 | 0.11 | 0.12 | 37.96 | 34.44 | 36.02
|  | 20 | 0.3362% | 0.14 | 0.12 | 0.12 | 37.13 | 35.1 | 36.13
|  | 21 | 0.3642% | 0.15 | 0.12 | 0.13 | 36.54 | 34.94 | 35.82
|  | 22 | 0.3708% | 0.15 | 0.12 | 0.13 | 37.47 | 34.81 | 36.05
|  | 23 | 0.4586% | 4.96 | 0.12 | 0.16 | 42.61 | 35.17 | 36.22
|  | 24 | 0.3752% | 0.14 | 0.12 | 0.13 | 37.47 | 34.96 | 36.18
|  | 25 | 0.3627% | 0.38 | 0.12 | 0.13 | 37.38 | 35.58 | 36.49
|  | 26 | 1.468% | 11.19 | 0.12 | 0.57 | 49.86 | 35.94 | 37.41
|  | 27 | 0.3278% | 0.13 | 0.11 | 0.12 | 37.32 | 35.72 | 36.5
|  | 28 | 0.3408% | 0.14 | 0.1 | 0.12 | 36.99 | 35.11 | 36.05
|  | 29 | 0.3431% | 0.14 | 0.12 | 0.12 | 37.71 | 35.63 | 36.37
|  | TOTAL | 267.5% | 213.61 | 53.03 | 113.53 | 1393.77 | 1076.63 | 1189.87
|  | AVERAGE | 9.224% | 7.3659 | 1.8286 | 3.9148 | 48.061 | 37.1252 | 41.03
|  | MAXIMUM | 32.81% | 18.94 | 10.9 | 13.65 | 74.5 | 48.47 | 55.58
|  | MINIMUM | 0.2982% | 0.13 | 0.1 | 0.12 | 36.54 | 34.44 | 35.82
PAGE 16
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL FIVE
|  | RUN DATE |  |  | PERMIT NUMBER 0054569-142-UO
|  | 2026-07-30 |  |  | 1/07/04 thru 1/06/09 |  |  | I.D. #:5006A11311
|  | FEBRUARY | % INFL. | MAX | MIN | WELL 5 | MAX | MIN | AVG
|  | 2004 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 17.21% | 14.8 | ER | 11.07 | 76 | 34.14 | 61.45
|  | 2 | 16.8% | 11.45 | 7.71 | 9.71 | 62.59 | 48.2 | 55.18
|  | 3 | 16.85% | 10.24 | 6.44 | 8.74 | 57.05 | 25.67 | 51.35
|  | 4 | 18.07% | 11.2 | 4.96 | 8.63 | 61.24 | 41.25 | 51.5
|  | 5 | 21.76% | 12.23 | 4.54 | 9.83 | 62.97 | 42.48 | 54.58
|  | 6 | 22.43% | 12.38 | 6.26 | 9.78 | 63.99 | 42.79 | 53.96
|  | 7 | 22.36% | 12.68 | 6.38 | 9.3 | 65.08 | 43.01 | 52.27
|  | 8 | 22.39% | 11.64 | 5.64 | 8.83 | 60.44 | 41.16 | 50.49
|  | 9 | 22.88% | 11.85 | 5.62 | 8.82 | 61.33 | 41.17 | 50.52
|  | 10 | 22.99% | 11.31 | 4.96 | 8.6 | 60.1 | 40.22 | 49.95
|  | 11 | 22.66% | 11.87 | 0.28 | 8.42 | 64.55 | 35.08 | 49.55
|  | 12 | 7.914% | 11.81 | ER | 2.88 | 62.72 | 34.02 | 40.47
|  | 13 |  | ER | ER | ER | 36.31 | 34.68 | 35.53
|  | 14 |  | ER | ER | ER | 36.05 | 34.72 | 35.43
|  | 15 | 11.17% | 8.06 | ER | 3.87 | 49.42 | 34.94 | 41.11
|  | 16 | 21.43% | 10.65 | 3.94 | 7.51 | 59.01 | 38.73 | 47.72
|  | 17 | 22.43% | 11.02 | 4.39 | 7.88 | 58.91 | 39.48 | 48.5
|  | 18 | 24.02% | 11.3 | 4.79 | 8.15 | 59.19 | 39.41 | 48.12
|  | 19 | 23.28% | 13.39 | ER | 8.17 | 69.14 | 33.74 | 48.29
|  | 20 | 23.06% | 10.81 | 4.4 | 8.23 | 58.62 | 38.87 | 48.49
|  | 21 | 29.38% | 14.09 | 6.14 | 10.49 | 70.6 | 41.98 | 56.34
|  | 22 | 24.22% | 11.88 | 4.54 | 8.49 | 61.27 | 38.82 | 48.99
|  | 23 | 20.29% | 14.84 | ER | 7.08 | 75.2 | 33.88 | 46.83
|  | 24 | 18.73% | 11.96 | ER | 6.49 | 62.59 | 33.5 | 45.61
|  | 25 | 23.85% | 11.16 | 5.46 | 8.55 | 59.04 | 41.46 | 49.93
|  | 26 | 24.98% | 15.73 | 6.34 | 9.7 | 80.8 | 44.43 | 54.38
|  | 27 | 22.89% | 11.18 | 5.15 | 8.38 | 59.75 | 40.52 | 49.61
|  | 28 | 16.24% | 10.98 | ER | 5.72 | 57.7 | 33.59 | 44.66
|  | 29 | 24.99% | 13.88 | 6.28 | 8.74 | 70.4 | 42.56 | 50.62
|  | TOTAL | 565.3% | 324.39 | 104.22 | 222.06 | 1782.06 | 1114.5 | 1421.43
|  | AVERAGE | 20.94% | 12.0144 | 5.211 | 8.2244 | 61.4503 | 38.431 | 49.0148
|  | MAXIMUM | 29.38% | 15.73 | 7.71 | 11.07 | 80.8 | 48.2 | 61.45
|  | MINIMUM | 7.914% | 8.06 | 0.28 | 2.88 | 36.05 | 25.67 | 35.43
PAGE 17
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
INJECTION WELL SUMMARY
RUN DATE
2026-07-30
| FEBRUARY | INFLUENT | EFFLUENT | EFFLUENT | IW-1 | IW-2 | IW-3 | IW-4 | IW-5 | TOTAL
| 2004 | FLOW | FLOW | SS | LBS SS | LBS SS | LBS SS | LBS SS | LBS SS | LBS SS
|  | MGD | MGD
| 1 | 64.329 | 61.984 | 22 | 2469.6408 | 2498.9976 | 2146.716 | 2199.9252 | 2031.1236 | 9146.478
| 2 | 57.786 | 56.028 | 44 | 4179.6744 | 4245.7272 | 3599.8776 | 5009.004 | 3563.1816 | 15588.4608
| 3 | 51.88 | 50.404 | 29 | 2471.8092 | 2512.9254 | 2118.6936 | 2994.2268 | 2113.8564 | 9217.2846
| 4 | 47.76 | 46.552 | 15 | 831.915 | 1296.036 | 1083.366 | 1541.232 | 1079.613 | 4290.93
| 5 | 45.168 | 43.397 | 14 | 857.0184 | 1350.9132 | 1155.924 | 565.1184 | 1147.7508 | 4511.6064
| 6 | 43.6 | 41.688 | 30 | 2739.69 | 2787.228 | 2434.446 | 32.526 | 2446.956 | 10408.32
| 7 | 41.587 | 39.508 | 19 | 1644.8148 | 1670.1684 | 1462.5858 | 20.5998 | 1473.678 | 6251.247
| 8 | 39.429 | 37.409 | 14 | 1146.5832 | 1164.0972 | 1019.3148 | 14.0112 | 1030.9908 | 4360.986
| 9 | 38.556 | 36.934 | 20 | 1631.304 | 1587.936 | 1456.164 | 21.684 | 1471.176 | 6146.58
| 10 | 37.403 | 36.412 | 18 | 1432.1448 | 1454.6628 | 1276.02 | 19.5156 | 1291.032 | 5453.8596
| 11 | 37.151 | 35.612 | 19 | 1487.9394 | 1508.5392 | 1269.2646 | 49.1226 | 1334.2332 | 5599.9764
| 12 | 36.39 | 35.115 | 13 | 1021.3164 | 1037.5794 | 910.728 | 535.5948 | 312.2496 | 3281.8734
| 13 | 35.781 | 35.419 | 17 | 1259.0064 | 1277.4378 | 870.5292 | 1620.5454
| 14 | 35.354 | 34.768 | 13 | 973.6116 | 992.043 | 552.942 | 1257.672
| 15 | 34.636 | 33.648 | 9 | 349.7796 | 595.2258 | 526.9212 | 766.3626 | 290.4822 | 1762.4088
| 16 | 35.04 | 34.446 | 18 | 1261.008 | 318.2544 | 1133.406 | 1336.068 | 1127.4012 | 3840.0696
| 17 | 35.135 | 34.9 | 21 | 1346.8266 | 684.7974 | 1246.9968 | 1450.1592 | 1380.1032 | 4658.724
| 18 | 33.933 | 33.292 | 24 | 1541.232 | 1851.48 | 1613.2896 | 38.0304 | 1631.304 | 6637.3056
| 19 | 35.089 | 33.685 | 15 | 1148.418 | 1173.438 | 861.939 | 15.012 | 1022.067 | 4205.862
| 20 | 35.694 | 34.079 | 15 | 1024.569 | 1170.936 | 1023.318 | 15.012 | 1029.573 | 4248.396
| 21 | 35.699 | 34.634 | 12 | 1174.9392 | 1209.9672 | 23.0184 | 13.0104 | 1049.8392 | 3457.764
| 22 | 35.057 | 33.622 | 14 | 1101.0468 | 1127.9016 | 699.3924 | 15.1788 | 991.2924 | 3919.6332
| 23 | 34.886 | 33.877 | 15 | 1207.215 | 1057.095 | 1068.354 | 20.016 | 885.708 | 4218.372
| 24 | 34.651 | 33.322 | 18 | 1376.6004 | 1402.1208 | 1241.4924 | 19.5156 | 974.2788 | 4994.4924
| 25 | 35.845 | 34.645 | 12 |  | 974.7792 |  | 13.0104 | 855.684
| 26 | 38.83 | 37.552 | 22 | 1157.7588 | 2062.3152 | 1796.2692 | 104.5836 | 1779.756 | 6796.0992
| 27 | 36.605 | 35.611 | 15 | 1168.434 | 1182.195 | 1044.585 | 15.012 | 1048.338 | 4443.552
| 28 | 35.216 | 33.794 | 20 | 1581.264 | 1637.976 | 1451.16 | 20.016 | 954.096 | 5624.496
| 29 | 34.979 | 33.219 | 12 | 561.4488 | 1003.8024 | 875.7 | 12.0096 | 874.6992 | 3315.6504
| TOTAL | 1143.469 | 1105.556 | 529 | 40147.0086 | 42836.5752 | 35962.4136 | 19733.7744 | 35190.4632 | 146380.4274
| AVERAGE | 39.43 | 38.1226 | 18.2414 | 1433.8217 | 1477.1233 | 1284.3719 | 680.475 | 1303.3505 | 5630.0164
PAGE 18
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
| RUN DATE |  |  |  | SOLIDS REMOVAL INVENTORY DATA SHEET
2026-07-30
| FEBRUARY | TONS | CAKE |  |  |  | FEBRUARY | RAGS | GRIT | OTHER
| 2004 | SLUDGE | TSS |  |  |  | 2004 |  |  | (vac)
| 1st - 7th | [5 empty] | 1st - 7th
| 1 | 25 | 16.66 |  |  |  | 1 |  | 10
| 2 | 150 | 17.85 |  |  |  | 2
| 3 | 75 | 16.31 |  |  |  | 3
| 4 | 100 |  |  |  |  | 4
| 5 | 100 | 17.67 |  |  |  | 5 |  | 10
| 6 | 100 |  |  |  |  | 6
| 7 | 25 |  |  |  |  | 7
| TOTAL = | 575 | 17.1225 | = AVG. |  |  | TOTAL = | 0 | 20 | 0
| 8th - 14th | [5 empty] | 8th - 14th
| 8 | 25 | 17.68 |  |  |  | 8
| 9 | 100 | 18.78 |  |  |  | 9 | 10 | 10
| 10 | 150 | 17.87 |  |  |  | 10
| 11 | 125 | 18.19 |  |  |  | 11
| 12 | 150 | 18.96 |  |  |  | 12 |  | 10
| 13 | 125 |  |  |  |  | 13 | 10
| 14 | 0 |  |  |  |  | 14
| TOTAL = | 675 | 18.296 | = AVG. |  |  | TOTAL = | 20 | 20 | 0
| 15th - 22nd | [5 empty] | 15th-22nd
| 15 | 25 | 17.49 |  |  |  | 15
| 16 | 150 | 16.73 |  |  |  | 16
| 17 | 150 | 17.49 |  |  |  | 17
| 18 | 100 | 17.62 |  |  |  | 18
| 19 | 150 | 17.46 |  |  |  | 19 |  | 10
| 20 | 150 |  |  |  |  | 20 | 10
| 21 | 25 |  |  |  |  | 21
| 22 | 0 |  |  |  |  | 22
| TOTAL = | 750 | 17.358 | = AVG. |  |  | TOTAL = | 10 | 10 | 0
| 23rd - 31st | [5 empty] | 23rd-31st
| 23 | 150 | 17.44 |  |  |  | 23
| 24 | 150 | 17.47 |  |  |  | 24
| 25 | 100 | 17.66 |  |  |  | 25
| 26 | 175 | 17.36 |  |  |  | 26 | 10 | 10
| 27 | 175 |  |  |  |  | 27
| 28 | 0 |  |  |  |  | 28
| 29 | 0 | 16.44 |  |  |  | 29
| TOTAL = | 750 | 17.274 | = AVG. |  |  | TOTAL = | 10 | 10 | 0
RAGS & GRIT go to Central LandFill
Other(VAC) go to BCSR
PAGE 19

## INJECTION PAGES
|  |  |  | UNDERGROUND INJECTION CONTROL | [10 empty] | UNDERGROUND INJECTION CONTROL | [10 empty] | UNDERGROUND INJECTION CONTROL
[15 empty] | MONTHLY OPERATING REPORT | [10 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES |  |  |  |  | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES |  |  |  |  | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [10 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [10 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-1 | [7 empty] | Wet Well Description: |  |  | Effuent Wet Well for IW-1, IW-2, IW3, IW-4 and IW-5 | [7 empty] | Monitoring Well Decription: |  |  | UPPER ZONE OF MONITORING WELL MW-1
Permit #: |  | 0054569-142-UO |  |  |  |  | Date of Issuance: |  | 2004-01-07 |  | Facility ID #: |  | 5006M02066 |  |  |  | Permit Number: |  |  | FLA041378 |  | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | 0054569-142-UO
[22 empty] | Monitoring Well ID #: |  |  | 5006A11311
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2009-01-06 | [7 empty] | Issue Date: |  |  | 1999-10-18 |  | As Identified in Permit: |  | Monitor Well MW-1 Upper Monitor Zone |  |  |  | Issue Date: |  |  | 2004-01-07
[22 empty] | Monitoring Well Interval: |  |  | 1288' to 1320'
Injection Well ID #: |  | 5006A11308 | [8 empty] | Wet Well ID #: |  | Well Facility U-001 |  |  |  | Expiration Date: |  |  | 2004-10-17 |  | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.7 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24 | Associated Injection Well(s):
Injection Interval: |  |  | 2799' to 3513' | [18 empty] | 500A11311 |  |  | INJECTION WELL IW-5
[11 empty] | Injection Well ID #: |  |  | Injection Well Description
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s): | [10 empty] | 5006A11308 |  |  | INJECTION WELL IW-1
[11 empty] | 5006A11309 |  |  | INJECTION WELL IW-2 | [7 empty] | REPORT MONTH / YEAR: |  | 2004-02-01 | DATE OF SAP / RECORDING: |  |  | 2004-02-03 | 2004-02-10 | 2004-02-17 | 2004-02-24
Monitoring Zone ID #: | [5 empty] | Description |  |  |  |  | 5006A11310 |  |  | INJECTION WELL IW-3
[11 empty] | N/A |  |  | INJECTION WELL IW-4 | [7 empty] | OPERATOR'S NAME: |  |  | BAYLER, J.
UO-06-279401 |  | UPPER ZONE OF MONITORING WELL MW-2 | [8 empty] | 5006A11311 |  |  | INJECTION WELL IW-5
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A
UO-06-279401 |  | LOWER ZONE OF MONITORING WELL MW-2
[11 empty] | THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [10 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [10 empty] | REPORT MONTH / YEAR: |  | 2004-02-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous |  |  | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2004-02-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous |  |  | OPERATOR'S NAME: |  |  | BAYLER, J.
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
OPERATOR'S NAME: |  |  | BAYLER, J. | [7 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A | [7 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4474-A | [7 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: |  |  |  | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 48.86 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 45.71 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: |  |  |  | PARAMETER |  |  |  | Sampling Frequency |  |  |  | VALUE |  | UNITS | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 48.31 | PSIG
[11 empty] | Nitrogen, Total as N |  |  |  |  | Daily/Monthly Average |  |  | 16.0112 |  | mg/L as N | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[11 empty] | Nitrogen, Nitrate, Total as N |  |  |  |  | Daily/Monthly Average |  |  | 0.25071 |  | mg/L as N | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7323 | mg/l
Total monthly flow | [7 empty] | 252.75 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 4037.5 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [7 empty] | Nitrogen, Total Kjeildahl as N |  |  |  |  | Daily/Monthly Average |  |  | 15.7605 |  | mg/L as N | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.869 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 16.78 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.5625 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 76.1 |  | PSIG | pH |  |  |  |  | Daily/Monthly Average |  |  | 6.5103 |  | s.u. | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 8.045 | Std units
Monthly average of the daily flow rates | [7 empty] | 9.0268 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 12417.5 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 16.0724 |  | MG | Phosphorus, Total as P |  |  |  |  | Daily/Monthly Average |  |  | 0.97576 |  | mg/L as P | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 2.896 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 73.5 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [10 empty] | Total Dissolved Solids (TDS) |  |  |  |  | Daily/Monthly Average |  |  | 1148.3103 |  | mg/L | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.05 | mg/l
Monthly average pressure | [7 empty] | 49.5603 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 887.5 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 35.5 |  | PSIG | Residue, Total filterable (TSS dried at 180 C) |  |  |  |  | Daily/Monthly Average |  |  | 18.2414 |  | mg/L | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 145 | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.8675 | mg/l
[11 empty] | Specific Conductance (Temperature Compensated) |  |  |  |  | Daily/Monthly Average |  |  | 2351.5862 |  | umhos/cm | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just | [6 empty] | Temperature, Water |  |  |  |  | Daily/Monthly Average |  |  | 79.1034 |  | deg C
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [9 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just |  |  | Date: |  |  |  |  | (Signature):
[12 empty] | (Signature): | [10 empty] | Date:
|  |  |  | UNDERGROUND INJECTION CONTROL | [21 empty] | UNDERGROUND INJECTION CONTROL
|  |  |  | MONTHLY OPERATING REPORT | [21 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES | [15 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [21 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-2 | [18 empty] | Monitoring Well Decription: |  |  | LOWER ZONE OF MONITORING WELL MW-1
Permit #: |  | 0054569-142-UO |  |  |  |  | Date of Issuance: |  | 2004-01-07 | [12 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | 0054569-142-UO
[22 empty] | Monitoring Well ID #: |  |  | 5006A11311
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2009-01-06 | [12 empty] | As Identified in Permit: |  | Monitor Well MW-1 Lower Monitor Zone |  |  |  | Issue Date: |  |  | 2004-01-07
[22 empty] | Monitoring Well Interval: |  |  | 1449' to 1557'
Injection Well ID #: |  | 5006A11309 | [19 empty] | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.7 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24
Injection Interval: |  |  | 2798' to 3518' | [18 empty] | 500A11311 |  |  | INJECTION WELL IW-5
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s):
[22 empty] | REPORT MONTH / YEAR: |  | 2004-02-01 | DATE OF SAP / RECORDING: |  |  | 2004-02-03 | 2004-02-10 | 2004-02-17 | 2004-02-24
Monitoring Zone ID #: | [5 empty] | Description
[22 empty] | OPERATOR'S NAME: |  |  | BAYLER, J.
UO-06-279401 |  | UPPER ZONE OF MONITORING WELL MW-2
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A
UO-06-279401 |  | LOWER ZONE OF MONITORING WELL MW-2
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [21 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2004-02-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
OPERATOR'S NAME: |  |  | BAYLER, J. | [18 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4474-A | [18 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 42.12 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 29.21 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: | [14 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 40.6928 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 9255 | mg/l
Total monthly flow | [7 empty] | 277.39 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 5575 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [18 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 9.58 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 18.79 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 11.505 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 79.4 |  | PSIG | [11 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7.42 | Std units
Monthly average of the daily flow rates | [7 empty] | 9.5652 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 16157.5 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 17.0087 |  | MG | [11 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 2.896 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 73.5 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [21 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.05 | mg/l
Monthly average pressure | [7 empty] | 49.4124 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 800 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 36.5 |  | PSIG | [11 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 230 | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.0225 | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [21 empty] | (Signature):
Date:
|  |  |  | UNDERGROUND INJECTION CONTROL | [21 empty] | UNDERGROUND INJECTION CONTROL
|  |  |  | MONTHLY OPERATING REPORT | [21 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES | [15 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [21 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-3 | [18 empty] | Monitoring Well Decription: |  |  | UPPER ZONE OF MONITORING WELL MW-2
Permit #: |  | 0054569-142-UO |  |  |  |  | Date of Issuance: |  | 2004-01-07 | [12 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | 0054569-142-UO
[22 empty] | Monitoring Well ID #: |  |  | 5006A11308 & 309
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2009-01-06 | [12 empty] | As Identified in Permit: |  | Monitor Well MW-2 Upper Monitor Zone |  |  |  | Issue Date: |  |  | 2004-01-07
[22 empty] | Monitoring Well Interval: |  |  | 1300' to 1344'
Injection Well ID #: |  | 5006A11310 | [19 empty] | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.7 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24
Injection Interval: |  |  | 2800' to 3977' | [18 empty] | 5006A11308 |  |  | INJECTION WELL IW-1
[22 empty] | 5006A11309 |  |  | INJECTION WELL IW-2
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s):
[22 empty] | REPORT MONTH / YEAR: |  | 2004-02-01 | DATE OF SAP / RECORDING: |  |  | 2004-02-03 | 2004-02-10 | 2004-02-17 | 2004-02-24
Monitoring Zone ID #: | [5 empty] | Description
[22 empty] | OPERATOR'S NAME: |  |  | BAYLER, J.
UO-06-279510 |  | UPPER ZONE OF MONITORING WELL MW-3
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A
UO-06-279510 |  | LOWER ZONE OF MONITORING WELL MW-3
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [21 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2004-02-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
OPERATOR'S NAME: |  |  | BAYLER, J. | [18 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4474-A | [18 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 48.86 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 45.71 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: | [14 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 48.2517 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7166.75 | mg/l
Total monthly flow | [7 empty] | 224.84 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 3950 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [18 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 2.7635 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 16.11 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.62 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 81.5 |  | PSIG | [11 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 8.0025 | Std units
Monthly average of the daily flow rates | [7 empty] | 8.03 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 12150 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 14.2124 |  | MG | [11 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 2.896 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 71.75 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [21 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.05 | mg/l
Monthly average pressure | [7 empty] | 50.0183 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 862.5 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 37.3 |  | PSIG | [11 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 142.5 | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.2875 | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [21 empty] | (Signature):
Date:
|  |  |  | UNDERGROUND INJECTION CONTROL | [21 empty] | UNDERGROUND INJECTION CONTROL
|  |  |  | MONTHLY OPERATING REPORT | [21 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES | [15 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [21 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-4 | [18 empty] | Monitoring Well Decription: |  |  | LOWER ZONE OF MONITORING WELL MW-2
Permit #: |  | 0054569-142-UO |  |  |  |  | Date of Issuance: |  | 2004-01-07 | [12 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | 0054569-142-UO
[22 empty] | Monitoring Well ID #: |  |  | 5006A11308 & 309
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2009-01-06 | [12 empty] | As Identified in Permit: |  | Monitor Well MW-2 Lower Monitor Zone |  |  |  | Issue Date: |  |  | 2004-01-07
[22 empty] | Monitoring Well Interval: |  |  | 1970' to 2025'
Injection Well ID #: |  | N/A | [19 empty] | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.7 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24
Injection Interval: |  |  | 2804' to 3977' | [18 empty] | 5006A11308 |  |  | INJECTION WELL IW-1
[22 empty] | 5006A11309 |  |  | INJECTION WELL IW-2
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s):
[22 empty] | REPORT MONTH / YEAR: |  | 2004-02-01 | DATE OF SAP / RECORDING: |  |  | 2004-02-03 | 2004-02-10 | 2004-02-17 | 2004-02-24
Monitoring Zone ID #: | [5 empty] | Description
[22 empty] | OPERATOR'S NAME: |  |  | BAYLER, J.
UO-06-279510 |  | UPPER ZONE OF MONITORING WELL MW-3
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A
UO-06-279510 |  | LOWER ZONE OF MONITORING WELL MW-3
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [21 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2004-02-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
OPERATOR'S NAME: |  |  | BAYLER, J. | [18 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4474-A | [18 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 42.12 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 29.21 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: | [14 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 40.6928 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 31195.5 | mg/l
Total monthly flow | [7 empty] | 113.53 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 18500 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [18 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.37 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 18.94 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 2.105 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 74.5 |  | PSIG | [11 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7.485 | Std units
Monthly average of the daily flow rates | [7 empty] | 3.9148 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 48750 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 6.4109 |  | MG | [11 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 2.896 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 70.25 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [21 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.05 | mg/l
Monthly average pressure | [7 empty] | 41.03 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 2500 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 36.3 |  | PSIG | [11 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 800 | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.05 | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [21 empty] | (Signature):
Date:
|  |  |  | UNDERGROUND INJECTION CONTROL | [21 empty] | UNDERGROUND INJECTION CONTROL
|  |  |  | MONTHLY OPERATING REPORT | [21 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES | [15 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [21 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-5 | [18 empty] | Monitoring Well Decription: |  |  | UPPER ZONE OF MONITORING WELL MW-3
Permit #: |  | 0054569-142-UO |  |  |  |  | Date of Issuance: |  | 2004-01-07 | [12 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | 0054569-142-UO
[22 empty] | Monitoring Well ID #: |  |  | 5006A11310
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2009-01-06 | [12 empty] | As Identified in Permit: |  | Monitor Well MW-3 Upper Monitor Zone |  |  |  | Issue Date: |  |  | 2004-01-07
[22 empty] | Monitoring Well Interval: |  |  | 1300' to 1349'
Injection Well ID #: |  | 5006A11311 | [19 empty] | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.7 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24
Injection Interval: |  |  | 2818' to 3462' | [18 empty] | 5006A11310 |  |  | INJECTION WELL IW-3
[22 empty] | N/A |  |  | INJECTION WELL IW-4
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s):
[22 empty] | REPORT MONTH / YEAR: |  | 2004-02-01 | DATE OF SAP / RECORDING: |  |  | 2004-02-03 | 2004-02-10 | 2004-02-17 | 2004-02-24
Monitoring Zone ID #: | [5 empty] | Description
[22 empty] | OPERATOR'S NAME: |  |  | BAYLER, J.
UO-06-279512 |  | UPPER ZONE OF MONITORING WELL MW-1
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A
UO-06-279512 |  | LOWER ZONE OF MONITORING WELL MW-1
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [21 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2004-02-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
OPERATOR'S NAME: |  |  | BAYLER, J. | [18 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4474-A | [18 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 31.97 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 17.63 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: | [14 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 30.0241 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 31195.5 | mg/l
Total monthly flow | [7 empty] | 222.06 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 18500 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [18 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.37 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 15.73 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 2.105 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 80.8 |  | PSIG | [11 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7.485 | Std units
Monthly average of the daily flow rates | [7 empty] | 8.2244 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 48750 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 14.5521 |  | MG | [11 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 2.896 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 70.25 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [21 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.05 | mg/l
Monthly average pressure | [7 empty] | 49.0148 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 2500 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 35.1 |  | PSIG | [11 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 800 | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.05 | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [21 empty] | (Signature):
Date:
UNDERGROUND INJECTION CONTROL
MONTHLY OPERATING REPORT
[22 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
[22 empty] | Monitoring Well Decription: |  |  | LOWER ZONE OF MONITORING WELL MW-3
[22 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | 0054569-142-UO
[22 empty] | Monitoring Well ID #: |  |  | 5006A11310
[22 empty] | As Identified in Permit: |  | Monitor Well MW-3 Lower Monitor Zone |  |  |  | Issue Date: |  |  | 2004-01-07
[22 empty] | Monitoring Well Interval: |  |  | 1970 to 2027'
Associated Injection Well(s):
[22 empty] | Injection Well ID #: |  |  | Injection Well Description
[22 empty] | 5006A11310 |  |  | INJECTION WELL IW-3
[22 empty] | N/A |  |  | INJECTION WELL IW-4
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
[22 empty] | REPORT MONTH / YEAR: |  | 2004-02-01 | DATE OF SAP / RECORDING: |  |  | 2004-02-03 | 2004-02-10 | 2004-02-17 | 2004-02-24
[22 empty] | OPERATOR'S NAME: |  |  | BAYLER, J.
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
[22 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
[22 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
[22 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 45.83 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 37.36 | PSIG
[22 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 44.5166 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
[22 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 28197.75 | mg/l
[22 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 17050 | mg/l
[22 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 2.3325 | mg/l
[22 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 3.1375 | mg/l
[22 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7.475 | Std units
[22 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 45500 | umho/cm
[22 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
[22 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 69 | deg. F
[22 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.05 | mg/l
[22 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 2137.5 | mg/l
[22 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 747.5 | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.04 | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
Date:

## DEP FORMS
Department of Environmental Protection Discharge Monitoring Report - Part A
When Completed mail this report to: Department of Environmental Protection, Wastewater Facilities Management Section, MS 3551, 2600 Blair Stone Road, Tallahassee, FL 32399-2400
PERMITEE NAME: | City of Fort Lauderdale |  |  |  |  | PERMIT NUMBER: |  | FLA041378 |  | REPORT: | Monthly
MAILING ADDRESS: | 949 NW 38th Street |  |  |  |  | LIMIT: |  | Final |  | GROUP: | Domestic
| Fort Lauderdale, FL 33309 |  |  |  |  | CLASS SIZE: |  | N/A |  | GMS TEST SITE
[6 empty] | GMS ID NO. |  | 5006M02066 |  | NO:
FACILITY: | City of Fort Lauderdale G. T. Lohmeyer WWTF |  |  |  |  | MONITORING GROUP NUMBER: |  | U-001
LOCATION: | 1765 SE 18th Street |  |  |  |  | PLANT SIZE/TREATMENT TYPE: |  | IIA
Fort Lauderdale, FL 33316
COUNTY: | Broward | [5 empty] | MONITORING PERIOD: |  |  | 2004-02-01
Parameter |  | Quantity of Loading |  | Units |  | Quality or Concentration |  | Units | No. Ex. | Frequency of Analysis | Sample Type
Flow | Sample Measurement | 16.0724 | 9.0268 | [5 empty] | 0
PARM Code 50050 1 Mon.Site No. EFF-002 | Permit Requirement | 18.3 (Peak Hour.) | Report (Mo. Avg.) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
Flow | Sample Measurement | 17.0087 | 9.5652 | [5 empty] | 0
PARM Code 50050 1 Mon.Site No. EFF-003 | Permit Requirement | 18.3 (Peak Hour.) | Report (Mo. Avg.) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
Flow | Sample Measurement | 14.2124 | 8.03 | [5 empty] | 0
PARM Code 50050 1 Mon.Site No. EFF-004 | Permit Requirement | 18.3 (Peak Hour.) | Report (Mo. Avg.) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
Flow | Sample Measurement | 6.4109 | 3.9148 | [5 empty] | 0
PARM Code 50050 1 Mon.Site No. EFF-005 | Permit Requirement | 18.0 (Peak Hour.) | Report (Mo. Avg.) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
Flow | Sample Measurement | 14.5521 | 8.2244 | [5 empty] | 0
PARM Code 50050 1 Mon.Site No. EFF-006 | Permit Requirement | 18.3 (Peak Hour.) | Report (Mo. Avg.) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
I certify under penalty of law that I have personally examined and am familiar with the informantion submitted herein; and based on my inquiry of those individuals immeadiately responsible for obtaining the information, I believe the submitted
information is true, accurate and complete. I am aware that there are significant penalties for submitting false information including the possiblity of fine and imprisonment.
NAME/TITLE OF PRINCIPAL EXECUTIVE OFFICER OR AUTHORIZED AGENT |  |  |  | SIGNATURE OF PRINCIPAL EXECUTIVE OFFICER OR AUTHORIZED AGENT |  |  |  |  | TELEPHONE |  | DATE (YY/MM/DD)
954-523-1002 ext 2021
REGIONAL WASTEWATER FACILITIES MANAGER
COMMENTS AND EXPLANATION OF ANY VIOLATIONS (Reference all attachments here):
Version 8/13/99
Department of Environmental Protection Discharge Monitoring Report - Part A (Continued)
[12 empty] | PERMITEE NAME: | City of Fort Lauderdale G. T. Lohmeyer WWTF |  |  |  | PERMIT NUMBER: |  | FLA041378 | MONITORING GROUP NUMBER: U-001 |  |  | REPORT: | Monthly
[20 empty] | MONITORING PERIOD: |  |  |  | 2004-02-01
[12 empty] | Parameter |  |  | Quantity of Loading |  | Units |  | Quality or Concentration |  | Units | No. Ex. | Frequency of Analysis | Sample Type
[12 empty] | BOD, Carbonaceous 5 day, 20C |  | Sample Measurement |  |  |  | 4.4 |  |  |  | 0
[12 empty] | PARM Code 80082 Y Mon.Site No. EFF-001 |  | Permit Requirement |  |  |  | 20.0 (An.Avg.) |  |  | mg/l |  | Daily | 24-hour FPC
[12 empty] | BOD, Carbonaceous 5 day, 20C |  | Sample Measurement |  |  |  | 3 | #DIV/0! | 5 |  | 0
[12 empty] | PARM Code 80082 1 Mon.Site No. EFF-001 |  | Permit Requirement |  |  |  | 30.0 (Mo.Avg.) | 45.0 (Week.Avg.) | 60.0 (Max.) | mg/l |  | Daily | 24-hour FPC
[12 empty] | Solids, Total Suspended |  | Sample Measurement |  |  |  | 14.8 |  |  |  | 0
[12 empty] | PARM Code 00530 Y Mon.Site No. EFF-001 |  | Permit Requirement |  |  |  | 20.0 (An.Avg.) |  |  | mg/l |  | Daily | 24-hour FPC
[12 empty] | Solids, Total Suspended |  | Sample Measurement |  |  |  | 18.2414 | 17.2623 | 44 |  | 0
[12 empty] | PARM Code 00530 1 Mon.Site No. EFF-001 |  | Permit Requirement |  |  |  | 30.0 (Mo.Avg.) | 45.0 (Week.Avg.) | 60.0 (Max.) | mg/l |  | Daily | 24-hour FPC
[12 empty] | pH |  | Sample Measurement |  |  |  | 6.2 |  |  |  | 0
[12 empty] | PARM Code 00400 1 Mon.Site No. EFF-001 |  | Permit Requirement |  |  |  | 6.0 (Min.) |  |  | s.u. |  | Continuous | Meter
[12 empty] | Flow |  | Sample Measurement | 34.764 | 39.43 | [5 empty] | 0
[12 empty] | PARM Code 50050 G Mon.Site No. INF-001 |  | Permit Requirement | 55.7 (3-Mo.Avg.) | Report (Mo.Avg.) | mgd | [5 empty] | Continuous | Flow meters with 24-hour recording chart
[12 empty] | BOD, Carbonaceous 5 day, 20C |  | Sample Measurement |  |  |  | 84.5069 |  |  |  | N/A
[12 empty] | PARM Code 80082 G Mon.Site No. INF-002 |  | Permit Requirement |  |  |  | Report (Mo.Avg.) |  |  | mg/l |  | Daily | 24-hour FPC
[12 empty] | Solids, Total Suspended |  | Sample Measurement |  |  |  | 109.4483 |  |  |  | N/A
[12 empty] | PARM Code 00530 G Mon.Site No. INF-002 |  | Permit Requirement |  |  |  | Report (Mo.Avg.) |  |  | mg/l |  | Daily | 24-hour FPC
Version 8/13/99

## JULIAN CONVERT
2004-02-01 | 38018 | 1999-01-01 | 1857
FROM DATE ON "DATA INPUT" PAGE | [5 empty] | 2004-02-01
2004
MONTHYY.PAR RANGE TO COMPILE (JULIAN DAY VALUES) FOR SPLIT PROGRAM ARE | [7 empty] | 32 | THROUGH | 1887
|  | 2 | FEBRUARY
[5 empty] | 2004-02-01 | 2004-02-01 | 2
2004-02-01 |  |  |  |  | 1 | JANUARY |  | 1995 | 1995-01-01
[5 empty] | 2 | FEBRUARY |  | 1996 | 1996-01-01
[5 empty] | 3 | MARCH |  | 1997 | 1997-01-01
FEBRUARY |  | 0 |  | 0 | 4 | APRIL |  | 1998 | 1998-01-01
|  | 0 |  | 0 | 5 | MAY |  | 1999 | 1999-01-01
|  | 1 |  |  | 6 | JUNE |  | 2000 | 2000-01-01
|  | 1 |  |  | 7 | JULY |  | 2001 | 2001-01-01
|  | 2 |  | 1 | 8 | AUGUST |  | 2002 | 2002-01-01
|  |  |  | 1 | 9 | SEPTEMBER |  | 2003 | 2003-01-01
[5 empty] | 10 | OCTOBER |  | 2004 | 2004-01-01
[5 empty] | 11 | NOVEMBER |  | 2005 | 2005-01-01
2004 |  |  |  |  | 12 | DECEMBER |  | 2006 | 2006-01-01
38018 | [6 empty] | FEBRUARY | 2007 | 2007-01-01
37987 | [7 empty] | 2008 | 2008-01-01
31 | 1 |  | 1 | 32 | Sunday
| 2 |  | 2 | 33 | Monday
| 3 |  | 3 | 34 | Tuesday
| 4 |  | 4 | 35 | Wednesday
| 5 |  | 5 | 36 | Thursday
| 6 |  | 6 | 37 | Friday
| 7 |  | 7 | 38 | Saturday
| 8 |  | 8 | 39 | Sunday
| 9 |  | 9 | 40 | Monday
| 10 |  | 10 | 41 | Tuesday
| 11 |  | 11 | 42 | Wednesday
| 12 |  | 12 | 43 | Thursday
| 13 |  | 13 | 44 | Friday
| 14 |  | 14 | 45 | Saturday
| 15 |  | 15 | 46 | Sunday
| 16 |  | 16 | 47 | Monday
| 17 |  | 17 | 48 | Tuesday
| 18 |  | 18 | 49 | Wednesday
| 19 |  | 19 | 50 | Thursday
| 20 |  | 20 | 51 | Friday
| 21 |  | 21 | 52 | Saturday
| 22 |  | 22 | 53 | Sunday
| 23 |  | 23 | 54 | Monday
| 24 |  | 24 | 55 | Tuesday
| 25 |  | 25 | 56 | Wednesday
| 26 |  | 26 | 57 | Thursday
| 27 |  | 27 | 58 | Friday
| 28 |  | 28 | 59 | Saturday
| 29 |  | 29 | 60 | Sunday
29