## DATA INPUT
ENTER THE AVERAGE MONTHLY INFLUENT FLOW
INTO THE CORROSPONDING BOXES BELOW:
AUGUST | 34.781 | JULY | 46.575
ENTER THE PRESENT MONTH AND YEAR IN BOX BELOW (A5) | [5 empty] | SEPTEMBER
2005-09-01 | [5 empty] | 2005
IW-1 | IW-2 | IW-3 | IW-4 | IW-5
36.37 | 36.72 | 38.58 | 38.13 | 37.01 | 2005-09-14
|  | ENTER INJECTION WELL SHUT-IN PRESSURE ABOVE |  |  | ENTER DATE OF SHUT-IN READINGS
ENTER SLUDGE DISPOSAL SITE FOR EACH WEEK BELOW
| WEEK 1 | WEEK 2 | WEEK 3 | WEEK 4
1 st | Central Sanitary Landfill | Central Sanitary Landfill | Central Sanitary Landfill | Central Sanitary Landfill
2 nd | Pompano Beach, FL | Pompano Beach, FL | Pompano Beach, FL | Pompano Beach, FL
RAW DATA REPORT ENTRY CATEGORIES
GTL PLANT DAILY PROCESS SUMMARY
[6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
TOTAL RAW INFLUENT FLOW (MGD) | [5 empty] | 44.155 | 43.606 | 45.086 | 46.793 | 39.825 | 50.104 | 48.237 | 45.618 | 45.168 | 45.52 | 49.087 | 47.528 | 44.966 | 42.538 | 41.743 | 41.521 | 41.027 | 40.734 | 41.144 | 45.32 | 46.859 | 44.822 | 43.123 | 41.29 | 39.825 | 39.284 | 38.725 | 38.518 | 38.756 | 39.011
TOTAL EFFLUENT FLOW (MGD) | [5 empty] | 43.754 | 44.116 | 44.987 | 46.452 | 38.836 | 48.696 | 48.292 | 45.806 | 45.549 | 44.478 | 47.463 | 47.359 | 45.15 | 42.375 | 41.095 | 41.375 | 40.767 | 40.413 | 41.229 | 44.951 | 46.387 | 45.099 | 44.944 | 41.105 | 38.836 | 38.682 | 38.832 | 38.739 | 38.89 | 38.827
MAXIMUM HOURLY RAW INFLUENT FLOW (MGD) | [5 empty] | 2.151 | 2.197 | 2.208 | 2.246 | 1.891 | 2.394 | 2.311 | 2.157 | 2.161 | 2.303 | 2.303 | 2.398 | 2.298 | 2.106 | 2.07 | 2.126 | 2.09 | 2.035 | 1.987 | 2.307 | 2.182 | 2.134 | 2.31 | 1.962 | 1.891 | 1.909 | 1.965 | 1.888 | 1.915 | 1.984
MAXIMUM INSTANANEOUS PEAK RAW INFUENT FLOW (MGD) | [5 empty] | 59.98 | 59.5 | 61.134 | 61.807 | 54.308 | 66.133 | 62.768 | 58.634 | 59.307 | 60.172 | 63.825 | 63.056 | 60.493 | 57.737 | 57.096 | 54.372 | 56.199 | 55.782 | 55.718 | 62.896 | 59.98 | 58.73 | 57.032 | 55.302 | 54.308 | 55.814 | 53.635 | 57.224 | 59.275 | 54.405
MINIMUM INSTANANEOUS PEAK RAW INFUENT FLOW (MGD) | [5 empty] | 18.807 | 19.576 | 23.87 | 26.337 | 20.313 | 26.85 | 30.407 | 25.023 | 27.33 | 24.895 | 29.67 | 26.561 | 24.382 | 20.185 | 20.986 | 22.428 | 20.569 | 19.672 | 19.127 | 23.357 | 28.132 | 20.089 | 25.92 | 22.844 | 20.313 | 17.685 | 20.089 | 19.576 | 18.647 | 16.852
TOTAL RETURN ACTIVATED SLUDGE FLOW (MGD) | [5 empty] | 13.08 | 13.552 | 13.792 | 13.747 | 13.058 | 13.562 | 13.619 | 13.824 | 14.501 | 14.298 | 13.354 | 13.291 | 12.523 | 12.463 | 12.3 | 13.681 | 13.369 | 13.562 | 13.171 | 13.787 | 13.378 | 13.278 | 13.829 | 13.442 | 13.058 | 12.387 | 12.376 | 12.43 | 12.408 | 13.65
TOTAL WASTE FLOW TO DEWATERING PROCESS (MG) | [5 empty] | 0.528 | 0.218 | 0 | 0 | 0.172 | 0.358 | 0.358 | 0.378 | 0.14 | 0 | 0.133 | 0.31 | 0.365 | 0.382 | 0.446 | 0.189 | 0 | 0.167 | 0.257 | 0 | 0.438 | 0.575 | 0.163 | 0 | 0.172 | 0.513 | 0.566 | 0.551 | 0.506 | 0.226
TOTAL DAILY RAINFALL | [5 empty] | 0 | 0.04 | 0.13 | 0.06 | 0.1 | 0.54 | 0.05 | 0.03 | 0 | 2.6 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 1.08 | 0.09 | 0.69 | 0.33 | 0 | 0.1 | 0.38 | 0 | 0.01 | 0.06 | 0.1
RAW INFLUENT pH | [5 empty] | 6.9 | 6.9 | 7 | 7 | 7.1 | 6.9 | 6.7 | 6.9 | 7 | 7 | 7.2 | 7.1 | 7.1 | 6.9 | 6.7 | 7 | 7.1 | 7 | 7 | 7 | 7 | 7 | 7 | 7.1 | 7.1 | 7.1 | 7 | 7 | 7.1 | 7
RAW INFLUENT HYDROGEN SULFIDE (PPM) | [5 empty] | 6 | 6 | 5 | 7 | 5 | 4 | 5 | 5 | 5 | 6 | 5 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 3 | 4 | 7 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
RAW INFLUENT TEMPERATURE (F ) | [5 empty] | 84 | 84 | 84 | 84 | 83 | 84 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 83 | 83 | 83 | 84 | 84 | 83.1
TOTAL DAILY KILOWATTS (FPL POWER CONSUMPTION) | [5 empty] | 33736 | 32718 | 32078 | 32180 | 31965 | 32127 | 32041 | 32083 | 32089 | 31956 | 32020 | 32010 | 32131 | 31944 | 31857 | 31762 | 31882 | 31870 | 32003 | 31750 | 31938 | 31995 | 32356 | 32038 | 31965 | 31722 | 31764 | 31841 | 31718 | 31966
GTL PLANT DAILY PROCESS SUMMARY
(CONTINUED)
[6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
FINAL EFFLUENT FREE CHLORINE RESIDUAL (PPM) | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FINAL EFFLUENT TOTAL CHLORINE RESIDUAL (PPM) | [5 empty] | 0 | 0.6 | 1 | 1.1 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0.9 | 0.7 | 1 | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | 0.8 | 1 | 0.9 | 0.7 | 0.7 | 0.6 | 0.6 | 0.7
FINAL EFFLUENT pH (daily average) | [5 empty] | 6.7 | 6.6 | 6.6 | 6.6 | 6.6 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.6 | 6.7 | 6.7 | 6.7 | 6.7 | 6.6 | 6.6 | 6.6 | 6.6 | 6.7 | 6.8 | 6.7 | 6.7 | 6.6 | 6.6 | 6.7 | 6.6 | 6.7 | 6.7 | 6.7
FINAL EFFLUENT pH (daily minimum) | [5 empty] | 6.6 | 6.4 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.7 | 6.6 | 6.6 | 6.5 | 6.6 | 6.6 | 6.5 | 6.6 | 6.7 | 6.5 | 6.6 | 6.6 | 6.6 | 6.6 | 6.5 | 6.6 | 6.6 | 6.6
FINAL EFFLUENT pH (daily maximum) | [5 empty] | 6.8 | 7 | 6.7 | 6.7 | 6.6 | 6.9 | 6.9 | 6.9 | 6.8 | 6.7 | 6.7 | 7 | 6.8 | 6.9 | 6.8 | 6.7 | 6.6 | 6.7 | 6.8 | 6.8 | 6.8 | 6.9 | 6.7 | 6.6 | 6.6 | 6.8 | 6.8 | 6.7 | 6.8 | 6.7
FINAL EFFLUENT TEMPARTURE (F ) | [5 empty] | 87 | 87 | 87 | 87 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 0 | 86 | 86 | 86 | 86 | 86 | 87 | 87 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86
AVERAGE CLARIFIER BLANKET DEPTH (INCHES) | [5 empty] | 17 | 19 | 32 | 32 | 29 | 20 | 21 | 18 | 20 | 33 | 28 | 27 | 24 | 20 | 18 | 17 | 34 | 27 | 16 | 22 | 23 | 18 | 21 | 38 | 29 | 21 | 20 | 19 | 15 | 18
FINAL EFFLUENT SAMPLE TEMPARTURE (C ) | [5 empty] | 4 | 0.5 | 2.8 | 4 | 4 | 4 | 4 | 4 | 10.4 | 4 | 4 | 0 | 4 | 4 | 4 | 4.5 | 7.6 | 4 | 4.4 | 4 | 4 | 4 | 0.7 | 4.6 | 4 | 4 | 4 | 4 | 3 | 3.2
TOTAL RETURN ACTIVATED SLUDGE FLOW TO REACTOR ONE (MGD) | [5 empty] | 6.249 | 6.329 | 6.311 | 6.33 | 6.511 | 6.16 | 6.173 | 6.089 | 6.294 | 6.305 | 6.172 | 6.302 | 6.304 | 6.281 | 6.246 | 6.306 | 6.321 | 6.4 | 6.295 | 6.101 | 6.168 | 6.158 | 6.321 | 6.446 | 6.511 | 6.348 | 6.248 | 6.314 | 6.357 | 6.275
TOTAL RETURN ACTIVATED SLUDGE FLOW TO REACTOR TWO (MGD) | [5 empty] | 6.83 | 7.223 | 7.481 | 7.417 | 6.547 | 7.403 | 7.446 | 7.736 | 8.206 | 7.994 | 7.182 | 6.989 | 6.219 | 6.182 | 6.055 | 7.375 | 7.048 | 7.162 | 6.876 | 7.686 | 7.21 | 7.12 | 7.508 | 6.996 | 6.547 | 6.04 | 6.128 | 6.115 | 6.051 | 7.376
GTL PLANT DAILY PROCESS SUMMARY
CONTINUED
[6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
TOTAL DAILY TRUCKING LOAD OF DEWATERED SLUDGE REMOVED | [5 empty] | 4 | 5 | 0 | 0 | 0 | 2 | 5 | 5 | 4 | 0 | 0 | 0 | 4 | 4 | 5 | 5 | 0 | 0 | 3 | 0 | 2 | 4 | 5 | 0 | 0 | 5 | 4 | 2 | 4 | 4
TOTAL DAILY HYDROGEN PEROXIDE CONSUMED (LBS) | [5 empty] | 289 | 0 | 0 | 140 | 0 | 299 | 449 | 369 | 0 | 0 | 279 | 0 | 0 | 0 | 299 | 0 | 0 | 0 | 0 | 0 | 0 | 998 | 0 | 0 | 309 | 240 | 170 | 0 | 200 | 0
TOTAL DAILY CHLORINE CONSUMED (LBS) | [5 empty] | 0 | 1240 | 1640 | 1320 | 1500 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 920 | 1800 | 1360 | 1460 | 1720 | 1360 | 1620 | 1460 | 1460 | 1520 | 1620 | 1500 | 1600 | 1520 | 1520 | 1200 | 1520
TOTAL DAILY POLYMER CONSUMED (GALS) | [5 empty] | 79 | 0 | 0 | 19 | 33 | 15 | 42 | 51 | 52 | 0 | 0 | 0 | 24 | 30 | 96 | 40 | 0 | 41 | 49 | 0 | 71 | 0 | 17 | 0 | 33 | 66 | 77 | 42 | 26 | 19
TOTAL TONS OF LIME DELIVERED DAILY | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTAL DAILY GASIOUS OXYGEN PRODUCED (TONS) | [5 empty] | 19.1 | 21.9 | 25.2 | 27.5 | 20.7 | 23.9 | 21.4 | 20 | 26.3 | 28.5 | 26.4 | 29.7 | 27.4 | 20.2 | 17.4 | 23.9 | 24.2 | 21.03 | 23.4 | 20.7 | 18.8 | 16.2 | 21.9 | 20.8 | 20.7 | 18.8 | 16.3 | 17.5 | 16.5 | 18.9
AVERAGE PERCENT OXYGEN PRODUCT PURITY | [5 empty] | 100 | 100 | 100 | 100 | 99 | 100 | 100 | 100 | 100 | 100 | 96 | 93 | 100 | 100 | 100 | 100 | 100 | 99 | 99 | 100 | 100 | 100 | 100 | 100 | 99 | 100 | 100 | 100 | 100 | 99
TOTAL DAILY LIQUID OXYGEN IN STORAGE (TONS) | [5 empty] | 138.5 | 143.5 | 145.2 | 145.8 | 142.8 | 139.7 | 139.2 | 139.8 | 140.4 | 141.5 | 138.8 | 142.6 | 139.7 | 140.8 | 141.1 | 139.8 | 140.2 | 140.9 | 142.1 | 141.9 | 143.1 | 141.7 | 141.8 | 143.2 | 142.6 | 143.3 | 145.3 | 144 | 144.5 | 145.2
MONITORING WELL PRESSURE DATA
MONITORING WELL ONE UPPER/LOWER LEVEL
| MW-1 |  | UPPER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
MINIMUM | [5 empty] | 48.97 | 49.01 | 49.06 | 49.12 | 45.44 | 45.78 | 49.25 | 49.27 | 49.29 | 49.22 | 49.13 | 47.16 | 47.67 | 49.06 | 49.01 | 49.03 | 49.02 | 49.03 | 46.76 | 47.05 | 49.07 | 47.74 | 47.78 | 48.92 | 48.96 | 49.03 | 46.71 | 47.1 | 49.06 | 49.08
MAXIMUM | [5 empty] | 49.25 | 49.27 | 49.34 | 49.37 | 49.29 | 49.62 | 49.49 | 49.54 | 49.55 | 49.49 | 49.42 | 49.37 | 49.45 | 49.42 | 49.39 | 49.4 | 49.38 | 49.38 | 49.35 | 49.56 | 49.36 | 49.33 | 49.13 | 49.18 | 49.23 | 49.3 | 49.3 | 49.46 | 49.35 | 49.34
AVERAGE | [5 empty] | 49.05 | 49.11 | 49.2 | 49.22 | 46.92 | 48.42 | 49.42 | 49.45 | 49.44 | 49.4 | 49.35 | 48.08 | 48.82 | 49.25 | 49.21 | 49.21 | 49.21 | 49.2 | 48.04 | 48.67 | 49.23 | 48.52 | 48.71 | 49.02 | 49.03 | 49.15 | 47.64 | 48.54 | 49.19 | 49.21
| MW-1 |  | LOWER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
MINIMUM | [5 empty] | 42.62 | 42.65 | 42.96 | 43 | 41.85 | 41.42 | 42.49 | 43.09 | 43.14 | 41.97 | 42.48 | 43.06 | 42.27 | 42.62 | 42.93 | 43.48 | 43.8 | 44.02 | 42.55 | 41.4 | 42.17 | 41.23 | 40.1 | 41.84 | 41.95 | 42.45 | 41.31 | 40.83 | 41.8 | 42.44
MAXIMUM | [5 empty] | 46.54 | 47.06 | 47.05 | 46.37 | 44.48 | 44.33 | 46.79 | 46.92 | 47.39 | 46.83 | 47.07 | 46.81 | 46.82 | 46.8 | 46.85 | 46.74 | 46.93 | 47.05 | 46.28 | 43.4 | 45.76 | 45.12 | 43.51 | 45.2 | 45.74 | 45.97 | 45.03 | 44.46 | 45.35 | 45.87
AVERAGE | [5 empty] | 43.83 | 44.29 | 44.15 | 44.17 | 43.6 | 42.58 | 44.12 | 44.58 | 44.9 | 44.49 | 44.64 | 44.35 | 44.26 | 44.29 | 44.55 | 44.8 | 45.03 | 45.12 | 44.25 | 42.6 | 43.94 | 43.22 | 42 | 43.13 | 43.58 | 43.98 | 43.13 | 42.23 | 43.22 | 43.77
MONITORING WELL TWO UPPER/LOWER LEVEL
| MW-2 |  | UPPER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
MINIMUM | [5 empty] | 33.19 | 33.27 | 33.21 | 33.36 | 28.81 | 28.59 | 32.84 | 33.15 | 33.23 | 32.8 | 32.98 | 29.5 | 29.1 | 32.78 | 32.98 | 33.22 | 33.39 | 33.57 | 28.95 | 28.41 | 32.98 | 19.72 | 18.96 | 24.19 | 23.95 | 24.07 | 19.47 | 19.63 | 24.07 | 24.26
MAXIMUM | [5 empty] | 34.86 | 35.2 | 34.69 | 34.51 | 33.91 | 33.75 | 34.85 | 34.95 | 35.43 | 34.83 | 34.88 | 33.53 | 34.74 | 34.59 | 34.64 | 34.73 | 34.62 | 34.73 | 34.63 | 33.57 | 34.64 | 34.4 | 25.03 | 25.42 | 25.48 | 25.75 | 24.55 | 25.13 | 25.51 | 25.4
AVERAGE | [5 empty] | 33.74 | 33.97 | 33.87 | 33.86 | 31.08 | 31.81 | 33.69 | 34 | 34.24 | 33.97 | 33.83 | 31.47 | 32.38 | 33.59 | 33.71 | 33.87 | 34.01 | 34.12 | 31.83 | 31.84 | 33.73 | 26.95 | 23.18 | 24.69 | 24.66 | 24.8 | 21.54 | 23.12 | 24.68 | 24.77
| MW-2 |  | LOWER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
MINIMUM | [5 empty] | 43.23 | 43.3 | 43.38 | 43.48 | 38.47 | 37.27 | 43.19 | 43.35 | 43.46 | 43.47 | 43.44 | 39.73 | 39.68 | 43.14 | 43.19 | 43.22 | 43.27 | 43.3 | 38.21 | 38.12 | 43.06 | 36.17 | 36.08 | 42.89 | 43.02 | 43.16 | 36.47 | 35.98 | 42.99 | 43.17
MAXIMUM | [5 empty] | 43.4 | 43.46 | 43.56 | 43.59 | 43.58 | 43.21 | 43.41 | 43.54 | 43.62 | 43.62 | 43.62 | 43.57 | 43.25 | 43.38 | 43.39 | 43.42 | 43.45 | 43.45 | 43.45 | 43.14 | 43.24 | 43.26 | 42.95 | 43.07 | 43.21 | 43.36 | 43.39 | 43.01 | 43.25 | 43.31
AVERAGE | [5 empty] | 43.37 | 43.41 | 43.48 | 43.5 | 40.26 | 41.62 | 43.35 | 43.46 | 43.5 | 43.51 | 43.51 | 41.04 | 41.95 | 43.3 | 43.34 | 43.37 | 43.42 | 43.44 | 40.9 | 41.44 | 43.07 | 39.46 | 40.97 | 42.99 | 43.04 | 43.36 | 38.53 | 41.08 | 43.04 | 43.26
MONITORING WELL THREE UPPER/LOWER LEVEL
| MW-3 |  | UPPER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
MINIMUM | [5 empty] | 33.7 | 33.77 | 33.86 | 33.99 | 24.64 | 24.47 | 34.17 | 34.32 | 34.4 | 34.35 | 34.29 | 20.13 | 20.05 | 33.76 | 33.89 | 33.97 | 34.04 | 34.06 | 25.69 | 25.48 | 34.29 | 23.63 | 23.42 | 33.95 | 34.08 | 34.22 | 21.07 | 21.06 | 33.79 | 34.02
MAXIMUM | [5 empty] | 33.91 | 34.02 | 34.13 | 34.21 | 34.16 | 34.28 | 34.49 | 34.62 | 34.7 | 34.63 | 34.61 | 34.52 | 33.89 | 34.13 | 34.21 | 34.29 | 34.33 | 34.36 | 34.33 | 34.48 | 34.63 | 34.65 | 34.09 | 34.27 | 34.39 | 34.48 | 34.45 | 33.84 | 34.15 | 34.21
AVERAGE | [5 empty] | 33.82 | 33.89 | 33.97 | 34.02 | 27.89 | 31.16 | 34.38 | 34.47 | 34.55 | 34.49 | 34.46 | 24.65 | 29.32 | 33.91 | 34.02 | 34.11 | 34.2 | 34.26 | 29.85 | 31.5 | 34.44 | 28.68 | 31.02 | 34.07 | 34.29 | 34.38 | 25.09 | 30.19 | 33.97 | 34.04
| MW-3 |  | LOWER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
MINIMUM | [5 empty] | 45.99 | 46.06 | 46.13 | 46.25 | 39.72 | 39.69 | 45.91 | 46.09 | 46.2 | 46.17 | 46.19 | 40.77 | 40.74 | 45.85 | 45.91 | 45.95 | 46.02 | 46.07 | 38.95 | 38.92 | 45.76 | 37.63 | 37.57 | 45.62 | 45.75 | 45.9 | 37.4 | 37.41 | 45.71 | 45.9
MAXIMUM | [5 empty] | 46.14 | 46.2 | 46.3 | 46.33 | 46.33 | 45.91 | 46.12 | 46.27 | 46.37 | 46.38 | 46.38 | 46.32 | 45.94 | 46.08 | 46.11 | 46.14 | 46.18 | 46.19 | 46.18 | 45.82 | 45.93 | 45.96 | 45.66 | 45.81 | 45.95 | 46.11 | 46.12 | 45.72 | 45.98 | 46.04
AVERAGE | [5 empty] | 46.02 | 46.06 | 46.23 | 46.34 | 41.89 | 44.03 | 45.97 | 46.17 | 46.37 | 46.36 | 46.38 | 42.62 | 44.25 | 45.95 | 46 | 46 | 46.06 | 46.08 | 42.45 | 43.57 | 45.89 | 41.44 | 43.31 | 45.76 | 45.88 | 45.99 | 40.04 | 43.27 | 45.88 | 45.99
MONITORING WELL RMW-1 UPPER/LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
[5 empty] | JULIAN DATE | 244 | 245 | 246 | 247 | 248 | 249 | 250 | 251 | 252 | 253 | 254 | 255 | 256 | 257 | 258 | 259 | 260 | 261 | 262 | 263 | 264 | 265 | 266 | 267 | 268 | 269 | 270 | 271 | 272 | 273
| RMW-1 |  | UPPER LEVEL
MINIMUM | [5 empty] | 45.08 | 45.08 | 45.11 | 45.08 | 42.41 | 42.36 | 32.81 | 26.6 | 44.99 | 45.04 | 45.04 | 45.04 | 45.04 | 44.95 | 44.84 | 44.78 | 44.78 | 44.76 | 44.74 | 0.25 | 44.81 | 44.8 | 44.76 | 44.77 | 44.83 | 44.93 | 45.01 | 44.94 | 44.92 | 44.9
MAXIMUM | [5 empty] | 45.23 | 45.22 | 45.22 | 45.22 | 45.13 | 44.7 | 44.92 | 45 | 45.11 | 45.13 | 45.14 | 45.16 | 45.15 | 45.1 | 45.01 | 44.92 | 44.9 | 44.88 | 44.87 | 44.97 | 44.92 | 44.87 | 44.85 | 44.86 | 44.95 | 45.05 | 45.1 | 45.09 | 45.05 | 45.04
AVERAGE | [5 empty] | 45.15 | 45.16 | 45.17 | 45.14 | 43.51 | 43.85 | 44.79 | 44.75 | 45.05 | 45.08 | 45.1 | 45.1 | 45.11 | 45.02 | 44.92 | 44.85 | 44.84 | 44.82 | 44.81 | 44.87 | 44.86 | 44.83 | 44.8 | 44.81 | 44.89 | 45 | 45.06 | 45.01 | 44.99 | 44.98
| RMW-1 |  | LOWER LEVEL
MINIMUM | [5 empty] | 23.21 | 23.23 | 23.24 | 23.25 | 21.18 | 20.73 | 20.42 | 20.34 | 22.58 | 22.56 | 22.51 | 22.53 | 22.53 | 22.48 | 22.45 | 22.46 | 22.48 | 22.5 | 22.5 | 0.25 | 22.53 | 22.51 | 22.47 | 22.45 | 22.46 | 22.54 | 22.58 | 22.55 | 22.57 | 22.58
MAXIMUM | [5 empty] | 23.33 | 23.31 | 23.33 | 23.35 | 23.31 | 22.39 | 22.58 | 22.63 | 22.72 | 22.71 | 22.67 | 22.7 | 22.7 | 22.63 | 22.58 | 22.56 | 22.55 | 22.55 | 22.6 | 22.72 | 22.64 | 22.62 | 22.59 | 22.59 | 22.62 | 22.69 | 22.7 | 22.67 | 22.71 | 22.68
AVERAGE | [5 empty] | 23.27 | 23.27 | 23.29 | 23.3 | 22.22 | 21.93 | 22.49 | 22.52 | 22.64 | 22.63 | 22.61 | 22.61 | 22.63 | 22.58 | 22.52 | 22.51 | 22.52 | 22.52 | 22.54 | 22.62 | 22.58 | 22.56 | 22.55 | 22.52 | 22.55 | 22.62 | 22.65 | 22.63 | 22.64 | 22.63
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
| INJECTION WELL ONE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 12.93 | 13.7 | 14.23 | 15.23 | 14.57 | 15.22 | 12.57 | 14.5 | 14.75 | 14.3 | 13.64 | 13.63 | 15.47 | 13.67 | 14.52 | 14.17 | 10.99 | 14.05 | 12.42 | 14.66 | 14.07 | 12.48 | 13.74 | 14.03 | 12.17 | 11.77 | 11 | 13.04 | 12.38 | 12.2
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 0 | 0 | 0 | 5.44 | 8.48 | 7.57 | 0 | 0.01 | 7.04 | 8.48 | 8.01 | 0 | 0 | 0 | 8.25 | 0.01 | 0 | 0.01 | 0.01 | 8.21 | 6.93 | 0 | 0 | 3.63 | 7.54 | 6.63 | 0 | 0 | 0 | 7.33
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 5.64 | 2.5 | 9.63 | 12.43 | 12.18 | 12.55 | 1.18 | 10.89 | 11.87 | 11.5 | 11.82 | 3.75 | 10.58 | 10.48 | 10.94 | 10.31 | 2.36 | 8.69 | 9 | 10.67 | 10.46 | 0.73 | 10.47 | 10.87 | 10.3 | 10.15 | 2.19 | 8.33 | 8.42 | 10.26
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 63.67 | 66.63 | 67.22 | 70.9 | 70.6 | 73 | 62.93 | 68.33 | 69.71 | 67.95 | 65.98 | 66.37 | 71.7 | 65.45 | 67.94 | 67.82 | 56.51 | 66.41 | 60.75 | 70.3 | 68.7 | 62.11 | 64.61 | 65.65 | 59.53 | 58.72 | 56.72 | 63.05 | 60.7 | 60.29
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 37.13 | 36.99 | 36.73 | 44.41 | 49.77 | 47.96 | 37.12 | 36.51 | 48.39 | 49.11 | 48.3 | 36.3 | 36.19 | 36.12 | 48.98 | 36.47 | 36.45 | 36.29 | 36.07 | 48.9 | 45.36 | 36.84 | 36.84 | 42.95 | 46.9 | 44.82 | 36.39 | 36.25 | 35.87 | 46.51
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 47.58 | 41.84 | 55.79 | 61.67 | 61.14 | 62.72 | 39.8 | 58.02 | 59.63 | 58.57 | 59.59 | 43.36 | 56.93 | 55.75 | 56.44 | 55.21 | 41.03 | 52.55 | 52.69 | 55.48 | 55.69 | 38.63 | 56.21 | 56.12 | 54.26 | 54.01 | 40.42 | 51.23 | 50.93 | 54.25
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
| INJECTION WELL TWO |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 14.6 | 15.29 | 14.18 | 14.22 | 14.94 | 15.57 | 16.08 | 12.24 | 14.99 | 14.93 | 14.01 | 15.67 | 12.22 | 14.14 | 14.24 | 15.56 | 14.43 | 13.41 | 12.8 | 14.99 | 14.42 | 14.69 | 11.42 | 13.31 | 12 | 11.99 | 14.67 | 12.28 | 12.78 | 12.53
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 9.04 | 8.5 | 0.06 | 0.06 | 0.06 | 7.72 | 9.75 | 0.06 | 0.06 | 5.83 | 8.26 | 7.1 | 0.05 | 0.05 | 0.05 | 0.06 | 7.77 | 0.06 | 0.06 | 0.05 | 7.08 | 8.92 | 0.06 | 0.05 | 0.05 | 6.74 | 6.69 | 0.05 | 0.05 | 0.05
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 12.06 | 12.45 | 2.94 | 9.8 | 10.08 | 12.9 | 13.17 | 0.9 | 10.51 | 11.78 | 12.14 | 11.9 | 0.71 | 9.07 | 9 | 10.72 | 11.42 | 2.54 | 8.81 | 8.69 | 10.7 | 12.56 | 0.81 | 8.61 | 8.51 | 10.42 | 10.86 | 2.4 | 8.31 | 8.77
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 66.27 | 69.19 | 64.16 | 65.33 | 69.43 | 71.8 | 72.1 | 58.14 | 68.59 | 66.87 | 64.85 | 69.9 | 58.43 | 65.95 | 65.98 | 68.94 | 65.23 | 61.3 | 60.04 | 69.19 | 67.88 | 66.42 | 57.41 | 61.76 | 57.5 | 57.72 | 66.06 | 57.29 | 59.7 | 59.43
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 50.16 | 48.21 | 37.24 | 37.31 | 37.75 | 47.09 | 51.94 | 37.11 | 37.71 | 45.77 | 47.42 | 45.25 | 36.97 | 36.39 | 37.21 | 37.36 | 46.13 | 37.32 | 36.3 | 36.61 | 44.72 | 49.42 | 36.9 | 37.22 | 37.01 | 44.05 | 43.89 | 36.77 | 36.16 | 36.6
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 58.07 | 59.14 | 43.14 | 55.36 | 55.85 | 61.69 | 61.6 | 39.59 | 55.86 | 57.55 | 58.62 | 57.61 | 38.95 | 52.23 | 51.93 | 54.72 | 55.68 | 41.54 | 51.33 | 51.01 | 54.82 | 59.38 | 39.27 | 51.06 | 50.17 | 53.06 | 54 | 40.86 | 49.71 | 50.6
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
| INJECTION WELL THREE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 12.99 | 13.49 | 13.15 | 10.91 | 14.03 | 14.35 | 14.22 | 13.52 | 11.48 | 12.87 | 13.15 | 13.87 | 14.11 | 12.34 | 13.34 | 15.67 | 12.86 | 13.03 | 12 | 14.04 | 13.26 | 13.05 | 12.7 | 9.99 | 11.37 | 11.22 | 12.97 | 12.07 | 12.2 | 11.8
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 8.58 | 8.24 | 8.65 | 0 | 0 | 5.15 | 8.91 | 7.57 | 0 | 0 | 0 | 6.9 | 7.51 | 0 | 0 | 2.56 | 7.56 | 7.46 | 0 | 0 | 6.85 | 8.43 | 7.84 | 0 | 0 | 0 | 6.63 | 7.18 | 0 | 0
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 11.1 | 11.31 | 11.55 | 0.65 | 9.01 | 12 | 11.84 | 11.5 | 0.64 | 8.98 | 11.28 | 10.8 | 11.38 | 1.33 | 8.05 | 10.49 | 10.48 | 10.42 | 2.47 | 7.66 | 10.01 | 11.33 | 10.97 | 0.58 | 7.7 | 8.02 | 9.99 | 9.98 | 2.31 | 7.8
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 67.37 | 70.4 | 67.4 | 59.59 | 71 | 73.3 | 73.5 | 68.57 | 61.34 | 65.96 | 66.27 | 70.9 | 71.8 | 63.39 | 67.3 | 79.5 | 66.17 | 66.44 | 61.72 | 70.8 | 69.01 | 67.58 | 64.74 | 58.16 | 58.74 | 58.91 | 67.23 | 63.13 | 62.76 | 60.61
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 51.19 | 49.22 | 50.33 | 38.61 | 38.28 | 44.69 | 53.05 | 48.69 | 38.5 | 37.69 | 38.87 | 46.18 | 47.71 | 37.67 | 37.76 | 42.96 | 47.13 | 46.94 | 38.34 | 37.41 | 45.57 | 50.47 | 49.33 | 38.03 | 37.54 | 37.32 | 44.87 | 46.41 | 37.71 | 37.36
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 59.27 | 60.35 | 61.13 | 40.96 | 56.23 | 62.96 | 62.83 | 60.99 | 40.67 | 54.86 | 59.57 | 58.7 | 60.3 | 41.33 | 52.16 | 56.84 | 56.82 | 56.71 | 43.25 | 51.34 | 55.94 | 60.54 | 58.89 | 39.94 | 50.69 | 51.17 | 55.13 | 55 | 42.51 | 50.95
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
FUTURE
| INJECTION WELL FOUR |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 13.32 | 13.77 | 13.42 | 14.74 | 13.99 | 15.01 | 14.45 | 13.59 | 14.21 | 12.84 | 11.32 | 14.26 | 14.47 | 13.29 | 13.92 | 15.82 | 13.01 | 13.12 | 12.13 | 13.62 | 13.85 | 13.25 | 12.8 | 13.51 | 11.89 | 11.64 | 13.22 | 12.15 | 12.25 | 11.63
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 0.05 | 0.05 | 8.8 | 8.43 | 0.05 | 0.05 | 6.41 | 7.67 | 8.08 | 0.05 | 0.05 | 0.05 | 7.68 | 1.86 | 0.05 | 0.05 | 0.05 | 7.54 | 7.69 | 0.05 | 7 | 0.06 | 7.95 | 7.79 | 0.05 | 0.05 | 0.05 | 7.26 | 7.04 | 0.05
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 9.38 | 9.48 | 11.87 | 12.24 | 2.91 | 10.78 | 12.02 | 11.59 | 11.62 | 1.59 | 0.9 | 10.52 | 11.6 | 11.06 | 2.79 | 8.07 | 8.72 | 10.57 | 10.86 | 8.28 | 10.36 | 11.32 | 11.08 | 10.78 | 2.48 | 7.93 | 8.32 | 10.14 | 10.27 | 2.24
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 67.86 | 70.9 | 67.87 | 71.7 | 69.51 | 73.6 | 74 | 69.11 | 70.7 | 66.53 | 59.32 | 71.4 | 72.2 | 67.95 | 68.78 | 80 | 66.85 | 67.07 | 62.25 | 66.87 | 69.49 | 68.14 | 65.35 | 66.49 | 60.35 | 59.49 | 67.75 | 63.7 | 63.35 | 59.82
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 39 | 37.51 | 50.96 | 49.42 | 38.69 | 37.74 | 48.5 | 49.36 | 49.35 | 37.88 | 38.33 | 38.28 | 48.35 | 39.59 | 38.28 | 37.09 | 37.2 | 47.59 | 47.65 | 38.13 | 46.23 | 37.84 | 49.97 | 47.65 | 37.94 | 37.35 | 37.14 | 47.1 | 46.65 | 37.94
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 56 | 57.29 | 61.66 | 62.66 | 45.07 | 60.17 | 63.32 | 61.59 | 60.74 | 41.72 | 40.66 | 58.33 | 60.8 | 58.36 | 43.65 | 52.54 | 54.12 | 57.3 | 57.46 | 52.78 | 56.5 | 60.7 | 59.48 | 57.21 | 42.66 | 51.12 | 52.77 | 55.62 | 55.44 | 42.09
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
| INJECTION WELL FIVE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 12.46 | 12.99 | 12.53 | 13.62 | 13.6 | 10.38 | 13.63 | 12.83 | 13.34 | 13.51 | 12.76 | 13.34 | 13.52 | 12.5 | 13.05 | 14.87 | 12.29 | 12.4 | 11.41 | 13.64 | 10.44 | 12.54 | ER | 12.67 | 11.13 | 10.87 | 12.48 | 11.5 | 11.57 | 11.52
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 0 | 0 | 0 | 7.87 | 8.3 | 0 | 0 | 5.9 | 7.66 | 7.94 | 7.62 | 6.72 | 5.96 | 2.27 | 7.91 | 0 | 0 | 0 | 7.35 | 7.82 | 0 | 0 | 5.6 | 7.38 | 7.57 | 0 | 0 | 0 | 6.72 | 7.13
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 5.61 | 8.49 | 9.04 | 11.43 | 11.42 | 0.6 | 10.07 | 10.93 | 10.95 | 10.87 | 11.17 | 10.42 | 10.88 | 10.46 | 10.33 | 1.9 | 7.8 | 8.22 | 10.24 | 9.86 | 4.79 | 9.21 | 11.61 | 10.15 | 9.8 | 2.24 | 7.49 | 7.89 | 9.67 | 9.79
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 66.92 | 69.91 | 66.97 | 70.8 | 70.4 | 56.96 | 72.9 | 68.18 | 69.63 | 67.87 | 65.5 | 70.4 | 71.3 | 65.35 | 67.74 | 78.6 | 65.72 | 65.95 | 61.32 | 70.2 | 59.91 | 67.05 | 64.3 | 65.43 | 59.31 | 57.03 | 66.79 | 62.69 | 62.42 | 60.08
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 37.61 | 36.37 | 37.8 | 48.47 | 49.63 | 36.8 | 37.42 | 48.2 | 48.33 | 49.05 | 48.12 | 45.9 | 47.44 | 39.97 | 48.9 | 36.24 | 35.95 | 37.17 | 46.71 | 48.77 | 37.6 | 36.73 | 48.4 | 46.61 | 46.75 | 36.87 | 35.86 | 36.94 | 45.69 | 46.38
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 49.52 | 55.55 | 56.77 | 61.65 | 60.97 | 39.57 | 59.78 | 60.42 | 59.61 | 58.4 | 59.35 | 58.3 | 59.76 | 57.29 | 56.27 | 41.4 | 52.39 | 53.23 | 56.43 | 55.34 | 45.73 | 56.84 | 58.37 | 56.11 | 54.04 | 41.15 | 51.16 | 51.78 | 54.35 | 54.04
GTL DAILY LABORATORY ANALYSIS REPORT DATA
| RAW INFLUENT DATA |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
RAW TOTAL SUSPENDED SOLIDS | [5 empty] | 90 | 112 | 90 | 44 | 66 | 82 | 40 | 32 | 152 | 46 | 84 | 28 | 122 | 100 | 76 | 48 | 106 | 90 | LS | 40 | 18 | 88 | 44 | 68 | 106 | 90 | 100 | 98 | 83 | 96
RAW FIXED SUSPENDED SOLIDS | [5 empty] | 26 | 24 | 12 | 0 | 20 | 20 | 24 | 16 | 70 | 0 | 30 | 4 | 24 | 28 | 12 | 14 | 20 | 20 | LS | 20 | 6 | 24 | 10 | 0 | 13 | 10 | 12 | 24 | 38 | 4
RAW ALKILINITY | [5 empty] | 194 | 192 | 194 | 196 | 198 | 196 | 196 | 189 | 191 | 194 | 208 | 188 | 192 | 216 | 214 | 203 | 202 | 208 | LS | 200 | 196 | 194 | 190 | 192 | 198 | 188 | 193 | 190 | 196 | 197
RAW CHLORIDES | [5 empty] | 480 | 550 | 540 | 470 | 460 | 680 | 550 | 500 | 550 | 610 | 560 | 690 | 710 | 540 | 550 | 600 | 660 | 650 | 690 | 710 | 600 | 540 | 580 | 550 | 570 | 590 | 620 | 700 | 640 | 650
RAW COD | [5 empty] | 130 | 133 | 120 | 116 | 121 | 124 | 158 | 130 | 135 | 145 | 192 | 126 | 125 | 134 | 111 | 159 | 168 | 141 | 189 | 153 | 139 | 127 | 157 | 195 | 168 | 186 | 157 | 210 | 163 | 144
RAW CBOD | [5 empty] | 46.9 | 36.2 | 34.6 | 28 | 31.9 | 32.7 | 16.4 | 45 | 76.9 | 86 | 54.9 | 57.9 | 58.3 | 58.3 | 63.9 | 53.36 | 53.11 | 67.3 | 70.78 | 65.89 | 37.47 | 61.5 | 64.47 | 63.15 | 63.2 | 71 | 123 | 66 | 81 | 102
RAW SUFATES | [5 empty] | 121.5 | 118.25 | 117.25 | 101.5 | 106.75 | 135 | 118.75 | 127 | 135 | 141.75 | 130.25 | 147.75 | 149.5 | 123.75 | 127 | 124.5 | 127.25 | 129.25 | 140.75 | 122.25 | 135.75 | 122 | 114.75 | 122.25 | 131.25 | 136 | 146.25 | 150.5 | 132.75 | 132.25
| EFFLUENT DATA |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
EFFLUENT TOTAL DISSOLVED SOLIDS | [5 empty] | 1022 | 1102 | 1086 | 945 | 1019 | 1208 | 1079 | 1228 | 1114 | 1257 | 1117 | 1390 | 1597 | 1155 | 1185 | 1340 | 1298 | 1350 | LS | 1336 | 1154 | 1193 | 1263 | 1172 | 1187 | 1226 | 1271 | 1368 | 1360 | 1344
EFFLUENT TOTAL SUSPENDED SOLIDS | [5 empty] | 23 | 10 | LS | 12 | 10 | 9 | 7 | 11 | 27 | 14 | 11 | 5 | 21 | 12 | 10 | 14 | 20 | 15 | LS | 8 | 6 | 17 | 21 | 16 | 16 | 14 | 17 | 8 | 8 | 14
EFFLUENT FIXED SUSPENDED SOLIDS | [5 empty] | 5 | 3 | LS | 0 | 8 | 3 | 5 | 0 | 17 | 7 | 8 | 1 | 2 | 5 | 1 | 10 | 9 | 5 | LS | 0 | 4 | 6 | 6 | 0 | 4 | 3 | 5 | 1 | 1 | 0
EFFLUENT ALKILINITY | [5 empty] | 192 | 184 | 188 | 184 | 192 | 192 | 192 | 186 | 185 | 189 | 202 | 202 | 188 | 212 | 202 | 194 | 184 | 190 | LS | 188 | 184 | 190 | 178 | 186 | 186 | 188 | 198 | 198 | 202 | 197
EFFLUENT TURBIDITY | [5 empty] | 3.94 | 5.27 | 4.55 | 4.58 | 4.16 | 3.76 | 2.73 | 4.25 | 4.21 | 3.94 | 3.17 | 3.35 | 3.9 | 4.33 | 5.77 | 5.97 | 5.7 | 4.08 | LS | 5.1 | 6.8 | 5.55 | 6.45 | 5.46 | 5.51 | 6.27 | 7.07 | 7.47 | 7.13 | 6.63
EFFLUENT CHLORIDES | [5 empty] | 510 | 570 | 550 | 490 | 500 | 620 | 530 | 610 | 560 | 620 | 520 | 690 | 790 | 550 | 560 | 550 | 680 | 660 | 720 | 660 | 620 | 560 | 600 | 590 | 600 | 600 | 610 | 680 | 660 | 670
EFFLUENT CONDUCTIVITY | [5 empty] | 2190 | 2320 | 2280 | 1970 | 2020 | 2500 | 2240 | 2460 | 2420 | 2500 | 2220 | 2830 | 3100 | 2320 | 2370 | 2530 | 2590 | 2660 | LS | 2620 | 2410 | 2390 | 2450 | 2410 | 2400 | 2470 | 2640 | 2680 | 2470 | 2690
EFFLUENT TOTAL BACTERIA COUNT | [5 empty] | TNTC | TNTC | 0 | 134 | 188 | 690 | TNTC | TNTC | TNTC | TNTC | TNTC | TNTC | TNTC | TNTC | 380 | 8 | 290 | 0 | 9 | TNTC | TNTC | 0 | 0 | 0 | 0 | 27 | 45 | 152 | 152 | 213
EFFLUENT FECAL BACTERIA COUNT | [5 empty] | TNTC | TNTC | 9 | 9 | 0 | 0 | 60000 | TNTC | TNTC | TNTC | TNTC | TNTC | 39000 | 50000 | 0 | 0 | 0 | 0 | 0 | TNTC | TNTC | 10 | 10 | 0 | 0 | 0 | 9 | 9 | 0 | 0
EFFLUENT COD | [5 empty] | 40.4 | 35.4 | 33.7 | 31 |  | 32.8 | 35.2 | 38.1 | 36.4 | 37.4 | 48.1 | 37.6 | 40.6 | 35.9 | 39.5 | 31.3 | 34.4 | 34.9 | 36 | 34.5 | 34.3 | 39.9 | 35.4 | 39.5 | 38.1 | 47 | 40.9 | 37.1 | 43.9 | 42.9
EFFLUENT CBOD | [5 empty] | 2.2 | 2.09 | 0.79 | 1 | 0.99 | 1.66 | 1 | 2.03 | 4.87 | 2.18 | 2.51 | 2.28 | 1.8 | 3.07 | 2.84 | 2.43 | 3.99 | 1.29 | 1.42 | 1 | 5.56 | 2.37 | 2.97 | 3.3 | 2.87 | 4 | 7 | 5 | 7 | 5
EFFLUENT SULFATES | [5 empty] | 108.75 | 111.5 | 107.25 | 102.75 | 110.25 | 121.5 | 115.25 | 109.75 | 122.5 | 104.75 | 128.5 | 141.5 | 115.75 | 115.75 | 141 | 120 | 122 | 124.5 | 133.25 | 113.25 | 125.5 | 108.25 | 116.5 | 117 | 120 | 119.25 | 124.5 | 126.75 | 111.5 | 110.75
LABORATORY NUTRIENT DATA
RAW INFLUENT | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
RAW AMMONIA (PPM) | [5 empty] | 9.5 | 9.8 | 10 | 11 | 7.5 | 9.7 | 8.8 | 9.4 | 9.5 | 9.5 | 9 | 9.4 | 12 | 13 | 9.4 | 15 | 14 | 13 | 13 | 12 | 6.7 | 8.8 | 10 | 12 | 8.1 | 12 | 12 | 12 | 12 | 12
RAW NITRATES (PPM) | [7 empty] | 0.053 | 0.0086 | 0.032 | 0.066 | 0.049 | 0.083 | 0.083 | 0.062 | 0.069 | 0.075 | 0.093 | 0.07 | 0.046 | 0.028 | 0.043 | 0.12 | 0.03 | 0.095 |  | 0.1 | 0.016 | 0.022 | 0.012 | 0.11 | 0.086 | 0.11 | 0.079 | 0.098
RAW TOTAL KNEDJAHL NITRIGEN | [5 empty] | 18 | 14 | 13 | 13 | 9.2 | 16 | 14 | 14 | 18 | 17 | 15 | 17 | 19 | 17 | 18 | 17 | 16 | 17 | 17 | 15 | 17 | 16 | 15 | 19 | 19 | 18 | 18 |  |  | 19
RAW TOTAL PHOSPHORUS | [5 empty] | 3.3 | 2.1 | 2 | 2 | 1.9 | 2.1 | 1.9 | 2 | 2.2 | 2 | 1.8 | 2 | 2.3 | 2.1 | 2.4 | 2.5 | 2.1 | 2.4 | 2.4 | 2 | 2 | 1.9 | 2 | 2.6 | 2.4 | 2.6 | 2.5 |  |  | 2.4
EFFLUENT | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
EFFLUENT AMMONIA (PPM) | [5 empty] | 7.8 | 7.8 | 8.1 | 7.1 | 5 | 6.2 | 6.5 | 7.6 | 6.8 | 8.9 | 6.4 | 8 | 9.9 | 8.8 | 10 | 9.6 | 7.2 | 8.8 | 9 | 7.2 | 7.5 | 8.4 | 7.2 | 6 | 7.2 | 8.8 | 7.6 | 7.4 | 9.9 | 8.7
EFFLUENT NITRATES (PPM) | [5 empty] | 0.1 | 0.2 | 0.25 | 0.24 | 0.024 | 0.37 | 0.31 | 0.31 | 0.27 | 0.74 | 0.21 | 0.5 | 0.066 | 0.96 | 0.12 | 0.82 | 0.43 | 0.31 | 0.31 | 0.34 | 0.26 | 0.25 | 0.54 | 0.24 | 0.27 | 0.29 | 0.34 | 0.28 | 0.3 | 0.28
EFFLUENT TOTAL KNEDJAHL NITRIGEN | [5 empty] | 10 | 9.5 | 8.6 | 7.7 | 6.1 | 10 | 10 | 9.6 | 12 | 10 | 10 | 12 | 12 | 13 | 14 | 10 | 9.1 | 8.8 | 9.5 | 8.3 | 12 | 12 | 0 | 11 | 12 | 12 | 13 |  |  | 12
EFFLUENT TOTAL PHOSPHORUS | [5 empty] | 0.93 | 0.97 | 0.78 | 0.88 | 0.5 | 0.48 | 0.62 | 1 | 0.74 | 0.79 | 0.77 | 0.56 | 0.78 | 0.96 | 1.7 | 1.5 | 1.3 | 0.95 | 0.95 | 0.86 | 1 | 1.5 | 1.4 | 1.4 | 1 | 1.3 | 1.6 |  |  | 1.1
LABORATORY REACTOR PROCESSES DATA
| REACTOR ONE TRAIN A |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
MIXED-LIQUIR SUSPENDED SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
AVERAGE SETTLABLE SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
MIXED LIQUIR VOLITLE SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
| REACTOR ONE TRAIN B |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
MIXED-LIQUIR SUSPENDED SOLIDS | [5 empty] | 2210 | 1910 | 2460 | 2400 | 2600 | 2290 | 2770 | 2110 | 3220 | 3020 | 2360 | 1940 | 2570 | 1900 | 1820 | 3250 | 2850 | 2710 | LS | 3130 | 1800 | 3360 | 2890 | 3150 | 2580 | 3380 | 1810 | 1630 | 1360 | ER
AVERAGE SETTLABLE SOLIDS | [5 empty] | 17 | 18 | 22 | 21 | 20 | 20 | 17 | 16 | 24 | 28 | 25 | 20 | 16 | 18 | 15 | 18 | 21 | 18 | LS | 18 | 18 | 16 | 19 | 25 | 23 | 20 | 17 | 16 | 14 | 20
MIXED LIQUIR VOLITLE SOLIDS | [5 empty] | 1670 | 1670 | 1720 | 2000 | 1900 | 1840 | 2060 | 1640 | 2450 | 2330 | 1760 | 1560 | 2030 | 1480 | 1510 | 2440 | 2230 | 2240 | LS | 2400 | 1400 | 2470 | 2360 | 560 | 2060 | 2220 | 1480 | 1410 | 1220 | ER
LABORATORY REACTOR PROCESSES DATA
CONTINUED
| REACTOR TWO TRAIN C |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
MIXED-LIQUIR SUSPENDED SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
AVERAGE SETTLABLE SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
MIXED LIQUIR VOLITLE SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
| REACTOR TWO TRAIN D |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
MIXED-LIQUIR SUSPENDED SOLIDS | [5 empty] | 1800 | 4220 | 2390 | 2850 | 2820 | 2790 | 3550 | 2380 | 2350 | 3020 | 2490 | 2160 | 2650 | 1980 | 2190 | 3020 | 2700 | 2370 | LS | 2140 | 1880 | 1970 | 3780 | 2560 | 2120 | 1920 | 1780 | 1310 | 1500 | ER
AVERAGE SETTLABLE SOLIDS | [5 empty] | 15 | 17 | 23 | 21 | 21 | 18 | 15 | 14 | 25 | 28 | 25 | 20 | 18 | 18 | 15 | 18 | 21 | 19 | LS | 20 | 17 | 15 | 18 | 26 | 25 | 18 | 16 | 15 | 14 | 24
MIXED LIQUIR VOLITLE SOLIDS | [5 empty] | 1430 | 2150 | 2140 | 2130 | 2320 | 2100 | 2500 | 1520 | 1860 | 2160 | 1940 | 1530 | 1990 | 1540 | 1770 | 2100 | 2050 | 1930 | LS | 1740 | 1520 | 1560 | 2980 | 2180 | 1730 | 1650 | 1450 | 1120 | 1290 | ER
LABORATORY RETURN ACTIVATED SLUDGE AND WASTE SLUDGE DATA
| RETURN ACTIVATED SLUDGE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
PERCENT RETURN SLUDGE TOTAL SUSPENDED SOLIDS | [5 empty] | 0.6 | 0.91 | 1.03 | 1.01 | 1.03 | 0.91 | 0.82 | 0.75 | 0.65 | 1.15 | 1.15 | 0.97 | 0.77 | 0.73 | 0.75 | 0.93 | 0.9 | 0.73 | LS | 0.64 | 0.49 | 0.58 | 0.88 | 1.02 | 0.18 | 0.86 | 0.58 | 0.57 | 0.56 | 0.71
PERCENT RETURN SLUDGE FIXED SUSPENDED SOLIDS | [5 empty] | 22.35 | 27.47 | 24.76 | 16.57 | 23.21 | 28.57 | 28.43 | 29.76 | 28.13 | 24.78 | 25.4 | 30 | 29.59 | 28.72 | 30.12 | 26.61 | 26.55 | 34.02 | LS | 32.3 | 29.67 | 33.85 | 25 | 24.77 | 25.66 | 26.26 | 29.49 | 31.88 | 33.33 | 28.57
|  | WASTE SLUDGE |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
PERCENT WASTE FEED TOTAL SUSPENDED SOLDS | [5 empty] | 1.33 |  |  |  |  | 1.78 | 1.17 | 1.59 |  |  | 1.99 | 1.69 | 1.64 | 0.59 | 1.07 |  |  | 1.17 | LS |  | 1.17 | 1.19 |  |  | 1.53 | 1.08 | 1.27 | 1.09 | 1.24
PERCENT WASTE FEED FIXED SUSPENDED SOLIDS | [5 empty] | 23.31 |  |  |  |  | 21.91 | 24.79 | 23.27 |  |  | 21.11 | 21.89 | 24.39 | 32.2 | 28.04 |  |  | 25.64 | LS |  | 25.64 | 26.05 |  |  | 21.57 | 25.93 | 24.41 | 27.52 | 24.19
WASTE FEED SLUDGE pH | [5 empty] | 6.42 |  |  |  |  | 6.63 | 6.43 | 6.5 |  |  | 6.31 | 6.37 | 6.48 | 6.6 | 6.53 |  |  | 6.55 | LS |  | 6.53 | 6.47 |  |  | 6.42 | 6.66 | 6.46 | 6.43 | 6.31
DEWATERING FILTRATE TOTAL SUSPENDED SOLIDS | [5 empty] | 0.15 |  |  |  |  | 0.22 | 0.18 | 0.18 |  |  | 0.29 | 0.3 | 0.26 | 0.22 | 0.19 |  |  | 0.2 | LS |  | 0.16 | 0.17 |  |  | 0.16 | 0.21 | 0.19 | 0.2 | 0.2
DEWATERING FILTRATE FIXED SUSPENDED SOLIDS | [5 empty] | 66.67 |  |  |  |  | 63.64 | 66.66 | 66.67 |  |  | 48.28 | 60 | 65.38 | 63.64 | 68.42 |  |  | 40 | LS |  | 81.25 | 76.47 |  |  | 68.75 | 61.9 | 73.68 | 65 | 70
DEWATERING FILTRATE pH | [5 empty] | 6.93 |  |  |  |  | 7.13 | 7.01 | 7.15 |  |  | 6.84 | 7.16 | 7.06 | 6.99 | 6.95 |  |  | 6.88 | LS |  | 7.04 | 7.04 |  |  | 6.94 | 7.01 | 7 | 6.95 | 6.93
| DEWATERED CAKE SLUDGE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
PERCENT TOTAL SOLIDS PRESS CAKE | [5 empty] | 20.55 |  |  |  |  | 19.17 | 19.88 | 19.23 |  |  | 12.6 | 18.45 | 18.56 | 20.03 | 24.11 |  |  | 17.75 | LS |  | 17.31 | 19.44 |  |  | 20.01 | 15.62 | 18.48 | 19.57 | 19.44
PERCENT FIXED SOLIDS PRESS CAKE | [5 empty] | 18.54 |  |  |  |  | 17.89 | 24.65 | 19.35 |  |  | 20.56 | 22.11 | 19.56 | 21.77 | 44.55 |  |  | 15.83 | LS |  | 15.55 | 20.58 |  |  | 21.99 | 18.25 | 18.89 | 17.68 | 16.82
PERCENT TOTAL SOLIDS LIME CAKE
OTHER SLUDGE REMOVAL
[6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
GRIT (CU.YDS.) | [5 empty] | 15: 10; 26: 10; 30: 10
RAGS (CU.YDS.) | [5 empty] | 2: 10; 8: 10; 29: 10
VACUUM DEBRIS (EST. GAL)
MONITORING WELLS LABORATORY DATA
| MONITOR WELL ONE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
UPPER LEVEL
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
MONITORING WELLS LABORATORY DATA
| MONITOR WELL TWO |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
UPPER LEVEL
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
MONITORING WELLS LABORATORY DATA
| MONITOR WELL THREE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
FUTURE
UPPER LEVEL
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
MONITORING WELLS LABORATORY DATA
| REGIONAL MONITOR WELL ONE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
UPPER LEVEL
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
SEPTEMBER |  | 0 |  | 0
|  | 1 |  | 2
0
0
|  | 0 |  | 0
2
[5 empty] | 1st WEEK | 1: 2nd WEEK; 2: 3rd WEEK; 3: 4th WEEK
| 1 |  | 1 |  | 1 | 1: 8; 2: 15; 3: 23
| 2 |  | 2 |  | 2 | 1: 9; 2: 16; 3: 24
| 3 |  | 3 |  | 3 | 1: 10; 2: 17; 3: 25
| 4 |  | 4 |  | 4 | 1: 11; 2: 18; 3: 26
| 5 |  | 5 |  | 5 | 1: 12; 2: 19; 3: 27
| 6 |  | 6 |  | 6 | 1: 13; 2: 20; 3: 28
| 7 |  | 7 |  | 7 | 1: 14; 2: 21; 3: 29
| 8 |  | 8 |  |  | 2: 22; 3: 30
| 9 |  | 9
| 10 |  | 10
| 11 |  | 11
| 12 |  | 12
| 13 |  | 13
| 14 |  | 14
| 15 |  | 15
| 16 |  | 16
| 17 |  | 17
| 18 |  | 18
| 19 |  | 19
| 20 |  | 20
| 21 |  | 21
| 22 |  | 22
| 23 |  | 23
| 24 |  | 24
| 25 |  | 25
| 26 |  | 26
| 27 |  | 27
| 28 |  | 28
29
30
| APRIL | MARCH | FEBRUARY
| AUGUST | JULY | JUNE
| DECEMBER | NOVEMBER | OCTOBER
| FEBRUARY | JANUARY | DECEMBER
| JANUARY | DECEMBER | NOVEMBER
| JUNE | MAY | APRIL
| JULY | JUNE | MAY | AUGUST
| MARCH | FEBRUARY | JANUARY | JULY
| MAY | APRIL | MARCH
| NOVEMBER | OCTOBER | SEPTEMBER
| OCTOBER | SEPTEMBER | AUGUST
| SEPTEMBER | AUGUST | JULY
| HYDROGEN PEROXIDE |  | 0.1465
| CHLORINE |  | 0.295
| POLYMER |  | 0.61
| FPL |  | 0.055
[6 empty] | 1st WEEK |  |  | 2nd WEEK |  |  | 3rd WEEK |  |  | 4th WEEK
[7 empty] | G | H | I | J
[5 empty] | MW1 UP | 1: 311
312
313
314
315
316
317
318

## MONITOR DATA
UNDERGROUND INJECTION CONTROL SECTION
MONTHLY OPERATING REPORT DATA SUMMARY
FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT MONTH/YEAR |  |  | SEPTEMBER |  | 2005
I.D. NUMBER: 5006M02066 | [5 empty] | LEAD OPERATOR: |  |  |  | MIKE JUST
TELEPHONE NUMBER: (954) 523-1002
MONITORING WELL 1 DATA | [6 empty] | I.D. # 5006A11311
MW-1
PERMIT/CERTIFICATION NUMBER | [6 empty] | 0054569-142-UO
PERMIT EXPIRATION DATE |  | 2009-01-06
UPPER MONITORING INTERVAL | [6 empty] | 1,288' - 1,320' |  |  |  | Ft. bls.
Sample Date |  | 2005-09-06 |  | 2005-09-13 |  | 2005-09-20 |  | 2005-09-28
Submittal Date |  | 2005-09-07 |  | 2005-09-14 |  | 2005-09-21 |  | 2005-09-29
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 49.62 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 45.44 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 75 |  | 76 |  | 75 |  | 75 |  |  | degrees (F) |  | 75.25
TDS |  | 7549 |  | 7393 |  | 7650 |  | 7484 |  |  | mg/l |  | 7519
CHLORIDE |  | 3800 |  | 3700 |  | 3750 |  | 3800 |  |  | mg/l |  | 3762.5
AMMONIA-N |  | 0.84 |  | 0.92 |  | 0.86 |  | 0.82 |  |  | mg/l |  | 0.86
TKN |  | 1.8 |  | 1.6 |  | 0.9 |  | 1.1 |  |  | mg/l |  | 1.35
pH |  | 8.29 |  | 7.98 |  | 7.97 |  | 8.06 |  |  | Std units |  | 8.075
CONDUCTIVITY |  | 12290 |  | 12020 |  | 12170 |  | 12120 |  |  | umho/cm |  | 12150
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.01 | < | 0.01 | < | 0.01 | < | 0.01 |  |  | mg/l |  | 0.01
SULFATE |  | 930 |  | 945 |  | 920 |  | 925 |  |  | mg/l |  | 930
C.O.D. 'S | [10 empty] | mg/l |  | #DIV/0!
IRON | [10 empty] | mg/l |  | #DIV/0!
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
LOWER MONITORING INTERVAL | [6 empty] | 1,449' - 1,557' |  |  |  | Ft. bls
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 47.39 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 40.1 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 73 |  | 76 |  | 74 |  | 74 |  |  | degrees (F) |  | 74.25
TDS |  | 9546 |  | 9843 |  | 9729 |  | 9182 |  |  | mg/l |  | 9575
CHLORIDE |  | 5200 |  | 4900 |  | 5100 |  | 5000 |  |  | mg/l |  | 5050
AMMONIA-N |  | 9.8 |  | 10 |  | 11 |  | 7.7 |  |  | mg/l |  | 9.625
TKN |  | 12 |  | 10 |  | NR |  | 11 |  |  | mg/l |  | 11
pH |  | 7.35 |  | 7.29 |  | 7.28 |  | 7.64 |  |  | Std units |  | 7.39
CONDUCTIVITY |  | 15590 |  | 15490 |  | 15740 |  | 15480 |  |  | umho/cm |  | 15575
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.01 | < | 0.01 | < | 0.01 | < | 0.01 |  |  | mg/l |  | 0.01
SULFATE |  | 860 |  | 963 |  | 913 |  | 763 |  |  | mg/l |  | 874.75
C.O.D. 'S | [10 empty] | mg/l |  | #DIV/0!
IRON | [10 empty] | mg/l |  | #DIV/0!
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
PAGE 24
UNDERGROUND INJECTION CONTROL SECTION
MONTHLY OPERATING REPORT DATA SUMMARY
FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT MONTH/YEAR |  |  | SEPTEMBER |  | 2005
I.D. NUMBER: 5006M02066 | [5 empty] | LEAD OPERATOR: |  |  |  | MIKE JUST
TELEPHONE NUMBER: (954) 523-1002
MONITORING WELL 2 DATA | [6 empty] | I.D. # 5006A11308 & 309
MW-2
PERMIT/CERTIFICATION NUMBER | [6 empty] | 0054569-142-UO
PERMIT EXPIRATION DATE |  | 2009-01-06
UPPER MONITORING INTERVAL | [6 empty] | 1,300' - 1,344' |  |  |  | Ft. bls.
Sample Date |  | 2005-09-06 |  | 2005-09-13 |  | 2005-09-20 |  | 2005-09-28
Submittal Date |  | 2005-09-07 |  | 2005-09-14 |  | 2005-09-21 |  | 2005-09-29
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 35.43 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 18.96 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 74 |  | 76 |  | 73 |  | 74 |  |  | degrees (F) |  | 74.25
TDS |  | 7372 |  | 7613 |  | 7490 |  | 7771 |  |  | mg/l |  | 7561.5
CHLORIDE |  | 3750 |  | 3650 |  | 3700 |  | 3650 |  |  | mg/l |  | 3687.5
AMMONIA-N |  | 0.83 |  | 0.87 |  | 0.85 |  | 0.81 |  |  | mg/l |  | 0.84
TKN |  | 1.3 |  | 0.89 |  | 0.9 |  | 1.2 |  |  | mg/l |  | 1.0725
pH |  | 8.21 |  | 8.03 |  | 7.56 |  | 8.12 |  |  | Std units |  | 7.98
CONDUCTIVITY |  | 11820 |  | 11640 |  | 11910 |  | 11830 |  |  | umho/cm |  | 11800
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.01 | < | 0.01 | < | 0.01 | < | 0.01 |  |  | mg/l |  | 0.01
SULFATE |  | 948 |  | 915 |  | 1068 |  | 808 |  |  | mg/l |  | 934.75
C.O.D. 'S | [10 empty] | mg/l |  | #DIV/0!
IRON | [10 empty] | mg/l |  | #DIV/0!
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
LOWER MONITORING INTERVAL | [6 empty] | 1,970' - 2,025' |  |  |  | Ft. bls
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 43.62 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 35.98 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 73 |  | 74 |  | 75 |  | 72 |  |  | degrees (F) |  | 73.5
TDS |  | 31689 |  | 32535 |  | 32378 |  | 31738 |  |  | mg/l |  | 32085
CHLORIDE |  | 16000 |  | 17200 |  | 17200 |  | 16200 |  |  | mg/l |  | 16650
AMMONIA-N |  | 1.4 |  | 1.4 |  | 1.6 |  | 1.3 |  |  | mg/l |  | 1.425
TKN |  | 1.9 |  | 2 |  | 1.9 |  | 2.1 |  |  | mg/l |  | 1.975
pH |  | 7.5 |  | 7.47 |  | 8.18 |  | 7.7 |  |  | Std units |  | 7.7125
CONDUCTIVITY |  | 46700 |  | 46100 |  | 4690 |  | 4640 |  |  | umho/cm |  | 25532.5
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.01 | < | 0.01 | < | 0.01 | < | 0.01 |  |  | mg/l |  | 0.01
SULFATE |  | 3130 |  | 2940 |  | 2470 |  | 2730 |  |  | mg/l |  | 2817.5
C.O.D. 'S | [10 empty] | mg/l |  | #DIV/0!
IRON | [10 empty] | mg/l |  | #DIV/0!
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
PAGE 25
UNDERGROUND INJECTION CONTROL SECTION
MONTHLY OPERATING REPORT DATA SUMMARY
FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT MONTH/YEAR |  |  | SEPTEMBER |  | 2005
I.D. NUMBER: 5006M02066 | [5 empty] | LEAD OPERATOR: |  |  |  | MIKE JUST
TELEPHONE NUMBER: (954) 523-1002
MONITORING WELL 2 DATA | [6 empty] | I.D. # 5006A11310
MW-3
PERMIT/CERTIFICATION NUMBER | [6 empty] | 0054569-142-UO
PERMIT EXPIRATION DATE |  | 2009-01-06
UPPER MONITORING INTERVAL | [6 empty] | 1,300' - 1,349' |  |  |  | Ft. bls.
Sample Date |  | 2005-09-06 |  | 2005-09-13 |  | 2005-09-20 |  | 2005-09-28
Submittal Date |  | 2005-09-07 |  | 2005-09-14 |  | 2005-09-21 |  | 2005-09-29
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 34.7 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 20.05 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 72 |  | 73 |  | 72 |  | 73 |  |  | degrees (F) |  | 72.5
TDS |  | 7532 |  | 8479 |  | 7574 |  | 7658 |  |  | mg/l |  | 7810.75
CHLORIDE |  | 3450 |  | 3700 |  | 3750 |  | 3800 |  |  | mg/l |  | 3675
AMMONIA-N |  | 0.84 |  | 0.77 |  | 0.92 |  | 0.78 |  |  | mg/l |  | 0.8275
TKN |  | 1 |  | 0.84 |  | 0.92 |  | 1.1 |  |  | mg/l |  | 0.965
pH |  | 8.26 |  | 8.28 |  | 8.19 |  | 8.32 |  |  | Std units |  | 8.2625
CONDUCTIVITY |  | 11950 |  | 11880 |  | 12100 |  | 12160 |  |  | umho/cm |  | 12022.5
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.01 | < | 0.01 | < | 0.01 | < | 0.01 |  |  | mg/l |  | 0.01
SULFATE |  | 960 |  | 890 |  | 883 |  | 893 |  |  | mg/l |  | 906.5
C.O.D. 'S | [10 empty] | mg/l |  | #DIV/0!
IRON | [10 empty] | mg/l |  | #DIV/0!
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
LOWER MONITORING INTERVAL | [6 empty] | 1,970' - 2,027' |  |  |  | Ft. bls
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 46.38 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 37.4 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 70 |  | 72 |  | 71 |  | 71 |  |  | degrees (F) |  | 71
TDS |  | 28726 |  | 29644 |  | 28378 |  | 28371 |  |  | mg/l |  | 28779.75
CHLORIDE |  | 15600 |  | 15800 |  | 14800 |  | 15400 |  |  | mg/l |  | 15400
AMMONIA-N |  | 1.8 |  | 2.8 |  | 2.8 |  | 2.3 |  |  | mg/l |  | 2.425
TKN |  | 2.5 |  | 3.2 |  | 2.9 |  | 3.2 |  |  | mg/l |  | 2.95
pH |  | 7.4 |  | 7.54 |  | 7.49 |  | 7.66 |  |  | Std units |  | 7.5225
CONDUCTIVITY |  | 42500 |  | 42000 |  | 42600 |  | 42400 |  |  | umho/cm |  | 42375
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.01 | < | 0.01 | < | 0.01 | < | 0.01 |  |  | mg/l |  | 0.01
SULFATE |  | 2830 |  | 2910 |  | 2940 |  | 2710 |  |  | mg/l |  | 2847.5
C.O.D. 'S | [10 empty] | mg/l |  | #DIV/0!
IRON | [10 empty] | mg/l |  | #DIV/0!
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
PAGE 26
UNDERGROUND INJECTION CONTROL SECTION
MONTHLY OPERATING REPORT DATA SUMMARY
FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT MONTH/YEAR |  |  | SEPTEMBER |  | 2005
I.D. NUMBER: 5006M02066 | [5 empty] | LEAD OPERATOR: |  |  |  | MIKE JUST
TELEPHONE NUMBER: (954) 523-1002
REGIONAL MONITORING WELL DATA
RMW-1
PERMIT NUMBER | [6 empty] | 0054569-142-UO
PERMIT EXPIRATION DATE |  | 2009-01-06
UPPER MONITORING INTERVAL | [6 empty] | 1300' - 1339' |  |  |  | Ft. bls.
Sample Date |  | 2005-09-06
Submittal Date |  | 2005-09-07
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 45.23 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 0.25 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 72 | [8 empty] | degrees (F) |  | 72
TDS |  | 5982 | [8 empty] | mg/l |  | 5982
CHLORIDE |  | 2800 | [8 empty] | mg/l |  | 2800
AMMONIA-N |  | 0.64 | [8 empty] | mg/l |  | 0.64
TKN |  | 0.96 | [8 empty] | mg/l |  | 0.96
pH |  | 8.48 | [8 empty] | Std units |  | 8.48
CONDUCTIVITY |  | 9280 | [8 empty] | umho/cm |  | 9280
FECAL COLIFORM |  | 0 | [8 empty] | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.01 | [8 empty] | mg/l |  | 0.01
SULFATE |  | 795 | [8 empty] | mg/l |  | 795
C.O.D. 'S | [10 empty] | mg/l |  | #DIV/0!
IRON | [10 empty] | mg/l |  | #DIV/0!
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
LOWER MONITORING INTERVAL | [6 empty] | 1500' - 1600' |  |  |  | Ft. bls
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 23.35 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 0.25 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 71 | [8 empty] | degrees (F) |  | 71
TDS |  | 27957 | [8 empty] | mg/l |  | 27957
CHLORIDE |  | 15600 | [8 empty] | mg/l |  | 15600
AMMONIA-N |  | 0.29 | [8 empty] | mg/l |  | 0.29
TKN |  | 0.67 | [8 empty] | mg/l |  | 0.67
pH |  | 7.51 | [8 empty] | Std units |  | 7.51
CONDUCTIVITY |  | 41600 | [8 empty] | umho/cm |  | 41600
FECAL COLIFORM |  | 0 | [8 empty] | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.01 | [8 empty] | mg/l |  | 0.01
SULFATE |  | 1870 | [8 empty] | mg/l |  | 1870
C.O.D. 'S | [10 empty] | mg/l |  | #DIV/0!
IRON | [10 empty] | mg/l |  | #DIV/0!
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
PAGE 27
Formulas:
LEAD OPERATOR: = [LEAD OPERATOR:, row above]+1

## WELL PRN DATA
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 1 |  |  | 244 | 245 | 246 | 247 | 248 | 249 | 250 | 251 | 252 | 253 | 254 | 255 | 256 | 257 | 258 | 259 | 260 | 261 | 262 | 263 | 264 | 265 | 266 | 267 | 268 | 269 | 270 | 271 | 272 | 273
244 | 12.93 | 0 | 5.64 | 63.67 | 37.13 | 47.58
245 | 13.7 | 0 | 2.5 | 66.63 | 36.99 | 41.84 |  |  | FLOW
246 | 14.23 | 0 | 9.63 | 67.22 | 36.73 | 55.79 | I |  | MAX | 12.93 | 13.7 | 14.23 | 15.23 | 14.57 | 15.22 | 12.57 | 14.5 | 14.75 | 14.3 | 13.64 | 13.63 | 15.47 | 13.67 | 14.52 | 14.17 | 10.99 | 14.05 | 12.42 | 14.66 | 14.07 | 12.48 | 13.74 | 14.03 | 12.17 | 11.77 | 11 | 13.04 | 12.38 | 12.2
247 | 15.23 | 5.44 | 12.43 | 70.9 | 44.41 | 61.67 | N |  | MIN | 0 | 0 | 0 | 5.44 | 8.48 | 7.57 | 0 | 0.01 | 7.04 | 8.48 | 8.01 | 0 | 0 | 0 | 8.25 | 0.01 | 0 | 0.01 | 0.01 | 8.21 | 6.93 | 0 | 0 | 3.63 | 7.54 | 6.63 | 0 | 0 | 0 | 7.33
248 | 14.57 | 8.48 | 12.18 | 70.6 | 49.77 | 61.14 | J |  | TOT | 5.64 | 2.5 | 9.63 | 12.43 | 12.18 | 12.55 | 1.18 | 10.89 | 11.87 | 11.5 | 11.82 | 3.75 | 10.58 | 10.48 | 10.94 | 10.31 | 2.36 | 8.69 | 9 | 10.67 | 10.46 | 0.73 | 10.47 | 10.87 | 10.3 | 10.15 | 2.19 | 8.33 | 8.42 | 10.26
249 | 15.22 | 7.57 | 12.55 | 73 | 47.96 | 62.72 | E | INJECTION WELL ONE
250 | 12.57 | 0 | 1.18 | 62.93 | 37.12 | 39.8 | C |  | PSI
251 | 14.5 | 0.01 | 10.89 | 68.33 | 36.51 | 58.02 | T |  | MAX | 63.67 | 66.63 | 67.22 | 70.9 | 70.6 | 73 | 62.93 | 68.33 | 69.71 | 67.95 | 65.98 | 66.37 | 71.7 | 65.45 | 67.94 | 67.82 | 56.51 | 66.41 | 60.75 | 70.3 | 68.7 | 62.11 | 64.61 | 65.65 | 59.53 | 58.72 | 56.72 | 63.05 | 60.7 | 60.29
252 | 14.75 | 7.04 | 11.87 | 69.71 | 48.39 | 59.63 | O |  | MIN | 37.13 | 36.99 | 36.73 | 44.41 | 49.77 | 47.96 | 37.12 | 36.51 | 48.39 | 49.11 | 48.3 | 36.3 | 36.19 | 36.12 | 48.98 | 36.47 | 36.45 | 36.29 | 36.07 | 48.9 | 45.36 | 36.84 | 36.84 | 42.95 | 46.9 | 44.82 | 36.39 | 36.25 | 35.87 | 46.51
253 | 14.3 | 8.48 | 11.5 | 67.95 | 49.11 | 58.57 | N |  | AVG | 47.58 | 41.84 | 55.79 | 61.67 | 61.14 | 62.72 | 39.8 | 58.02 | 59.63 | 58.57 | 59.59 | 43.36 | 56.93 | 55.75 | 56.44 | 55.21 | 41.03 | 52.55 | 52.69 | 55.48 | 55.69 | 38.63 | 56.21 | 56.12 | 54.26 | 54.01 | 40.42 | 51.23 | 50.93 | 54.25
254 | 13.64 | 8.01 | 11.82 | 65.98 | 48.3 | 59.59
255 | 13.63 | 0 | 3.75 | 66.37 | 36.3 | 43.36 | W
256 | 15.47 | 0 | 10.58 | 71.7 | 36.19 | 56.93 | E
257 | 13.67 | 0 | 10.48 | 65.45 | 36.12 | 55.75 | L
258 | 14.52 | 8.25 | 10.94 | 67.94 | 48.98 | 56.44 | L
259 | 14.17 | 0.01 | 10.31 | 67.82 | 36.47 | 55.21 | O
260 | 10.99 | 0 | 2.36 | 56.51 | 36.45 | 41.03 | N
261 | 14.05 | 0.01 | 8.69 | 66.41 | 36.29 | 52.55 | E
262 | 12.42 | 0.01 | 9 | 60.75 | 36.07 | 52.69
263 | 14.66 | 8.21 | 10.67 | 70.3 | 48.9 | 55.48 | D
264 | 14.07 | 6.93 | 10.46 | 68.7 | 45.36 | 55.69 | A
265 | 12.48 | 0 | 0.73 | 62.11 | 36.84 | 38.63 | T
266 | 13.74 | 0 | 10.47 | 64.61 | 36.84 | 56.21 | A
267 | 14.03 | 3.63 | 10.87 | 65.65 | 42.95 | 56.12
268 | 12.17 | 7.54 | 10.3 | 59.53 | 46.9 | 54.26
269 | 11.77 | 6.63 | 10.15 | 58.72 | 44.82 | 54.01
270 | 11 | 0 | 2.19 | 56.72 | 36.39 | 40.42
271 | 13.04 | 0 | 8.33 | 63.05 | 36.25 | 51.23
272 | 12.38 | 0 | 8.42 | 60.7 | 35.87 | 50.93
273 | 12.2 | 7.33 | 10.26 | 60.29 | 46.51 | 54.25
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 2 |  |  | 244 | 245 | 246 | 247 | 248 | 249 | 250 | 251 | 252 | 253 | 254 | 255 | 256 | 257 | 258 | 259 | 260 | 261 | 262 | 263 | 264 | 265 | 266 | 267 | 268 | 269 | 270 | 271 | 272 | 273
244 | 14.6 | 9.04 | 12.06 | 66.27 | 50.16 | 58.07
245 | 15.29 | 8.5 | 12.45 | 69.19 | 48.21 | 59.14 |  |  | FLOW
246 | 14.18 | 0.06 | 2.94 | 64.16 | 37.24 | 43.14 | I |  | MAX | 14.6 | 15.29 | 14.18 | 14.22 | 14.94 | 15.57 | 16.08 | 12.24 | 14.99 | 14.93 | 14.01 | 15.67 | 12.22 | 14.14 | 14.24 | 15.56 | 14.43 | 13.41 | 12.8 | 14.99 | 14.42 | 14.69 | 11.42 | 13.31 | 12 | 11.99 | 14.67 | 12.28 | 12.78 | 12.53
247 | 14.22 | 0.06 | 9.8 | 65.33 | 37.31 | 55.36 | N |  | MIN | 9.04 | 8.5 | 0.06 | 0.06 | 0.06 | 7.72 | 9.75 | 0.06 | 0.06 | 5.83 | 8.26 | 7.1 | 0.05 | 0.05 | 0.05 | 0.06 | 7.77 | 0.06 | 0.06 | 0.05 | 7.08 | 8.92 | 0.06 | 0.05 | 0.05 | 6.74 | 6.69 | 0.05 | 0.05 | 0.05
248 | 14.94 | 0.06 | 10.08 | 69.43 | 37.75 | 55.85 | J |  | TOT | 12.06 | 12.45 | 2.94 | 9.8 | 10.08 | 12.9 | 13.17 | 0.9 | 10.51 | 11.78 | 12.14 | 11.9 | 0.71 | 9.07 | 9 | 10.72 | 11.42 | 2.54 | 8.81 | 8.69 | 10.7 | 12.56 | 0.81 | 8.61 | 8.51 | 10.42 | 10.86 | 2.4 | 8.31 | 8.77
249 | 15.57 | 7.72 | 12.9 | 71.8 | 47.09 | 61.69 | E | INJECTION WELL TWO
250 | 16.08 | 9.75 | 13.17 | 72.1 | 51.94 | 61.6 | C |  | PSI
251 | 12.24 | 0.06 | 0.9 | 58.14 | 37.11 | 39.59 | T |  | MAX | 66.27 | 69.19 | 64.16 | 65.33 | 69.43 | 71.8 | 72.1 | 58.14 | 68.59 | 66.87 | 64.85 | 69.9 | 58.43 | 65.95 | 65.98 | 68.94 | 65.23 | 61.3 | 60.04 | 69.19 | 67.88 | 66.42 | 57.41 | 61.76 | 57.5 | 57.72 | 66.06 | 57.29 | 59.7 | 59.43
252 | 14.99 | 0.06 | 10.51 | 68.59 | 37.71 | 55.86 | I |  | MIN | 50.16 | 48.21 | 37.24 | 37.31 | 37.75 | 47.09 | 51.94 | 37.11 | 37.71 | 45.77 | 47.42 | 45.25 | 36.97 | 36.39 | 37.21 | 37.36 | 46.13 | 37.32 | 36.3 | 36.61 | 44.72 | 49.42 | 36.9 | 37.22 | 37.01 | 44.05 | 43.89 | 36.77 | 36.16 | 36.6
253 | 14.93 | 5.83 | 11.78 | 66.87 | 45.77 | 57.55 | O |  | AVG | 58.07 | 59.14 | 43.14 | 55.36 | 55.85 | 61.69 | 61.6 | 39.59 | 55.86 | 57.55 | 58.62 | 57.61 | 38.95 | 52.23 | 51.93 | 54.72 | 55.68 | 41.54 | 51.33 | 51.01 | 54.82 | 59.38 | 39.27 | 51.06 | 50.17 | 53.06 | 54 | 40.86 | 49.71 | 50.6
254 | 14.01 | 8.26 | 12.14 | 64.85 | 47.42 | 58.62 | N
255 | 15.67 | 7.1 | 11.9 | 69.9 | 45.25 | 57.61
256 | 12.22 | 0.05 | 0.71 | 58.43 | 36.97 | 38.95 | W
257 | 14.14 | 0.05 | 9.07 | 64.41 | 36.39 | 52.23 | E
258 | 14.24 | 0.05 | 9 | 65.98 | 37.21 | 51.93 | L
259 | 15.56 | 0.06 | 10.72 | 68.94 | 37.36 | 54.72 | L
260 | 14.43 | 7.77 | 11.42 | 65.23 | 46.13 | 55.68
261 | 13.41 | 0.06 | 2.54 | 61.3 | 37.32 | 41.54 | T
262 | 12.8 | 0.06 | 8.81 | 60.04 | 36.3 | 51.33 | W
263 | 14.99 | 0.05 | 8.69 | 69.19 | 36.61 | 51.01 | O
264 | 14.42 | 7.08 | 10.7 | 67.88 | 44.72 | 54.82
265 | 14.69 | 8.92 | 12.56 | 66.42 | 49.42 | 59.38 | D
266 | 11.42 | 0.06 | 0.81 | 57.41 | 36.9 | 39.27 | A
267 | 13.31 | 0.05 | 8.61 | 61.76 | 37.22 | 51.06 | T
268 | 12 | 0.05 | 8.51 | 57.5 | 37.01 | 50.17 | A
269 | 11.99 | 6.74 | 10.42 | 57.72 | 44.05 | 53.06
270 | 14.67 | 6.69 | 10.86 | 66.06 | 43.89 | 54
271 | 12.28 | 0.05 | 2.4 | 57.29 | 36.77 | 40.86
272 | 12.78 | 0.05 | 8.31 | 59.7 | 36.16 | 49.71
273 | 12.53 | 0.05 | 8.77 | 59.43 | 36.6 | 50.6
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 3 |  |  | 244 | 245 | 246 | 247 | 248 | 249 | 250 | 251 | 252 | 253 | 254 | 255 | 256 | 257 | 258 | 259 | 260 | 261 | 262 | 263 | 264 | 265 | 266 | 267 | 268 | 269 | 270 | 271 | 272 | 273
244 | 12.99 | 8.58 | 11.1 | 67.37 | 51.19 | 59.27
245 | 13.49 | 8.24 | 11.31 | 70.4 | 49.22 | 60.35 |  |  | FLOW
246 | 13.15 | 8.65 | 11.55 | 67.4 | 50.33 | 61.13 | I |  | MAX | 12.99 | 13.49 | 13.15 | 10.91 | 14.03 | 14.35 | 14.22 | 13.52 | 11.48 | 12.87 | 13.15 | 13.87 | 14.11 | 12.34 | 13.34 | 15.67 | 12.86 | 13.03 | 12 | 14.04 | 13.26 | 13.05 | 12.7 | 9.99 | 11.37 | 11.22 | 12.97 | 12.07 | 12.2 | 11.8
247 | 10.91 | 0 | 0.65 | 59.59 | 38.61 | 40.96 | N |  | MIN | 8.58 | 8.24 | 8.65 | 0 | 0 | 5.15 | 8.91 | 7.57 | 0 | 0 | 0 | 6.9 | 7.51 | 0 | 0 | 2.56 | 7.56 | 7.46 | 0 | 0 | 6.85 | 8.43 | 7.84 | 0 | 0 | 0 | 6.63 | 7.18 | 0 | 0
248 | 14.03 | 0 | 9.01 | 71 | 38.28 | 56.23 | J |  | TOT | 11.1 | 11.31 | 11.55 | 0.65 | 9.01 | 12 | 11.84 | 11.5 | 0.64 | 8.98 | 11.28 | 10.8 | 11.38 | 1.33 | 8.05 | 10.49 | 10.48 | 10.42 | 2.47 | 7.66 | 10.01 | 11.33 | 10.97 | 0.58 | 7.7 | 8.02 | 9.99 | 9.98 | 2.31 | 7.8
249 | 14.35 | 5.15 | 12 | 73.3 | 44.69 | 62.96 | E | INJECTION WELL THREE
250 | 14.22 | 8.91 | 11.84 | 73.5 | 53.05 | 62.83 | C |  | PSI
251 | 13.52 | 7.57 | 11.5 | 68.57 | 48.69 | 60.99 | T |  | MAX | 67.37 | 70.4 | 67.4 | 59.59 | 71 | 73.3 | 73.5 | 68.57 | 61.34 | 65.96 | 66.27 | 70.9 | 71.8 | 63.39 | 67.3 | 79.5 | 66.17 | 66.44 | 61.72 | 70.8 | 69.01 | 67.58 | 64.74 | 58.16 | 58.74 | 58.91 | 67.23 | 63.13 | 62.76 | 60.61
252 | 11.48 | 0 | 0.64 | 61.34 | 38.5 | 40.67 | I |  | MIN | 51.19 | 49.22 | 50.33 | 38.61 | 38.28 | 44.69 | 53.05 | 48.69 | 38.5 | 37.69 | 38.87 | 46.18 | 47.71 | 37.67 | 37.76 | 42.96 | 47.13 | 46.94 | 38.34 | 37.41 | 45.57 | 50.47 | 49.33 | 38.03 | 37.54 | 37.32 | 44.87 | 46.41 | 37.71 | 37.36
253 | 12.87 | 0 | 8.98 | 65.96 | 37.69 | 54.86 | O |  | AVG | 59.27 | 60.35 | 61.13 | 40.96 | 56.23 | 62.96 | 62.83 | 60.99 | 40.67 | 54.86 | 59.57 | 58.7 | 60.3 | 41.33 | 52.16 | 56.84 | 56.82 | 56.71 | 43.25 | 51.34 | 55.94 | 60.54 | 58.89 | 39.94 | 50.69 | 51.17 | 55.13 | 55 | 42.51 | 50.95
254 | 13.15 | 0 | 11.28 | 66.27 | 38.87 | 59.57 | N
255 | 13.87 | 6.9 | 10.8 | 70.9 | 46.18 | 58.7
256 | 14.11 | 7.51 | 11.38 | 71.8 | 47.71 | 60.3 | W
257 | 12.34 | 0 | 1.33 | 63.39 | 37.67 | 41.33 | E
258 | 13.34 | 0 | 8.05 | 67.3 | 37.76 | 52.16 | L
259 | 15.67 | 2.56 | 10.49 | 79.5 | 42.96 | 56.84 | L
260 | 12.86 | 7.56 | 10.48 | 66.17 | 47.13 | 56.82
261 | 13.03 | 7.46 | 10.42 | 66.44 | 46.94 | 56.71 | T
262 | 12 | 0 | 2.47 | 61.72 | 38.34 | 43.25 | H
263 | 14.04 | 0 | 7.66 | 70.8 | 37.41 | 51.34 | R
264 | 13.26 | 6.85 | 10.01 | 69.01 | 45.57 | 55.94 | E
265 | 13.05 | 8.43 | 11.33 | 67.58 | 50.47 | 60.54 | E
266 | 12.7 | 7.84 | 10.97 | 64.74 | 49.33 | 58.89
267 | 9.99 | 0 | 0.58 | 58.16 | 38.03 | 39.94 | D
268 | 11.37 | 0 | 7.7 | 58.74 | 37.54 | 50.69 | A
269 | 11.22 | 0 | 8.02 | 58.91 | 37.32 | 51.17 | T
270 | 12.97 | 6.63 | 9.99 | 67.23 | 44.87 | 55.13 | A
271 | 12.07 | 7.18 | 9.98 | 63.13 | 46.41 | 55
272 | 12.2 | 0 | 2.31 | 62.76 | 37.71 | 42.51
273 | 11.8 | 0 | 7.8 | 60.61 | 37.36 | 50.95
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 4 |  |  | 244 | 245 | 246 | 247 | 248 | 249 | 250 | 251 | 252 | 253 | 254 | 255 | 256 | 257 | 258 | 259 | 260 | 261 | 262 | 263 | 264 | 265 | 266 | 267 | 268 | 269 | 270 | 271 | 272 | 273
244 | 13.32 | 0.05 | 9.38 | 67.86 | 39 | 56
245 | 13.77 | 0.05 | 9.48 | 70.9 | 37.51 | 57.29 |  |  | FLOW
246 | 13.42 | 8.8 | 11.87 | 67.87 | 50.96 | 61.66 | I |  | MAX | 13.32 | 13.77 | 13.42 | 14.74 | 13.99 | 15.01 | 14.45 | 13.59 | 14.21 | 12.84 | 11.32 | 14.26 | 14.47 | 13.29 | 13.92 | 15.82 | 13.01 | 13.12 | 12.13 | 13.62 | 13.85 | 13.25 | 12.8 | 13.51 | 11.89 | 11.64 | 13.22 | 12.15 | 12.25 | 11.63
247 | 14.74 | 8.43 | 12.24 | 71.7 | 49.42 | 62.66 | N |  | MIN | 0.05 | 0.05 | 8.8 | 8.43 | 0.05 | 0.05 | 6.41 | 7.67 | 8.08 | 0.05 | 0.05 | 0.05 | 7.68 | 1.86 | 0.05 | 0.05 | 0.05 | 7.54 | 7.69 | 0.05 | 7 | 0.06 | 7.95 | 7.79 | 0.05 | 0.05 | 0.05 | 7.26 | 7.04 | 0.05
248 | 13.99 | 0.05 | 2.91 | 69.51 | 38.69 | 45.07 | J |  | TOT | 9.38 | 9.48 | 11.87 | 12.24 | 2.91 | 10.78 | 12.02 | 11.59 | 11.62 | 1.59 | 0.9 | 10.52 | 11.6 | 11.06 | 2.79 | 8.07 | 8.72 | 10.57 | 10.86 | 8.28 | 10.36 | 11.32 | 11.08 | 10.78 | 2.48 | 7.93 | 8.32 | 10.14 | 10.27 | 2.24
249 | 15.01 | 0.05 | 10.78 | 73.6 | 37.74 | 60.17 | E | INJECTION WELL FOUR
250 | 14.45 | 6.41 | 12.02 | 74 | 48.5 | 63.32 | C |  | PSI
251 | 13.59 | 7.67 | 11.59 | 69.11 | 49.36 | 61.59 | T |  | MAX | 67.86 | 70.9 | 67.87 | 71.7 | 69.51 | 73.6 | 74 | 69.11 | 70.7 | 66.53 | 59.32 | 71.4 | 72.2 | 67.95 | 68.78 | 80 | 66.85 | 67.07 | 62.25 | 66.87 | 69.49 | 68.14 | 65.35 | 66.49 | 60.35 | 59.49 | 67.75 | 63.7 | 63.35 | 59.82
252 | 14.21 | 8.08 | 11.62 | 70.7 | 49.35 | 60.74 | I |  | MIN | 39 | 37.51 | 50.96 | 49.42 | 38.69 | 37.74 | 48.5 | 49.36 | 49.35 | 37.88 | 38.33 | 38.28 | 48.35 | 39.59 | 38.28 | 37.09 | 37.2 | 47.59 | 47.65 | 38.13 | 46.23 | 37.84 | 49.97 | 47.65 | 37.94 | 37.35 | 37.14 | 47.1 | 46.65 | 37.94
253 | 12.84 | 0.05 | 1.59 | 66.53 | 37.88 | 41.72 | O |  | AVG | 56 | 57.29 | 61.66 | 62.66 | 45.07 | 60.17 | 63.32 | 61.59 | 60.74 | 41.72 | 40.66 | 58.33 | 60.8 | 58.36 | 43.65 | 52.54 | 54.12 | 57.3 | 57.46 | 52.78 | 56.5 | 60.7 | 59.48 | 57.21 | 42.66 | 51.12 | 52.77 | 55.62 | 55.44 | 42.09
254 | 11.32 | 0.05 | 0.9 | 59.32 | 38.33 | 40.66 | N
255 | 14.26 | 0.05 | 10.52 | 71.4 | 38.28 | 58.33
256 | 14.47 | 7.68 | 11.6 | 72.2 | 48.35 | 60.8 | W
257 | 13.29 | 1.86 | 11.06 | 66.42 | 39.59 | 58.36 | E
258 | 13.92 | 0.05 | 2.79 | 68.78 | 38.28 | 43.65 | L
259 | 15.82 | 0.05 | 8.07 | 80 | 37.09 | 52.54 | L
260 | 13.01 | 0.05 | 8.72 | 66.85 | 37.2 | 54.12
261 | 13.12 | 7.54 | 10.57 | 67.07 | 47.59 | 57.3 | F
262 | 12.13 | 7.69 | 10.86 | 62.25 | 47.65 | 57.46 | O
263 | 13.62 | 0.05 | 8.28 | 66.87 | 38.13 | 52.78 | U
264 | 13.85 | 7 | 10.36 | 69.49 | 46.23 | 56.5 | R
265 | 13.25 | 0.06 | 11.32 | 68.14 | 37.84 | 60.7
266 | 12.8 | 7.95 | 11.08 | 65.35 | 49.97 | 59.48 | D
267 | 13.51 | 7.79 | 10.78 | 66.49 | 47.65 | 57.21 | A
268 | 11.89 | 0.05 | 2.48 | 60.35 | 37.94 | 42.66 | T
269 | 11.64 | 0.05 | 7.93 | 59.49 | 37.35 | 51.12 | A
270 | 13.22 | 0.05 | 8.32 | 67.75 | 37.14 | 52.77
271 | 12.15 | 7.26 | 10.14 | 63.7 | 47.1 | 55.62
272 | 12.25 | 7.04 | 10.27 | 63.35 | 46.65 | 55.44
273 | 11.63 | 0.05 | 2.24 | 59.82 | 37.94 | 42.09
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 5 |  |  | 244 | 245 | 246 | 247 | 248 | 249 | 250 | 251 | 252 | 253 | 254 | 255 | 256 | 257 | 258 | 259 | 260 | 261 | 262 | 263 | 264 | 265 | 266 | 267 | 268 | 269 | 270 | 271 | 272 | 273
244 | 12.46 | 0 | 5.61 | 66.92 | 37.61 | 49.52
245 | 12.99 | 0 | 8.49 | 69.91 | 36.37 | 55.55 |  |  | FLOW
246 | 12.53 | 0 | 9.04 | 66.97 | 37.8 | 56.77 | I |  | MAX | 12.46 | 12.99 | 12.53 | 13.62 | 13.6 | 10.38 | 13.63 | 12.83 | 13.34 | 13.51 | 12.76 | 13.34 | 13.52 | 12.5 | 13.05 | 14.87 | 12.29 | 12.4 | 11.41 | 13.64 | 10.44 | 12.54 | ER | 12.67 | 11.13 | 10.87 | 12.48 | 11.5 | 11.57 | 11.52
247 | 13.62 | 7.87 | 11.43 | 70.8 | 48.47 | 61.65 | N |  | MIN | 0 | 0 | 0 | 7.87 | 8.3 | 0 | 0 | 5.9 | 7.66 | 7.94 | 7.62 | 6.72 | 5.96 | 2.27 | 7.91 | 0 | 0 | 0 | 7.35 | 7.82 | 0 | 0 | 5.6 | 7.38 | 7.57 | 0 | 0 | 0 | 6.72 | 7.13
248 | 13.6 | 8.3 | 11.42 | 70.4 | 49.63 | 60.97 | J |  | TOT | 5.61 | 8.49 | 9.04 | 11.43 | 11.42 | 0.6 | 10.07 | 10.93 | 10.95 | 10.87 | 11.17 | 10.42 | 10.88 | 10.46 | 10.33 | 1.9 | 7.8 | 8.22 | 10.24 | 9.86 | 4.79 | 9.21 | 11.61 | 10.15 | 9.8 | 2.24 | 7.49 | 7.89 | 9.67 | 9.79
249 | 10.38 | 0 | 0.6 | 56.96 | 36.8 | 39.57 | E | INJECTION WELL FIVE
250 | 13.63 | 0 | 10.07 | 72.9 | 37.42 | 59.78 | C |  | PSI
251 | 12.83 | 5.9 | 10.93 | 68.18 | 48.2 | 60.42 | T |  | MAX | 66.92 | 69.91 | 66.97 | 70.8 | 70.4 | 56.96 | 72.9 | 68.18 | 69.63 | 67.87 | 65.5 | 70.4 | 71.3 | 65.35 | 67.74 | 78.6 | 65.72 | 65.95 | 61.32 | 70.2 | 59.91 | 67.05 | 64.3 | 65.43 | 59.31 | 57.03 | 66.79 | 62.69 | 62.42 | 60.08
252 | 13.34 | 7.66 | 10.95 | 69.63 | 48.33 | 59.61 | I |  | MIN | 37.61 | 36.37 | 37.8 | 48.47 | 49.63 | 36.8 | 37.42 | 48.2 | 48.33 | 49.05 | 48.12 | 45.9 | 47.44 | 39.97 | 48.9 | 36.24 | 35.95 | 37.17 | 46.71 | 48.77 | 37.6 | 36.73 | 48.4 | 46.61 | 46.75 | 36.87 | 35.86 | 36.94 | 45.69 | 46.38
253 | 13.51 | 7.94 | 10.87 | 67.87 | 49.05 | 58.4 | O |  | AVG | 49.52 | 55.55 | 56.77 | 61.65 | 60.97 | 39.57 | 59.78 | 60.42 | 59.61 | 58.4 | 59.35 | 58.3 | 59.76 | 57.29 | 56.27 | 41.4 | 52.39 | 53.23 | 56.43 | 55.34 | 45.73 | 56.84 | 58.37 | 56.11 | 54.04 | 41.15 | 51.16 | 51.78 | 54.35 | 54.04
254 | 12.76 | 7.62 | 11.17 | 65.5 | 48.12 | 59.35 | N
255 | 13.34 | 6.72 | 10.42 | 70.4 | 45.9 | 58.3
256 | 13.52 | 5.96 | 10.88 | 71.3 | 47.44 | 59.76 | W
257 | 12.5 | 2.27 | 10.46 | 65.35 | 39.97 | 57.29 | E
258 | 13.05 | 7.91 | 10.33 | 67.74 | 48.9 | 56.27 | L
259 | 14.87 | 0 | 1.9 | 78.6 | 36.24 | 41.4 | L
260 | 12.29 | 0 | 7.8 | 65.72 | 35.95 | 52.39
261 | 12.4 | 0 | 8.22 | 65.95 | 37.17 | 53.23 | F
262 | 11.41 | 7.35 | 10.24 | 61.32 | 46.71 | 56.43 | I
263 | 13.64 | 7.82 | 9.86 | 70.2 | 48.77 | 55.34 | V
264 | 10.44 | 0 | 4.79 | 59.91 | 37.6 | 45.73 | E
265 | 12.54 | 0 | 9.21 | 67.05 | 36.73 | 56.84
266 | ER | 5.6 | 11.61 | 64.3 | 48.4 | 58.37 | D
267 | 12.67 | 7.38 | 10.15 | 65.43 | 46.61 | 56.11 | A
268 | 11.13 | 7.57 | 9.8 | 59.31 | 46.75 | 54.04 | T
269 | 10.87 | 0 | 2.24 | 57.03 | 36.87 | 41.15 | A
270 | 12.48 | 0 | 7.49 | 66.79 | 35.86 | 51.16
271 | 11.5 | 0 | 7.89 | 62.69 | 36.94 | 51.78
272 | 11.57 | 6.72 | 9.67 | 62.42 | 45.69 | 54.35
273 | 11.52 | 7.13 | 9.79 | 60.08 | 46.38 | 54.04

## RMW PRN DATA
julian | u-avg | u-min | u-max | l-avg | l-min | l-max
244 | 23.27 | 23.21 | 23.33 | 45.15 | 45.08 | 45.23 | R |  |  | 244 | 245 | 246 | 247 | 248 | 249 | 250 | 251 | 252 | 253 | 254 | 255 | 256 | 257 | 258 | 259 | 260 | 261 | 262 | 263 | 264 | 265 | 266 | 267 | 268 | 269 | 270 | 271 | 272 | 273
245 | 23.27 | 23.23 | 23.31 | 45.16 | 45.08 | 45.22 | E
246 | 23.29 | 23.24 | 23.33 | 45.17 | 45.11 | 45.22 | G |  | LOW
247 | 23.3 | 23.25 | 23.35 | 45.14 | 45.08 | 45.22 | I |  | MIN | 23.21 | 23.23 | 23.24 | 23.25 | 21.18 | 20.73 | 20.42 | 20.34 | 22.58 | 22.56 | 22.51 | 22.53 | 22.53 | 22.48 | 22.45 | 22.46 | 22.48 | 22.5 | 22.5 | 0.25 | 22.53 | 22.51 | 22.47 | 22.45 | 22.46 | 22.54 | 22.58 | 22.55 | 22.57 | 22.58
248 | 22.22 | 21.18 | 23.31 | 43.51 | 42.41 | 45.13 | O |  | MAX | 23.33 | 23.31 | 23.33 | 23.35 | 23.31 | 22.39 | 22.58 | 22.63 | 22.72 | 22.71 | 22.67 | 22.7 | 22.7 | 22.63 | 22.58 | 22.56 | 22.55 | 22.55 | 22.6 | 22.72 | 22.64 | 22.62 | 22.59 | 22.59 | 22.62 | 22.69 | 22.7 | 22.67 | 22.71 | 22.68
249 | 21.93 | 20.73 | 22.39 | 43.85 | 42.36 | 44.7 | N |  | AVG | 23.27 | 23.27 | 23.29 | 23.3 | 22.22 | 21.93 | 22.49 | 22.52 | 22.64 | 22.63 | 22.61 | 22.61 | 22.63 | 22.58 | 22.52 | 22.51 | 22.52 | 22.52 | 22.54 | 22.62 | 22.58 | 22.56 | 22.55 | 22.52 | 22.55 | 22.62 | 22.65 | 22.63 | 22.64 | 22.63
250 | 22.49 | 20.42 | 22.58 | 44.79 | 32.81 | 44.92 | A | RMW
251 | 22.52 | 20.34 | 22.63 | 44.75 | 26.6 | 45 | L |  | UP
252 | 22.64 | 22.58 | 22.72 | 45.05 | 44.99 | 45.11 |  |  | MIN | 45.08 | 45.08 | 45.11 | 45.08 | 42.41 | 42.36 | 32.81 | 26.6 | 44.99 | 45.04 | 45.04 | 45.04 | 45.04 | 44.95 | 44.84 | 44.78 | 44.78 | 44.76 | 44.74 | 0.25 | 44.81 | 44.8 | 44.76 | 44.77 | 44.83 | 44.93 | 45.01 | 44.94 | 44.92 | 44.9
253 | 22.63 | 22.56 | 22.71 | 45.08 | 45.04 | 45.13 | M |  | MAX | 45.23 | 45.22 | 45.22 | 45.22 | 45.13 | 44.7 | 44.92 | 45 | 45.11 | 45.13 | 45.14 | 45.16 | 45.15 | 45.1 | 45.01 | 44.92 | 44.9 | 44.88 | 44.87 | 44.97 | 44.92 | 44.87 | 44.85 | 44.86 | 44.95 | 45.05 | 45.1 | 45.09 | 45.05 | 45.04
254 | 22.61 | 22.51 | 22.67 | 45.1 | 45.04 | 45.14 | O |  | AVG | 45.15 | 45.16 | 45.17 | 45.14 | 43.51 | 43.85 | 44.79 | 44.75 | 45.05 | 45.08 | 45.1 | 45.1 | 45.11 | 45.02 | 44.92 | 44.85 | 44.84 | 44.82 | 44.81 | 44.87 | 44.86 | 44.83 | 44.8 | 44.81 | 44.89 | 45 | 45.06 | 45.01 | 44.99 | 44.98
255 | 22.61 | 22.53 | 22.7 | 45.1 | 45.04 | 45.16 | N
256 | 22.63 | 22.53 | 22.7 | 45.11 | 45.04 | 45.15 | I
257 | 22.58 | 22.48 | 22.63 | 45.02 | 44.95 | 45.1 | T
258 | 22.52 | 22.45 | 22.58 | 44.92 | 44.84 | 45.01 | O
259 | 22.51 | 22.46 | 22.56 | 44.85 | 44.78 | 44.92 | R
260 | 22.52 | 22.48 | 22.55 | 44.84 | 44.78 | 44.9
261 | 22.52 | 22.5 | 22.55 | 44.82 | 44.76 | 44.88 | W
262 | 22.54 | 22.5 | 22.6 | 44.81 | 44.74 | 44.87 | E
263 | 22.62 | 0.25 | 22.72 | 44.87 | 0.25 | 44.97 | L
264 | 22.58 | 22.53 | 22.64 | 44.86 | 44.81 | 44.92 | L
265 | 22.56 | 22.51 | 22.62 | 44.83 | 44.8 | 44.87
266 | 22.55 | 22.47 | 22.59 | 44.8 | 44.76 | 44.85
267 | 22.52 | 22.45 | 22.59 | 44.81 | 44.77 | 44.86 | R
268 | 22.55 | 22.46 | 22.62 | 44.89 | 44.83 | 44.95 | M
269 | 22.62 | 22.54 | 22.69 | 45 | 44.93 | 45.05 | W
270 | 22.65 | 22.58 | 22.7 | 45.06 | 45.01 | 45.1
271 | 22.63 | 22.55 | 22.67 | 45.01 | 44.94 | 45.09 | O
272 | 22.64 | 22.57 | 22.71 | 44.99 | 44.92 | 45.05 | N
273 | 22.63 | 22.58 | 22.68 | 44.98 | 44.9 | 45.04 | E
244 | 43.83 | 42.62 | 46.54 | 49.05 | 48.97 | 49.25 | M |  |  | 244 | 245 | 246 | 247 | 248 | 249 | 250 | 251 | 252 | 253 | 254 | 255 | 256 | 257 | 258 | 259 | 260 | 261 | 262 | 263 | 264 | 265 | 266 | 267 | 268 | 269 | 270 | 271 | 272 | 273
245 | 44.29 | 42.65 | 47.06 | 49.11 | 49.01 | 49.27 | O
246 | 44.15 | 42.96 | 47.05 | 49.2 | 49.06 | 49.34 | N |  | LOW
247 | 44.17 | 43 | 46.37 | 49.22 | 49.12 | 49.37 | I |  | MIN | 42.62 | 42.65 | 42.96 | 43 | 41.85 | 41.42 | 42.49 | 43.09 | 43.14 | 41.97 | 42.48 | 43.06 | 42.27 | 42.62 | 42.93 | 43.48 | 43.8 | 44.02 | 42.55 | 41.4 | 42.17 | 41.23 | 40.1 | 41.84 | 41.95 | 42.45 | 41.31 | 40.83 | 41.8 | 42.44
248 | 43.6 | 41.85 | 44.48 | 46.92 | 45.44 | 49.29 | T |  | MAX | 46.54 | 47.06 | 47.05 | 46.37 | 44.48 | 44.33 | 46.79 | 46.92 | 47.39 | 46.83 | 47.07 | 46.81 | 46.82 | 46.8 | 46.85 | 46.74 | 46.93 | 47.05 | 46.28 | 43.4 | 45.76 | 45.12 | 43.51 | 45.2 | 45.74 | 45.97 | 45.03 | 44.46 | 45.35 | 45.87
249 | 42.58 | 41.42 | 44.33 | 48.42 | 45.78 | 49.62 | O |  | AVG | 43.83 | 44.29 | 44.15 | 44.17 | 43.6 | 42.58 | 44.12 | 44.58 | 44.9 | 44.49 | 44.64 | 44.35 | 44.26 | 44.29 | 44.55 | 44.8 | 45.03 | 45.12 | 44.25 | 42.6 | 43.94 | 43.22 | 42 | 43.13 | 43.58 | 43.98 | 43.13 | 42.23 | 43.22 | 43.77
250 | 44.12 | 42.49 | 46.79 | 49.42 | 49.25 | 49.49 | R | MW-1
251 | 44.58 | 43.09 | 46.92 | 49.45 | 49.27 | 49.54 |  |  | UP
252 | 44.9 | 43.14 | 47.39 | 49.44 | 49.29 | 49.55 | W |  | MIN | 48.97 | 49.01 | 49.06 | 49.12 | 45.44 | 45.78 | 49.25 | 49.27 | 49.29 | 49.22 | 49.13 | 47.16 | 47.67 | 49.06 | 49.01 | 49.03 | 49.02 | 49.03 | 46.76 | 47.05 | 49.07 | 47.74 | 47.78 | 48.92 | 48.96 | 49.03 | 46.71 | 47.1 | 49.06 | 49.08
253 | 44.49 | 41.97 | 46.83 | 49.4 | 49.22 | 49.49 | E |  | MAX | 49.25 | 49.27 | 49.34 | 49.37 | 49.29 | 49.62 | 49.49 | 49.54 | 49.55 | 49.49 | 49.42 | 49.37 | 49.45 | 49.42 | 49.39 | 49.4 | 49.38 | 49.38 | 49.35 | 49.56 | 49.36 | 49.33 | 49.13 | 49.18 | 49.23 | 49.3 | 49.3 | 49.46 | 49.35 | 49.34
254 | 44.64 | 42.48 | 47.07 | 49.35 | 49.13 | 49.42 | L |  | AVG | 49.05 | 49.11 | 49.2 | 49.22 | 46.92 | 48.42 | 49.42 | 49.45 | 49.44 | 49.4 | 49.35 | 48.08 | 48.82 | 49.25 | 49.21 | 49.21 | 49.21 | 49.2 | 48.04 | 48.67 | 49.23 | 48.52 | 48.71 | 49.02 | 49.03 | 49.15 | 47.64 | 48.54 | 49.19 | 49.21
255 | 44.35 | 43.06 | 46.81 | 48.08 | 47.16 | 49.37 | L
256 | 44.26 | 42.27 | 46.82 | 48.82 | 47.67 | 49.45
257 | 44.29 | 42.62 | 46.8 | 49.25 | 49.06 | 49.42 | O
258 | 44.55 | 42.93 | 46.85 | 49.21 | 49.01 | 49.39 | N
259 | 44.8 | 43.48 | 46.74 | 49.21 | 49.03 | 49.4 | E
260 | 45.03 | 43.8 | 46.93 | 49.21 | 49.02 | 49.38
261 | 45.12 | 44.02 | 47.05 | 49.2 | 49.03 | 49.38 | I
262 | 44.25 | 42.55 | 46.28 | 48.04 | 46.76 | 49.35 | N
263 | 42.6 | 41.4 | 43.4 | 48.67 | 47.05 | 49.56 | J
264 | 43.94 | 42.17 | 45.76 | 49.23 | 49.07 | 49.36 | E
265 | 43.22 | 41.23 | 45.12 | 48.52 | 47.74 | 49.33 | C
266 | 42 | 40.1 | 43.51 | 48.71 | 47.78 | 49.13 | T
267 | 43.13 | 41.84 | 45.2 | 49.02 | 48.92 | 49.18 | I
268 | 43.58 | 41.95 | 45.74 | 49.03 | 48.96 | 49.23 | O
269 | 43.98 | 42.45 | 45.97 | 49.15 | 49.03 | 49.3 | N
270 | 43.13 | 41.31 | 45.03 | 47.64 | 46.71 | 49.3
271 | 42.23 | 40.83 | 44.46 | 48.54 | 47.1 | 49.46 | W
272 | 43.22 | 41.8 | 45.35 | 49.19 | 49.06 | 49.35 | E
273 | 43.77 | 42.44 | 45.87 | 49.21 | 49.08 | 49.34 | L
L
244 | 43.37 | 43.23 | 43.4 | 33.74 | 33.19 | 34.86 | M |  |  | 244 | 245 | 246 | 247 | 248 | 249 | 250 | 251 | 252 | 253 | 254 | 255 | 256 | 257 | 258 | 259 | 260 | 261 | 262 | 263 | 264 | 265 | 266 | 267 | 268 | 269 | 270 | 271 | 272 | 273
245 | 43.41 | 43.3 | 43.46 | 33.97 | 33.27 | 35.2 | O
246 | 43.48 | 43.38 | 43.56 | 33.87 | 33.21 | 34.69 | N |  | LOW
247 | 43.5 | 43.48 | 43.59 | 33.86 | 33.36 | 34.51 | I |  | MIN | 43.23 | 43.3 | 43.38 | 43.48 | 38.47 | 37.27 | 43.19 | 43.35 | 43.46 | 43.47 | 43.44 | 39.73 | 39.68 | 43.14 | 43.19 | 43.22 | 43.27 | 43.3 | 38.21 | 38.12 | 43.06 | 36.17 | 36.08 | 42.89 | 43.02 | 43.16 | 36.47 | 35.98 | 42.99 | 43.17
248 | 40.26 | 38.47 | 43.58 | 31.08 | 28.81 | 33.91 | T |  | MAX | 43.4 | 43.46 | 43.56 | 43.59 | 43.58 | 43.21 | 43.41 | 43.54 | 43.62 | 43.62 | 43.62 | 43.57 | 43.25 | 43.38 | 43.39 | 43.42 | 43.45 | 43.45 | 43.45 | 43.14 | 43.24 | 43.26 | 42.95 | 43.07 | 43.21 | 43.36 | 43.39 | 43.01 | 43.25 | 43.31
249 | 41.62 | 37.27 | 43.21 | 31.81 | 28.59 | 33.75 | O |  | AVG | 43.37 | 43.41 | 43.48 | 43.5 | 40.26 | 41.62 | 43.35 | 43.46 | 43.5 | 43.51 | 43.51 | 41.04 | 41.95 | 43.3 | 43.34 | 43.37 | 43.42 | 43.44 | 40.9 | 41.44 | 43.07 | 39.46 | 40.97 | 42.99 | 43.04 | 43.36 | 38.53 | 41.08 | 43.04 | 43.26
250 | 43.35 | 43.19 | 43.41 | 33.69 | 32.84 | 34.85 | R | MW-2
251 | 43.46 | 43.35 | 43.54 | 34 | 33.15 | 34.95 |  |  | UP
252 | 43.5 | 43.46 | 43.62 | 34.24 | 33.23 | 35.43 | W |  | MIN | 33.19 | 33.27 | 33.21 | 33.36 | 28.81 | 28.59 | 32.84 | 33.15 | 33.23 | 32.8 | 32.98 | 29.5 | 29.1 | 32.78 | 32.98 | 33.22 | 33.39 | 33.57 | 28.95 | 28.41 | 32.98 | 19.72 | 18.96 | 24.19 | 23.95 | 24.07 | 19.47 | 19.63 | 24.07 | 24.26
253 | 43.51 | 43.47 | 43.62 | 33.97 | 32.8 | 34.83 | E |  | MAX | 34.86 | 35.2 | 34.69 | 34.51 | 33.91 | 33.75 | 34.85 | 34.95 | 35.43 | 34.83 | 34.88 | 33.53 | 34.74 | 34.59 | 34.64 | 34.73 | 34.62 | 34.73 | 34.63 | 33.57 | 34.64 | 34.4 | 25.03 | 25.42 | 25.48 | 25.75 | 24.55 | 25.13 | 25.51 | 25.4
254 | 43.51 | 43.44 | 43.62 | 33.83 | 32.98 | 34.88 | L |  | AVG | 33.74 | 33.97 | 33.87 | 33.86 | 31.08 | 31.81 | 33.69 | 34 | 34.24 | 33.97 | 33.83 | 31.47 | 32.38 | 33.59 | 33.71 | 33.87 | 34.01 | 34.12 | 31.83 | 31.84 | 33.73 | 26.95 | 23.18 | 24.69 | 24.66 | 24.8 | 21.54 | 23.12 | 24.68 | 24.77
255 | 41.04 | 39.73 | 43.57 | 31.47 | 29.5 | 33.53 | L
256 | 41.95 | 39.68 | 43.25 | 32.38 | 29.1 | 34.74
257 | 43.3 | 43.14 | 43.38 | 33.59 | 32.78 | 34.59 | T
258 | 43.34 | 43.19 | 43.39 | 33.71 | 32.98 | 34.64 | W
259 | 43.37 | 43.22 | 43.42 | 33.87 | 33.22 | 34.73 | O
260 | 43.42 | 43.27 | 43.45 | 34.01 | 33.39 | 34.62
261 | 43.44 | 43.3 | 43.45 | 34.12 | 33.57 | 34.73 | I
262 | 40.9 | 38.21 | 43.45 | 31.83 | 28.95 | 34.63 | N
263 | 41.44 | 38.12 | 43.14 | 31.84 | 28.41 | 33.57 | J
264 | 43.07 | 43.06 | 43.24 | 33.73 | 32.98 | 34.64 | E
265 | 39.46 | 36.17 | 43.26 | 26.95 | 19.72 | 34.4 | C
266 | 40.97 | 36.08 | 42.95 | 23.18 | 18.96 | 25.03 | T
267 | 42.99 | 42.89 | 43.07 | 24.69 | 24.19 | 25.42 | I
268 | 43.04 | 43.02 | 43.21 | 24.66 | 23.95 | 25.48 | O
269 | 43.36 | 43.16 | 43.36 | 24.8 | 24.07 | 25.75 | N
270 | 38.53 | 36.47 | 43.39 | 21.54 | 19.47 | 24.55
271 | 41.08 | 35.98 | 43.01 | 23.12 | 19.63 | 25.13 | W
272 | 43.04 | 42.99 | 43.25 | 24.68 | 24.07 | 25.51 | E
273 | 43.26 | 43.17 | 43.31 | 24.77 | 24.26 | 25.4 | L
L
244 | 46.02 | 45.99 | 46.14 | 33.82 | 33.7 | 33.91 | M |  |  | 244 | 245 | 246 | 247 | 248 | 249 | 250 | 251 | 252 | 253 | 254 | 255 | 256 | 257 | 258 | 259 | 260 | 261 | 262 | 263 | 264 | 265 | 266 | 267 | 268 | 269 | 270 | 271 | 272 | 273
245 | 46.06 | 46.06 | 46.2 | 33.89 | 33.77 | 34.02 | O
246 | 46.23 | 46.13 | 46.3 | 33.97 | 33.86 | 34.13 | N |  | LOW
247 | 46.34 | 46.25 | 46.33 | 34.02 | 33.99 | 34.21 | I |  | MIN | 45.99 | 46.06 | 46.13 | 46.25 | 39.72 | 39.69 | 45.91 | 46.09 | 46.2 | 46.17 | 46.19 | 40.77 | 40.74 | 45.85 | 45.91 | 45.95 | 46.02 | 46.07 | 38.95 | 38.92 | 45.76 | 37.63 | 37.57 | 45.62 | 45.75 | 45.9 | 37.4 | 37.41 | 45.71 | 45.9
248 | 41.89 | 39.72 | 46.33 | 27.89 | 24.64 | 34.16 | T |  | MAX | 46.14 | 46.2 | 46.3 | 46.33 | 46.33 | 45.91 | 46.12 | 46.27 | 46.37 | 46.38 | 46.38 | 46.32 | 45.94 | 46.08 | 46.11 | 46.14 | 46.18 | 46.19 | 46.18 | 45.82 | 45.93 | 45.96 | 45.66 | 45.81 | 45.95 | 46.11 | 46.12 | 45.72 | 45.98 | 46.04
249 | 44.03 | 39.69 | 45.91 | 31.16 | 24.47 | 34.28 | O |  | AVG | 46.02 | 46.06 | 46.23 | 46.34 | 41.89 | 44.03 | 45.97 | 46.17 | 46.37 | 46.36 | 46.38 | 42.62 | 44.25 | 45.95 | 46 | 46 | 46.06 | 46.08 | 42.45 | 43.57 | 45.89 | 41.44 | 43.31 | 45.76 | 45.88 | 45.99 | 40.04 | 43.27 | 45.88 | 45.99
250 | 45.97 | 45.91 | 46.12 | 34.38 | 34.17 | 34.49 | R | MW-3
251 | 46.17 | 46.09 | 46.27 | 34.47 | 34.32 | 34.62 |  |  | UP
252 | 46.37 | 46.2 | 46.37 | 34.55 | 34.4 | 34.7 | W |  | MIN | 33.7 | 33.77 | 33.86 | 33.99 | 24.64 | 24.47 | 34.17 | 34.32 | 34.4 | 34.35 | 34.29 | 20.13 | 20.05 | 33.76 | 33.89 | 33.97 | 34.04 | 34.06 | 25.69 | 25.48 | 34.29 | 23.63 | 23.42 | 33.95 | 34.08 | 34.22 | 21.07 | 21.06 | 33.79 | 34.02
253 | 46.36 | 46.17 | 46.38 | 34.49 | 34.35 | 34.63 | E |  | MAX | 33.91 | 34.02 | 34.13 | 34.21 | 34.16 | 34.28 | 34.49 | 34.62 | 34.7 | 34.63 | 34.61 | 34.52 | 33.89 | 34.13 | 34.21 | 34.29 | 34.33 | 34.36 | 34.33 | 34.48 | 34.63 | 34.65 | 34.09 | 34.27 | 34.39 | 34.48 | 34.45 | 33.84 | 34.15 | 34.21
254 | 46.38 | 46.19 | 46.38 | 34.46 | 34.29 | 34.61 | L |  | AVG | 33.82 | 33.89 | 33.97 | 34.02 | 27.89 | 31.16 | 34.38 | 34.47 | 34.55 | 34.49 | 34.46 | 24.65 | 29.32 | 33.91 | 34.02 | 34.11 | 34.2 | 34.26 | 29.85 | 31.5 | 34.44 | 28.68 | 31.02 | 34.07 | 34.29 | 34.38 | 25.09 | 30.19 | 33.97 | 34.04
255 | 42.62 | 40.77 | 46.32 | 24.65 | 20.13 | 34.52 | L
256 | 44.25 | 40.74 | 45.94 | 29.32 | 20.05 | 33.89
257 | 45.95 | 45.85 | 46.08 | 33.91 | 33.76 | 34.13 | T
258 | 46 | 45.91 | 46.11 | 34.02 | 33.89 | 34.21 | H
259 | 46 | 45.95 | 46.14 | 34.11 | 33.97 | 34.29 | R
260 | 46.06 | 46.02 | 46.18 | 34.2 | 34.04 | 34.33 | E
261 | 46.08 | 46.07 | 46.19 | 34.26 | 34.06 | 34.36 | E
262 | 42.45 | 38.95 | 46.18 | 29.85 | 25.69 | 34.33
263 | 43.57 | 38.92 | 45.82 | 31.5 | 25.48 | 34.48 | I
264 | 45.89 | 45.76 | 45.93 | 34.44 | 34.29 | 34.63 | N
265 | 41.44 | 37.63 | 45.96 | 28.68 | 23.63 | 34.65 | J
266 | 43.31 | 37.57 | 45.66 | 31.02 | 23.42 | 34.09 | E
267 | 45.76 | 45.62 | 45.81 | 34.07 | 33.95 | 34.27 | C
268 | 45.88 | 45.75 | 45.95 | 34.29 | 34.08 | 34.39 | T
269 | 45.99 | 45.9 | 46.11 | 34.38 | 34.22 | 34.48 | I
270 | 40.04 | 37.4 | 46.12 | 25.09 | 21.07 | 34.45 | O
271 | 43.27 | 37.41 | 45.72 | 30.19 | 21.06 | 33.84 | N
272 | 45.88 | 45.71 | 45.98 | 33.97 | 33.79 | 34.15
273 | 45.99 | 45.9 | 46.04 | 34.04 | 34.02 | 34.21 | W
E
L
L

## SHIFT DATA
PERSONNEL LIST
CHIEF OPERATORS
JUST, M. | CO# 2769-A |  |  |  |  | "A" | [5 empty] | "A"
McGEARY, J. | CO# 4545-A |  |  |  |  | "A" | [5 empty] | "A"
BAYLER, J. | CO# 4474-A |  |  |  |  | "A" | [5 empty] | "A"
SET SHIFT CODES THAN USE BUTTONS
HULL | CO# 5613-C | 21 | 1 | BAROFSKY | CO# 5096-C | "C" |  | 20 | 2D | HULL | CO# 5613-C | "C" |  | 1 | 10 | 21
BAROFSKY | CO# 5096-C | 25 | 4 | BENTLEY | CO# 9366-C | "C" |  | 21 | 1 | BAROFSKY | CO# 5096-C | "C" |  | 2 | 11 | 22
JVACANT | CO# XXXX-X | 26 | 5 | CURMODE | CO# 9379-A | "A" |  | 22 | 2 | JVACANT | CO# XXXX-X | N/A |  | 2D | 12 | 20
THOMAS | CO# 12833-B | 20 | 2D | HULL | CO# 5613-C | "C" |  | 23 | 3 | THOMAS | CO# 12833-B | "B" |  | 2XR | 13 | 24
VACANT OP2 | CO# XXXX-X | 22 | 2 | JVACANT | CO# XXXX-X | N/A |  | 24 | 2XR | VACANT OP2 | CO# XXXX-X | N/A |  | 3 | 14 | 23
BENTLEY | CO# 9366-C | 23 | 3 | THOMAS | CO# 12833-B | "B" |  | 25 | 4 | BENTLEY | CO# 9366-C | "C" |  | 4 | 15 | 25
CURMODE | CO# 9379-A | 24 | 2XR | VACANT OP2 | CO# XXXX-X | N/A |  | 26 | 5 | CURMODE | CO# 9379-A | "A" |  | 5 | 16 | 26
SET SHIFT CODES THAN USE BUTTONS
ROUSE | CO# XXXXX-X | 15 | 2R | ANDERSON | CO# XXXXX-X | N/A |  | 10 | 1D | ROUSE | CO# XXXXX-X | N/A |  | 1 | 1 | 11
KOKLAS | CO# 13506-C | 18 | 3 | DESHIELDS | CO# XXXXX-X | N/A |  | 11 | 1 | KOKLAS | CO# 13506-C | "C" |  | 1D | 2 | 10
VERBOSH | CO# 12667-C | 14 | 4A | HENDERSON | CO# 5087-B | "B" |  | 12 | 5 | VERBOSH | CO# 12667-C | "C" |  | 2R | 3 | 15
PEUGEOT | CO# 12817-C | 11 | 1 | KOKLAS | CO# 13506-C | "C" |  | 13 | 3D | PEUGEOT | CO# 12817-C | "C" |  | 3 | 4 | 18
HENDERSON | CO# 5087-B | 17 | 4 | NOBERT | CO# 9661-C | "C" |  | 14 | 4A | HENDERSON | CO# 5087-B | "B" |  | 3D | 5 | 13
ANDERSON | CO# XXXXX-X | 13 | 3D | PEUGEOT | CO# 12817-C | "C" |  | 15 | 2R | ANDERSON | CO# XXXXX-X | N/A |  | 4 | 6 | 17
SANDERS | CO# 13500-B | 10 | 1D | ROUSE | CO# XXXXX-X | N/A |  | 16 | 5A | SANDERS | CO# 13500-B | "B" |  | 4A | 7 | 14
NOBERT | CO# 9661-C | 16 | 5A | SANDERS | CO# 13500-B | "B" |  | 17 | 4 | NOBERT | CO# 9661-C | "C" |  | 5 | 8 | 12
DESHIELDS | CO# XXXXX-X | 12 | 5 | VERBOSH | CO# 12667-C | "C" |  | 18 | 3 | DESHIELDS | CO# XXXXX-X | N/A |  | 5A | 9 | 16
[12 empty] | 3 | J. TINKER | 3291-C
[12 empty] | 1 | G. SLAYTON | 2606-B
[12 empty] | 2 | H. WALKER | 4700-A
OPERATOR II' S
BAROFSKY, J. | CO# 5096-C | 1 | "C" | BAROFSKY, J. | 1 | CO# 5096-C |  |  | 1 | 10 | 21 | 5 | J. BENTLEY | X
JVACANT | CO# XXXX-X | 4 | "C" | BENTLEY, J. | 4 | CO# 9366-C |  |  | 2 | 11 | 22 | 1D | S. CURMODE | X
THOMAS, P. | CO# 12833 B | 5 | "A" | CURMODE, S. | 5 | CO# 9379-A |  |  | 2D | 12 | 20 | 4 | K. HENDERSON | 5087-B
BENTLEY, J. | CO# 9366-C | 2D | "C" | HULL, S. | 2D | CO# 5613-C |  |  | 2R | 13 | 24 | 3D | K. JONES | 2466-C
CURMODE, S. | CO# 9379-A | 2 | N/A | JVACANT | 2 | CO# XXXX-X |  |  | 3 | 14 | 23 | 3 | G. KLEYNHANS | 7367-C
HULL, S. | CO# 5613-C | 3 | "B" | THOMAS, P. | 3 | CO# 12833 B |  |  | 4 | 15 | 25 | 2 | A. MORROW | 9164-C
HULL, S. | #N/A | 2XR | N/A | ZVACANT | 2XR |  |  |  | 5 | 16 | 26 | 1 | J. RAINFORTH | 2718-C
OPERATOR I' S
PEUGEOT, P. | CO# 12817-C | 5A | N/A | DESHIELDS, D | 5A | CO# XXXXX-X | 5A | DESHIELDS, D | 1 | 1 | 11
PEUGEOT, P. | CO# 12817-C | 3 | N/A | FVACANT | 3 | CO# XXXXX-X | 3 | FVACANT | 1D | 2 | 10
ROUSE, Y | CO# XXXXX-X | 4 | "B" | HENDERSON, K. | 4 | CO# 5087-B | 4 | HENDERSON, K. | 2R | 3 | 15
NOBERT, B. | CO# 9661-C | 4A | "C" | KOKLAS, D. | 4A | CO# 13506-C | 4A | KOKLAS, D. | 3 | 4 | 18
FVACANT | CO# XXXXX-X | 2 | "C" | NOBERT, B. | 2 | CO# 9661-C | 2 | NOBERT, B. | 3D | 5 | 13
SANDERS, C. | CO# 13500-B | 1 | "C" | PEUGEOT, P. | 1 | CO# 12817-C | 1 | PEUGEOT, P. | 4 | 6 | 17
HENDERSON, K. | CO# 5087-B | 1D | "C" | ROUSE, Y | 1D | CO# XXXXX-X | 1D | ROUSE, Y | 4A | 7 | 14
1 | #N/A | 3D | "B" | SANDERS, C. | 3D | CO# 13500-B | 3D | SANDERS, C. | 5 | 8 | 12
KOKLAS, D. | CO# 13506-C | 5 | "C" | VERBOSH, R. | 5 | CO# 12667-C | 5 | VERBOSH, R. | 5A | 9 | 16
|  | 4 | 1 | BERNARDI, J | 4 | CO# XXXX-X
|  | 3 | 2 | FREIDLAND, M. | 3 | CO# 13437-C
|  | 5A | 3 | FUTURE, 5A | 5A | CO# XXXX-X
|  | 1 | 4 | HENDERSON, K. | 1 | CO# 5087-B
|  | 2 | 5 | KOKLAS, D. | 2 | CO# 13506-C
|  | 5 | 6 | NOBERT, B. | 5 | CO# 9661-C
|  | 4A | 7 | PEUGEOT, P. | 4A | CO# 12817-C
|  | 1D | 8 | SANDERS, C. | 1D | CO# 13500-C
|  | 3D | 9 | VERBOSH, R. | 3D | CO# 12667-C

## COVER PAGE
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
|  | SEPTEMBER |  | 2005
| OPERATOR | TITLE | CERTIFICATE # | TOTAL COST |  |  | 67351.6643
1 ST SHIFT |  |  |  | PEAK TO FLOW RATIO |  |  | 1.1563
2230-0630 | BAROFSKY | OP. II | CO# 5096-C
| KOKLAS | OP. I | CO# 13506-C |  | TOTAL SUSPENDED SOLIDS
| ROUSE | OP. I DEWAT | CO# XXXXX-X |  |  |  | LBS/DAY
|  |  |  | RAW INFLUENT |  |  | 27901.1344
2 ND SHIFT |  |  |  | FINAL EFFLUENT |  |  | 4852.8356
0630-1430 | McGEARY, J. | CHIEF | CO# 4545-A |  | TOTAL CBOD
| JVACANT | OP. II RELIEF | CO# XXXX-X |  |  |  | LBS/DAY
| HULL | OP. II DEWAT | CO# 5613-C | RAW INFLUENT |  |  | 21335.1131
| ANDERSON | OP. I RELIEF | CO# XXXXX-X | FINAL EFFLUENT |  |  | 1042.1034
CHEMICALS
3 RD SHIFT | BAYLER, J. | CHIEF | CO# 4474-A |  |  | COST | POUNDS
1430-2230 | THOMAS | OP. II | CO# 12833-B | HYDROGEN PEROXIDE |  | 592.0065 | 4041
| DESHIELDS | OP. I | CO# XXXXX-X | CHLORINE |  | 9186.3 | 31140
| PEUGEOT | OP. I | CO# 12817-C | POLYMER |  | 4690.5828 | 7689.48
SLUDGE REMOVED
4 TH SHIFT | [6 empty] | TONS
WEEKEND | BENTLEY | OP. II | CO# 9366-C | DRY TONS |  |  | 358.8402
2230-1030 | NOBERT | OP. I | CO# 9661-C |  | ENERGY
| HENDERSON | OPI | CO# 5087-B |  |  | COST | KILOWATTS
5 TH SHIFT |  |  |  | FPL CONSUMPTION |  | 52882.775 | 961505
WEEKEND | CURMODE | OP. II | CO# 9379-A
1030-2230 | VERBOSH | OP. I | CO# 12667-C | POPULATION EQUIVALENCE |  |  | 125500.6653
| SANDERS | OP. I | CO# 13500-B
This Monthly Operation Report prepared by: |  |  | BAYLER, J. | CO# 4474-A
State DEP Plant Classification: Class "A" Level "II"
I certify that I am familiar with the information contained in this report and that to the best of my knowledge and
belief, such information is true, complete and accurate.
Facilitiy Manager's Signature: ____________________________________ CO# __________________
Division Manager's Signature: ____________________________________ CO# __________________
Please direct all inquiries reguarding this report to the City Official Mailing Address:
Director of Public Services |  |  | Phone (954) 776-5151
City of Fort Lauderdale
P.O. Drawer 14250 |  |  | Copies mailed: Date ________________ To: DEP _____
Fort Lauderdale, Florida | [5 empty] | DNRP _____
33302
PAGE 1

## PRINT PAGES
UNDERGROUND INJECTION CONTROL SECTION
[29 empty] | MONTHLY OPERATING REPORT DATA SUMMARY | [13 empty] | DEP From # 17-801.900 (1) | [11 empty] | DEP From # 17-801.900 (1) | [19 empty] | DAILY SAMPLE RESULTS - PART B
[25 empty] | FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT DATE: |  | SEPTEMBER | 2005 | [8 empty] | Form Title:Domestic Wastewater Treatment | [11 empty] | Form Title:Domestic Wastewater Treatment
[25 empty] | I.D. NUMBER: 5006M02066 |  |  |  |  | CHIEF OPERATOR: |  |  | McGEARY, J. | CO# 4545-A | [8 empty] | Plant Monthly Operating Report | [11 empty] | Plant Monthly Operating Report | [15 empty] | Permit Number: |  | FLA041378 |  |  |  |  | Three-month Average Daily Flow: | [5 empty] | 41.5624
[25 empty] | TELEPHONE NUMBER: (954) 523-1002 | [17 empty] | Effective Date: July 1, 1991 | [11 empty] | Effective Date: July 1, 1991 | [15 empty] | Monitoring Period |  | From: | 2005-09-01 | To: | 2005-10-01 |  | (TMADF):/Permitted Capacity)x100: | [5 empty] | 74.62%
[19 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [9 empty] | INJECTION WELL DATA | [13 empty] | DEP Application No. __________________ | [11 empty] | DEP Application No. __________________ | [11 empty] | Department of Natural Resource Protection
[5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [13 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [6 empty] | IW-1 | IW-2 |  | IW-3 |  | IW-4 | IW-5 | [35 empty] | Laboratory/Licensing/Enforcement |  |  |  | Flow | Flow | Flow | Flow | Flow | Flow | CBOD5 | CBOD5 | TSS | TSS | pH | pH | TDS | NH-3 | TKN | pH | cond. | temp. | TP
[5 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [13 empty] | MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING | [5 empty] | PERMIT/CERTIFICATION NUMBER: | 0054569-142-UO | 0054569-142-UO |  | 0054569-142-UO |  | 0054569-142-UO | 0054569-142-UO | [19 empty] | DOMESTIC WASTEWATER TREATMENT PLANT | [11 empty] | BROWARD COUNTY DEPARTMENT OF NATURAL RESOURCE PROTECTION | [5 empty] | 218 S. W. 1st Avenue |  |  | (MGD) | (MGD) | (MGD) | (MGD) | (MGD) | (mg/l) | (mg/l) | (mg/l) | (mg/l) | (Min) | (Max) | mg/L | mg/L | mg/L | units | umho/ | F | mg/L
[5 empty] | MONTHLY OPERATIONAL REPORT | [13 empty] | MONITORING WELL ONE |  |  |  | 1/07/04 thru 1/06/09 |  | PERMIT EXPIRATION DATE: | 2009-01-06 | 2009-01-06 |  | 2009-01-06 |  | 2009-01-06 | 2009-01-06 | [19 empty] | MONTHLY OPERATING REPORT | [11 empty] | WASTEWATER TREATMENT PLANT | [5 empty] | Fort Lauderdale, FL 33301 | [17 empty] | cm
[5 empty] | PROCESS DATA | [11 empty] | MW-1 | I.D. #: 5066A11311 |  |  | PERMIT # 0054569-142-UO |  |  |  | CASING DEPTH | 2799' | 2798' |  | 2800' |  | 2804' | 2818' | [8 empty] | DOMESTIC WASTEWATER TREATMENT PLANT |  |  |  |  | (34) | [8 empty] | MONTH: | SEPTEMBER |  | YEAR: | 2005 |  |  |  |  | MONTHLY SLUDGE REPORTS | [5 empty] | Tel. No. (954) 765-4804 | Code | 50050 | 50050 | 50050 | 50050 | 50050 | 50050 | 80082 | 80082 | 00530 | 00530 | 00400 | 00400
| RUN DATE | [14 empty] | RUN DATE | [8 empty] | TOTAL DEPTH | 3513' | 3518' |  | 3977' |  | 3305' | 3462' | [8 empty] | MONTHLY OPERATING REPORT |  |  |  |  | DAY OF | FLOW | CHLORINE | CHLORINE | CBOD5 | TSS | CBOD5 | TSS | PH |  |  | EFFLUENT NUTRIENTS (MG/L) |  |  | I. | [10 empty] | Mon. Site | INF-001 | EFF-003 | EFF-004 | EFF-005 | EFF-006 | EFF-007 | INF-002 | EFF-001 | INF-002 | EFF-002 | EFF-002 | EFF-002
| 2026-07-30 | [14 empty] | 2026-07-30 |  | UPPER MONITOR ZONE |  |  |  |  | LOWER MONITOR ZONE |  | AVERAGE DAILY FLOW: | 8.705 | 8.7847 |  | 8.3877 |  | 8.7257 | 8.7777 | MGD | [7 empty] | Part II - General Information |  |  |  |  | THE |  | RESIDUAL | RESIDUAL | INFLUENT | INFLUENT | EFFLUENT | EFFLUENT | EFFLUENT | TKN | NH3-N | NITRATE | TOTAL | FECAL | Plant Name: | GEORGE T. LOHMEYER WASTEWATER TREATMENT FACILITY | [6 empty] | MONTH: | SEPTEMBER |  | 1 | 44.155 | 5.64 | 12.06 | 11.1 | 9.38 | 5.61 | 46.9 | 2.2 | 90 | 23 | 6.7 | 6.7 | 1022 | 7.8 | 10 | 6.7 | 2190 | 87 | 0.93
[17 empty] | MIN | MAX | AVG |  |  | MIN | MAX | AVG | **MAX DAILY FLOW PER MO (mg): | 12.55 | 13.17 |  | 12 |  | 12.24 | 11.61 | MG | [12 empty] | MONTH | (MGD) | AFTER | AFTER DE- | [8 empty] | P | COLIFORM | II. | [7 empty] | YEAR: | 2005 |  | 2 | 43.606 | 2.5 | 12.45 | 11.31 | 9.48 | 8.49 | 36.2 | 2.09 | 112 | 10 | 6.4 | 6.4 | 1102 | 7.8 | 9.5 | 6.6 | 2320 | 87 | 0.97
| SEPTEMBER | INFLUENT | HOURLY | INFLUENT | INFLUENT | RAS | PERCENT | WAS | RAIN | Sufates | [5 empty] | SEPTEMBER | FT HEAD | FT HEAD | FT HEAD |  |  | FT HEAD | FT HEAD | FT HEAD | ** PEAK HR FLOW (MGD) ON MAX DAY: | 11.6095 | 11.6484 |  | 11.1108 |  | 11.5722 | 11.7131 | MGD |  | (1) Month: |  | SEPTEMBER |  | Year: | 2005 |  | Parameter | Units | STORET | Value |  |  | CONTACT | CHLORINATION | MG/L | MG/L | MG/L | MG/L | [6 empty] | A) | Sludge Treatment Provided: |  |  |  |  | B) | Sludge Dewater Processes |  |  |  | 3 | 45.086 | 9.63 | 2.94 | 11.55 | 11.87 | 9.04 | 34.6 | 0.79 | 90 | LS | 6.6 | 6.7 | 1086 | 8.1 | 8.6 | 6.6 | 2280 | 87 | 0.78
| 2005 | FLOW | MAXIMUM | MAXIMUM | MINIMUM | FLOW | RAS | FLOW | INCHES | [6 empty] | 2005 | ABOVE | ABOVE | ABOVE |  |  | ABOVE | ABOVE | ABOVE | MAX SUSTAINED INJECTION PRESSURE: | 73 | 72.1 |  | 79.5 |  | 80 | 78.6 | PSIG |  | (2) Plant's DEP Identification Number: |  |  |  |  | 5006M02066 |  |  |  | Code |  | 1 | 44.155 | 0 |  | 46.9 | 90 | 2.2 | 23 | 6.7 | 10 | 7.8 | 0.1 | 0.93 | TNTC |  |  | Aerobic Digestion | [5 empty] | Thickner |  |  | 4 | 46.793 | 12.43 | 9.8 | 0.65 | 12.24 | 11.43 | 28 | 1 | 44 | 12 | 6.6 | 6.7 | 945 | 7.1 | 7.7 | 6.6 | 1970 | 87 | 0.88
|  | MGD | MGD | MGD | MGD | MGD |  | MGD | [8 empty] | NGVD | NGVD | NGVD |  |  | NGVD | NGVD | NGVD | MONTHLY AVG. INJECTION PRESSURE: | 52.918 | 52.1467 |  | 53.9343 |  | 54.6603 | 54.519 | PSIG |  | (3) Plant Name: |  |  |  | George T. Lohmeyer Regional Wastewater |  |  | (16) Monthly average daily flow | mgd | 050053 | 43.3311 | 2 | 43.606 | 0.6 |  | 36.2 | 112 | 2.09 | 10 | 6.6 | 9.5 | 7.8 | 0.2 | 0.97 | TNTC |  |  | Anaerobic Digestion | [5 empty] | DGA___X___Filter Press |  |  | 5 | 39.825 | 12.18 | 10.08 | 9.01 | 2.91 | 11.42 | 31.9 | 0.99 | 66 | 10 | 6.6 | 6.6 | 1019 | 5 | 6.1 | 6.6 | 2020 | 86 | 0.5
| 1 | 44.155 | 2.151 | 59.98 | 18.807 | 13.08 | 29.62% | 0.528 | 0 | 121.5 |  | 1 |  |  |  | 1 | 48.97 | 49.25 | 49.27 |  |  | 42.62 | 46.54 | 43.83 | *** MAX INJECTION PRESSURE PERMITTED: | 99 | 99 |  | 99 |  | 99 | 99 | PSIG |  |  |  |  | Treatment Facility |  |  |  | (17) Permitted capacity | mgd | - | 55.7 | 3 | 45.086 | 1 |  | 34.6 | 90 | 0.79 | LS | 6.6 | 8.6 | 8.1 | 0.25 | 0.78 | 9 |  |  | Other | [5 empty] | Centrifuge Drying Beds, Bed #______ |  |  | 6 | 50.104 | 12.55 | 12.9 | 12 | 10.78 | 0.6 | 32.7 | 1.66 | 82 | 9 | 6.6 | 6.9 | 1208 | 6.2 | 10 | 6.7 | 2500 | 86 | 0.48
| 2 | 43.606 | 2.197 | 59.5 | 19.576 | 13.552 | 31.08% | 0.218 | 0.04 | 118.25 |  | 2 |  |  |  | 2 | 49.01 | 49.27 | 49.05 |  |  | 42.65 | 47.06 | 44.29 | ***NOTE: (INJECTION PRESSURE NOT TO EXCEED 66% TESTED PRESSURE | [9 empty] | (4) Plant Address: |  |  | 1765 S.E. 18th Street at |  |  |  | (18) Three-month average daily flow | mgd | - | 41.5624 | 4 | 46.793 | 1.1 |  | 28 | 44 | 1 | 12 | 6.6 | 7.7 | 7.1 | 0.24 | 0.88 | 9 | [8 empty] | Heat Treatment____No Treatment |  |  | 7 | 48.237 | 1.18 | 13.17 | 11.84 | 12.02 | 10.07 | 16.4 | 1 | 40 | 7 | 6.6 | 6.9 | 1079 | 6.5 | 10 | 6.7 | 2240 | 86 | 0.62
| 3 | 45.086 | 2.208 | 61.134 | 23.87 | 13.792 | 30.59% | 0 | 0.13 | 117.25 |  | 3 |  |  |  | 3 | 49.06 | 49.34 | 49.2 |  |  | 42.96 | 47.05 | 44.15 | TESTED CASING PRESSURE DURING MIT | 150 | 150 |  | 150 |  | 150 | 150 | PSIG |  |  |  |  | Eisenhower Boulevard |  |  |  | (19) Percent of permitted capacity | % | - | 74.62% | 5 | 39.825 | 0.9 |  | 31.9 | 66 | 0.99 | 10 | 6.6 | 6.1 | 5 | 0.024 | 0.5 | 0 | [7 empty] | x | Other: | Press Dewatered |  | 8 | 45.618 | 10.89 | 0.9 | 11.5 | 11.59 | 10.93 | 45 | 2.03 | 32 | 11 | 6.6 | 6.9 | 1228 | 7.6 | 9.6 | 6.7 | 2460 | 86 | 1
| 4 | 46.793 | 2.246 | 61.807 | 26.337 | 13.747 | 29.38% | 0 | 0.06 | 101.5 |  | 4 |  |  |  | 4 | 49.12 | 49.37 | 49.22 |  |  | 43 | 46.37 | 44.17 | [10 empty] | (5) City: |  | Fort Lauderdale |  |  |  |  | (20) CBOD5 Effluent | mg/L | 080082 | 2.8837 | 6 | 50.104 | 0.9 |  | 32.7 | 82 | 1.66 | 9 | 6.7 | 10 | 6.2 | 0.37 | 0.48 | 0 | [9 empty] | To Landfill |  | 9 | 45.168 | 11.87 | 10.51 | 0.64 | 11.62 | 10.95 | 76.9 | 4.87 | 152 | 27 | 6.6 | 6.8 | 1114 | 6.8 | 12 | 6.7 | 2420 | 86 | 0.74
| 5 | 39.825 | 1.891 | 54.308 | 20.313 | 13.058 | 32.79% | 0.172 | 0.1 | 106.75 |  | 5 |  |  |  | 5 | 45.44 | 49.29 | 46.92 |  |  | 41.85 | 44.48 | 43.6 |  |  | MONITORING WELL DATA | [7 empty] | (6) County: |  | Broward |  |  |  |  | (21) CBOD5 Effluent | lbs/day | - | 1042.1034 | 7 | 48.237 | 0 |  | 16.4 | 40 | 1 | 7 | 6.7 | 10 | 6.5 | 0.31 | 0.62 | 60000 | III. | Final Sludge Disposal: | [9 empty] | 10 | 45.52 | 11.5 | 11.78 | 8.98 | 1.59 | 10.87 | 86 | 2.18 | 46 | 14 | 6.6 | 6.7 | 1257 | 8.9 | 10 | 6.7 | 2500 | 86 | 0.79
| 6 | 50.104 | 2.394 | 66.133 | 26.85 | 13.562 | 27.07% | 0.358 | 0.54 | 135 |  | 6 |  |  |  | 6 | 45.78 | 49.62 | 48.42 |  |  | 41.42 | 44.33 | 42.58 |  | MW-1 | MW-2 |  | MW-3 |  | RMW-1 |  |  |  | (7) Phone Number: |  |  | (954) 523-1002 |  |  |  | (22) TSS Effluent | mg/L | 900201 | 13.4286 | 8 | 45.618 | 0 |  | 45 | 32 | 2.03 | 11 | 6.7 | 9.6 | 7.6 | 0.31 | 1 | TNTC | A) | Liquid Sludge Disposal: | [9 empty] | 11 | 49.087 | 11.82 | 12.14 | 11.28 | 0.9 | 11.17 | 54.9 | 2.51 | 84 | 11 | 6.6 | 6.7 | 1117 | 6.4 | 10 | 6.6 | 2220 | 86 | 0.77
| 7 | 48.237 | 2.311 | 62.768 | 30.407 | 13.619 | 28.23% | 0.358 | 0.05 | 118.75 |  | 7 |  |  |  | 7 | 49.25 | 49.49 | 49.42 |  |  | 42.49 | 46.79 | 44.12 | PERMIT NUMBER | 0054569-142-UO | 0054569-142-UO |  | 0054569-142-UO |  | 0054569-142-UO |  |  |  | (8) Permit Number: |  |  | FLA041378 |  |  |  | (23) TSS Effluent | lbs/day | - | 4852.8356 | 9 | 45.168 | 0 |  | 76.9 | 152 | 4.87 | 27 | 6.7 | 12 | 6.8 | 0.27 | 0.74 | TNTC |  | WEEK OF | SEPTEMBER | GALLONS | % SOLIDS |  |  | HAULERS |  |  | DISPOSAL SITE | 12 | 47.528 | 3.75 | 11.9 | 10.8 | 10.52 | 10.42 | 57.9 | 2.28 | 28 | 5 | 6.6 | 7 | 1390 | 8 | 12 | 6.7 | 2830 | 0 | 0.56
| 8 | 45.618 | 2.157 | 58.634 | 25.023 | 13.824 | 30.3% | 0.378 | 0.03 | 127 |  | 8 |  |  |  | 8 | 49.27 | 49.54 | 49.45 |  |  | 43.09 | 46.92 | 44.58 | UPPER MONITORING INTERVAL | 1288'-1320' | 1300'-1344' |  | 1300'-1349' |  | 1300'-1339' |  | Ft. bls. |  | (9) Plant Type: |  |  | Oxygen Activated Sludge |  |  |  | (24) Minimum pH |  | - | 6.4 | 10 | 45.52 | 0 |  | 86 | 46 | 2.18 | 14 | 6.7 | 10 | 8.9 | 0.74 | 0.79 | TNTC | [11 empty] | 13 | 44.966 | 10.58 | 0.71 | 11.38 | 11.6 | 10.88 | 58.3 | 1.8 | 122 | 21 | 6.7 | 6.8 | 1597 | 9.9 | 12 | 6.7 | 3100 | 86 | 0.78
| 9 | 45.168 | 2.161 | 59.307 | 27.33 | 14.501 | 32.1% | 0.14 | 0 | 135 |  | 9 |  |  |  | 9 | 49.29 | 49.55 | 49.44 |  |  | 43.14 | 47.39 | 44.9 | MONTHLY MAX DAILY PRESSURE | 49.62 | 35.43 |  | 34.7 |  | 45.23 |  | FT. HEAD |  | (10) Test Site Identification Number: |  |  |  |  | 5006X10744 |  | (25) Maximum pH |  | - | 7 | 11 | 49.087 | 0 |  | 54.9 | 84 | 2.51 | 11 | 6.6 | 10 | 6.4 | 0.21 | 0.77 | TNTC |  | FIRST THRU SEVENTH | [9 empty] | 14 | 42.538 | 10.48 | 9.07 | 1.33 | 11.06 | 10.46 | 58.3 | 3.07 | 100 | 12 | 6.6 | 6.9 | 1597 | 8.8 | 13 | 6.7 | 2320 | 86 | 0.96
| 10 | 45.52 | 2.303 | 60.172 | 24.895 | 14.298 | 31.41% | 0 | 2.6 | 141.75 |  | 10 |  |  |  | 10 | 49.22 | 49.49 | 49.4 |  |  | 41.97 | 46.83 | 44.49 | MONTHLY MIN DAILY PRESSURE | 45.44 | 18.96 |  | 20.05 |  | 0.25 |  | FT. HEAD |  | (11) Fecal Coliform Method | [6 empty] | (26) Total N | mg/L | 000600 | 10.481 | 12 | 47.528 | 0 |  | 57.9 | 28 | 2.28 | 5 | 6.7 | 12 | 8 | 0.5 | 0.56 | TNTC | [11 empty] | 15 | 41.743 | 10.94 | 9 | 8.05 | 2.79 | 10.33 | 63.9 | 2.84 | 76 | 10 | 6.6 | 6.8 | 1185 | 10 | 14 | 6.7 | 2370 | 86 | 1.7
| 11 | 49.087 | 2.303 | 63.825 | 29.67 | 13.354 | 27.2% | 0.133 | 0.15 | 130.25 |  | 11 |  |  |  | 11 | 49.13 | 49.42 | 49.35 |  |  | 42.48 | 47.07 | 44.64 | TDS (MONTHLY AVERAGE) | 7519 | 7561.5 |  | 7810.75 |  | 5982 |  | mg/l |  |  | XX | Membrane Filter |  |  |  |  | (27) TKN | mg/L | 000625 | 10.15 | 13 | 44.966 | 0 |  | 58.3 | 122 | 1.8 | 21 | 6.7 | 12 | 9.9 | 0.066 | 0.78 | 39000 |  | EIGHT THRU FORTEENTH | [9 empty] | 16 | 41.521 | 10.31 | 10.72 | 10.49 | 8.07 | 1.9 | 53.36 | 2.43 | 48 | 14 | 6.5 | 6.7 | 1340 | 9.6 | 10 | 6.6 | 2530 | 86 | 1.5
| 12 | 47.528 | 2.398 | 63.056 | 26.561 | 13.291 | 27.96% | 0.31 | 0 | 147.75 |  | 12 |  |  |  | 12 | 47.16 | 49.37 | 48.08 |  |  | 43.06 | 46.81 | 44.35 | CHLORIDE (MONTHLY AVERAGE) | 3762.5 | 3687.5 |  | 3675 |  | 2800 |  | mg/l |  |  |  | Most Probable Number |  |  |  |  | (28) Ammonia (NH3 - N) | mg/L | 000610 | 7.8467 | 14 | 42.538 | 0.8 |  | 58.3 | 100 | 3.07 | 12 | 6.7 | 13 | 8.8 | 0.96 | 0.96 | 50000 |  | FIFTHTEENTH THRU | [9 empty] | 17 | 41.027 | 2.36 | 11.42 | 10.48 | 8.72 | 7.8 | 53.11 | 3.99 | 106 | 20 | 6.6 | 6.6 | 1298 | 7.2 | 9.1 | 6.6 | 2590 | 86 | 1.3
| 13 | 44.966 | 2.298 | 60.493 | 24.382 | 12.523 | 27.85% | 0.365 | 0 | 149.5 |  | 13 |  |  |  | 13 | 47.67 | 49.45 | 48.82 |  |  | 42.27 | 46.82 | 44.26 | AMMONIA-N (MONTHLY AVERAGE) | 0.86 | 0.84 |  | 0.8275 |  | 0.64 |  | mg/l |  | (12) Type of Effluent Disposal or Reclaimed Water Reuse | [6 empty] | (29) Nitrate | mg/L | 071850 | 0.331 | 15 | 41.743 | 0.9 |  | 63.9 | 76 | 2.84 | 10 | 6.7 | 14 | 10 | 0.12 | 1.7 | 0 |  | TWENTY SECOND | [9 empty] | 18 | 40.734 | 8.69 | 2.54 | 10.42 | 10.57 | 8.22 | 67.3 | 1.29 | 90 | 15 | 6.6 | 6.7 | 1350 | 8.8 | 8.8 | 6.6 | 2660 | 87 | 0.95
| 14 | 42.538 | 2.106 | 57.737 | 20.185 | 12.463 | 29.3% | 0.382 | 0 | 123.75 |  | 14 |  |  |  | 14 | 49.06 | 49.42 | 49.25 |  |  | 42.62 | 46.8 | 44.29 | TKN (MONTHLY AVERAGE) | 1.35 | 1.0725 |  | 0.965 |  | 0.96 |  | mg/l |  |  |  | Deep Well Injection |  |  |  |  | (30) Total Phosphorus | mg/L | 000665 | 1.0114 | 16 | 41.521 | 0.7 |  | 53.36 | 48 | 2.43 | 14 | 6.6 | 10 | 9.6 | 0.82 | 1.5 | 0 |  | TWENTY THIRD THRU | [9 empty] | 19 | 41.144 | 9 | 8.81 | 2.47 | 10.86 | 10.24 | 70.78 | 1.42 | LS | LS | 6.5 | 6.8 | LS | 9 | 9.5 | 6.6 | LS | 87 | 0.95
| 15 | 41.743 | 2.07 | 57.096 | 20.986 | 12.3 | 29.47% | 0.446 | 0 | 127 |  | 15 |  |  |  | 15 | 49.01 | 49.39 | 49.21 |  |  | 42.93 | 46.85 | 44.55 | pH (MONTHLY AVERAGE) | 8.075 | 7.98 |  | 8.2625 |  | 8.48 |  | Std units |  | (13) Limited Wet Wheather Discharge Activated | [6 empty] | (31) Minimum Chlorine Residual | mg/L | - | 0 | 17 | 41.027 | 1 |  | 53.11 | 106 | 3.99 | 20 | 6.6 | 9.1 | 7.2 | 0.43 | 1.3 | 0 |  | THIRTY FIRST | [9 empty] | 20 | 45.32 | 10.67 | 8.69 | 7.66 | 8.28 | 9.86 | 65.89 | 1 | 40 | 8 | 6.6 | 6.8 | 1336 | 7.2 | 8.3 | 6.7 | 2620 | 86 | 0.86
| 16 | 41.521 | 2.126 | 54.372 | 22.428 | 13.681 | 32.95% | 0.189 | 0 | 124.5 |  | 16 |  |  |  | 16 | 49.03 | 49.4 | 49.21 |  |  | 43.48 | 46.74 | 44.8 | CONDUCTIVITY (MONTHLY AVERAGE) | 12150 | 11800 |  | 12022.5 |  | 9280 |  | umho/cm |  |  |  | YES |  | XX | Not Applicable |  | (32) Maximum Chlorine Residual | mg/L | - | 1.1 | 18 | 40.734 | 0.9 |  | 67.3 | 90 | 1.29 | 15 | 6.6 | 8.8 | 8.8 | 0.31 | 0.95 | 0 | [11 empty] | 21 | 46.859 | 10.46 | 10.7 | 10.01 | 10.36 | 4.79 | 37.47 | 5.56 | 18 | 6 | 6.7 | 6.8 | 1154 | 7.5 | 12 | 6.8 | 2410 | 86 | 1
| 17 | 41.027 | 2.09 | 56.199 | 20.569 | 13.369 | 32.59% | 0 | 0 | 127.25 |  | 17 |  |  |  | 17 | 49.02 | 49.38 | 49.21 |  |  | 43.8 | 46.93 | 45.03 | FECAL COLIFORM (MONTHLY AVERAGE) | 0 | 0 |  | 0 |  | 0 |  | # col/100ml |  |  |  | NO |  |  |  |  | (33) Other Effluent Parameters |  |  |  | 19 | 41.144 | 0.9 |  | 70.78 | LS | 1.42 | LS | 6.6 | 9.5 | 9 | 0.31 | 0.95 | 0 | B) | Solid Sludge Hauled from Plant: | [9 empty] | 22 | 44.822 | 0.73 | 12.56 | 11.33 | 11.32 | 9.21 | 61.5 | 2.37 | 88 | 17 | 6.5 | 6.9 | 1193 | 8.4 | 12 | 6.7 | 2390 | 86 | 1.5
| 18 | 40.734 | 2.035 | 55.782 | 19.672 | 13.562 | 33.29% | 0.167 | 0 | 129.25 |  | 18 |  |  |  | 18 | 49.03 | 49.38 | 49.2 |  |  | 44.02 | 47.05 | 45.12 | TEMPERATURE (MONTHLY AVERAGE) | 75.25 | 74.25 |  | 72.5 |  | 72 |  | deg. F | [12 empty] | 20 | 45.32 | 0.8 |  | 65.89 | 40 | 1 | 8 | 6.7 | 8.3 | 7.2 | 0.34 | 0.86 | TNTC |  | WEEK OF | SEPTEMBER | TONS |  | % SOLIDS |  | HAULERS |  |  | DISPOSAL SITE | 23 | 43.123 | 10.47 | 0.81 | 10.97 | 11.08 | 11.61 | 64.47 | 2.97 | 44 | 21 | 6.6 | 6.7 | 1263 | 7.2 | 0 | 6.7 | 2450 | 86 | 1.4
| 19 | 41.144 | 1.987 | 55.718 | 19.127 | 13.171 | 32.01% | 0.257 | 0.07 | 140.75 |  | 19 |  |  |  | 19 | 46.76 | 49.35 | 48.04 |  |  | 42.55 | 46.28 | 44.25 | TOTAL PHOSPHOROUS (MONTHLY AVG.) | 0.01 | 0.01 |  | 0.01 |  | 0.01 |  | mg/l |  | (14) Cumulative Days of Wet Wheather Discharge | [10 empty] | 21 | 46.859 | 0.8 |  | 37.47 | 18 | 5.56 | 6 | 6.8 | 12 | 7.5 | 0.26 | 1 | TNTC | [10 empty] | Central Sanitary Landfill | 24 | 41.29 | 10.87 | 8.61 | 0.58 | 10.78 | 10.15 | 63.15 | 3.3 | 68 | 16 | 6.6 | 6.6 | 1172 | 6 | 11 | 6.6 | 2410 | 86 | 1.4
| 20 | 45.32 | 2.307 | 62.896 | 23.357 | 13.787 | 30.42% | 0 | 1.08 | 122.25 |  | 20 |  |  |  | 20 | 47.05 | 49.56 | 48.67 |  |  | 41.4 | 43.4 | 42.6 | SULFATE (MONTHLY AVERAGE) | 930 | 934.75 |  | 906.5 |  | 795 |  | mg/l |  |  |  | N/A | [8 empty] | 22 | 44.822 | 0.8 |  | 61.5 | 88 | 2.37 | 17 | 6.7 | 12 | 8.4 | 0.25 | 1.5 | 10 |  | FIRST THRU SEVENTH |  | 352 |  | 19.8667 |  | SYNAGRO |  |  | Pompano Beach, FL | 25 | 39.825 | 10.3 | 8.51 | 7.7 | 2.48 | 9.8 | 63.2 | 2.87 | 106 | 16 | 6.6 | 6.6 | 1187 | 7.2 | 12 | 6.6 | 2400 | 86 | 1
| 21 | 46.859 | 2.182 | 59.98 | 28.132 | 13.378 | 28.55% | 0.438 | 0.09 | 135.75 |  | 21 |  |  |  | 21 | 49.07 | 49.36 | 49.23 |  |  | 42.17 | 45.76 | 43.94 | C.O.D. (MONTHLY AVERAGE) | #DIV/0! | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | mg/l |  | (15) Plant Staffing: | [10 empty] | 23 | 43.123 | 0.8 |  | 64.47 | 44 | 2.97 | 21 | 6.7 | 0 | 7.2 | 0.54 | 1.4 | 10 | [10 empty] | Central Sanitary Landfill | 26 | 39.284 | 10.15 | 10.42 | 8.02 | 7.93 | 2.24 | 71 | 4 | 90 | 14 | 6.6 | 6.8 | 1226 | 8.8 | 12 | 6.7 | 2470 | 86 | 1.3
| 22 | 44.822 | 2.134 | 58.73 | 20.089 | 13.278 | 29.62% | 0.575 | 0.69 | 122 |  | 22 |  |  |  | 22 | 47.74 | 49.33 | 48.52 |  |  | 41.23 | 45.12 | 43.22 | IRON (MONTHLY AVERAGE) | #DIV/0! | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | mg/l | [12 empty] | 24 | 41.29 | 1 |  | 63.15 | 68 | 3.3 | 16 | 6.6 | 11 | 6 | 0.24 | 1.4 | 0 |  | EIGHT THRU FORTEENTH |  | 374 |  | 17.774 |  | SYNAGRO |  |  | Pompano Beach, FL | 27 | 38.725 | 2.19 | 10.86 | 9.99 | 8.32 | 7.49 | 123 | 7 | 100 | 17 | 6.5 | 6.8 | 1271 | 7.6 | 13 | 6.6 | 2640 | 86 | 1.6
| 23 | 43.123 | 2.31 | 57.032 | 25.92 | 13.829 | 32.07% | 0.163 | 0.33 | 114.75 |  | 23 |  |  |  | 23 | 47.78 | 49.13 | 48.71 |  |  | 40.1 | 43.51 | 42 | SULFIDE (MONTHLY AVERAGE) | #DIV/0! | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | mg/l |  |  | Day Shift Operator: |  |  | Class | "A" | Cert. No. | CO# 4545-A |  |  |  | 25 | 39.825 | 0.9 |  | 63.2 | 106 | 2.87 | 16 | 6.6 | 12 | 7.2 | 0.27 | 1 | 0 |  | FIFTHTEENTH THRU | [8 empty] | Central Sanitary Landfill | 28 | 38.518 | 8.33 | 2.4 | 9.98 | 10.14 | 7.89 | 66 | 5 | 98 | 8 | 6.6 | 6.7 | 1368 | 7.4 |  | 6.7 | 2680 | 86
| 24 | 41.29 | 1.962 | 55.302 | 22.844 | 13.442 | 32.56% | 0 | 0 | 122.25 |  | 24 |  |  |  | 24 | 48.92 | 49.18 | 49.02 |  |  | 41.84 | 45.2 | 43.13 | LOWER MONITORING INTERVAL | 1449'-1557' | 1970'-2025' |  | 1970'-2027' |  | 1500'-1600' |  | Ft. bls | [12 empty] | 26 | 39.284 | 0.7 |  | 71 | 90 | 4 | 14 | 6.7 | 12 | 8.8 | 0.29 | 1.3 | 0 |  | TWENTY SECOND |  | 418 |  | 17.774 |  | SYNAGRO |  |  | Pompano Beach, FL | 29 | 38.756 | 8.42 | 8.31 | 2.31 | 10.27 | 9.67 | 81 | 7 | 83 | 8 | 6.6 | 6.8 | 1360 | 9.9 |  | 6.7 | 2470 | 86
| 25 | 39.825 | 1.891 | 54.308 | 20.313 | 13.058 | 32.79% | 0.172 | 0.1 | 131.25 |  | 25 |  |  |  | 25 | 48.96 | 49.23 | 49.03 |  |  | 41.95 | 45.74 | 43.58 | MONTHLY MAX DAILY PRESSURE | 47.39 | 43.62 |  | 46.38 |  | 23.35 |  | FT. HEAD |  |  | Evening Shift Operator: |  |  | Class | "A" | Cert. No. | CO# 4474-A |  |  |  | 27 | 38.725 | 0.7 |  | 123 | 100 | 7 | 17 | 6.6 | 13 | 7.6 | 0.34 | 1.6 | 9 |  | TWENTY THIRD THRU | [8 empty] | Central Sanitary Landfill | 30 | 39.011 | 10.26 | 8.77 | 7.8 | 2.24 | 9.79 | 102 | 5 | 96 | 14 | 6.6 | 6.7 | 1344 | 8.7 | 12 | 6.7 | 2690 | 86 | 1.1
| 26 | 39.284 | 1.909 | 55.814 | 17.685 | 12.387 | 31.53% | 0.513 | 0.38 | 136 |  | 26 |  |  |  | 26 | 49.03 | 49.3 | 49.15 |  |  | 42.45 | 45.97 | 43.98 | MONTHLY MIN DAILY PRESSURE | 40.1 | 35.98 |  | 37.4 |  | 0.25 |  | FT. HEAD | [12 empty] | 28 | 38.518 | 0.6 |  | 66 | 98 | 5 | 8 | 6.7 |  | 7.4 | 0.28 |  | 9 |  | THIRTY FIRST |  | 528 |  | 18.624 |  | SYNAGRO |  |  | Pompano Beach, FL | 31
| 27 | 38.725 | 1.965 | 53.635 | 20.089 | 12.376 | 31.96% | 0.566 | 0 | 146.25 |  | 27 |  |  |  | 27 | 46.71 | 49.3 | 47.64 |  |  | 41.31 | 45.03 | 43.13 | TDS (MONTHLY AVERAGE) | 9575 | 32085 |  | 28779.75 |  | 27957 |  | mg/l |  |  | Night Shift Operator: |  |  | Class | "C" | Cert. No. | CO# 5613-C |  |  |  | 29 | 38.756 | 0.6 |  | 81 | 83 | 7 | 8 | 6.7 |  | 9.9 | 0.3 |  | 0 | C) | Monthly quantities of solid sludge stockpiled at plant.Solid Sludge Hauled from Plant: | [9 empty] | TOT | 1299.933 | 261.15 | 263.54 | 251.63 | 261.77 | 263.33 | 1771.13 | 86.51 | 2239 | 376 | 197.7 | 202.5 | 35808 | 235.4 | 284.2 | 199.9 | 71150 | 2500 | 28.32
| 28 | 38.518 | 1.888 | 57.224 | 19.576 | 12.43 | 32.27% | 0.551 | 0.01 | 150.5 |  | 28 |  |  |  | 28 | 47.1 | 49.46 | 48.54 |  |  | 40.83 | 44.46 | 42.23 | CHLORIDE (MONTHLY AVERAGE) | 5050 | 16650 |  | 15400 |  | 15600 |  | mg/l | [12 empty] | 30 | 39.011 | 0.7 |  | 102 | 96 | 5 | 14 | 6.7 | 12 | 8.7 | 0.28 | 1.1 | 0 |  | 1) | Additions |  |  | Cubic Yards | [5 empty] | AVG | 43.3311 | 8.705 | 8.7847 | 8.3877 | 8.7257 | 8.7777 | 59.0377 | 2.8837 | 77.2069 | 13.4286 | 6.59 | 6.75 | 1234.7586 | 7.8467 | 10.15 | 6.6633 | 2453.4483 | 83.3333 | 1.0114
| 29 | 38.756 | 1.915 | 59.275 | 18.647 | 12.408 | 32.02% | 0.506 | 0.06 | 132.75 |  | 29 |  |  |  | 29 | 49.06 | 49.35 | 49.19 |  |  | 41.8 | 45.35 | 43.22 | AMMONIA-N (MONTHLY AVERAGE) | 9.625 | 1.425 |  | 2.425 |  | 0.29 |  | mg/l |  |  | Lead Operator:_________________________________ | [28 empty] | Tons | [5 empty] | MAX | 50.104 | 12.55 | 13.17 | 12 | 12.24 | 11.61 | 123 | 7 | 152 | 27 | 6.7 | 7 | 1597 | 10 | 14 | 6.8 | 3100 | 87 | 1.7
| 30 | 39.011 | 1.984 | 54.405 | 16.852 | 13.65 | 34.99% | 0.226 | 0.1 | 132.25 |  | 30 |  |  |  | 30 | 49.08 | 49.34 | 49.21 |  |  | 42.44 | 45.87 | 43.77 | TKN (MONTHLY AVERAGE) | 11 | 1.975 |  | 2.95 |  | 0.67 |  | mg/l | [5 empty] | Signature |  | Cert. No. |  |  |  |  | Lead Operator : This is to certify that I am familar with the information contained on this report and that to the best of | [14 empty] | 2) | Removals |  |  | Cubic Yards | [5 empty] | MIN | 38.518 | 0.73 | 0.71 | 0.58 | 0.9 | 0.6 | 16.4 | 0.79 | 18 | 5 | 6.4 | 6.4 | 945 | 5 | 0 | 6.6 | 1970 | 0 | 0.48
[25 empty] | pH (MONTHLY AVERAGE) | 7.39 | 7.7125 |  | 7.5225 |  | 7.51 |  | Std units | [12 empty] | my knowledge and belief, this information is true, complete and accuate. | [16 empty] | X |  | Tons | [6 empty] | item #1 | 11.6095 | 11.6484 | 11.1108 | 11.5722 | 11.7131 | MAX HOURLY FLOW (MG) = |  |  |  | 2.398 | ON THE | 12 | DAY OF THIS MONTH
| TOTAL | 1299.933 | 63.879 | 1756.622 | 680.492 | 398.77 |  | 8.111 | 6.61 | 3868.75 | [5 empty] | TOTAL | 1450.78 | 1481.31 | 1467.07 |  |  | 1269.92 | 1380.52 | 1316.8 | CONDUCTIVITY (MONTHLY AVERAGE) | 15575 | 25532.5 |  | 42375 |  | 41600 |  | umho/cm | [33 empty] | Signature |  |  |  |  | item #2 | 52.918 | 52.1467 | 53.9343 | 54.6603 | 54.519
| AVERAGE | 43.3311 | 2.1293 | 58.5541 | 22.6831 | 13.2923 | 30.68% | 0.33796 | 0.22033 | 128.9583 | [5 empty] | AVERAGE | 48.3593 | 49.377 | 48.9023 |  |  | 42.3307 | 46.0173 | 43.8933 | FECAL COLIFORM (MONTHLY AVERAGE) | 0 | 0 |  | 0 |  | 0 |  | # col/100ml | [12 empty] | Signed: ____________________________ Date: ___________________ | [20 empty] | Title |  |  |  |  | item #3 | 36.37 | 36.72 | 38.58 | 38.13 | 37.01
[16 empty] | MAXIMUM | 49.29 | 49.62 | 49.45 |  |  | 44.02 | 47.39 | 45.12 | TEMPERATURE (MONTHLY AVERAGE) | 74.25 | 73.5 |  | 71 |  | 71 |  | deg. F | [33 empty] | Date |  |  |  | item #1 | =monthly maximum of the daily flows (MG), with peakhour flow (MGD) on the day of the month with maximum flow = | [14 empty] | 2.398 | MG/hour multiplied by
[16 empty] | MINIMUM | 45.44 | 49.13 | 46.92 |  |  | 40.1 | 43.4 | 42 | TOTAL PHOSPHOROUS (MONTHLY AVG.) | 0.01 | 0.01 |  | 0.01 |  | 0.01 |  | mg/l | [12 empty] | Name: Michael A. Just | [14 empty] | * Sludge Reports should be submitted along with the monthly operating reports to Broward County Department | [10 empty] | the % of average % of TOTAL RAW FLOW to each Injection well.
[25 empty] | SULFATE (MONTHLY AVERAGE) | 874.75 | 2817.5 |  | 2847.5 |  | 1870 |  | mg/l | [27 empty] | of Natural Resource Protection, 218 S. W. 1st Avenue, Fort Lauderdale, Florida 33301 | [9 empty] | item #2 | =monthly average injection well pressure at injection well (psig)
[25 empty] | C.O.D. (MONTHLY AVERAGE) | #DIV/0! | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | mg/l | [12 empty] | Company Name: City of Fort Lauderdale Telephone No. (954) 523-1002 | [24 empty] | item #3 | =monthly wellhead pressure with no flow (shut-in pressure,psig)
[25 empty] | IRON (MONTHLY AVERAGE) | #DIV/0! | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | mg/l | [37 empty] | PLANT STAFFING
[5 empty] | PAGE 2 | [19 empty] | SULFIDE (MONTHLY AVERAGE) | #DIV/0! | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | mg/l | [37 empty] | Day Shift Operator |  |  | Class: | "A" | Certificate No. | CO# 4545-A | Name: |  | McGEARY, J.
[71 empty] | Evening Shift Operator |  |  | Class: | "A" | Certificate No. | CO# 4474-A | Name: |  | BAYLER, J.
[20 empty] | PAGE 20 | [50 empty] | Night Shift Operator |  |  | Class: | "C" | Certificate No. | CO# 5613-C | Name: |  | BAROFSKY
[71 empty] | Lead Operator |  |  | Class: | 0 | Certificate No. | CO# 2769-A | Name: |  | JUST, M.
[71 empty] | Type of Effluent Disposal or Reclaimed Water Reuse: |  |  |  |  | DEEPWELL INJECTION
[71 empty] | Permited Wet Weather Discharge Activated: |  |  |  | YES: |  | NO: |  |  | Not Applicable |  | X
[28 empty] | Page 28 | [42 empty] | If Yes, cumulative days of wet weather:
Attach additional sheets if necessary to list all certified operators. See page 1 "COVER PAGE" of supplental attachements.
DEP form 62-620.910(10), effective November 29, 1994
[19 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [47 empty] | Department of Natural Resource Protection
[5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [13 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [47 empty] | Division of Pollution Prevention and Remediation Programs
[5 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [13 empty] | MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING | [50 empty] | 218 S. W. 1st Avenue
[5 empty] | MONTHLY OPERATIONAL REPORT | [13 empty] | MONITORING WELL TWO |  |  |  | 1/07/04 thru 1/06/09 | [39 empty] | SLUDGE HAULERS MONTHLY REPORT | [6 empty] | Fort Lauderdale, FL 33301
[5 empty] | INFLUENT DATA | [11 empty] | MW-2 | I.D. #: 5066A11308 & 09 |  |  | PERMIT # 0054569-142-UO | [41 empty] | BROWARD COUNTY CODE SECTION 27-356 (d)(4)(1) | [5 empty] | Tel. No. (954) 523-1002
| RUN DATE | [14 empty] | RUN DATE | [52 empty] | *FAX (954) 519-1245
| 2026-07-30 | [14 empty] | 2026-07-30 |  | UPPER MONITOR ZONE |  |  |  |  | LOWER MONITOR ZONE
[17 empty] | MIN | MAX | AVG |  |  | MIN | MAX | AVG | [35 empty] | Plant Name: | GEORGE T. LOHMEYER WASTEWATER TREATMENT FACILITY
| SEPTEMBER | RAW | RAW TSS | RAW SS | RAW | RAW | RAW | RAW | RAW | RAW | [5 empty] | SEPTEMBER | FT HEAD | FT HEAD | FT HEAD |  |  | FT HEAD | FT HEAD | FT HEAD | [35 empty] | Address: | 1765 S.E. 18th Street at Eisenhower Boulevard | [6 empty] | MONTH: | SEPTEMBER
| 2005 | CBOD | TOTAL | FIXED | COD | pH | CL_ | ALK. | H2S | TEMP.(F) | [5 empty] | 2005 | ABOVE | ABOVE | ABOVE |  |  | ABOVE | ABOVE | ABOVE | [35 empty] | Phone: | (954) 523-1002 * FAX (954) 468-1577 | [6 empty] | YEAR: | 2005
[17 empty] | NGVD | NGVD | NGVD |  |  | NGVD | NGVD | NGVD
| 1 | 46.9 | 90 | 26 | 130 | 6.9 | 480 | 194 | 6 | 84 | [5 empty] | 1 | 33.19 | 34.86 | 33.74 |  |  | 43.23 | 43.4 | 43.37 | [35 empty] | a) | WEEK OF | SEPTEMBER |  | Type of Sludge |  |  | Disopsal Site |  |  | Cubic Yards
| 2 | 36.2 | 112 | 24 | 133 | 6.9 | 550 | 192 | 6 | 84 | [5 empty] | 2 | 33.27 | 35.2 | 33.97 |  |  | 43.3 | 43.46 | 43.41
| 3 | 34.6 | 90 | 12 | 120 | 7 | 540 | 194 | 5 | 84 | [5 empty] | 3 | 33.21 | 34.69 | 33.87 |  |  | 43.38 | 43.56 | 43.48 | [36 empty] | FIRST THRU SEVENTH |  |  | GRIT |  |  | Central Landfill |  |  | 0
| 4 | 28 | 44 | 0 | 116 | 7 | 470 | 196 | 7 | 84 | [5 empty] | 4 | 33.36 | 34.51 | 33.86 |  |  | 43.48 | 43.59 | 43.5
| 5 | 31.9 | 66 | 20 | 121 | 7.1 | 460 | 198 | 5 | 83 | [5 empty] | 5 | 28.81 | 33.91 | 31.08 |  |  | 38.47 | 43.58 | 40.26 | [36 empty] | EIGHT THRU FORTEENTH |  |  | GRIT |  |  | Central Landfill |  |  | 0
| 6 | 32.7 | 82 | 20 | 124 | 6.9 | 680 | 196 | 4 | 84 | [5 empty] | 6 | 28.59 | 33.75 | 31.81 |  |  | 37.27 | 43.21 | 41.62 | [36 empty] | FIFTHTEENTH THRU
| 7 | 16.4 | 40 | 24 | 158 | 6.7 | 550 | 196 | 5 | 83 | [5 empty] | 7 | 32.84 | 34.85 | 33.69 |  |  | 43.19 | 43.41 | 43.35 | [36 empty] | TWENTY SECOND |  |  | GRIT |  |  | Central Landfill |  |  | 10
| 8 | 45 | 32 | 16 | 130 | 6.9 | 500 | 189 | 5 | 83 | [5 empty] | 8 | 33.15 | 34.95 | 34 |  |  | 43.35 | 43.54 | 43.46 | [36 empty] | TWENTY THIRD THRU
| 9 | 76.9 | 152 | 70 | 135 | 7 | 550 | 191 | 5 | 83 | [5 empty] | 9 | 33.23 | 35.43 | 34.24 |  |  | 43.46 | 43.62 | 43.5 | [36 empty] | THIRTY FIRST |  |  | GRIT |  |  | Central Landfill |  |  | 20
| 10 | 86 | 46 | 0 | 145 | 7 | 610 | 194 | 6 | 83 | [5 empty] | 10 | 32.8 | 34.83 | 33.97 |  |  | 43.47 | 43.62 | 43.51
| 11 | 54.9 | 84 | 30 | 192 | 7.2 | 560 | 208 | 5 | 83 | [5 empty] | 11 | 32.98 | 34.88 | 33.83 |  |  | 43.44 | 43.62 | 43.51 | [35 empty] | b) | WEEK OF | SEPTEMBER |  | Type of Sludge |  |  | Disopsal Site |  |  | Cubic Yards
| 12 | 57.9 | 28 | 4 | 126 | 7.1 | 690 | 188 | 4 | 83 | [5 empty] | 12 | 29.5 | 33.53 | 31.47 |  |  | 39.73 | 43.57 | 41.04
| 13 | 58.3 | 122 | 24 | 125 | 7.1 | 710 | 192 | 5 | 83 | [5 empty] | 13 | 29.1 | 34.74 | 32.38 |  |  | 39.68 | 43.25 | 41.95 | [36 empty] | FIRST THRU SEVENTH |  |  | RAGS |  |  | Central Landfill |  |  | 10
| 14 | 58.3 | 100 | 28 | 134 | 6.9 | 540 | 216 | 5 | 84 | [5 empty] | 14 | 32.78 | 34.59 | 33.59 |  |  | 43.14 | 43.38 | 43.3
| 15 | 63.9 | 76 | 12 | 111 | 6.7 | 550 | 214 | 5 | 84 | [5 empty] | 15 | 32.98 | 34.64 | 33.71 |  |  | 43.19 | 43.39 | 43.34 | [36 empty] | EIGHT THRU FORTEENTH |  |  | RAGS |  |  | Central Landfill |  |  | 10
| 16 | 53.36 | 48 | 14 | 159 | 7 | 600 | 203 | 5 | 84 | [5 empty] | 16 | 33.22 | 34.73 | 33.87 |  |  | 43.22 | 43.42 | 43.37 | [36 empty] | FIFTHTEENTH THRU
| 17 | 53.11 | 106 | 20 | 168 | 7.1 | 660 | 202 | 5 | 84 | [5 empty] | 17 | 33.39 | 34.62 | 34.01 |  |  | 43.27 | 43.45 | 43.42 | [36 empty] | TWENTY SECOND |  |  | RAGS |  |  | Central Landfill |  |  | 0
| 18 | 67.3 | 90 | 20 | 141 | 7 | 650 | 208 | 5 | 84 | [5 empty] | 18 | 33.57 | 34.73 | 34.12 |  |  | 43.3 | 43.45 | 43.44 | [36 empty] | TWENTY THIRD THRU
| 19 | 70.78 | LS | LS | 189 | 7 | 690 | LS | 5 | 84 | [5 empty] | 19 | 28.95 | 34.63 | 31.83 |  |  | 38.21 | 43.45 | 40.9 | [36 empty] | THIRTY FIRST |  |  | RAGS |  |  | Central Landfill |  |  | 10
| 20 | 65.89 | 40 | 20 | 153 | 7 | 710 | 200 | 3 | 84 | [5 empty] | 20 | 28.41 | 33.57 | 31.84 |  |  | 38.12 | 43.14 | 41.44 | [36 empty] | BCSR = Broward County Septage Receiving
| 21 | 37.47 | 18 | 6 | 139 | 7 | 600 | 196 | 4 | 84 | [5 empty] | 21 | 32.98 | 34.64 | 33.73 |  |  | 43.06 | 43.24 | 43.07 | [35 empty] | c) | WEEK OF | SEPTEMBER |  | Type of Sludge |  |  | Disopsal Site |  |  | Gallons
| 22 | 61.5 | 88 | 24 | 127 | 7 | 540 | 194 | 7 | 84 | [5 empty] | 22 | 19.72 | 34.4 | 26.95 |  |  | 36.17 | 43.26 | 39.46
| 23 | 64.47 | 44 | 10 | 157 | 7 | 580 | 190 | 5 | 84 | [5 empty] | 23 | 18.96 | 25.03 | 23.18 |  |  | 36.08 | 42.95 | 40.97 | [36 empty] | FIRST THRU SEVENTH |  |  | VAC/Plastic & Rags |  |  | BCSR |  |  | 0
| 24 | 63.15 | 68 | 0 | 195 | 7.1 | 550 | 192 | 5 | 84 | [5 empty] | 24 | 24.19 | 25.42 | 24.69 |  |  | 42.89 | 43.07 | 42.99
| 25 | 63.2 | 106 | 13 | 168 | 7.1 | 570 | 198 | 5 | 83 | [5 empty] | 25 | 23.95 | 25.48 | 24.66 |  |  | 43.02 | 43.21 | 43.04 | [36 empty] | EIGHT THRU FORTEENTH |  |  | VAC/Plastic & Rags |  |  | BCSR |  |  | 0
| 26 | 71 | 90 | 10 | 186 | 7.1 | 590 | 188 | 5 | 83 | [5 empty] | 26 | 24.07 | 25.75 | 24.8 |  |  | 43.16 | 43.36 | 43.36 | [36 empty] | FIFTHTEENTH THRU
| 27 | 123 | 100 | 12 | 157 | 7 | 620 | 193 | 5 | 83 | [5 empty] | 27 | 19.47 | 24.55 | 21.54 |  |  | 36.47 | 43.39 | 38.53 | [36 empty] | TWENTY SECOND |  |  | VAC/Plastic & Rags |  |  | BSCR |  |  | 0
| 28 | 66 | 98 | 24 | 210 | 7 | 700 | 190 | 5 | 84 | [5 empty] | 28 | 19.63 | 25.13 | 23.12 |  |  | 35.98 | 43.01 | 41.08 | [36 empty] | TWENTY THIRD THRU
| 29 | 81 | 83 | 38 | 163 | 7.1 | 640 | 196 | 5 | 84 | [5 empty] | 29 | 24.07 | 25.51 | 24.68 |  |  | 42.99 | 43.25 | 43.04 | [36 empty] | THIRTY FIRST |  |  | VAC/Plastic & Rags |  |  | BSCR |  |  | 0
| 30 | 102 | 96 | 4 | 144 | 7 | 650 | 197 | 5 | 83.1 | [5 empty] | 30 | 24.26 | 25.4 | 24.77 |  |  | 43.17 | 43.31 | 43.26 | [35 empty] | TOTALS
[61 empty] | a) | 30 | cu.yds |  | GRIT |  | Signature
| TOTAL | 1771.13 | 2239 | 525 | 4456 | 209.9 | 17790 | 5705 | 152 | 2508.1 | [5 empty] | TOTAL | 868.63 | 962.95 | 917 |  |  | 1240.89 | 1301.16 | 1273.97 | [36 empty] | b) | 30 | cu.yds |  | RAGS |  | Title
| AVERAGE | 59.0377 | 77.2069 | 20.1923 | 148.5333 | 6.9967 | 593 | 196.7241 | 5.0667 | 83.6033 | [5 empty] | AVERAGE | 28.9543 | 32.0983 | 30.5667 |  |  | 41.363 | 43.372 | 42.4657 | [36 empty] | c) | 0 | gal. |  | VAC/Plastic & Rags |  | Date
[16 empty] | MAXIMUM | 33.57 | 35.43 | 34.24 |  |  | 43.48 | 43.62 | 43.51
[16 empty] | MINIMUM | 18.96 | 24.55 | 21.54 |  |  | 35.98 | 42.95 | 38.53 | [36 empty] | * Sludge Reports should be submitted along with the monthly operating reports to Broward County Department
of Natural Resource Protection, 218 S. W. 1st Avenue, Fort Lauderdale, Florida 33301
PAGE 3
PAGE 21
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
[5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [13 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
[5 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [13 empty] | MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
[5 empty] | MONTHLY OPERATIONAL REPORT | [13 empty] | MONITORING WELL THREE |  |  |  | 1/07/04 thru 1/06/09
[5 empty] | EFFLUENT DATA PART 1 | [11 empty] | MW-3 | I.D. #: 5066A11310 |  |  | PERMIT # 0054569-142-UO
RUN DATE
[16 empty] | 2026-07-30 |  | UPPER MONITOR ZONE |  |  |  |  | LOWER MONITOR ZONE
| RUN DATE | [15 empty] | MIN | MAX | AVG |  |  | MIN | MAX | AVG
| 2026-07-30 | [14 empty] | SEPTEMBER | FT HEAD | FT HEAD | FT HEAD |  |  | FT HEAD | FT HEAD | FT HEAD
[14 empty] | BOD | TSS | 2005 | ABOVE | ABOVE | ABOVE |  |  | ABOVE | ABOVE | ABOVE
| SEPTEMBER | EFFLUENT | EFFL. TSS | EFFL. SS | EFFLUENT | EFFL. | EFFL. | EFFL. | EFFL. | EFFL. | TDS |  |  | MONTHLY AVG OVER 30 | MONTHLY AVG OVER 30 |  | NGVD | NGVD | NGVD |  |  | NGVD | NGVD | NGVD
| 2005 | CBOD | TOTAL | FIXED | COD | CL_ | ALK. | TURB. | COND. | TEMP.(F) |  |  |  | 0 | 0 | 1 | 33.7 | 33.91 | 33.82 |  |  | 45.99 | 46.14 | 46.02
[14 empty] | WEKKLY OVER 45 | WEKKLY OVER 45 | 2 | 33.77 | 34.02 | 33.89 |  |  | 46.06 | 46.2 | 46.06
| 1 | 2.2 | 23 | 5 | 40.4 | 510 | 192 | 3.94 | 2190 | 87 | 1022 | 1 |  | 0 | 0 | 3 | 33.86 | 34.13 | 33.97 |  |  | 46.13 | 46.3 | 46.23
| 2 | 2.09 | 10 | 3 | 35.4 | 570 | 184 | 5.27 | 2320 | 87 | 1102 | 1 |  | SINGLE DAY OVER 60 | SINGLE DAY OVER 60 | 4 | 33.99 | 34.21 | 34.02 |  |  | 46.25 | 46.33 | 46.34
| 3 | 0.79 | LS | LS | 33.7 | 550 | 188 | 4.55 | 2280 | 87 | 1086 | 1 |  | 0 | 0 | 5 | 24.64 | 34.16 | 27.89 |  |  | 39.72 | 46.33 | 41.89
| 4 | 1 | 12 | 0 | 31 | 490 | 184 | 4.58 | 1970 | 87 | 945 | 1 |  | 0 | 0 | 6 | 24.47 | 34.28 | 31.16 |  |  | 39.69 | 45.91 | 44.03
| 5 | 0.99 | 10 | 8 |  | 500 | 192 | 4.16 | 2020 | 86 | 1019 | 1 |  |  |  | 7 | 34.17 | 34.49 | 34.38 |  |  | 45.91 | 46.12 | 45.97
| 6 | 1.66 | 9 | 3 | 32.8 | 620 | 192 | 3.76 | 2500 | 86 | 1208 | 1 |  |  |  | 8 | 34.32 | 34.62 | 34.47 |  |  | 46.09 | 46.27 | 46.17
| 7 | 1 | 7 | 5 | 35.2 | 530 | 192 | 2.73 | 2240 | 86 | 1079 | 1 | 1.39 | 1.39 | 11.8333 | 9 | 34.4 | 34.7 | 34.55 |  |  | 46.2 | 46.37 | 46.37
| 8 | 2.03 | 11 | 0 | 38.1 | 610 | 186 | 4.25 | 2460 | 86 | 1228 | 1 |  | 1.3657 | 9.8333 | 10 | 34.35 | 34.63 | 34.49 |  |  | 46.17 | 46.38 | 46.36
| 9 | 4.87 | 27 | 17 | 36.4 | 560 | 185 | 4.21 | 2420 | 86 | 1114 | 1 |  | 1.7629 | 12.6667 | 11 | 34.29 | 34.61 | 34.46 |  |  | 46.19 | 46.38 | 46.38
| 10 | 2.18 | 14 | 7 | 37.4 | 620 | 189 | 3.94 | 2500 | 86 | 1257 | 1 |  | 1.9614 | 12.8571 | 12 | 20.13 | 34.52 | 24.65 |  |  | 40.77 | 46.32 | 42.62
| 11 | 2.51 | 11 | 8 | 48.1 | 520 | 202 | 3.17 | 2220 | 86 | 1117 | 1 |  | 2.1771 | 12.7143 | 13 | 20.05 | 33.89 | 29.32 |  |  | 40.74 | 45.94 | 44.25
| 12 | 2.28 | 5 | 1 | 37.6 | 690 | 202 | 3.35 | 2830 | 0 | 1390 | 1 |  | 2.3614 | 12 | 14 | 33.76 | 34.13 | 33.91 |  |  | 45.85 | 46.08 | 45.95
| 13 | 1.8 | 21 | 2 | 40.6 | 790 | 188 | 3.9 | 3100 | 86 | 1597 | 1 |  | 2.3814 | 13.7143 | 15 | 33.89 | 34.21 | 34.02 |  |  | 45.91 | 46.11 | 46
| 14 | 3.07 | 12 | 5 | 35.9 | 550 | 212 | 4.33 | 2320 | 86 | 1597 | 1 | 2.6771 | 2.6771 | 14.4286 | 16 | 33.97 | 34.29 | 34.11 |  |  | 45.95 | 46.14 | 46
| 15 | 2.84 | 10 | 1 | 39.5 | 560 | 202 | 5.77 | 2370 | 86 | 1185 | 1 |  | 2.7929 | 14.2857 | 17 | 34.04 | 34.33 | 34.2 |  |  | 46.02 | 46.18 | 46.06
| 16 | 2.43 | 14 | 10 | 31.3 | 550 | 194 | 5.97 | 2530 | 86 | 1340 | 1 |  | 2.4443 | 12.4286 | 18 | 34.06 | 34.36 | 34.26 |  |  | 46.07 | 46.19 | 46.08
| 17 | 3.99 | 20 | 9 | 34.4 | 680 | 184 | 5.7 | 2590 | 86 | 1298 | 1 |  | 2.7029 | 13.2857 | 19 | 25.69 | 34.33 | 29.85 |  |  | 38.95 | 46.18 | 42.45
| 18 | 1.29 | 15 | 5 | 34.9 | 660 | 190 | 4.08 | 2660 | 87 | 1350 | 1 |  | 2.5286 | 13.8571 | 20 | 25.48 | 34.48 | 31.5 |  |  | 38.92 | 45.82 | 43.57
| 19 | 1.42 | LS | LS | 36 | 720 | LS | LS | LS | 87 | LS | 1 |  | 2.4057 | 15.3333 | 21 | 34.29 | 34.63 | 34.44 |  |  | 45.76 | 45.93 | 45.89
| 20 | 1 | 8 | 0 | 34.5 | 660 | 188 | 5.1 | 2620 | 86 | 1336 | 1 |  | 2.2914 | 13.1667 | 22 | 23.63 | 34.65 | 28.68 |  |  | 37.63 | 45.96 | 41.44
| 21 | 5.56 | 6 | 4 | 34.3 | 620 | 184 | 6.8 | 2410 | 86 | 1154 | 1 | 2.6471 | 2.6471 | 12.1667 | 23 | 23.42 | 34.09 | 31.02 |  |  | 37.57 | 45.66 | 43.31
| 22 | 2.37 | 17 | 6 | 39.9 | 560 | 190 | 5.55 | 2390 | 86 | 1193 | 1 |  | 2.58 | 13.3333 | 24 | 33.95 | 34.27 | 34.07 |  |  | 45.62 | 45.81 | 45.76
| 23 | 2.97 | 21 | 6 | 35.4 | 600 | 178 | 6.45 | 2450 | 86 | 1263 | 1 |  | 2.6571 | 14.5 | 25 | 34.08 | 34.39 | 34.29 |  |  | 45.75 | 45.95 | 45.88
| 24 | 3.3 | 16 | 0 | 39.5 | 590 | 186 | 5.46 | 2410 | 86 | 1172 | 1 |  | 2.5586 | 13.8333 | 26 | 34.22 | 34.48 | 34.38 |  |  | 45.9 | 46.11 | 45.99
| 25 | 2.87 | 16 | 4 | 38.1 | 600 | 186 | 5.51 | 2400 | 86 | 1187 | 1 |  | 2.7843 | 14 | 27 | 21.07 | 34.45 | 25.09 |  |  | 37.4 | 46.12 | 40.04
| 26 | 4 | 14 | 3 | 47 | 600 | 188 | 6.27 | 2470 | 86 | 1226 | 1 |  | 3.1529 | 14 | 28 | 21.06 | 33.84 | 30.19 |  |  | 37.41 | 45.72 | 43.27
| 27 | 7 | 17 | 5 | 40.9 | 610 | 198 | 7.07 | 2640 | 86 | 1271 | 1 |  | 4.01 | 15.2857 | 29 | 33.79 | 34.15 | 33.97 |  |  | 45.71 | 45.98 | 45.88
| 28 | 5 | 8 | 1 | 37.1 | 680 | 198 | 7.47 | 2680 | 86 | 1368 | 1 |  | 3.93 | 15.5714 | 30 | 34.02 | 34.21 | 34.04 |  |  | 45.9 | 46.04 | 45.99
| 29 | 7 | 8 | 1 | 43.9 | 660 | 202 | 7.13 | 2470 | 86 | 1360 | 1 |  | 4.5914 | 14.2857
| 30 | 5 | 14 | 0 | 42.9 | 670 | 197 | 6.63 | 2690 | 86 | 1344 | 1 |  | 4.8814 | 13.2857 | TOTAL | 910.56 | 1029.46 | 973.09 |  |  | 1308.23 | 1382.97 | 1348.25
[12 empty] | 0 | 4.39 | 5.145 | 12.8333 | AVERAGE | 30.352 | 34.3153 | 32.4363 |  |  | 43.6077 | 46.099 | 44.9417
| TOTAL | 86.51 | 376 | 119 | 1092.2 | 18130 | 5553 | 147.1 | 71150 | 2500 | 35808 |  |  |  |  | MAXIMUM | 34.4 | 34.7 | 34.55 |  |  | 46.25 | 46.38 | 46.38
| AVERAGE | 2.8837 | 13.4286 | 5.1739 | 37.6621 | 604.3333 | 191.4828 | 5.0724 | 2453.4483 | 86.2069 | 1234.7586 |  |  | 2.8072 | 13.42 | MINIMUM | 20.05 | 33.84 | 24.65 |  |  | 37.4 | 45.66 | 40.04
| MAXIMUM | 7 | 27
[5 empty] | PAGE 4 | [14 empty] | PAGE 22
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
[5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [13 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
[5 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [13 empty] | MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
[5 empty] | MONTHLY OPERATIONAL REPORT | [13 empty] | REGIONAL MONITORING WELL ONE
[5 empty] | EFFLUENT DATA PART 2 | [13 empty] | RMW-1 |  |  |  | 1/07/04 thru 1/06/09
[16 empty] | RUN DATE |  |  |  |  | PERMIT # 0054569-142-UO
[16 empty] | 2026-07-30 |  | UPPER MONITOR ZONE |  |  |  |  | LOWER MONITOR ZONE
RUN DATE | [16 empty] | MIN | MAX | AVG |  |  | MIN | MAX | AVG
2026-07-30 | [15 empty] | SEPTEMBER | FT HEAD | FT HEAD | FT HEAD |  |  | FT HEAD | FT HEAD | FT HEAD
[16 empty] | 2005 | ABOVE | ABOVE | ABOVE |  |  | ABOVE | ABOVE | ABOVE
| SEPTEMBER | EFF. BACT. | EFF. BACT. | FREE | TOTAL | EFFL. | EFF PH | EFF PH | EFF. SAP | AVG. | Sufates | [5 empty] | NGVD | NGVD | NGVD |  |  | NGVD | NGVD | NGVD
| 2005 | TOTAL | FECAL | CL2 | CL2 | pH | MIN | MAX | TEMP.(C) | BLK. | [5 empty] | 1 | 45.08 | 45.23 | 45.15 |  |  | 23.21 | 23.33 | 23.27
[16 empty] | 2 | 45.08 | 45.22 | 45.16 |  |  | 23.23 | 23.31 | 23.27
| 1 | TNTC | TNTC | 0 | 0 | 6.7 | 6.7 | 6.7 | 4 | 17 | 108.75 |  |  |  |  | 3 | 45.11 | 45.22 | 45.17 |  |  | 23.24 | 23.33 | 23.29
| 2 | TNTC | TNTC | 0 | 0.6 | 6.6 | 6.4 | 6.4 | 0.5 | 19 | 111.5 |  |  |  |  | 4 | 45.08 | 45.22 | 45.14 |  |  | 23.25 | 23.35 | 23.3
| 3 | 0 | 9 | 0 | 1 | 6.6 | 6.6 | 6.7 | 2.8 | 32 | 107.25 |  |  |  |  | 5 | 42.41 | 45.13 | 43.51 |  |  | 21.18 | 23.31 | 22.22
| 4 | 134 | 9 | 0 | 1.1 | 6.6 | 6.6 | 6.7 | 4 | 32 | 102.75 |  |  |  |  | 6 | 42.36 | 44.7 | 43.85 |  |  | 20.73 | 22.39 | 21.93
| 5 | 188 | 0 | 0 | 0.9 | 6.6 | 6.6 | 6.6 | 4 | 29 | 110.25 |  |  |  |  | 7 | 32.81 | 44.92 | 44.79 |  |  | 20.42 | 22.58 | 22.49
| 6 | 690 | 0 | 0 | 0.9 | 6.7 | 6.6 | 6.9 | 4 | 20 | 121.5 |  |  |  |  | 8 | 26.6 | 45 | 44.75 |  |  | 20.34 | 22.63 | 22.52
| 7 | TNTC | 60000 | 0 | 0 | 6.7 | 6.6 | 6.9 | 4 | 21 | 115.25 |  |  |  |  | 9 | 44.99 | 45.11 | 45.05 |  |  | 22.58 | 22.72 | 22.64
| 8 | TNTC | TNTC | 0 | 0 | 6.7 | 6.6 | 6.9 | 4 | 18 | 109.75 |  |  |  |  | 10 | 45.04 | 45.13 | 45.08 |  |  | 22.56 | 22.71 | 22.63
| 9 | TNTC | TNTC | 0 | 0 | 6.7 | 6.6 | 6.8 | 10.4 | 20 | 122.5 |  |  |  |  | 11 | 45.04 | 45.14 | 45.1 |  |  | 22.51 | 22.67 | 22.61
| 10 | TNTC | TNTC | 0 | 0 | 6.7 | 6.6 | 6.7 | 4 | 33 | 104.75 |  |  |  |  | 12 | 45.04 | 45.16 | 45.1 |  |  | 22.53 | 22.7 | 22.61
| 11 | TNTC | TNTC | 0 | 0 | 6.6 | 6.6 | 6.7 | 4 | 28 | 128.5 |  |  |  |  | 13 | 45.04 | 45.15 | 45.11 |  |  | 22.53 | 22.7 | 22.63
| 12 | TNTC | TNTC | 0 | 0 | 6.7 | 6.6 | 7 | 0 | 27 | 141.5 |  |  |  |  | 14 | 44.95 | 45.1 | 45.02 |  |  | 22.48 | 22.63 | 22.58
| 13 | TNTC | 39000 | 0 | 0 | 6.7 | 6.7 | 6.8 | 4 | 24 | 115.75 |  |  |  |  | 15 | 44.84 | 45.01 | 44.92 |  |  | 22.45 | 22.58 | 22.52
| 14 | TNTC | 50000 | 0.2 | 0.8 | 6.7 | 6.6 | 6.9 | 4 | 20 | 115.75 |  |  |  |  | 16 | 44.78 | 44.92 | 44.85 |  |  | 22.46 | 22.56 | 22.51
| 15 | 380 | 0 | 0.1 | 0.9 | 6.7 | 6.6 | 6.8 | 4 | 18 | 141 |  |  |  |  | 17 | 44.78 | 44.9 | 44.84 |  |  | 22.48 | 22.55 | 22.52
| 16 | 8 | 0 | 0 | 0.7 | 6.6 | 6.5 | 6.7 | 4.5 | 17 | 120 |  |  |  |  | 18 | 44.76 | 44.88 | 44.82 |  |  | 22.5 | 22.55 | 22.52
| 17 | 290 | 0 | 0 | 1 | 6.6 | 6.6 | 6.6 | 7.6 | 34 | 122 |  |  |  |  | 19 | 44.74 | 44.87 | 44.81 |  |  | 22.5 | 22.6 | 22.54
| 18 | 0 | 0 | 0 | 0.9 | 6.6 | 6.6 | 6.7 | 4 | 27 | 124.5 |  |  |  |  | 20 | 0.25 | 44.97 | 44.87 |  |  | 0.25 | 22.72 | 22.62
| 19 | 9 | 0 | 0 | 0.9 | 6.6 | 6.5 | 6.8 | 4.4 | 16 | 133.25 |  |  |  |  | 21 | 44.81 | 44.92 | 44.86 |  |  | 22.53 | 22.64 | 22.58
| 20 | TNTC | TNTC | 0.1 | 0.8 | 6.7 | 6.6 | 6.8 | 4 | 22 | 113.25 |  |  |  |  | 22 | 44.8 | 44.87 | 44.83 |  |  | 22.51 | 22.62 | 22.56
| 21 | TNTC | TNTC | 0 | 0.8 | 6.8 | 6.7 | 6.8 | 4 | 23 | 125.5 |  |  |  |  | 23 | 44.76 | 44.85 | 44.8 |  |  | 22.47 | 22.59 | 22.55
| 22 | 0 | 10 | 0 | 0.8 | 6.7 | 6.5 | 6.9 | 4 | 18 | 108.25 |  |  |  |  | 24 | 44.77 | 44.86 | 44.81 |  |  | 22.45 | 22.59 | 22.52
| 23 | 0 | 10 | 0 | 0.8 | 6.7 | 6.6 | 6.7 | 0.7 | 21 | 116.5 |  |  |  |  | 25 | 44.83 | 44.95 | 44.89 |  |  | 22.46 | 22.62 | 22.55
| 24 | 0 | 0 | 0 | 1 | 6.6 | 6.6 | 6.6 | 4.6 | 38 | 117 |  |  |  |  | 26 | 44.93 | 45.05 | 45 |  |  | 22.54 | 22.69 | 22.62
| 25 | 0 | 0 | 0 | 0.9 | 6.6 | 6.6 | 6.6 | 4 | 29 | 120 |  |  |  |  | 27 | 45.01 | 45.1 | 45.06 |  |  | 22.58 | 22.7 | 22.65
| 26 | 27 | 0 | 0 | 0.7 | 6.7 | 6.6 | 6.8 | 4 | 21 | 119.25 |  |  |  |  | 28 | 44.94 | 45.09 | 45.01 |  |  | 22.55 | 22.67 | 22.63
| 27 | 45 | 9 | 0 | 0.7 | 6.6 | 6.5 | 6.8 | 4 | 20 | 124.5 |  |  |  |  | 29 | 44.92 | 45.05 | 44.99 |  |  | 22.57 | 22.71 | 22.64
| 28 | 152 | 9 | 0 | 0.6 | 6.7 | 6.6 | 6.7 | 4 | 19 | 126.75 |  |  |  |  | 30 | 44.9 | 45.04 | 44.98 |  |  | 22.58 | 22.68 | 22.63
| 29 | 152 | 0 | 0 | 0.6 | 6.7 | 6.6 | 6.8 | 3 | 15 | 111.5
| 30 | 213 | 0 | 0 | 0.7 | 6.7 | 6.6 | 6.7 | 3.2 | 18 | 110.75 |  |  |  |  | TOTAL | 1267.45 | 1350.76 | 1346.32 |  |  | 648.67 | 682.43 | 679.15
[16 empty] | AVERAGE | 42.2483 | 45.0253 | 44.8773 |  |  | 21.6223 | 22.7477 | 22.6383
| TOTAL | 2288 | 149056 | 0.4 | 18.1 | 199.9 | 197.7 | 202.5 | 117.7 | 696 | 3549.75 |  |  |  |  | MAXIMUM | 45.11 | 45.23 | 45.17 |  |  | 23.25 | 23.35 | 23.3
| AVERAGE | 127.1111 | 7097.9048 | 0.013333 | 0.60333 | 6.6633 | 6.59 | 6.75 | 3.7968 | 23.2 | 118.325 |  |  |  |  | MINIMUM | 0.25 | 44.7 | 43.51 |  |  | 0.25 | 22.39 | 21.93
[7 empty] | 6.4 | 7
[7 empty] | MIN | MAX
PAGE 5
PAGE 23
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
NUTRIENTS
RUN DATE
| 2026-07-30 |  | INFLUENT | [5 empty] | EFFLUENT
| SEPTEMBER | INFLUENT | INFLUENT | INFLUENT | INFLUENT |  | EFFL. | EFFL. | EFFL. | EFFL.
| 2005 | NH-3 | N03-N | TKN | TOT P |  | NH-3 | N03-N | TKN | TOT P
| 1 | 9.5 |  | 18 | 3.3 |  | 7.8 | 0.1 | 10 | 0.93
| 2 | 9.8 |  | 14 | 2.1 |  | 7.8 | 0.2 | 9.5 | 0.97
| 3 | 10 | 0.053 | 13 | 2 |  | 8.1 | 0.25 | 8.6 | 0.78
| 4 | 11 | 0.0086 | 13 | 2 |  | 7.1 | 0.24 | 7.7 | 0.88
| 5 | 7.5 | 0.032 | 9.2 | 1.9 |  | 5 | 0.024 | 6.1 | 0.5
| 6 | 9.7 | 0.066 | 16 | 2.1 |  | 6.2 | 0.37 | 10 | 0.48
| 7 | 8.8 | 0.049 | 14 | 1.9 |  | 6.5 | 0.31 | 10 | 0.62
| 8 | 9.4 | 0.083 | 14 | 2 |  | 7.6 | 0.31 | 9.6 | 1
| 9 | 9.5 | 0.083 | 18 | 2.2 |  | 6.8 | 0.27 | 12 | 0.74
| 10 | 9.5 | 0.062 | 17 | 2 |  | 8.9 | 0.74 | 10 | 0.79
| 11 | 9 | 0.069 | 15 | 1.8 |  | 6.4 | 0.21 | 10 | 0.77
| 12 | 9.4 | 0.075 | 17 | 2 |  | 8 | 0.5 | 12 | 0.56
| 13 | 12 | 0.093 | 19 | 2.3 |  | 9.9 | 0.066 | 12 | 0.78
| 14 | 13 | 0.07 | 17 | 2.1 |  | 8.8 | 0.96 | 13 | 0.96
| 15 | 9.4 | 0.046 | 18 | 2.4 |  | 10 | 0.12 | 14 | 1.7
| 16 | 15 | 0.028 | 17 | 2.5 |  | 9.6 | 0.82 | 10 | 1.5
| 17 | 14 | 0.043 | 16 | 2.1 |  | 7.2 | 0.43 | 9.1 | 1.3
| 18 | 13 | 0.12 | 17 | 2.4 |  | 8.8 | 0.31 | 8.8 | 0.95
| 19 | 13 | 0.03 | 17 | 2.4 |  | 9 | 0.31 | 9.5 | 0.95
| 20 | 12 | 0.095 | 15 | 2 |  | 7.2 | 0.34 | 8.3 | 0.86
| 21 | 6.7 |  | 17 | 2 |  | 7.5 | 0.26 | 12 | 1
| 22 | 8.8 | 0.1 | 16 | 1.9 |  | 8.4 | 0.25 | 12 | 1.5
| 23 | 10 | 0.016 | 15 | 2 |  | 7.2 | 0.54 | 0 | 1.4
| 24 | 12 | 0.022 | 19 | 2.6 |  | 6 | 0.24 | 11 | 1.4
| 25 | 8.1 | 0.012 | 19 | 2.4 |  | 7.2 | 0.27 | 12 | 1
| 26 | 12 | 0.11 | 18 | 2.6 |  | 8.8 | 0.29 | 12 | 1.3
| 27 | 12 | 0.086 | 18 | 2.5 |  | 7.6 | 0.34 | 13 | 1.6
| 28 | 12 | 0.11 |  |  |  | 7.4 | 0.28
| 29 | 12 | 0.079 |  |  |  | 9.9 | 0.3
| 30 | 12 | 0.098 | 19 | 2.4 |  | 8.7 | 0.28 | 12 | 1.1
| TOTAL | 320.1 | 1.7386 | 455.2 | 61.9 | TOT. | 235.4 | 9.93 | 284.2 | 28.32
| AVERAGE | 10.67 | 0.064393 | 16.2571 | 2.2107 | AVG. | 7.8467 | 0.331 | 10.15 | 1.0114
PAGE 6
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
REACTOR ONE PROCESS
RUN DATE
| 2026-07-30 |  | TRAIN "A" | [5 empty] | TRAIN "B"
| SEPTEMBER | MLSS | MLVSS | SS | SVI |  | MLSS | MLVSS | SS | SVI
| 2005 | "A" | "A" | "A" | "A" |  | "B" | "B" | "B" | "B"
| 1 | O/S | O/S | O/S |  |  | 2210 | 1670 | 17 | 76.9231
| 2 | O/S | O/S | O/S |  |  | 1910 | 1670 | 18 | 94.2408
| 3 | O/S | O/S | O/S |  |  | 2460 | 1720 | 22 | 89.4309
| 4 | O/S | O/S | O/S |  |  | 2400 | 2000 | 21 | 87.5
| 5 | O/S | O/S | O/S |  |  | 2600 | 1900 | 20 | 76.9231
| 6 | O/S | O/S | O/S |  |  | 2290 | 1840 | 20 | 87.3362
| 7 | O/S | O/S | O/S |  |  | 2770 | 2060 | 17 | 61.3718
| 8 | O/S | O/S | O/S |  |  | 2110 | 1640 | 16 | 75.8294
| 9 | O/S | O/S | O/S |  |  | 3220 | 2450 | 24 | 74.5342
| 10 | O/S | O/S | O/S |  |  | 3020 | 2330 | 28 | 92.7152
| 11 | O/S | O/S | O/S |  |  | 2360 | 1760 | 25 | 105.9322
| 12 | O/S | O/S | O/S |  |  | 1940 | 1560 | 20 | 103.0928
| 13 | O/S | O/S | O/S |  |  | 2570 | 2030 | 16 | 62.2568
| 14 | O/S | O/S | O/S |  |  | 1900 | 1480 | 18 | 94.7368
| 15 | O/S | O/S | O/S |  |  | 1820 | 1510 | 15 | 82.4176
| 16 | O/S | O/S | O/S |  |  | 3250 | 2440 | 18 | 55.3846
| 17 | O/S | O/S | O/S |  |  | 2850 | 2230 | 21 | 73.6842
| 18 | O/S | O/S | O/S |  |  | 2710 | 2240 | 18 | 66.4207
| 19 | O/S | O/S | O/S |  |  | LS | LS | LS
| 20 | O/S | O/S | O/S |  |  | 3130 | 2400 | 18 | 57.508
| 21 | O/S | O/S | O/S |  |  | 1800 | 1400 | 18 | 100
| 22 | O/S | O/S | O/S |  |  | 3360 | 2470 | 16 | 47.619
| 23 | O/S | O/S | O/S |  |  | 2890 | 2360 | 19 | 65.7439
| 24 | O/S | O/S | O/S |  |  | 3150 | 560 | 25 | 79.3651
| 25 | O/S | O/S | O/S |  |  | 2580 | 2060 | 23 | 89.1473
| 26 | O/S | O/S | O/S |  |  | 3380 | 2220 | 20 | 59.1716
| 27 | O/S | O/S | O/S |  |  | 1810 | 1480 | 17 | 93.9227
| 28 | O/S | O/S | O/S |  |  | 1630 | 1410 | 16 | 98.1595
| 29 | O/S | O/S | O/S |  |  | 1360 | 1220 | 14 | 102.9412
| 30 | O/S | O/S | O/S |  |  | ER | ER | 20
|  | O/S | O/S | O/S
| TOTAL | 0 | 0 | 0 |  |  | 69480 | 52110 | 560
| AVERAGE | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 2481.4286 | 1861.0714 | 19.3103 | 77.8195
PAGE 7
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
REACTOR TWO PROCESS
RUN DATE
| 2026-07-30 |  | TRAIN "C" | [5 empty] | TRAIN "D"
| SEPTEMBER | MLSS | MLVSS | SS | SVI |  | MLSS | MLVSS | SS | SVI
| 2005 | "C" | "C" | "C" | "C" |  | "D" | "D" | "D" | "D"
| 1 | O/S | O/S | O/S |  |  | 1800 | 1430 | 15 | 83.3333
| 2 | O/S | O/S | O/S |  |  | 4220 | 2150 | 17 | 40.2844
| 3 | O/S | O/S | O/S |  |  | 2390 | 2140 | 23 | 96.2343
| 4 | O/S | O/S | O/S |  |  | 2850 | 2130 | 21 | 73.6842
| 5 | O/S | O/S | O/S |  |  | 2820 | 2320 | 21 | 74.4681
| 6 | O/S | O/S | O/S |  |  | 2790 | 2100 | 18 | 64.5161
| 7 | O/S | O/S | O/S |  |  | 3550 | 2500 | 15 | 42.2535
| 8 | O/S | O/S | O/S |  |  | 2380 | 1520 | 14 | 58.8235
| 9 | O/S | O/S | O/S |  |  | 2350 | 1860 | 25 | 106.383
| 10 | O/S | O/S | O/S |  |  | 3020 | 2160 | 28 | 92.7152
| 11 | O/S | O/S | O/S |  |  | 2490 | 1940 | 25 | 100.4016
| 12 | O/S | O/S | O/S |  |  | 2160 | 1530 | 20 | 92.5926
| 13 | O/S | O/S | O/S |  |  | 2650 | 1990 | 18 | 67.9245
| 14 | O/S | O/S | O/S |  |  | 1980 | 1540 | 18 | 90.9091
| 15 | O/S | O/S | O/S |  |  | 2190 | 1770 | 15 | 68.4932
| 16 | O/S | O/S | O/S |  |  | 3020 | 2100 | 18 | 59.6026
| 17 | O/S | O/S | O/S |  |  | 2700 | 2050 | 21 | 77.7778
| 18 | O/S | O/S | O/S |  |  | 2370 | 1930 | 19 | 80.1688
| 19 | O/S | O/S | O/S |  |  | LS | LS | LS
| 20 | O/S | O/S | O/S |  |  | 2140 | 1740 | 20 | 93.4579
| 21 | O/S | O/S | O/S |  |  | 1880 | 1520 | 17 | 90.4255
| 22 | O/S | O/S | O/S |  |  | 1970 | 1560 | 15 | 76.1421
| 23 | O/S | O/S | O/S |  |  | 3780 | 2980 | 18 | 47.619
| 24 | O/S | O/S | O/S |  |  | 2560 | 2180 | 26 | 101.5625
| 25 | O/S | O/S | O/S |  |  | 2120 | 1730 | 25 | 117.9245
| 26 | O/S | O/S | O/S |  |  | 1920 | 1650 | 18 | 93.75
| 27 | O/S | O/S | O/S |  |  | 1780 | 1450 | 16 | 89.8876
| 28 | O/S | O/S | O/S |  |  | 1310 | 1120 | 15 | 114.5038
| 29 | O/S | O/S | O/S |  |  | 1500 | 1290 | 14 | 93.3333
| 30 | O/S | O/S | O/S |  |  | ER | ER | 24
|  | O/S | O/S | O/S
| TOTAL | 0 | 0 | 0 |  |  | 68690 | 52380 | 559
| AVERAGE | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 2453.2143 | 1870.7143 | 19.2759 | 78.5739
PAGE 8
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
RAS SUMMARY
RUN DATE
2026-07-30
| SEPTEMBER | R-1 | R-2 | TOTAL | F/M | TOTAL | SLUDGE | % TOT | % FIX | % VOL.
| 2005 | TOT. RAS | TOT. RAS | MLVSS | RATIO | MLSS | AGE | RAS | RAS | RAS
|  | MGD | MGD
| 1 | 6.249 | 6.83 | 3100 | 0.78591 | 4010 | 0.85771 | 0.6 | 22.35 | 77.65
| 2 | 6.329 | 7.223 | 3820 | 0.48615 | 6130 | 1.0669 | 0.91 | 27.47 | 72.53
| 3 | 6.311 | 7.481 | 3860 | 0.47546 | 4850 | 1.016 | 1.03 | 24.76 | 75.24
| 4 | 6.33 | 7.417 | 4130 | 0.37322 | 5250 | 2.1674 | 1.01 | 16.57 | 83.43
| 5 | 6.511 | 6.547 | 4220 | 0.35417 | 5420 | 1.7527 | 1.03 | 23.21 | 76.79
| 6 | 6.16 | 7.403 | 3940 | 0.48922 | 5080 | 1.051 | 0.91 | 28.57 | 71.43
| 7 | 6.173 | 7.446 | 4560 | 0.2041 | 6320 | 2.7842 | 0.82 | 28.43 | 71.57
| 8 | 6.089 | 7.736 | 3160 | 0.76426 | 4490 | 2.6144 | 0.75 | 29.76 | 70.24
| 9 | 6.294 | 8.206 | 4310 | 0.94811 | 5570 | 0.6896 | 0.65 | 28.13 | 71.87
| 10 | 6.305 | 7.994 | 4490 | 1.0257 | 6040 | 2.4519 | 1.15 | 24.78 | 75.22
| 11 | 6.172 | 7.182 | 3700 | 0.85688 | 4850 | 0.9998 | 1.15 | 25.4 | 74.6
| 12 | 6.302 | 6.989 | 3090 | 1.0477 | 4100 | 2.6188 | 0.97 | 30 | 70
| 13 | 6.304 | 6.219 | 4020 | 0.7672 | 5220 | 0.80881 | 0.77 | 29.59 | 70.41
| 14 | 6.281 | 6.182 | 3020 | 0.96609 | 3880 | 0.77531 | 0.73 | 28.72 | 71.28
| 15 | 6.246 | 6.055 | 3280 | 0.95674 | 4010 | 1.0744 | 0.75 | 30.12 | 69.88
| 16 | 6.306 | 7.375 | 4540 | 0.57413 | 6270 | 2.6741 | 0.93 | 26.61 | 73.39
| 17 | 6.321 | 7.048 | 4280 | 0.59894 | 5550 | 1.0848 | 0.9 | 26.55 | 73.45
| 18 | 6.4 | 7.162 | 4170 | 0.77342 | 5080 | 1.1778 | 0.73 | 34.02 | 65.98
| 19 | 6.295 | 6.876 |  |  |  | NA | LS | LS
| 20 | 6.101 | 7.686 | 4140 | 0.84857 | 5270 | 2.471 | 0.64 | 32.3 | 67.7
| 21 | 6.168 | 7.21 | 2920 | 0.70742 | 3680 | 3.7085 | 0.49 | 29.67 | 70.33
| 22 | 6.158 | 7.12 | 4030 | 0.80472 | 5330 | 1.1486 | 0.58 | 33.85 | 66.15
| 23 | 6.321 | 7.508 | 5340 | 0.6125 | 6670 | 2.988 | 0.88 | 25 | 75
| 24 | 6.446 | 6.996 | 2740 | 1.1196 | 5710 | 1.7286 | 1.02 | 24.77 | 75.23
| 25 | 6.511 | 6.547 | 3790 | 0.78129 | 4700 | 0.94636 | 0.18 | 25.66 | 74.34
| 26 | 6.348 | 6.04 | 3870 | 0.8479 | 5300 | 1.2742 | 0.86 | 26.26 | 73.74
| 27 | 6.248 | 6.128 | 2930 | 1.9125 | 3590 | 0.78799 | 0.58 | 29.49 | 70.51
| 28 | 6.314 | 6.115 | 2530 | 1.1821 | 2940 | 0.66203 | 0.57 | 31.88 | 68.12
| 29 | 6.357 | 6.051 | 2510 | 1.4714 | 2860 | 0.75573 | 0.56 | 33.33 | 66.67
| 30 | 6.275 | 7.376 |  |  |  |  | 0.71 | 28.57 | 71.43
| TOTAL | 188.625 | 210.148 | 104490 |  | 138170 |  | 22.86 | 805.82 | 2094.18
| AVERAGE | 6.2875 | 7.0049 | 3731.7857 | 0.80648 | 4934.6429 | 1.2538 | 0.78828 | 27.7869 | 72.2131
PAGE 9
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
DEWATERING DATA
RUN DATE
| 2026-07-30 |  | FEED SLUDGE |  |  |  |  | FILTRATE RETURN
| SEPTEMBER | % TOT. | % FIX. | % VOL. | pH |  | % TOT. | % FIX. | % VOL. | pH
| 2005 | FEED | FEED | FEED |  |  | FILT. | FILT. | FILT.
| 1 | 1.33 | 23.31 | 76.69 | 6.42 |  | 0.15 | 66.67 | 33.33 | 6.93
2
3
4
5
| 6 | 1.78 | 21.91 | 78.09 | 6.63 |  | 0.22 | 63.64 | 36.36 | 7.13
| 7 | 1.17 | 24.79 | 75.21 | 6.43 |  | 0.18 | 66.66 | 33.34 | 7.01
| 8 | 1.59 | 23.27 | 76.73 | 6.5 |  | 0.18 | 66.67 | 33.33 | 7.15
9
10
| 11 | 1.99 | 21.11 | 78.89 | 6.31 |  | 0.29 | 48.28 | 51.72 | 6.84
| 12 | 1.69 | 21.89 | 78.11 | 6.37 |  | 0.3 | 60 | 40 | 7.16
| 13 | 1.64 | 24.39 | 75.61 | 6.48 |  | 0.26 | 65.38 | 34.62 | 7.06
| 14 | 0.59 | 32.2 | 67.8 | 6.6 |  | 0.22 | 63.64 | 36.36 | 6.99
| 15 | 1.07 | 28.04 | 71.96 | 6.53 |  | 0.19 | 68.42 | 31.58 | 6.95
16
17
| 18 | 1.17 | 25.64 | 74.36 | 6.55 |  | 0.2 | 40 | 60 | 6.88
| 19 | LS | LS |  | LS |  | LS | LS |  | LS
20
| 21 | 1.17 | 25.64 | 74.36 | 6.53 |  | 0.16 | 81.25 | 18.75 | 7.04
| 22 | 1.19 | 26.05 | 73.95 | 6.47 |  | 0.17 | 76.47 | 23.53 | 7.04
23
24
| 25 | 1.53 | 21.57 | 78.43 | 6.42 |  | 0.16 | 68.75 | 31.25 | 6.94
| 26 | 1.08 | 25.93 | 74.07 | 6.66 |  | 0.21 | 61.9 | 38.1 | 7.01
| 27 | 1.27 | 24.41 | 75.59 | 6.46 |  | 0.19 | 73.68 | 26.32 | 7
| 28 | 1.09 | 27.52 | 72.48 | 6.43 |  | 0.2 | 65 | 35 | 6.95
| 29 | 1.24 | 24.19 | 75.81 | 6.31 |  | 0.2 | 70 | 30 | 6.93
30
| TOTAL | 22.59 | 421.86 | 1278.14 | 110.1 |  | 3.48 | 1106.41 | 593.59 | 119.01
| AVERAGE | 1.3288 | 24.8153 | 75.1847 | 6.4765 |  | 0.20471 | 65.0829 | 34.9171 | 7.0006
PAGE 10
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
SLUDGE VOLUME REMOVED
RUN DATE
2026-07-30
|  | SEPTEMBER | TRAILERS | TONS | DRY TONS | % LIME | % TOT. | % FIX. | % VOL.
|  | 2005 | REMOVED | SLUDGE | REMOVED | CAKE | CAKE | CAKE | CAKE
|  | 1 | 4 | 88 | 29.2834 |  | 20.55 | 18.54 | 81.46
|  | 2 | 5 | 110
|  | 3 | 0 | 0
|  | 4 | 0 | 0
|  | 5 | 0 | 0
|  | 6 | 2 | 44 | 26.5729 |  | 19.17 | 17.89 | 82.11
|  | 7 | 5 | 110 | 17.4665 |  | 19.88 | 24.65 | 75.35
|  | 8 | 5 | 110 | 25.0625 |  | 19.23 | 19.35 | 80.65
|  | 9 | 4 | 88
|  | 10 | 0 | 0
|  | 11 | 0 | 0 | 11.0367 |  | 12.6 | 20.56 | 79.44
|  | 12 | 0 | 0 | 21.8466 |  | 18.45 | 22.11 | 77.89
|  | 13 | 4 | 88 | 24.9616 |  | 18.56 | 19.56 | 80.44
|  | 14 | 4 | 88 | 9.3983 |  | 20.03 | 21.77 | 78.23
|  | 15 | 5 | 110 | 19.9001 |  | 24.11 | 44.55 | 55.45
|  | 16 | 5 | 110
|  | 17 | 0 | 0
|  | 18 | 0 | 0 | 8.1478 |  | 17.75 | 15.83 | 84.17
|  | 19 | 3 | 66 |  |  | LS | LS
|  | 20 | 0 | 0
|  | 21 | 2 | 44 | 21.3696 |  | 17.31 | 15.55 | 84.45
|  | 22 | 4 | 88 | 28.5332 |  | 19.44 | 20.58 | 79.42
|  | 23 | 5 | 110
|  | 24 | 0 | 0
|  | 25 | 0 | 0 | 10.9738 |  | 20.01 | 21.99 | 78.01
|  | 26 | 5 | 110 | 23.1035 |  | 15.62 | 18.25 | 81.75
|  | 27 | 4 | 88 | 29.9748 |  | 18.48 | 18.89 | 81.11
|  | 28 | 2 | 44 | 25.0446 |  | 19.57 | 17.68 | 82.32
|  | 29 | 4 | 88 | 26.1642 |  | 19.44 | 16.82 | 83.18
|  | 30 | 4 | 88
|  | TOTAL | 76 | 1672 | 358.8402 | 0 | 320.2 | 354.57 | 1345.43
|  | AVERAGE | 2.5333 | 55.7333 | 21.1082 | #DIV/0! | 18.8353 | 20.8571 | 79.1429
PAGE 11
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
CHEMICAL USEAGE
RUN DATE
2026-07-30
| SEPTEMBER | H2O2 | CL2 | POLYMER | POLYMER | LIME | GOX | O2 % | LOX | FPL
| 2005 | POUNDS | POUNDS | GALLONS | POUNDS | DELV. | TONS | PURITY | TONS | KW
| 1 | 289 | 0 | 79 | 658.86 | 0 | 19.1 | 100% | 138.5 | 33736
| 2 | 0 | 1240 | 0 | 0 | 0 | 21.9 | 100% | 143.5 | 32718
| 3 | 0 | 1640 | 0 | 0 | 0 | 25.2 | 100% | 145.2 | 32078
| 4 | 140 | 1320 | 19 | 158.46 | 0 | 27.5 | 100% | 145.8 | 32180
| 5 | 0 | 1500 | 33 | 275.22 | 0 | 20.7 | 99% | 142.8 | 31965
| 6 | 299 | 280 | 15 | 125.1 | 0 | 23.9 | 100% | 139.7 | 32127
| 7 | 449 | 0 | 42 | 350.28 | 0 | 21.4 | 100% | 139.2 | 32041
| 8 | 369 | 0 | 51 | 425.34 | 0 | 20 | 100% | 139.8 | 32083
| 9 | 0 | 0 | 52 | 433.68 | 0 | 26.3 | 100% | 140.4 | 32089
| 10 | 0 | 0 | 0 | 0 | 0 | 28.5 | 100% | 141.5 | 31956
| 11 | 279 | 0 | 0 | 0 | 0 | 26.4 | 96% | 138.8 | 32020
| 12 | 0 | 0 | 0 | 0 | 0 | 29.7 | 93% | 142.6 | 32010
| 13 | 0 | 0 | 24 | 200.16 | 0 | 27.4 | 100% | 139.7 | 32131
| 14 | 0 | 920 | 30 | 250.2 | 0 | 20.2 | 100% | 140.8 | 31944
| 15 | 299 | 1800 | 96 | 800.64 | 0 | 17.4 | 100% | 141.1 | 31857
| 16 | 0 | 1360 | 40 | 333.6 | 0 | 23.9 | 100% | 139.8 | 31762
| 17 | 0 | 1460 | 0 | 0 | 0 | 24.2 | 100% | 140.2 | 31882
| 18 | 0 | 1720 | 41 | 341.94 | 0 | 21.03 | 99% | 140.9 | 31870
| 19 | 0 | 1360 | 49 | 408.66 | 0 | 23.4 | 99% | 142.1 | 32003
| 20 | 0 | 1620 | 0 | 0 | 0 | 20.7 | 100% | 141.9 | 31750
| 21 | 0 | 1460 | 71 | 592.14 | 0 | 18.8 | 100% | 143.1 | 31938
| 22 | 998 | 1460 | 0 | 0 | 0 | 16.2 | 100% | 141.7 | 31995
| 23 | 0 | 1520 | 17 | 141.78 | 0 | 21.9 | 100% | 141.8 | 32356
| 24 | 0 | 1620 | 0 | 0 | 0 | 20.8 | 100% | 143.2 | 32038
| 25 | 309 | 1500 | 33 | 275.22 | 0 | 20.7 | 99% | 142.6 | 31965
| 26 | 240 | 1600 | 66 | 550.44 | 0 | 18.8 | 100% | 143.3 | 31722
| 27 | 170 | 1520 | 77 | 642.18 | 0 | 16.3 | 100% | 145.3 | 31764
| 28 | 0 | 1520 | 42 | 350.28 | 0 | 17.5 | 100% | 144 | 31841
| 29 | 200 | 1200 | 26 | 216.84 | 0 | 16.5 | 100% | 144.5 | 31718
| 30 | 0 | 1520 | 19 | 158.46 | 0 | 18.9 | 99% | 145.2 | 31966
| TOTAL | 4041 | 31140 | 922 | 7689.48 | 0 | 655.23 |  | 4259 | 961505
| AVERAGE | 134.7 | 1038 | 30.7333 | 256.316 | 0 | 21.841 | 99.47% | 141.9667 | 32050.1667
PAGE 12
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL ONE
|  | RUN DATE |  |  | PERMIT NUMBER 0054569-142-UO
|  | 2026-07-30 |  |  | 1/07/04 thru 1/06/09 |  |  | I.D. #:5006A11308
|  | SEPTEMBER | % INFL. | MAX | MIN | WELL 1 | MAX | MIN | AVG
|  | 2005 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 12.77% | 12.93 | 0 | 5.64 | 63.67 | 37.13 | 47.58
|  | 2 | 5.733% | 13.7 | 0 | 2.5 | 66.63 | 36.99 | 41.84
|  | 3 | 21.36% | 14.23 | 0 | 9.63 | 67.22 | 36.73 | 55.79
|  | 4 | 26.56% | 15.23 | 5.44 | 12.43 | 70.9 | 44.41 | 61.67
|  | 5 | 30.58% | 14.57 | 8.48 | 12.18 | 70.6 | 49.77 | 61.14
|  | 6 | 25.05% | 15.22 | 7.57 | 12.55 | 73 | 47.96 | 62.72
|  | 7 | 2.446% | 12.57 | 0 | 1.18 | 62.93 | 37.12 | 39.8
|  | 8 | 23.87% | 14.5 | 0.01 | 10.89 | 68.33 | 36.51 | 58.02
|  | 9 | 26.28% | 14.75 | 7.04 | 11.87 | 69.71 | 48.39 | 59.63
|  | 10 | 25.26% | 14.3 | 8.48 | 11.5 | 67.95 | 49.11 | 58.57
|  | 11 | 24.08% | 13.64 | 8.01 | 11.82 | 65.98 | 48.3 | 59.59
|  | 12 | 7.89% | 13.63 | 0 | 3.75 | 66.37 | 36.3 | 43.36
|  | 13 | 23.53% | 15.47 | 0 | 10.58 | 71.7 | 36.19 | 56.93
|  | 14 | 24.64% | 13.67 | 0 | 10.48 | 65.45 | 36.12 | 55.75
|  | 15 | 26.21% | 14.52 | 8.25 | 10.94 | 67.94 | 48.98 | 56.44
|  | 16 | 24.83% | 14.17 | 0.01 | 10.31 | 67.82 | 36.47 | 55.21
|  | 17 | 5.752% | 10.99 | 0 | 2.36 | 56.51 | 36.45 | 41.03
|  | 18 | 21.33% | 14.05 | 0.01 | 8.69 | 66.41 | 36.29 | 52.55
|  | 19 | 21.87% | 12.42 | 0.01 | 9 | 60.75 | 36.07 | 52.69
|  | 20 | 23.54% | 14.66 | 8.21 | 10.67 | 70.3 | 48.9 | 55.48
|  | 21 | 22.32% | 14.07 | 6.93 | 10.46 | 68.7 | 45.36 | 55.69
|  | 22 | 1.629% | 12.48 | 0 | 0.73 | 62.11 | 36.84 | 38.63
|  | 23 | 24.28% | 13.74 | 0 | 10.47 | 64.61 | 36.84 | 56.21
|  | 24 | 26.33% | 14.03 | 3.63 | 10.87 | 65.65 | 42.95 | 56.12
|  | 25 | 25.86% | 12.17 | 7.54 | 10.3 | 59.53 | 46.9 | 54.26
|  | 26 | 25.84% | 11.77 | 6.63 | 10.15 | 58.72 | 44.82 | 54.01
|  | 27 | 5.655% | 11 | 0 | 2.19 | 56.72 | 36.39 | 40.42
|  | 28 | 21.63% | 13.04 | 0 | 8.33 | 63.05 | 36.25 | 51.23
|  | 29 | 21.73% | 12.38 | 0 | 8.42 | 60.7 | 35.87 | 50.93
|  | 30 | 26.3% | 12.2 | 7.33 | 10.26 | 60.29 | 46.51 | 54.25
|  | TOTAL | 605.2% | 406.1 | 93.58 | 261.15 | 1960.25 | 1232.92 | 1587.54
|  | AVERAGE | 20.17% | 13.5367 | 3.1193 | 8.705 | 65.3417 | 41.0973 | 52.918
|  | MAXIMUM | 30.58% | 15.47 | 8.48 | 12.55 | 73 | 49.77 | 62.72
|  | MINIMUM | 1.629% | 10.99 | 0 | 0.73 | 56.51 | 35.87 | 38.63
PAGE 13
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL TWO
|  | RUN DATE |  |  | PERMIT NUMBER 0054569-142-UO
|  | 2026-07-30 |  |  | 1/07/04 thru 1/06/09 |  |  | I.D. #:5006A11309
|  | SEPTEMBER | % INFL. | MAX | MIN | WELL 2 | MAX | MIN | AVG
|  | 2005 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 27.31% | 14.6 | 9.04 | 12.06 | 66.27 | 50.16 | 58.07
|  | 2 | 28.55% | 15.29 | 8.5 | 12.45 | 69.19 | 48.21 | 59.14
|  | 3 | 6.521% | 14.18 | 0.06 | 2.94 | 64.16 | 37.24 | 43.14
|  | 4 | 20.94% | 14.22 | 0.06 | 9.8 | 65.33 | 37.31 | 55.36
|  | 5 | 25.31% | 14.94 | 0.06 | 10.08 | 69.43 | 37.75 | 55.85
|  | 6 | 25.75% | 15.57 | 7.72 | 12.9 | 71.8 | 47.09 | 61.69
|  | 7 | 27.3% | 16.08 | 9.75 | 13.17 | 72.1 | 51.94 | 61.6
|  | 8 | 1.973% | 12.24 | 0.06 | 0.9 | 58.14 | 37.11 | 39.59
|  | 9 | 23.27% | 14.99 | 0.06 | 10.51 | 68.59 | 37.71 | 55.86
|  | 10 | 25.88% | 14.93 | 5.83 | 11.78 | 66.87 | 45.77 | 57.55
|  | 11 | 24.73% | 14.01 | 8.26 | 12.14 | 64.85 | 47.42 | 58.62
|  | 12 | 25.04% | 15.67 | 7.1 | 11.9 | 69.9 | 45.25 | 57.61
|  | 13 | 1.579% | 12.22 | 0.05 | 0.71 | 58.43 | 36.97 | 38.95
|  | 14 | 21.32% | 14.14 | 0.05 | 9.07 | 65.95 | 36.39 | 52.23
|  | 15 | 21.56% | 14.24 | 0.05 | 9 | 65.98 | 37.21 | 51.93
|  | 16 | 25.82% | 15.56 | 0.06 | 10.72 | 68.94 | 37.36 | 54.72
|  | 17 | 27.84% | 14.43 | 7.77 | 11.42 | 65.23 | 46.13 | 55.68
|  | 18 | 6.236% | 13.41 | 0.06 | 2.54 | 61.3 | 37.32 | 41.54
|  | 19 | 21.41% | 12.8 | 0.06 | 8.81 | 60.04 | 36.3 | 51.33
|  | 20 | 19.17% | 14.99 | 0.05 | 8.69 | 69.19 | 36.61 | 51.01
|  | 21 | 22.83% | 14.42 | 7.08 | 10.7 | 67.88 | 44.72 | 54.82
|  | 22 | 28.02% | 14.69 | 8.92 | 12.56 | 66.42 | 49.42 | 59.38
|  | 23 | 1.878% | 11.42 | 0.06 | 0.81 | 57.41 | 36.9 | 39.27
|  | 24 | 20.85% | 13.31 | 0.05 | 8.61 | 61.76 | 37.22 | 51.06
|  | 25 | 21.37% | 12 | 0.05 | 8.51 | 57.5 | 37.01 | 50.17
|  | 26 | 26.52% | 11.99 | 6.74 | 10.42 | 57.72 | 44.05 | 53.06
|  | 27 | 28.04% | 14.67 | 6.69 | 10.86 | 66.06 | 43.89 | 54
|  | 28 | 6.231% | 12.28 | 0.05 | 2.4 | 57.29 | 36.77 | 40.86
|  | 29 | 21.44% | 12.78 | 0.05 | 8.31 | 59.7 | 36.16 | 49.71
|  | 30 | 22.48% | 12.53 | 0.05 | 8.77 | 59.43 | 36.6 | 50.6
|  | TOTAL | 607.2% | 418.6 | 94.39 | 263.54 | 1932.86 | 1229.99 | 1564.4
|  | AVERAGE | 20.24% | 13.9533 | 3.1463 | 8.7847 | 64.4287 | 40.9997 | 52.1467
|  | MAXIMUM | 28.55% | 16.08 | 9.75 | 13.17 | 72.1 | 51.94 | 61.69
|  | MINIMUM | 1.579% | 11.42 | 0.05 | 0.71 | 57.29 | 36.16 | 38.95
PAGE 14
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL THREE
|  | RUN DATE |  |  | PERMIT NUMBER 0054569-142-UO
|  | 2026-07-30 |  |  | 1/07/04 thru 1/06/09 |  |  | I.D. #:5006A11310
|  | SEPTEMBER | % INFL. | MAX | MIN | WELL 3 | MAX | MIN | AVG
|  | 2005 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 25.14% | 12.99 | 8.58 | 11.1 | 67.37 | 51.19 | 59.27
|  | 2 | 25.94% | 13.49 | 8.24 | 11.31 | 70.4 | 49.22 | 60.35
|  | 3 | 25.62% | 13.15 | 8.65 | 11.55 | 67.4 | 50.33 | 61.13
|  | 4 | 1.389% | 10.91 | 0 | 0.65 | 59.59 | 38.61 | 40.96
|  | 5 | 22.62% | 14.03 | 0 | 9.01 | 71 | 38.28 | 56.23
|  | 6 | 23.95% | 14.35 | 5.15 | 12 | 73.3 | 44.69 | 62.96
|  | 7 | 24.55% | 14.22 | 8.91 | 11.84 | 73.5 | 53.05 | 62.83
|  | 8 | 25.21% | 13.52 | 7.57 | 11.5 | 68.57 | 48.69 | 60.99
|  | 9 | 1.417% | 11.48 | 0 | 0.64 | 61.34 | 38.5 | 40.67
|  | 10 | 19.73% | 12.87 | 0 | 8.98 | 65.96 | 37.69 | 54.86
|  | 11 | 22.98% | 13.15 | 0 | 11.28 | 66.27 | 38.87 | 59.57
|  | 12 | 22.72% | 13.87 | 6.9 | 10.8 | 70.9 | 46.18 | 58.7
|  | 13 | 25.31% | 14.11 | 7.51 | 11.38 | 71.8 | 47.71 | 60.3
|  | 14 | 3.127% | 12.34 | 0 | 1.33 | 63.39 | 37.67 | 41.33
|  | 15 | 19.28% | 13.34 | 0 | 8.05 | 67.3 | 37.76 | 52.16
|  | 16 | 25.26% | 15.67 | 2.56 | 10.49 | 79.5 | 42.96 | 56.84
|  | 17 | 25.54% | 12.86 | 7.56 | 10.48 | 66.17 | 47.13 | 56.82
|  | 18 | 25.58% | 13.03 | 7.46 | 10.42 | 66.44 | 46.94 | 56.71
|  | 19 | 6.003% | 12 | 0 | 2.47 | 61.72 | 38.34 | 43.25
|  | 20 | 16.9% | 14.04 | 0 | 7.66 | 70.8 | 37.41 | 51.34
|  | 21 | 21.36% | 13.26 | 6.85 | 10.01 | 69.01 | 45.57 | 55.94
|  | 22 | 25.28% | 13.05 | 8.43 | 11.33 | 67.58 | 50.47 | 60.54
|  | 23 | 25.44% | 12.7 | 7.84 | 10.97 | 64.74 | 49.33 | 58.89
|  | 24 | 1.405% | 9.99 | 0 | 0.58 | 58.16 | 38.03 | 39.94
|  | 25 | 19.33% | 11.37 | 0 | 7.7 | 58.74 | 37.54 | 50.69
|  | 26 | 20.42% | 11.22 | 0 | 8.02 | 58.91 | 37.32 | 51.17
|  | 27 | 25.8% | 12.97 | 6.63 | 9.99 | 67.23 | 44.87 | 55.13
|  | 28 | 25.91% | 12.07 | 7.18 | 9.98 | 63.13 | 46.41 | 55
|  | 29 | 5.96% | 12.2 | 0 | 2.31 | 62.76 | 37.71 | 42.51
|  | 30 | 19.99% | 11.8 | 0 | 7.8 | 60.61 | 37.36 | 50.95
|  | TOTAL | 579.2% | 386.05 | 116.02 | 251.63 | 1993.59 | 1295.83 | 1618.03
|  | AVERAGE | 19.31% | 12.8683 | 3.8673 | 8.3877 | 66.453 | 43.1943 | 53.9343
|  | MAXIMUM | 25.94% | 15.67 | 8.91 | 12 | 79.5 | 53.05 | 62.96
|  | MINIMUM | 1.389% | 9.99 | 0 | 0.58 | 58.16 | 37.32 | 39.94
PAGE 15
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL FOUR
|  | RUN DATE |  |  | PERMIT NUMBER 0054569-142-UO
|  | 2026-07-30 |  |  | 1/07/04 thru 1/06/09
|  | SEPTEMBER | % INFL. | MAX | MIN | WELL 4 | MAX | MIN | AVG
|  | 2005 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 21.24% | 13.32 | 0.05 | 9.38 | 67.86 | 39 | 56
|  | 2 | 21.74% | 13.77 | 0.05 | 9.48 | 70.9 | 37.51 | 57.29
|  | 3 | 26.33% | 13.42 | 8.8 | 11.87 | 67.87 | 50.96 | 61.66
|  | 4 | 26.16% | 14.74 | 8.43 | 12.24 | 71.7 | 49.42 | 62.66
|  | 5 | 7.307% | 13.99 | 0.05 | 2.91 | 69.51 | 38.69 | 45.07
|  | 6 | 21.52% | 15.01 | 0.05 | 10.78 | 73.6 | 37.74 | 60.17
|  | 7 | 24.92% | 14.45 | 6.41 | 12.02 | 74 | 48.5 | 63.32
|  | 8 | 25.41% | 13.59 | 7.67 | 11.59 | 69.11 | 49.36 | 61.59
|  | 9 | 25.73% | 14.21 | 8.08 | 11.62 | 70.7 | 49.35 | 60.74
|  | 10 | 3.493% | 12.84 | 0.05 | 1.59 | 66.53 | 37.88 | 41.72
|  | 11 | 1.833% | 11.32 | 0.05 | 0.9 | 59.32 | 38.33 | 40.66
|  | 12 | 22.13% | 14.26 | 0.05 | 10.52 | 71.4 | 38.28 | 58.33
|  | 13 | 25.8% | 14.47 | 7.68 | 11.6 | 72.2 | 48.35 | 60.8
|  | 14 | 26% | 13.29 | 1.86 | 11.06 | 67.95 | 39.59 | 58.36
|  | 15 | 6.684% | 13.92 | 0.05 | 2.79 | 68.78 | 38.28 | 43.65
|  | 16 | 19.44% | 15.82 | 0.05 | 8.07 | 80 | 37.09 | 52.54
|  | 17 | 21.25% | 13.01 | 0.05 | 8.72 | 66.85 | 37.2 | 54.12
|  | 18 | 25.95% | 13.12 | 7.54 | 10.57 | 67.07 | 47.59 | 57.3
|  | 19 | 26.4% | 12.13 | 7.69 | 10.86 | 62.25 | 47.65 | 57.46
|  | 20 | 18.27% | 13.62 | 0.05 | 8.28 | 66.87 | 38.13 | 52.78
|  | 21 | 22.11% | 13.85 | 7 | 10.36 | 69.49 | 46.23 | 56.5
|  | 22 | 25.26% | 13.25 | 0.06 | 11.32 | 68.14 | 37.84 | 60.7
|  | 23 | 25.69% | 12.8 | 7.95 | 11.08 | 65.35 | 49.97 | 59.48
|  | 24 | 26.11% | 13.51 | 7.79 | 10.78 | 66.49 | 47.65 | 57.21
|  | 25 | 6.227% | 11.89 | 0.05 | 2.48 | 60.35 | 37.94 | 42.66
|  | 26 | 20.19% | 11.64 | 0.05 | 7.93 | 59.49 | 37.35 | 51.12
|  | 27 | 21.48% | 13.22 | 0.05 | 8.32 | 67.75 | 37.14 | 52.77
|  | 28 | 26.33% | 12.15 | 7.26 | 10.14 | 63.7 | 47.1 | 55.62
|  | 29 | 26.5% | 12.25 | 7.04 | 10.27 | 63.35 | 46.65 | 55.44
|  | 30 | 5.742% | 11.63 | 0.05 | 2.24 | 59.82 | 37.94 | 42.09
|  | TOTAL | 603.2% | 400.49 | 102.01 | 261.77 | 2028.4 | 1274.71 | 1639.81
|  | AVERAGE | 20.11% | 13.3497 | 3.4003 | 8.7257 | 67.6133 | 42.4903 | 54.6603
|  | MAXIMUM | 26.5% | 15.82 | 8.8 | 12.24 | 80 | 50.96 | 63.32
|  | MINIMUM | 1.833% | 11.32 | 0.05 | 0.9 | 59.32 | 37.09 | 40.66
PAGE 16
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL FIVE
|  | RUN DATE |  |  | PERMIT NUMBER 0054569-142-UO
|  | 2026-07-30 |  |  | 1/07/04 thru 1/06/09 |  |  | I.D. #:5006A11311
|  | SEPTEMBER | % INFL. | MAX | MIN | WELL 5 | MAX | MIN | AVG
|  | 2005 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 12.71% | 12.46 | 0 | 5.61 | 66.92 | 37.61 | 49.52
|  | 2 | 19.47% | 12.99 | 0 | 8.49 | 69.91 | 36.37 | 55.55
|  | 3 | 20.05% | 12.53 | 0 | 9.04 | 66.97 | 37.8 | 56.77
|  | 4 | 24.43% | 13.62 | 7.87 | 11.43 | 70.8 | 48.47 | 61.65
|  | 5 | 28.68% | 13.6 | 8.3 | 11.42 | 70.4 | 49.63 | 60.97
|  | 6 | 1.198% | 10.38 | 0 | 0.6 | 56.96 | 36.8 | 39.57
|  | 7 | 20.88% | 13.63 | 0 | 10.07 | 72.9 | 37.42 | 59.78
|  | 8 | 23.96% | 12.83 | 5.9 | 10.93 | 68.18 | 48.2 | 60.42
|  | 9 | 24.24% | 13.34 | 7.66 | 10.95 | 69.63 | 48.33 | 59.61
|  | 10 | 23.88% | 13.51 | 7.94 | 10.87 | 67.87 | 49.05 | 58.4
|  | 11 | 22.76% | 12.76 | 7.62 | 11.17 | 65.5 | 48.12 | 59.35
|  | 12 | 21.92% | 13.34 | 6.72 | 10.42 | 70.4 | 45.9 | 58.3
|  | 13 | 24.2% | 13.52 | 5.96 | 10.88 | 71.3 | 47.44 | 59.76
|  | 14 | 24.59% | 12.5 | 2.27 | 10.46 | 65.35 | 39.97 | 57.29
|  | 15 | 24.75% | 13.05 | 7.91 | 10.33 | 67.74 | 48.9 | 56.27
|  | 16 | 4.576% | 14.87 | 0 | 1.9 | 78.6 | 36.24 | 41.4
|  | 17 | 19.01% | 12.29 | 0 | 7.8 | 65.72 | 35.95 | 52.39
|  | 18 | 20.18% | 12.4 | 0 | 8.22 | 65.95 | 37.17 | 53.23
|  | 19 | 24.89% | 11.41 | 7.35 | 10.24 | 61.32 | 46.71 | 56.43
|  | 20 | 21.76% | 13.64 | 7.82 | 9.86 | 70.2 | 48.77 | 55.34
|  | 21 | 10.22% | 10.44 | 0 | 4.79 | 59.91 | 37.6 | 45.73
|  | 22 | 20.55% | 12.54 | 0 | 9.21 | 67.05 | 36.73 | 56.84
|  | 23 | 26.92% | ER | 5.6 | 11.61 | 64.3 | 48.4 | 58.37
|  | 24 | 24.58% | 12.67 | 7.38 | 10.15 | 65.43 | 46.61 | 56.11
|  | 25 | 24.61% | 11.13 | 7.57 | 9.8 | 59.31 | 46.75 | 54.04
|  | 26 | 5.702% | 10.87 | 0 | 2.24 | 57.03 | 36.87 | 41.15
|  | 27 | 19.34% | 12.48 | 0 | 7.49 | 66.79 | 35.86 | 51.16
|  | 28 | 20.48% | 11.5 | 0 | 7.89 | 62.69 | 36.94 | 51.78
|  | 29 | 24.95% | 11.57 | 6.72 | 9.67 | 62.42 | 45.69 | 54.35
|  | 30 | 25.1% | 11.52 | 7.13 | 9.79 | 60.08 | 46.38 | 54.04
|  | TOTAL | 610.6% | 363.39 | 117.72 | 263.33 | 1987.63 | 1282.68 | 1635.57
|  | AVERAGE | 20.35% | 12.5307 | 3.924 | 8.7777 | 66.2543 | 42.756 | 54.519
|  | MAXIMUM | 28.68% | 14.87 | 8.3 | 11.61 | 78.6 | 49.63 | 61.65
|  | MINIMUM | 1.198% | 10.38 | 0 | 0.6 | 56.96 | 35.86 | 39.57
PAGE 17
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
INJECTION WELL SUMMARY
RUN DATE
2026-07-30
| SEPTEMBER | INFLUENT | EFFLUENT | EFFLUENT | IW-1 | IW-2 | IW-3 | IW-4 | IW-5 | TOTAL
| 2005 | FLOW | FLOW | SS | LBS SS | LBS SS | LBS SS | LBS SS | LBS SS | LBS SS
|  | MGD | MGD
| 1 | 44.155 | 43.754 | 23 | 1081.8648 | 2313.3492 | 2129.202 | 1799.2716 | 1076.1102 | 6600.5262
| 2 | 43.606 | 44.116 | 10 | 208.5 | 1038.33 | 943.254 | 790.632 | 708.066 | 2898.15
| 3 | 45.086 | 44.987 | LS | [5 empty] | #VALUE!
| 4 | 46.793 | 46.452 | 12 | 1243.9944 | 980.784 | 65.052 | 1224.9792 | 1143.9144 | 3433.7448
| 5 | 39.825 | 38.836 | 10 | 1015.812 | 840.672 | 751.434 | 242.694 | 952.428 | 3560.346
| 6 | 50.104 | 48.696 | 9 | 942.003 | 968.274 | 900.72 | 809.1468 | 45.036 | 2856.033
| 7 | 48.237 | 48.292 | 7 | 68.8884 | 768.8646 | 691.2192 | 701.7276 | 587.8866 | 2116.8588
| 8 | 45.618 | 45.806 | 11 | 999.0486 | 82.566 | 1055.01 | 1063.2666 | 1002.7182 | 3139.3428
| 9 | 45.168 | 45.549 | 27 | 2672.8866 | 2366.6418 | 144.1152 | 2616.5916 | 2465.721 | 7649.3646
| 10 | 45.52 | 44.478 | 14 | 1342.74 | 1375.4328 | 1048.5048 | 185.6484 | 1269.1812 | 5035.8588
| 11 | 49.087 | 47.463 | 11 | 1084.3668 | 1113.7236 | 1034.8272 | 82.566 | 1024.7358 | 4257.6534
| 12 | 47.528 | 47.359 | 5 | 156.375 | 496.23 | 450.36 | 438.684 | 434.514 | 1537.479
| 13 | 44.966 | 45.15 | 21 | 1852.9812 | 124.3494 | 1993.0932 | 2031.624 | 1905.5232 | 5875.947
| 14 | 42.538 | 42.375 | 12 | 1048.8384 | 907.7256 | 133.1064 | 1106.8848 | 1046.8368 | 3136.5072
| 15 | 41.743 | 41.095 | 10 | 912.396 | 750.6 | 671.37 | 232.686 | 861.522 | 3195.888
| 16 | 41.521 | 41.375 | 14 | 1203.7956 | 1251.6672 | 1224.8124 | 942.2532 | 221.844 | 3902.1192
| 17 | 41.027 | 40.767 | 20 | 393.648 | 1904.856 | 1748.064 | 1454.496 | 1301.04 | 5347.608
| 18 | 40.734 | 40.413 | 15 | 1087.119 | 317.754 | 1303.542 | 1322.307 | 1028.322 | 3736.737
| 19 | 41.144 | 41.229 | LS | [5 empty] | #VALUE!
| 20 | 45.32 | 44.951 | 8 | 711.9024 | 579.7968 | 511.0752 | 552.4416 | 657.8592 | 2460.6336
| 21 | 46.859 | 46.387 | 6 | 523.4184 | 535.428 | 500.9004 | 518.4144 | 239.6916 | 1799.4384
| 22 | 44.822 | 45.099 | 17 | 103.4994 | 1780.7568 | 1606.3674 | 1604.9496 | 1305.7938 | 4796.4174
| 23 | 43.123 | 44.944 | 21 | 1833.7158 | 141.8634 | 1921.2858 | 1940.5512 | 2033.3754 | 5930.2404
| 24 | 41.29 | 41.105 | 16 | 1450.4928 | 1148.9184 | 77.3952 | 1438.4832 | 1354.416 | 4031.2224
| 25 | 39.825 | 38.836 | 16 | 1374.432 | 1135.5744 | 1027.488 | 330.9312 | 1307.712 | 4845.2064
| 26 | 39.284 | 38.682 | 14 | 1185.114 | 1216.6392 | 936.4152 | 925.9068 | 261.5424 | 3599.7108
| 27 | 38.725 | 38.832 | 17 | 310.4982 | 1539.7308 | 1416.3822 | 1179.6096 | 1061.9322 | 4328.5434
| 28 | 38.518 | 38.739 | 8 | 555.7776 | 160.128 | 665.8656 | 676.5408 | 526.4208 | 1908.192
| 29 | 38.756 | 38.89 | 8 | 561.7824 | 554.4432 | 154.1232 | 685.2144 | 645.1824 | 1915.5312
| 30 | 39.011 | 38.827 | 14 | 1197.9576 | 1023.9852 | 910.728 | 261.5424 | 1143.0804 | 4275.7512
| TOTAL | 1299.933 | 1293.484 | 376 | 27123.8484 | 27419.0844 | 26015.7126 | 27160.044 | 27612.4056 | #VALUE!
| AVERAGE | 43.3311 | 43.1161 | 13.4286 | 968.7089 | 979.253 | 929.1326 | 970.0016 | 986.1573 | #VALUE!
PAGE 18
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
| RUN DATE |  |  |  | SOLIDS REMOVAL INVENTORY DATA SHEET
2026-07-30
| SEPTEMBER | TONS | CAKE |  |  |  | SEPTEMBER | RAGS | GRIT | OTHER
| 2005 | SLUDGE | TSS |  |  |  | 2005 |  |  | (vac)
| 1st - 7th | [5 empty] | 1st - 7th
| 1 | 88 | 20.55 |  |  |  | 1
| 2 | 110 |  |  |  |  | 2 | 10
| 3 | 0 |  |  |  |  | 3
| 4 | 0 |  |  |  |  | 4
| 5 | 0 |  |  |  |  | 5
| 6 | 44 | 19.17 |  |  |  | 6
| 7 | 110 | 19.88 |  |  |  | 7
| TOTAL = | 352 | 19.8667 | = AVG. |  |  | TOTAL = | 10 | 0 | 0
| 8th - 14th | [5 empty] | 8th - 14th
| 8 | 110 | 19.23 |  |  |  | 8 | 10
| 9 | 88 |  |  |  |  | 9
| 10 | 0 |  |  |  |  | 10
| 11 | 0 | 12.6 |  |  |  | 11
| 12 | 0 | 18.45 |  |  |  | 12
| 13 | 88 | 18.56 |  |  |  | 13
| 14 | 88 | 20.03 |  |  |  | 14
| TOTAL = | 374 | 17.774 | = AVG. |  |  | TOTAL = | 10 | 0 | 0
| 15th - 22nd | [5 empty] | 15th-22nd
| 15 | 110 | 24.11 |  |  |  | 15 |  | 10
| 16 | 110 |  |  |  |  | 16
| 17 | 0 |  |  |  |  | 17
| 18 | 0 | 17.75 |  |  |  | 18
| 19 | 66 | LS |  |  |  | 19
| 20 | 0 |  |  |  |  | 20
| 21 | 44 | 17.31 |  |  |  | 21
| 22 | 88 | 19.44 |  |  |  | 22
| TOTAL = | 418 | 19.6525 | = AVG. |  |  | TOTAL = | 0 | 10 | 0
| 23rd - 31st | [5 empty] | 23rd-31st
| 23 | 110 |  |  |  |  | 23
| 24 | 0 |  |  |  |  | 24
| 25 | 0 | 20.01 |  |  |  | 25
| 26 | 110 | 15.62 |  |  |  | 26 |  | 10
| 27 | 88 | 18.48 |  |  |  | 27
| 28 | 44 | 19.57 |  |  |  | 28
| 29 | 88 | 19.44 |  |  |  | 29 | 10
| 30 | 88 |  |  |  |  | 30 |  | 10
| TOTAL = | 528 | 18.624 | = AVG. |  |  | TOTAL = | 10 | 20 | 0
RAGS & GRIT go to Central LandFill
Other(VAC) go to BCSR
PAGE 19

## INJECTION PAGES
|  |  |  | UNDERGROUND INJECTION CONTROL | [10 empty] | UNDERGROUND INJECTION CONTROL | [10 empty] | UNDERGROUND INJECTION CONTROL
[15 empty] | MONTHLY OPERATING REPORT | [10 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES |  |  |  |  | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES |  |  |  |  | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [10 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [10 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-1 | [7 empty] | Wet Well Description: |  |  | Effuent Wet Well for IW-1, IW-2, IW3, IW-4 and IW-5 | [7 empty] | Monitoring Well Decription: |  |  | UPPER ZONE OF MONITORING WELL MW-1
Permit #: |  | 0054569-142-UO |  |  |  |  | Date of Issuance: |  | 2004-01-07 |  | Facility ID #: |  | 5006M02066 |  |  |  | Permit Number: |  |  | FLA041378 |  | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | 0054569-142-UO
[22 empty] | Monitoring Well ID #: |  |  | 5006A11311
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2009-01-06 | [7 empty] | Issue Date: |  |  | 1999-10-18 |  | As Identified in Permit: |  | Monitor Well MW-1 Upper Monitor Zone |  |  |  | Issue Date: |  |  | 2004-01-07
[22 empty] | Monitoring Well Interval: |  |  | 1288' to 1320'
Injection Well ID #: |  | 5006A11308 | [8 empty] | Wet Well ID #: |  | Well Facility U-001 |  |  |  | Expiration Date: |  |  | 2004-10-17 |  | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.7 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24 | Associated Injection Well(s):
Injection Interval: |  |  | 2799' to 3513' | [18 empty] | 500A11311 |  |  | INJECTION WELL IW-5
[11 empty] | Injection Well ID #: |  |  | Injection Well Description
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s): | [10 empty] | 5006A11308 |  |  | INJECTION WELL IW-1
[11 empty] | 5006A11309 |  |  | INJECTION WELL IW-2 | [7 empty] | REPORT MONTH / YEAR: |  | 2005-09-01 | DATE OF SAP / RECORDING: |  |  | 2005-09-06 | 2005-09-13 | 2005-09-20 | 2005-09-28
Monitoring Zone ID #: | [5 empty] | Description |  |  |  |  | 5006A11310 |  |  | INJECTION WELL IW-3
[11 empty] | N/A |  |  | INJECTION WELL IW-4 | [7 empty] | OPERATOR'S NAME: |  |  | McGEARY, J.
UO-06-279401 |  | UPPER ZONE OF MONITORING WELL MW-2 | [8 empty] | 5006A11311 |  |  | INJECTION WELL IW-5
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4545-A
UO-06-279401 |  | LOWER ZONE OF MONITORING WELL MW-2
[11 empty] | THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [10 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [10 empty] | REPORT MONTH / YEAR: |  | 2005-09-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous |  |  | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2005-09-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous |  |  | OPERATOR'S NAME: |  |  | McGEARY, J.
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
OPERATOR'S NAME: |  |  | McGEARY, J. | [7 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4545-A | [7 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4545-A | [7 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: |  |  |  | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 49.62 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 45.44 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: |  |  |  | PARAMETER |  |  |  | Sampling Frequency |  |  |  | VALUE |  | UNITS | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 48.9023 | PSIG
[11 empty] | Nitrogen, Total as N |  |  |  |  | Daily/Monthly Average |  |  | 10.481 |  | mg/L as N | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[11 empty] | Nitrogen, Nitrate, Total as N |  |  |  |  | Daily/Monthly Average |  |  | 0.331 |  | mg/L as N | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7519 | mg/l
Total monthly flow | [7 empty] | 261.15 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 3762.5 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [7 empty] | Nitrogen, Total Kjeildahl as N |  |  |  |  | Daily/Monthly Average |  |  | 10.15 |  | mg/L as N | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.86 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 15.47 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.35 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 73 |  | PSIG | pH |  |  |  |  | Daily/Monthly Average |  |  | 6.6633 |  | s.u. | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 8.075 | Std units
Monthly average of the daily flow rates | [7 empty] | 8.705 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 12150 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 11.6095 |  | MG | Phosphorus, Total as P |  |  |  |  | Daily/Monthly Average |  |  | 1.0114 |  | mg/L as P | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 2.398 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 75.25 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [10 empty] | Total Dissolved Solids (TDS) |  |  |  |  | Daily/Monthly Average |  |  | 1234.7586 |  | mg/L | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.01 | mg/l
Monthly average pressure | [7 empty] | 52.918 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 930 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 36.37 |  | PSIG | Residue, Total filterable (TSS dried at 180 C) |  |  |  |  | Daily/Monthly Average |  |  | 13.4286 |  | mg/L | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[11 empty] | Specific Conductance (Temperature Compensated) |  |  |  |  | Daily/Monthly Average |  |  | 2453.4483 |  | umhos/cm | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just | [6 empty] | Temperature, Water |  |  |  |  | Daily/Monthly Average |  |  | 86.2069 |  | deg C
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [9 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just |  |  | Date: |  |  |  |  | (Signature):
[12 empty] | (Signature): | [10 empty] | Date:
|  |  |  | UNDERGROUND INJECTION CONTROL | [21 empty] | UNDERGROUND INJECTION CONTROL
|  |  |  | MONTHLY OPERATING REPORT | [21 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES | [15 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [21 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-2 | [18 empty] | Monitoring Well Decription: |  |  | LOWER ZONE OF MONITORING WELL MW-1
Permit #: |  | 0054569-142-UO |  |  |  |  | Date of Issuance: |  | 2004-01-07 | [12 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | 0054569-142-UO
[22 empty] | Monitoring Well ID #: |  |  | 5006A11311
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2009-01-06 | [12 empty] | As Identified in Permit: |  | Monitor Well MW-1 Lower Monitor Zone |  |  |  | Issue Date: |  |  | 2004-01-07
[22 empty] | Monitoring Well Interval: |  |  | 1449' to 1557'
Injection Well ID #: |  | 5006A11309 | [19 empty] | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.7 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24
Injection Interval: |  |  | 2798' to 3518' | [18 empty] | 500A11311 |  |  | INJECTION WELL IW-5
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s):
[22 empty] | REPORT MONTH / YEAR: |  | 2005-09-01 | DATE OF SAP / RECORDING: |  |  | 2005-09-06 | 2005-09-13 | 2005-09-20 | 2005-09-28
Monitoring Zone ID #: | [5 empty] | Description
[22 empty] | OPERATOR'S NAME: |  |  | McGEARY, J.
UO-06-279401 |  | UPPER ZONE OF MONITORING WELL MW-2
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4545-A
UO-06-279401 |  | LOWER ZONE OF MONITORING WELL MW-2
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [21 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2005-09-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
OPERATOR'S NAME: |  |  | McGEARY, J. | [18 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4545-A | [18 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 47.39 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 40.1 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: | [14 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 43.8933 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 9575 | mg/l
Total monthly flow | [7 empty] | 263.54 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 5050 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [18 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 9.625 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 16.08 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 11 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 72.1 |  | PSIG | [11 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7.39 | Std units
Monthly average of the daily flow rates | [7 empty] | 8.7847 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 15575 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 11.6484 |  | MG | [11 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 2.398 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 74.25 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [21 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.01 | mg/l
Monthly average pressure | [7 empty] | 52.1467 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 874.75 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 36.72 |  | PSIG | [11 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [21 empty] | (Signature):
Date:
|  |  |  | UNDERGROUND INJECTION CONTROL | [21 empty] | UNDERGROUND INJECTION CONTROL
|  |  |  | MONTHLY OPERATING REPORT | [21 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES | [15 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [21 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-3 | [18 empty] | Monitoring Well Decription: |  |  | UPPER ZONE OF MONITORING WELL MW-2
Permit #: |  | 0054569-142-UO |  |  |  |  | Date of Issuance: |  | 2004-01-07 | [12 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | 0054569-142-UO
[22 empty] | Monitoring Well ID #: |  |  | 5006A11308 & 309
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2009-01-06 | [12 empty] | As Identified in Permit: |  | Monitor Well MW-2 Upper Monitor Zone |  |  |  | Issue Date: |  |  | 2004-01-07
[22 empty] | Monitoring Well Interval: |  |  | 1300' to 1344'
Injection Well ID #: |  | 5006A11310 | [19 empty] | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.7 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24
Injection Interval: |  |  | 2800' to 3977' | [18 empty] | 5006A11308 |  |  | INJECTION WELL IW-1
[22 empty] | 5006A11309 |  |  | INJECTION WELL IW-2
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s):
[22 empty] | REPORT MONTH / YEAR: |  | 2005-09-01 | DATE OF SAP / RECORDING: |  |  | 2005-09-06 | 2005-09-13 | 2005-09-20 | 2005-09-28
Monitoring Zone ID #: | [5 empty] | Description
[22 empty] | OPERATOR'S NAME: |  |  | McGEARY, J.
UO-06-279510 |  | UPPER ZONE OF MONITORING WELL MW-3
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4545-A
UO-06-279510 |  | LOWER ZONE OF MONITORING WELL MW-3
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [21 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2005-09-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
OPERATOR'S NAME: |  |  | McGEARY, J. | [18 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4545-A | [18 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 35.43 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 18.96 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: | [14 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 30.5667 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7561.5 | mg/l
Total monthly flow | [7 empty] | 251.63 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 3687.5 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [18 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.84 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 15.67 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.0725 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 79.5 |  | PSIG | [11 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7.98 | Std units
Monthly average of the daily flow rates | [7 empty] | 8.3877 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 11800 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 11.1108 |  | MG | [11 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 2.398 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 74.25 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [21 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.01 | mg/l
Monthly average pressure | [7 empty] | 53.9343 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 934.75 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 38.58 |  | PSIG | [11 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [21 empty] | (Signature):
Date:
|  |  |  | UNDERGROUND INJECTION CONTROL | [21 empty] | UNDERGROUND INJECTION CONTROL
|  |  |  | MONTHLY OPERATING REPORT | [21 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES | [15 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [21 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-4 | [18 empty] | Monitoring Well Decription: |  |  | LOWER ZONE OF MONITORING WELL MW-2
Permit #: |  | 0054569-142-UO |  |  |  |  | Date of Issuance: |  | 2004-01-07 | [12 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | 0054569-142-UO
[22 empty] | Monitoring Well ID #: |  |  | 5006A11308 & 309
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2009-01-06 | [12 empty] | As Identified in Permit: |  | Monitor Well MW-2 Lower Monitor Zone |  |  |  | Issue Date: |  |  | 2004-01-07
[22 empty] | Monitoring Well Interval: |  |  | 1970' to 2025'
Injection Well ID #: |  | N/A | [19 empty] | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.7 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24
Injection Interval: |  |  | 2804' to 3977' | [18 empty] | 5006A11308 |  |  | INJECTION WELL IW-1
[22 empty] | 5006A11309 |  |  | INJECTION WELL IW-2
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s):
[22 empty] | REPORT MONTH / YEAR: |  | 2005-09-01 | DATE OF SAP / RECORDING: |  |  | 2005-09-06 | 2005-09-13 | 2005-09-20 | 2005-09-28
Monitoring Zone ID #: | [5 empty] | Description
[22 empty] | OPERATOR'S NAME: |  |  | McGEARY, J.
UO-06-279510 |  | UPPER ZONE OF MONITORING WELL MW-3
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4545-A
UO-06-279510 |  | LOWER ZONE OF MONITORING WELL MW-3
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [21 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2005-09-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
OPERATOR'S NAME: |  |  | McGEARY, J. | [18 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4545-A | [18 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 43.62 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 35.98 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: | [14 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 42.4657 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 32085 | mg/l
Total monthly flow | [7 empty] | 261.77 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 16650 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [18 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.425 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 15.82 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.975 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 80 |  | PSIG | [11 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7.7125 | Std units
Monthly average of the daily flow rates | [7 empty] | 8.7257 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 25532.5 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 11.5722 |  | MG | [11 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 2.398 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 73.5 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [21 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.01 | mg/l
Monthly average pressure | [7 empty] | 54.6603 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 2817.5 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 38.13 |  | PSIG | [11 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [21 empty] | (Signature):
Date:
|  |  |  | UNDERGROUND INJECTION CONTROL | [21 empty] | UNDERGROUND INJECTION CONTROL
|  |  |  | MONTHLY OPERATING REPORT | [21 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES | [15 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [21 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-5 | [18 empty] | Monitoring Well Decription: |  |  | UPPER ZONE OF MONITORING WELL MW-3
Permit #: |  | 0054569-142-UO |  |  |  |  | Date of Issuance: |  | 2004-01-07 | [12 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | 0054569-142-UO
[22 empty] | Monitoring Well ID #: |  |  | 5006A11310
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2009-01-06 | [12 empty] | As Identified in Permit: |  | Monitor Well MW-3 Upper Monitor Zone |  |  |  | Issue Date: |  |  | 2004-01-07
[22 empty] | Monitoring Well Interval: |  |  | 1300' to 1349'
Injection Well ID #: |  | 5006A11311 | [19 empty] | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.7 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24
Injection Interval: |  |  | 2818' to 3462' | [18 empty] | 5006A11310 |  |  | INJECTION WELL IW-3
[22 empty] | N/A |  |  | INJECTION WELL IW-4
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s):
[22 empty] | REPORT MONTH / YEAR: |  | 2005-09-01 | DATE OF SAP / RECORDING: |  |  | 2005-09-06 | 2005-09-13 | 2005-09-20 | 2005-09-28
Monitoring Zone ID #: | [5 empty] | Description
[22 empty] | OPERATOR'S NAME: |  |  | McGEARY, J.
UO-06-279512 |  | UPPER ZONE OF MONITORING WELL MW-1
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4545-A
UO-06-279512 |  | LOWER ZONE OF MONITORING WELL MW-1
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [21 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2005-09-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
OPERATOR'S NAME: |  |  | McGEARY, J. | [18 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4545-A | [18 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 34.7 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 20.05 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: | [14 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 32.4363 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7810.75 | mg/l
Total monthly flow | [7 empty] | 263.33 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 3675 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [18 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.8275 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 14.87 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.965 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 78.6 |  | PSIG | [11 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 8.2625 | Std units
Monthly average of the daily flow rates | [7 empty] | 8.7777 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 12022.5 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 11.7131 |  | MG | [11 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 2.398 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 72.5 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [21 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.01 | mg/l
Monthly average pressure | [7 empty] | 54.519 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 906.5 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 37.01 |  | PSIG | [11 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [21 empty] | (Signature):
Date:
UNDERGROUND INJECTION CONTROL
MONTHLY OPERATING REPORT
[22 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
[22 empty] | Monitoring Well Decription: |  |  | LOWER ZONE OF MONITORING WELL MW-3
[22 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | 0054569-142-UO
[22 empty] | Monitoring Well ID #: |  |  | 5006A11310
[22 empty] | As Identified in Permit: |  | Monitor Well MW-3 Lower Monitor Zone |  |  |  | Issue Date: |  |  | 2004-01-07
[22 empty] | Monitoring Well Interval: |  |  | 1970 to 2027'
Associated Injection Well(s):
[22 empty] | Injection Well ID #: |  |  | Injection Well Description
[22 empty] | 5006A11310 |  |  | INJECTION WELL IW-3
[22 empty] | N/A |  |  | INJECTION WELL IW-4
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
[22 empty] | REPORT MONTH / YEAR: |  | 2005-09-01 | DATE OF SAP / RECORDING: |  |  | 2005-09-06 | 2005-09-13 | 2005-09-20 | 2005-09-28
[22 empty] | OPERATOR'S NAME: |  |  | McGEARY, J.
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4545-A
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
[22 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
[22 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
[22 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 46.38 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 37.4 | PSIG
[22 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 44.9417 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
[22 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 28779.75 | mg/l
[22 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 15400 | mg/l
[22 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 2.425 | mg/l
[22 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 2.95 | mg/l
[22 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7.5225 | Std units
[22 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 42375 | umho/cm
[22 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
[22 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 71 | deg. F
[22 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.01 | mg/l
[22 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 2847.5 | mg/l
[22 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
Date:

## DEP PART-A FORMS
30 | [5 empty] | Department of Environmental Protection Discharge Monitoring Report - Part A
When Completed mail this report to: Department of Environmental Protection, Southeast District, 400 North Congress Avenue, Suite 200 West Palm Beach, FL, 33401
| PERMITEE NAME: | City of Fort Lauderdale |  |  |  |  | PERMIT NUMBER: |  | FLA041378 |  | REPORT: | Monthly
| MAILING ADDRESS: | 949 NW 38th Street |  |  |  |  | LIMIT: |  | Final |  | GROUP: | Domestic
|  | Fort Lauderdale, FL 33309 |  |  |  |  | CLASS SIZE: |  | N/A |  | GMS TEST SITE
[7 empty] | MONITORING GROUP NUMBER: |  | U-001 |  | NO:
| FACILITY: | City of Fort Lauderdale G. T. Lohmeyer WWTF |  |  |  |  | MONITORING GROUP DESC: |  | Effluent Disposal including Influent
| LOCATION: | 1765 SE 18th Street |  |  |  |  | NO DISCHARGE FROM SITE:
Fort Lauderdale, FL 33316
| COUNTY: | Broward |  |  |  |  | MONITORING PERIOD: | From: | 2005-09-01 |  | To: | 2005-09-30
| Parameter |  | Quantity of Loading |  | Units |  | Quality or Concentration |  | Units | No. Ex. | Frequency of Analysis | Sample Type
| Flow | Sample Measurement | 8.7777 | 11.7131 | [5 empty] | 0
| PARM Code 50050 1 Mon.Site No. EFF-007 | Permit Requirement | Report (Mo. Avg.) | Report (Peak Hour) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
| Flow | Sample Measurement | 8.7257 | 11.5722 | [5 empty] | 0
| PARM Code 50050 P Mon.Site No. EFF-006 | Permit Requirement | Report (Mo. Avg.) | Report (Peak Hour) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
| Flow | Sample Measurement | 8.3877 | 11.1108 | [5 empty] | 0
| PARM Code 50050 Q Mon.Site No. EFF-005 | Permit Requirement | Report (Mo. Avg.) | Report (Peak Hour) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
| Flow | Sample Measurement | 8.7847 | 11.6484 | [5 empty] | 0
| PARM Code 50050 R Mon.Site No. EFF-004 | Permit Requirement | Report (Mo. Avg.) | Report (Peak Hour) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
| Flow | Sample Measurement | 8.705 | 11.6095 | [5 empty] | 0
| PARM Code 50050 S Mon.Site No. EFF-003 | Permit Requirement | Report (Mo. Avg.) | Report (Peak Hour) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
| BOD, Carbonaceous 5 day, 20C | Sample Measurement |  |  |  | 4.3 |  |  |  | 0
| PARM Code 80082 Y Mon.Site No. EFF-002 | Permit Requirement |  |  |  | 20.0 (An.Avg.) |  |  | mg/l |  | Daily | 24-hour FPC
I certify under penalty of law that I have personally examined and am familiar with the informantion submitted herein; and based on my inquiry of those individuals immeadiately responsible for obtaining the information, I believe the submitted
information is true, accurate and complete. I am aware that there are significant penalties for submitting false information including the possiblity of fine and imprisonment.
| NAME/TITLE OF PRINCIPAL EXECUTIVE OFFICER OR AUTHORIZED AGENT |  |  |  | SIGNATURE OF PRINCIPAL EXECUTIVE OFFICER OR AUTHORIZED AGENT |  |  |  |  | TELEPHONE |  | DATE (YY/MM/DD)
954-523-1002 ext 2021
REGIONAL WASTEWATER FACILITIES MANAGER
COMMENTS AND EXPLANATION OF ANY VIOLATIONS (Reference all attachments here):
Version 3/30/05
Discharge Monitoring Report - Part A (Continued)
[13 empty] | FACILITY: | City of Fort Lauderdale G. T. Lohmeyer WWTF | [5 empty] | MONITORING GROUP NUMBER: U-001 |  |  | PERMIT NUMBER: |  | FLA041378
[20 empty] | MONITORING PERIOD: |  | From: | 2005-09-01 | To: | 2005-09-30
[13 empty] | Parameter |  |  | Quantity of Loading |  | Units |  | Quality or Concentration |  | Units | No. Ex. | Frequency of Analysis | Sample Type
[13 empty] | BOD, Carbonaceous 5 day, 20C |  | Sample Measurement |  |  |  | 2.8837 | 2.8072 | 7 |  | 0
[13 empty] | PARM Code 80082 1 Mon.Site No. EFF-002 |  | Permit Requirement |  |  |  | 30.0 (Mo.Avg.) | 45.0 (Week.Avg.) | 60.0 (Max.) | mg/l |  | Daily | 24-hour FPC
[13 empty] | Solids, Total Suspended |  | Sample Measurement |  |  |  | 17.7 |  |  |  | 0
[13 empty] | PARM Code 00530 Y Mon.Site No. EFF-002 |  | Permit Requirement |  |  |  | 20.0 (An.Avg.) |  |  | mg/l |  | Daily | 24-hour FPC
[13 empty] | Solids, Total Suspended |  | Sample Measurement |  |  |  | 13.4286 | 13.42 | 27 |  | 0
[13 empty] | PARM Code 00530 1 Mon.Site No. EFF-002 |  | Permit Requirement |  |  |  | 30.0 (Mo.Avg.) | 45.0 (Week.Avg.) | 60.0 (Max.) | mg/l |  | Daily | 24-hour FPC
[13 empty] | pH |  | Sample Measurement |  |  |  | 6.4 |  |  |  | 0
[13 empty] | PARM Code 00400 1 Mon.Site No. EFF-002 |  | Permit Requirement |  |  |  | 6.0 (Min.) |  |  | s.u. |  | Continuous | Meter
[13 empty] | Flow |  | Sample Measurement | 36.8 | [6 empty] | N/A
[13 empty] | PARM Code 50050 G Mon.Site No. INF-001 |  | Permit Requirement | Report (An.Avg.) |  | mgd | [5 empty] | Continuous | Flow meters and totalizers
[13 empty] | Flow |  | Sample Measurement | 43.3311 | 41.5624 | [5 empty] | 0
[13 empty] | PARM Code 50050 T Mon.Site No. INF-001 |  | Permit Requirement | Report (Mo.Avg.) | 55.7 (3-Mo.Avg.) | mgd | [5 empty] | Continuous | Flow meters and totalizers
[13 empty] | BOD, Carbonaceous 5 day, 20C |  | Sample Measurement |  |  |  | 59.0377 |  |  |  | N/A
[13 empty] | PARM Code 80082 G Mon.Site No. INF-002 |  | Permit Requirement |  |  |  | Report (Mo.Avg.) |  |  | mg/l |  | Daily | 24-hour FPC
[13 empty] | Solids, Total Suspended |  | Sample Measurement |  |  |  | 77.2069 |  |  |  | N/A
[13 empty] | PARM Code 00530 G Mon.Site No. INF-002 |  | Permit Requirement |  |  |  | Report (Mo.Avg.) |  |  | mg/l |  | Daily | 24-hour FPC
[13 empty] | Percent Capacity, (TMADF/Permitted Capacity) x 100 |  | Sample Measurement |  |  |  | 74.62% |  |  |  | 0
[13 empty] | PARM Code 00530 G Mon.Site No. INF-002 |  | Permit Requirement |  |  |  | Report (Mo.Total) |  |  | mg/l |  | PERCENT | Calculated
Version 03/30/05
Formulas:
Monthly = ([FLA041378]-1)+A2

## DEP PART-B FORMS
DAILY SAMPLE RESULTS - B
| Permit Number |  | FLA041378 |  |  | Facility: | City of Fort Lauderdale G. T. Lohmeyer WWTF
| Monitoring Period: |  | From: | 2005-09-01 |  | To: | 2005-09-30
|  | CBOD5 (mg/L | pH (Max) | pH (Min) | TSS (mg/L | Flow (mgd) | Flow (mgd) | Flow (mgd) | Flow (mgd) | Flow (mgd)
Code |  | 80082 | 00400 | 00400 | 00530 | 50050 | 50050 | 50050 | 50050 | 50050
Mon. Site |  | EFF-002 | EFF-002 | EFF-002 | EFF-002 | EFF-003 | EFF-004 | EFF-005 | EFF-006 | EFF-007
1 |  | 2.2 | 6.7 | 6.7 | 23 | 5.64 | 12.06 | 11.1 | 9.38 | 5.61
2 |  | 2.09 | 6.4 | 6.4 | 10 | 2.5 | 12.45 | 11.31 | 9.48 | 8.49
3 |  | 0.79 | 6.7 | 6.6 | LS | 9.63 | 2.94 | 11.55 | 11.87 | 9.04
4 |  | 1 | 6.7 | 6.6 | 12 | 12.43 | 9.8 | 0.65 | 12.24 | 11.43
5 |  | 0.99 | 6.6 | 6.6 | 10 | 12.18 | 10.08 | 9.01 | 2.91 | 11.42
6 |  | 1.66 | 6.9 | 6.6 | 9 | 12.55 | 12.9 | 12 | 10.78 | 0.6
7 |  | 1 | 6.9 | 6.6 | 7 | 1.18 | 13.17 | 11.84 | 12.02 | 10.07
8 |  | 2.03 | 6.9 | 6.6 | 11 | 10.89 | 0.9 | 11.5 | 11.59 | 10.93
9 |  | 4.87 | 6.8 | 6.6 | 27 | 11.87 | 10.51 | 0.64 | 11.62 | 10.95
10 |  | 2.18 | 6.7 | 6.6 | 14 | 11.5 | 11.78 | 8.98 | 1.59 | 10.87
11 |  | 2.51 | 6.7 | 6.6 | 11 | 11.82 | 12.14 | 11.28 | 0.9 | 11.17
12 |  | 2.28 | 7 | 6.6 | 5 | 3.75 | 11.9 | 10.8 | 10.52 | 10.42
13 |  | 1.8 | 6.8 | 6.7 | 21 | 10.58 | 0.71 | 11.38 | 11.6 | 10.88
14 |  | 3.07 | 6.9 | 6.6 | 12 | 10.48 | 9.07 | 1.33 | 11.06 | 10.46
15 |  | 2.84 | 6.8 | 6.6 | 10 | 10.94 | 9 | 8.05 | 2.79 | 10.33
16 |  | 2.43 | 6.7 | 6.5 | 14 | 10.31 | 10.72 | 10.49 | 8.07 | 1.9
17 |  | 3.99 | 6.6 | 6.6 | 20 | 2.36 | 11.42 | 10.48 | 8.72 | 7.8
18 |  | 1.29 | 6.7 | 6.6 | 15 | 8.69 | 2.54 | 10.42 | 10.57 | 8.22
19 |  | 1.42 | 6.8 | 6.5 | LS | 9 | 8.81 | 2.47 | 10.86 | 10.24
20 |  | 1 | 6.8 | 6.6 | 8 | 10.67 | 8.69 | 7.66 | 8.28 | 9.86
21 |  | 5.56 | 6.8 | 6.7 | 6 | 10.46 | 10.7 | 10.01 | 10.36 | 4.79
22 |  | 2.37 | 6.9 | 6.5 | 17 | 0.73 | 12.56 | 11.33 | 11.32 | 9.21
23 |  | 2.97 | 6.7 | 6.6 | 21 | 10.47 | 0.81 | 10.97 | 11.08 | 11.61
24 |  | 3.3 | 6.6 | 6.6 | 16 | 10.87 | 8.61 | 0.58 | 10.78 | 10.15
25 |  | 2.87 | 6.6 | 6.6 | 16 | 10.3 | 8.51 | 7.7 | 2.48 | 9.8
26 |  | 4 | 6.8 | 6.6 | 14 | 10.15 | 10.42 | 8.02 | 7.93 | 2.24
27 |  | 7 | 6.8 | 6.5 | 17 | 2.19 | 10.86 | 9.99 | 8.32 | 7.49
28 |  | 5 | 6.7 | 6.6 | 8 | 8.33 | 2.4 | 9.98 | 10.14 | 7.89
29 |  | 7 | 6.8 | 6.6 | 8 | 8.42 | 8.31 | 2.31 | 10.27 | 9.67
30 |  | 5 | 6.7 | 6.6 | 14 | 10.26 | 8.77 | 7.8 | 2.24 | 9.79
31
Total |  | 86.51 | 202.5 | 197.7 | 376 | 261.15 | 263.54 | 251.63 | 261.77 | 263.33
Mo. Avg. |  | 2.8837 | 6.75 | 6.59 | 13.4286 | 8.705 | 8.7847 | 8.3877 | 8.7257 | 8.7777
PLANT STAFFING
Day Shift Operator |  |  | Class: | "A" | Certificate No. | CO# 4545-A | Name: |  | McGEARY, J.
Evening Shift Operator |  |  | Class: | "A" | Certificate No. | CO# 4474-A | Name: |  | BAYLER, J.
Night Shift Operator |  |  | Class: | "C" | Certificate No. | CO# 5613-C | Name: |  | BAROFSKY
Lead Operator |  |  | Class: | 0 | Certificate No. | CO# 2769-A | Name: |  | JUST, M.
DAILY SAMPLE RESULTS - B
| Permit Number |  | FLA041378 |  |  | Facility: | City of Fort Lauderdale G. T. Lohmeyer WWTF
| Monitoring Period: |  | From: | 2005-09-01 |  | To: | 2005-09-30
|  | Flow (mgd) | CBOD5 (mg/L | TSS (mg/L
Code |  | 50050 | 80082 | 00530
Mon. Site |  | INF-001 | INF-002 | INF-002
1 |  | 44.155 | 46.9 | 90
2 |  | 43.606 | 36.2 | 112
3 |  | 45.086 | 34.6 | 90
4 |  | 46.793 | 28 | 44
5 |  | 39.825 | 31.9 | 66
6 |  | 50.104 | 32.7 | 82
7 |  | 48.237 | 16.4 | 40
8 |  | 45.618 | 45 | 32
9 |  | 45.168 | 76.9 | 152
10 |  | 45.52 | 86 | 46
11 |  | 49.087 | 54.9 | 84
12 |  | 47.528 | 57.9 | 28
13 |  | 44.966 | 58.3 | 122
14 |  | 42.538 | 58.3 | 100
15 |  | 41.743 | 63.9 | 76
16 |  | 41.521 | 53.36 | 48
17 |  | 41.027 | 53.11 | 106
18 |  | 40.734 | 67.3 | 90
19 |  | 41.144 | 70.78 | LS
20 |  | 45.32 | 65.89 | 40
21 |  | 46.859 | 37.47 | 18
22 |  | 44.822 | 61.5 | 88
23 |  | 43.123 | 64.47 | 44
24 |  | 41.29 | 63.15 | 68
25 |  | 39.825 | 63.2 | 106
26 |  | 39.284 | 71 | 90
27 |  | 38.725 | 123 | 100
28 |  | 38.518 | 66 | 98
29 |  | 38.756 | 81 | 83
30 |  | 39.011 | 102 | 96
31
Total |  | 1299.933 | 1771.13 | 2239
Mo. Avg. |  | 43.3311 | 59.0377 | 77.2069

## JULIAN CONVERT
2005-09-01 | 38596 | 1999-01-01 | 2435
FROM DATE ON "DATA INPUT" PAGE | [5 empty] | 2005-09-01
2005
MONTHYY.PAR RANGE TO COMPILE (JULIAN DAY VALUES) FOR SPLIT PROGRAM ARE | [7 empty] | 244 | THROUGH | 2466
|  | 9 | SEPTEMBER
[5 empty] | 2005-09-01 | 2005-09-01 | 9
2005-09-01 |  |  |  |  | 1 | JANUARY |  | 1995 | 1995-01-01
[5 empty] | 2 | FEBRUARY |  | 1996 | 1996-01-01
[5 empty] | 3 | MARCH |  | 1997 | 1997-01-01
SEPTEMBER |  | 0 |  | 0 | 4 | APRIL |  | 1998 | 1998-01-01
|  | 1 |  | 2 | 5 | MAY |  | 1999 | 1999-01-01
|  | 0 |  |  | 6 | JUNE |  | 2000 | 2000-01-01
|  | 0 |  |  | 7 | JULY |  | 2001 | 2001-01-01
|  | 0 |  | 0 | 8 | AUGUST |  | 2002 | 2002-01-01
|  |  |  | 2 | 9 | SEPTEMBER |  | 2003 | 2003-01-01
[5 empty] | 10 | OCTOBER |  | 2004 | 2004-01-01
[5 empty] | 11 | NOVEMBER |  | 2005 | 2005-01-01
2005 |  |  |  |  | 12 | DECEMBER |  | 2006 | 2006-01-01
38596 | [6 empty] | SEPTEMBER | 2007 | 2007-01-01
38353 | [7 empty] | 2008 | 2008-01-01
243 | 1 |  | 1 | 244 | Thursday
| 2 |  | 2 | 245 | Friday
| 3 |  | 3 | 246 | Saturday
| 4 |  | 4 | 247 | Sunday
| 5 |  | 5 | 248 | Monday
| 6 |  | 6 | 249 | Tuesday
| 7 |  | 7 | 250 | Wednesday
| 8 |  | 8 | 251 | Thursday
| 9 |  | 9 | 252 | Friday
| 10 |  | 10 | 253 | Saturday
| 11 |  | 11 | 254 | Sunday
| 12 |  | 12 | 255 | Monday
| 13 |  | 13 | 256 | Tuesday
| 14 |  | 14 | 257 | Wednesday
| 15 |  | 15 | 258 | Thursday
| 16 |  | 16 | 259 | Friday
| 17 |  | 17 | 260 | Saturday
| 18 |  | 18 | 261 | Sunday
| 19 |  | 19 | 262 | Monday
| 20 |  | 20 | 263 | Tuesday
| 21 |  | 21 | 264 | Wednesday
| 22 |  | 22 | 265 | Thursday
| 23 |  | 23 | 266 | Friday
| 24 |  | 24 | 267 | Saturday
| 25 |  | 25 | 268 | Sunday
| 26 |  | 26 | 269 | Monday
| 27 |  | 27 | 270 | Tuesday
| 28 |  | 28 | 271 | Wednesday
| 29 |  | 29 | 272 | Thursday
| 30 |  | 30 | 273 | Friday
30