## DATA INPUT
ENTER THE AVERAGE MONTHLY INFLUENT FLOW
INTO THE CORROSPONDING BOXES BELOW:
FEBRUARY | 30.955 | JANUARY | 32.476
ENTER THE PRESENT MONTH AND YEAR IN BOX BELOW (A5) | [5 empty] | MARCH
2003-03-01 | [5 empty] | 2003
IW-1 | IW-2 | IW-3 | IW-4 | IW-5
36.1 | 36.3 | 37.1 | 34.8 | 35.3 | 2003-03-10
|  | ENTER INJECTION WELL SHUT-IN PRESSURE ABOVE |  |  | ENTER DATE OF SHUT-IN READINGS
ENTER SLUDGE DISPOSAL SITE FOR EACH WEEK BELOW
| WEEK 1 | WEEK 2 | WEEK 3 | WEEK 4
1 st | Nutri-Cylcle Inc. | Nutri-Cylcle Inc. | Nutri-Cylcle Inc. | Nutri-Cylcle Inc.
2 nd | Arcadia, FL | Arcadia, FL | Arcadia, FL | Arcadia, FL
RAW DATA REPORT ENTRY CATEGORIES
GTL PLANT DAILY PROCESS SUMMARY
[6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TOTAL RAW INFLUENT FLOW (MGD) | [5 empty] | 31.303 | 31.465 | 32.224 | 32.434 | 32.068 | 32.35 | 32.283 | 31.8 | 31.931 | 32.743 | 33.859 | 32.93 | 32.074 | 31.677 | 31.615 | 32.063 | 35.171 | 36.093 | 36.2 | 35.581 | 34.452 | 33.509 | 33.525 | 34.625 | 33.396 | 33.14 | 33.979 | 35.305 | 34.501 | 33.07 | 32.206
TOTAL EFFLUENT FLOW (MGD) | [5 empty] | 29.461 | 29.665 | 30.868 | 30.986 | 30.495 | 30.705 | 31.113 | 29.962 | 29.95 | 31.095 | 31.632 | 31.505 | 30.475 | 30.542 | 28.96 | 30.459 | 34.621 | 34.749 | 34.937 | 34.521 | 34.299 | 31.519 | 31.804 | 32.716 | 31.646 | 31.573 | 32.397 | 33.876 | 32.378 | 31.377 | 30.387
MAXIMUM HOURLY RAW INFLUENT FLOW (MGD) | [5 empty] | 1.722 | 1.715 | 1.736 | 1.706 | 1.683 | 1.692 | 1.675 | 1.703 | 1.714 | 1.671 | 1.707 | 1.719 | 1.671 | 1.674 | 1.748 | 1.728 | 1.802 | 1.893 | 1.883 | 1.836 | 1.775 | 1.774 | 1.736 | 1.78 | 1.755 | 1.742 | 1.808 | 1.901 | 1.854 | 1.73 | 1.736
MAXIMUM INSTANANEOUS PEAK RAW INFUENT FLOW (MGD) | [5 empty] | 52.656 | 53.688 | 51.531 | 52.25 | 53.094 | 49.438 | 50.781 | 51.563 | 52.219 | 51.281 | 51.656 | 52.469 | 51.344 | 51.594 | 52.688 | 53.063 | 56.313 | 53.438 | 55.938 | 54.063 | 53.625 | 53.906 | 51.219 | 53.781 | 52.656 | 51.031 | 54.25 | 57.969 | 53.375 | 52.688 | 50.469
MINIMUM INSTANANEOUS PEAK RAW INFUENT FLOW (MGD) | [5 empty] | 0.594 | 0.594 | 0.313 | 1 | 0.438 | 0.563 | 0.906 | 0.625 | 1.094 | 1.156 | 1.158 | 0.875 | 1 | 0.781 | 0.531 | 0.813 | 1.9094 | 11.781 | 0.813 | 1.094 | 1.125 | 8.344 | 10.344 | 10.281 | 12.031 | 1.031 | 11.906 | 4.5 | 9.781 | 0.719 | 2.063
TOTAL RETURN ACTIVATED SLUDGE FLOW (MGD) | [5 empty] | 12.556 | 12.491 | 12.339 | 12.7 | 13.149 | 13.232 | 13.228 | 12.401 | 12.633 | 13.131 | 13.14 | 12.934 | 12.647 | 13.535 | 12.58 | 12.792 | 13.616 | 13.906 | 13.239 | 13.598 | 13.459 | 12.414 | 12.512 | 13.045 | 13.76 | 13.675 | 13.991 | 13.787 | 12.877 | 12.682 | 12.912
TOTAL WASTE FLOW TO DEWATERING PROCESS (MG) | [5 empty] | 0 | 0.19797 | 0.55866 | 0.55326 | 0.56425 | 0.54754 | 0.17834 | 0 | 0.148 | 0.52059 | 0.52 | 0.507 | 0.57 | 0.16569 | 0 | 0 | 0 | 0 | 0.24 | 0.63 | 0.36563 | 0 | 0.22671 | 0.663 | 0.582 | 0.595 | 0.599 | 0.31678 | 0 | 0.32697 | 0.515
TOTAL DAILY RAINFALL | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 1.2 | 0 | 0 | 0 | 0.25 | 0 | 0.86 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0 | 0 | 0 | 0.75 | 0 | 0 | 0 | 0.05
RAW INFLUENT pH | [5 empty] | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 6.4 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.1 | 7.2 | 7.2 | 7.2 | 7.2 | 7.3 | 7.2 | 7.2 | 7.2 | 7 | 7 | 7.1 | 7.2 | 7.2 | 7.2 | 7.2
RAW INFLUENT HYDROGEN SULFIDE (PPM) | [5 empty] | 8 | 7 | 6 | 6 | 6 | 8 | 5 | 7 | 8 | 7 | 6 | 6 | 6 | 7 | 7 | 5 | 6 | 4 | 5 | 5 | 6 | 7 | 7 | 7 | 6 | 5 | 6 | 5 | 6 | 7 | 7
RAW INFLUENT TEMPERATURE (F ) | [5 empty] | 80 | 83 | 80 | 80 | 81 | 81 | 81 | 81 | 82 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 80 | 81 | 81 | 81 | 81 | 81 | 81 | 80 | 77 | 81 | 79 | 78 | 80 | 81 | 80
TOTAL DAILY KILOWATTS (FPL POWER CONSUMPTION) | [5 empty] | 22742 | 24511 | 27200 | 27100 | 26845 | 25999 | 23807 | 21868 | 25937 | 25813 | 28210 | 25730 | 25012 | 21583 | 22656 | 23994 | 25679 | 24569 | 27239 | 23948 | 24947 | 22121 | 23788 | 30152 | 27012 | 22059 | 33189 | 38295 | 35192 | 36507 | 28324
GTL PLANT DAILY PROCESS SUMMARY
(CONTINUED)
[6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
FINAL EFFLUENT FREE CHLORINE RESIDUAL (PPM) | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FINAL EFFLUENT TOTAL CHLORINE RESIDUAL (PPM) | [5 empty] | 1.1 | 1 | 0.8 | 0.9 | 0.9 | 0.9 | 1.1 | 1.1 | 1.1 | 1 | 0.9 | 1 | 0.9 | 1 | 1 | 0.8 | 0.9 | 0.8 | 0.9 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 1 | 0.8 | 0.9 | 1.2 | 1.1 | 1
FINAL EFFLUENT pH (daily average) | [5 empty] | 6.4 | 6.4 | 6.4 | 6.5 | 6.4 | 6.4 | 6.3 | 6.3 | 6.4 | 6.4 | 6.4 | 6.4 | 6.3 | 6.3 | 6.4 | 6.3 | 6.4 | 6.4 | 6.5 | 6.5 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.3 | 6.3 | 6.4 | 6.4 | 6.4
FINAL EFFLUENT pH (daily minimum) | [5 empty] | 6.3 | 6.3 | 6.4 | 6.4 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.4 | 6.4 | 6.2 | 6.2 | 6.3 | 6.2 | 6.3 | 6.3 | 6.4 | 6.4 | 6.3 | 6.3 | 6.3 | 6.3 | 6.4 | 6.4 | 6.3 | 6.2 | 6.3 | 6.3 | 6.3
FINAL EFFLUENT pH (daily maximum) | [5 empty] | 6.4 | 6.4 | 6.5 | 6.6 | 6.4 | 6.5 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.5 | 6.4 | 6.4 | 6.4 | 6.5 | 6.5 | 6.6 | 6.6 | 6.5 | 6.5 | 6.4 | 6.5 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4
FINAL EFFLUENT TEMPARTURE (F ) | [5 empty] | 79 | 79 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 81 | 80 | 80 | 80 | 80 | 81 | 81 | 81 | 81 | 80 | 80 | 80 | 80 | 80 | 81 | 80 | 79
AVERAGE CLARIFIER BLANKET DEPTH (INCHES) | [5 empty] | 49 | 41 | 43 | 44 | 34 | 33 | 34 | 48 | 46 | 58 | 58 | 40 | 36 | 38 | 57 | 51 | 71 | 59 | 44 | 63 | 63 | 89 | 69 | 71 | 67 | 59 | 52 | 64 | 63 | 59 | 56
FINAL EFFLUENT SAMPLE TEMPARTURE (C ) | [5 empty] | 2 | 5 | 3 | 0 | 0.5 | 5 | 2 | 2 | 0 | 0 | 4 | 5 | 5 | 3 | 2 | 5 | 5 | 5 | 5 | 5 | 4 | 3 | 0.5 | 5 | 5 | 5 | 5 | 0 | 1 | 5 | 5
TOTAL RETURN ACTIVATED SLUDGE FLOW TO REACTOR ONE (MGD) | [5 empty] | 6.532 | 6.562 | 6.468 | 6.476 | 6.483 | 6.46 | 6.433 | 6.432 | 6.464 | 6.389 | 6.456 | 6.492 | 6.6 | 6.686 | 6.447 | 6.507 | 6.68 | 6.491 | 6.432 | 6.528 | 6.468 | 6.431 | 6.373 | 6.425 | 6.481 | 6.475 | 6.597 | 6.502 | 6.544 | 6.539 | 6.489
TOTAL RETURN ACTIVATED SLUDGE FLOW TO REACTOR TWO (MGD) | [5 empty] | 6.024 | 5.929 | 5.872 | 6.232 | 6.666 | 6.772 | 6.785 | 5.97 | 6.17 | 6.748 | 6.685 | 6.442 | 6.047 | 6.848 | 6.133 | 6.285 | 6.936 | 7.415 | 6.808 | 7.071 | 6.991 | 5.933 | 6.138 | 6.621 | 7.278 | 7.201 | 7.395 | 7.284 | 6.333 | 6.142 | 6.424
GTL PLANT DAILY PROCESS SUMMARY
CONTINUED
[6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TOTAL DAILY TRUCKING LOAD OF DEWATERED SLUDGE REMOVED | [5 empty] | 0 | 1 | 6 | 5 | 6 | 8 | 3 | 0 | 1 | 6 | 6 | 6 | 6 | 4 | 0 | 0 | 0 | 0 | 2 | 7 | 5 | 0 | 2 | 7 | 6 | 7 | 6 | 5 | 0 | 2 | 6
TOTAL DAILY HYDROGEN PEROXIDE CONSUMED (LBS) | [5 empty] | 2495 | 2435 | 2017 | 1388 | 1178 | 2356 | 2545 | 2695 | 2843 | 2994 | 3004 | 3114 | 3263 | 3064 | 3164 | 2834 | 2944 | 2824 | 3463 | 2155 | 1308 | 1408 | 419 | 1977 | 2924 | 2435 | 2575 | 2455 | 2584 | 2565 | 2165
TOTAL DAILY CHLORINE CONSUMED (LBS) | [5 empty] | 1180 | 1180 | 1220 | 1140 | 1340 | 1220 | 1300 | 1260 | 1140 | 1360 | 1180 | 1160 | 1320 | 1300 | 1120 | 1170 | 1260 | 1040 | 1200 | 1240 | 1180 | 1100 | 1420 | 1160 | 1160 | 1180 | 1240 | 1120 | 1100 | 940 | 1120
TOTAL DAILY POLYMER CONSUMED (GALS) | [5 empty] | 0 | 34 | 83 | 138 | 77 | 0 | 33 | 0 | 22 | 70 | 123 | 9 | 68 | 20 | 0 | 2 | 9 | 15 | 24 | 0 | 123 | 0 | 45 | 59 | 42 | 66 | 65 | 25 | 0 | 81 | 52
TOTAL TONS OF LIME DELIVERED DAILY | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTAL DAILY GASIOUS OXYGEN PRODUCED (TONS) | [5 empty] | 34.7 | 36.6 | 37.3 | 36 | 37.4 | 37.8 | 37.8 | 36 | 37.4 | 38 | 39 | 38.9 | 38.9 | 39.9 | 40.2 | 38.4 | 39.5 | 42.3 | 45.8 | 41.2 | 39.7 | 42.1 | 34.5 | 36.7 | 38 | 38 | 37.6 | 39.6 | 42.7 | 42.4 | 39.4
AVERAGE PERCENT OXYGEN PRODUCT PURITY | [5 empty] | 99.5 | 99.2 | 99.2 | 99.4 | 99.1 | 99.1 | 99.1 | 99.6 | 99.3 | 99 | 99.3 | 99.3 | 99.2 | 99 | 98.9 | 99.3 | 99 | 98.5 | 99.2 | 99 | 98.2 | 98.2 | ER | 99.7 | 99.1 | 98.9 | 98.7 | 98 | 97.6 | 97.9 | 98.9
TOTAL DAILY LIQUID OXYGEN IN STORAGE (TONS) | [5 empty] | 152 | 152 | 154 | 156 | 156 | 157 | 157 | 157 | 156 | 156 | 157 | 158 | 159 | 158 | 158 | 158 | 158 | 159 | 157 | 160 | 160 | 160 | 160 | 161 | 161 | 162 | 163 | 157 | 115 | 117 | 116
MONITORING WELL PRESSURE DATA
MONITORING WELL ONE UPPER/LOWER LEVEL
| MW-1 |  | UPPER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MINIMUM | [5 empty] | 47.7 | 47.79 | 46.5 | 46.92 | 47.56 | 47.64 | 47.62 | 47.61 | 47.68 | 43.22 | 29.06 | ER | 47.39 | 47.75 | 47.82 | 33.32 | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER
MAXIMUM | [5 empty] | 48.07 | 48.15 | 48.11 | 47.75 | 47.84 | 47.85 | 47.84 | 47.8 | 47.86 | 47.91 | 48.2 | 47.98 | 47.97 | 48.07 | 48.17 | 48.28 | 48.41 | ER | ER | 14.86 | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER
AVERAGE | [5 empty] | 47.94 | 47.96 | 47.32 | 47.38 | 47.66 | 47.73 | 47.69 | 47.64 | 47.79 | 45.67 | 46.37 | 47.53 | 47.86 | 47.95 | 48 | 47.89 | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER
| MW-1 |  | LOWER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MINIMUM | [5 empty] | 41.45 | 41.49 | 29.97 | 29.93 | 41.2 | 41.36 | 41.36 | 41.38 | 41.42 | 33.05 | 25.75 | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER
MAXIMUM | [5 empty] | 42.11 | 42.37 | 41.71 | 41.3 | 41.43 | 41.55 | 41.54 | 41.55 | 41.65 | 41.59 | 41.34 | 41.44 | 41.42 | ER | ER | ER | ER | ER | ER | 13.47 | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER
AVERAGE | [5 empty] | 41.79 | 42.07 | 35.03 | 37.58 | 41.38 | 41.46 | 41.47 | 41.47 | 41.5 | 36.98 | 38.07 | 41.12 | ER | ER | ER | ER | ER | ER | 10.7 | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER
MONITORING WELL TWO UPPER/LOWER LEVEL
| MW-2 |  | UPPER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MINIMUM | bar: 1 to 31
MAXIMUM | bar: 1 to 31
AVERAGE | bar: 1 to 31
| MW-2 |  | LOWER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MINIMUM | [5 empty] | 41.75 | 41.88 | 30.92 | 30.87 | 41.6 | 41.78 | 41.84 | 41.83 | 41.92 | 33.77 | 26.64 | ER | ER | 41.58 | 41.76 | 30.27 | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER
MAXIMUM | [5 empty] | 42 | 42.11 | 42.08 | 41.62 | 41.82 | 41.89 | 41.9 | 41.92 | 42.02 | 42.06 | 41.52 | 41.73 | 41.77 | 41.88 | 42.02 | 42.15 | 42.27 | ER | ER | 36.17 | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER
AVERAGE | [5 empty] | 41.92 | 41.98 | 35.83 | 38.05 | 41.71 | 41.9 | 41.93 | 41.93 | 41.98 | 37.6 | 38.46 | 41.31 | 38.29 | 41.84 | 41.96 | 41.83 | 29.88 | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER
MONITORING WELL THREE UPPER/LOWER LEVEL
| MW-3 |  | UPPER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MINIMUM | [5 empty] | 29.76 | 29.86 | 22.68 | 22.51 | 30.02 | 30.17 | 30.22 | 30.21 | 30.32 | 17.36 | 17.27 | ER | ER | 29.9 | 30.02 | 23.16 | ER | ER | ER | ER | 23.88 | 30.15 | 30.2 | 17.97 | 17.91 | 29.92 | 30.19 | 30.35 | 30.37 | 30.29 | 19.62
MAXIMUM | [5 empty] | 30.08 | 30.17 | 30.12 | 30.12 | 30.31 | 30.38 | 30.38 | 30.39 | 30.5 | 30.52 | 29.68 | 29.96 | 30.09 | 30.22 | 30.34 | 30.47 | 30.57 | ER | ER | 30.4 | 30.4 | 30.39 | 30.42 | 30.51 | 29.94 | 30.31 | 30.54 | 30.59 | 30.58 | 30.58 | 30.29
AVERAGE | [5 empty] | 29.95 | 30 | 25.93 | 27.56 | 30.19 | 30.29 | 30.33 | 30.33 | 30.45 | 23.32 | 24.94 | 29.72 | 28.81 | 30.07 | 30.22 | 30.23 | 21.39 | ER | ER | 16.51 | 30.22 | 30.26 | 30.34 | 23.5 | 25.97 | 30.11 | 30.39 | 30.48 | 30.48 | 30.49 | 24.39
| MW-3 |  | LOWER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MINIMUM | [5 empty] | 44.77 | 44.91 | 37.66 | 37.63 | 44.64 | 44.81 | 44.88 | 44.86 | 44.95 | 36.75 | 28.13 | ER | ER | 44.72 | 44.85 | 32.14 | ER | ER | ER | ER | 33.43 | 45.01 | 45.08 | 39.79 | 39.81 | 44.73 | 44.95 | 45.11 | 45.11 | 45.07 | 36.78
MAXIMUM | [5 empty] | 45 | 45.13 | 45.09 | 44.64 | 44.83 | 44.92 | 44.94 | 44.95 | 45.04 | 45.09 | 44.5 | 44.74 | 44.83 | 44.98 | 45.1 | 45.21 | 45.33 | ER | ER | 45.09 | 45.1 | 45.14 | 45.21 | 45.29 | 44.73 | 45.02 | 45.22 | 45.28 | 45.27 | 45.33 | 45.1
AVERAGE | [5 empty] | 44.95 | 44.99 | 40.92 | 42.28 | 44.83 | 44.93 | 44.97 | 44.95 | 45 | 40.65 | 41.48 | 44.27 | 42.72 | 44.89 | 44.99 | 44.84 | 31.58 | ER | ER | 19.98 | 44.91 | 45.02 | 45.06 | 42.34 | 43.01 | 44.89 | 45.02 | 45.18 | 45.18 | 45.28 | 41.47
MONITORING WELL RMW-1 UPPER/LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
[5 empty] | JULIAN DATE | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90
| RMW-1 |  | UPPER LEVEL
MINIMUM | [5 empty] | 42.35 | 42.44 | 32.05 | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | 8.95 | 8.97 | ER | ER | ER | ER | ER | ER | 8.98 | 8.97 | ER | 8.99 | 8.97 | 8.97 | ER | ER | 8.92
MAXIMUM | [5 empty] | 42.51 | 42.59 | 42.57 | 67.07 | 67.59 | 67.94 | 68.02 | 67.78 | 67.05 | 31.03 | 67.93 | 67.94 | 67.97 | 66.48 | 56.41 | 32.01 | 67.82 | 67.84 | 67.55 | 67.68 | 67.05 | 67 | 33.03 | 33.76 | 68 | 60.17 | 19.02 | 48.73 | 66.63 | 68.02 | 24.76
AVERAGE | [5 empty] | 42.44 | 42.51 | 36.72 | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | 14.02 | 12.71 | ER | ER | ER | ER | ER | ER | 11.04 | 12.35 | ER | 16.17 | 10.84 | 15.69 | ER | ER | 10.56
| RMW-1 |  | LOWER LEVEL
MINIMUM | [5 empty] | 21.54 | 21.61 | 19.83 | 19.58 | 20.99 | 21.19 | 21.25 | 21.21 | 21.32 | 21.39 | 21.36 | 21.31 | 21.32 | 21.36 | 21.43 | 21.51 | 21.64 | 21.77 | 21.72 | 21.67 | 21.61 | 21.56 | 21.59 | 21.59 | 21.58 | 21.6 | 21.67 | 21.73 | 21.7 | 21.63 | 19.72
MAXIMUM | [5 empty] | 21.68 | 21.76 | 21.77 | 21 | 21.21 | 21.3 | 21.32 | 21.32 | 21.43 | 21.5 | 21.48 | 21.47 | 21.46 | 21.51 | 21.59 | 21.67 | 21.85 | 21.84 | 21.81 | 21.76 | 21.75 | 21.7 | 21.69 | 21.78 | 21.71 | 21.73 | 21.86 | 21.87 | 21.79 | 21.83 | 21.63
AVERAGE | [5 empty] | 21.61 | 21.69 | 20.83 | 20.59 | 21.09 | 21.25 | 21.28 | 21.29 | 21.38 | 21.43 | 21.42 | 21.4 | 21.39 | 21.45 | 21.53 | 21.6 | 21.76 | 21.8 | 21.76 | 21.7 | 21.66 | 21.62 | 21.65 | 21.69 | 21.64 | 21.68 | 21.78 | 21.8 | 21.75 | 21.76 | 20.74
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
| INJECTION WELL ONE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 10.91 | 12.1 | 12.8 | 12.39 | 11.74 | 12.77 | 12.85 | 11.12 | 11.96 | 12.65 | 12.77 | 12.9 | 12.82 | 10.19 | 11.05 | 11.2 | 12.09 | ER | ER | 11.03 | 14.65 | 11.56 | 11.37 | 13.03 | 11.31 | 11.38 | 11.75 | 11.85 | 11.68 | 11.33 | 11.25
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 5.33 | 5.47 | 4.07 | 4.59 | 4.52 | 3.36 | 4.51 | 4.06 | 4.03 | 2.53 | 0 | ER | ER | ER | 4.72 | 4.24 | ER | ER | ER | ER | 4.45 | 4.9 | 4.39 | 4.18 | 4.29 | 4.03 | 4.25 | 4.18 | 4.16 | 4.2 | 3.93
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 8.38 | 8.41 | 8.19 | 8.21 | 8.1 | 8.17 | 8.25 | 8.16 | 7.94 | 8.26 | 7.54 | 8.25 | 4.12 | 2.54 | 7.93 | 8.03 | 5.16 | ER | ER | 2.26 | 8.86 | 8.29 | 8.41 | 8.95 | 8.33 | 8.31 | 8.53 | 8.97 | 8.54 | 8.27 | 8.03
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 54.19 | 57.73 | 60.11 | 60.59 | 59.92 | 59.55 | 60.17 | 54.03 | 57.21 | 59.8 | 60.14 | 60.01 | 60.2 | 56.96 | 54.67 | 55.44 | 58.07 | ER | ER | 54.51 | 66.63 | 56.96 | 55.84 | 60.68 | 56.55 | 55.49 | 56.47 | 56.74 | 56.47 | 55.2 | 54.57
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 40.5 | 40.42 | 38.02 | 38.63 | 38.54 | 36.89 | 38.74 | 38.34 | 37.97 | 38.44 | 25.87 | ER | 0.06 | 33.26 | 39.4 | 28.32 | ER | ER | ER | ER | 21.01 | 40.23 | 39.42 | 40.89 | 39.13 | 38.7 | 38.95 | 38.88 | 38.82 | 38.86 | 36.86
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 47.37 | 47.46 | 47.36 | 46.98 | 46.76 | 46.87 | 47.09 | 46.88 | 46.44 | 47.46 | 46.69 | 47.12 | 46.81 | 47.15 | 46.65 | 46.77 | 29.37 | ER | ER | 12.03 | 48.72 | 47.62 | 47.92 | 48.93 | 47.58 | 47.56 | 48.04 | 49.15 | 48.17 | 47.47 | 46.33
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
| INJECTION WELL TWO |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 10.97 | 12.14 | 12.94 | 12.52 | 11.78 | 12.76 | 12.93 | 11.15 | 12.07 | 12.74 | ER | 12.93 | 12.89 | 11.8 | 11.12 | 11.34 | 12.24 | ER | ER | 11.17 | 14.76 | 11.66 | 11.43 | 12.47 | 11.49 | 11.41 | 11.82 | 11.9 | 11.74 | 11.38 | 12.79
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 5.2 | 5.35 | 3.71 | 4.35 | 4.32 | 2.74 | 4.27 | 3.79 | 3.61 | 0.04 | 3.73 | ER | 2.5 | 3.76 | 4.53 | 3.96 | ER | ER | ER | ER | 4.31 | 4.63 | 4.27 | 4.91 | 4.11 | 3.84 | 4.12 | 4.18 | 4 | 4.1 | 3.63
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 8.39 | 8.44 | 8.16 | 8.21 | 8.09 | 8.16 | 8.27 | 8.19 | 7.95 | 8.24 | 9.13 | 8.29 | 8.16 | 8.2 | 7.99 | 8.09 | 5.17 | ER | ER | 2.3 | 8.93 | 8.33 | 8.38 | 8.76 | 8.37 | 8.35 | 8.57 | 9 | 8.6 | 8.32 | 8.08
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 53.29 | 56.77 | 59 | 59.55 | 58.76 | 58.43 | 59 | 53.12 | 56.21 | 58.63 | 89.5 | 58.84 | 59.05 | ER | 53.58 | 54.41 | 56.92 | ER | ER | 53.48 | 65.34 | 55.9 | 54.73 | 57.76 | 55.42 | 54.41 | 55.33 | 55.66 | 55.38 | 54.2 | 54.16
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 39.72 | 39.65 | 37.29 | 37.89 | 37.81 | 36.19 | 38.01 | 37.59 | 37.25 | 36.2 | 25.32 | ER | 36.4 | 37.83 | 38.66 | 27.77 | ER | ER | ER | ER | 30.57 | 39.48 | 38.67 | 40.31 | 38.33 | 37.95 | 38.19 | 38.12 | 38.06 | 38.09 | 35.24
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 46.49 | 46.58 | 46.47 | 46.11 | 45.88 | 46 | 46.21 | 45.97 | 45.59 | 46.5 | 48.87 | 46.23 | 46.35 | 46.35 | 45.78 | 45.87 | 28.98 | ER | ER | 11.8 | 47.83 | 46.75 | 47.01 | 48.01 | 46.64 | 46.65 | 47.11 | 48.18 | 47.25 | 46.54 | 45.44
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
| INJECTION WELL THREE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 9.58 | 10.58 | 11.3 | 10.93 | 10.27 | 11.1 | 11.29 | 9.73 | 10.58 | 11.1 | 13.98 | 11.29 | 11.31 | 10.34 | 9.73 | 9.88 | 10.59 | ER | ER | ER | 10.29 | 10.42 | 10.17 | 11.59 | 10.2 | 10.12 | 10.43 | 10.52 | 10.39 | 10.03 | 9.9
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 4.58 | 4.61 | 3.22 | 3.7 | 3.64 | 2.47 | 3.67 | ER | 3.1 | 1.31 | ER | ER | ER | 3.26 | 3.82 | 3.35 | ER | ER | ER | ER | ER | 4.11 | 3.77 | ER | 3.66 | 3.37 | 3.6 | 3.63 | 3.58 | 3.55 | 3.25
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 7.31 | 7.36 | 7.09 | 7.12 | 7.01 | 7.09 | 7.16 | 6.25 | 6.89 | 7.16 | 7.42 | 7.2 | 6.79 | 7.12 | 6.9 | 6.98 | 4.48 | ER | ER | ER | ER | 7.38 | 7.47 | 6.93 | 7.41 | 7.39 | 7.56 | 7.94 | 7.57 | 7.3 | 7.1
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 54.54 | 58.13 | 60.53 | 61.03 | 60.32 | 59.97 | 60.59 | 54.35 | 57.61 | 60.2 | 72.1 | 60.37 | 60.58 | 57.26 | 54.98 | 55.8 | 58.44 | ER | ER | 54.81 | 57.37 | 57.28 | 56.13 | 61.02 | 56.86 | 55.79 | 56.79 | 57.06 | 56.72 | 55.5 | 54.87
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 40.65 | 40.57 | 38.13 | 38.75 | 38.66 | 36.97 | 38.86 | 35.49 | 38.08 | 38.53 | 26 | ER | ER | 38.69 | 39.52 | 28.42 | ER | ER | ER | ER | 21.12 | 40.35 | 39.53 | 36.24 | 39.24 | 38.8 | 39.05 | 38.99 | 38.9 | 38.92 | 37.13
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 47.62 | 47.69 | 47.58 | 47.22 | 46.98 | 47.09 | 47.31 | 45.9 | 46.66 | 47.68 | 48.51 | 47.34 | 41.95 | 47.48 | 46.85 | 46.99 | 29.51 | ER | ER | 12.09 | 47.96 | 47.81 | 48.13 | 47.79 | 47.8 | 47.75 | 48.25 | 49.34 | 48.37 | 47.65 | 46.61
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
FUTURE
| INJECTION WELL FOUR |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 0.13 | 0.13 | 0.14 | 0.14 | 0.14 | 0.13 | 0.14 | 0.14 | 0.14 | 0.13 | 0.23 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.13 | ER | ER | 0.11 | 0.14 | 0.15 | 0.14 | 0.14 | 0.14 | 0.14 | 0.13 | 0.14 | 0.15 | 0.14 | 0.12
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.11 | 0.1 | 0.1 | 0.1 | 0.05 | ER | 0.11 | 0.1 | 0.1 | 0.06 | ER | ER | ER | ER | 0.07 | 0.12 | 0.11 | 0.11 | 0.1 | 0.11 | 0.11 | 0.11 | 0.11 | 0.1 | 0.07
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.12 | 0.12 | 0.12 | 0.11 | 0.11 | 0.12 | 0.12 | 0.12 | 0.12 | 0.11 | 0.07 | ER | ER | 0.02 | 0.12 | 0.13 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.13 | 0.12 | 0.1
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 35.15 | 35.69 | 35.93 | 36.05 | 35.68 | 35.87 | 36.49 | 36.96 | 37.21 | 37.4 | 38.4 | 37.27 | 37.52 | 59.8 | 37.41 | 37.63 | 38.04 | ER | ER | 37.27 | 37.74 | 37.73 | 37.66 | 38.13 | 37.74 | 41.5 | 41.65 | 41.77 | 41.67 | 41.45 | 40.87
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 32.43 | 32.33 | 32.66 | 32.86 | 32.92 | 32.45 | 32.83 | 34.1 | 34.15 | 34.3 | 17.94 | ER | 34.27 | 34.75 | 35.24 | 22 | ER | ER | ER | ER | 23.51 | 35.26 | 35.14 | 35.13 | 35.2 | 35.84 | 39.23 | 39 | 38.94 | 38.88 | 34.04
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 33.84 | 33.88 | 34.18 | 34.19 | 34.15 | 34.13 | 34.66 | 35.64 | 35.61 | 35.68 | 35.74 | 35.49 | 35.84 | 36.21 | 36.31 | 36.29 | 22.62 | ER | ER | 8.65 | 36.4 | 36.44 | 36.52 | 36.63 | 36.66 | 39.81 | 40.45 | 40.59 | 40.39 | 40.17 | 39.59
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
| INJECTION WELL FIVE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 9.68 | 10.67 | 11.34 | 10.97 | 10.44 | 11.17 | 11.33 | 9.81 | 10.6 | 11.23 | 13.79 | 11.28 | 11.3 | 10.37 | 9.76 | 9.93 | 10.69 | ER | ER | 9.74 | 13.04 | 10.27 | 10.01 | 10.69 | 10.11 | 10 | 10.33 | 10.4 | 10.29 | 9.97 | 9.82
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | ER | ER | 3.65 | 4.18 | 4.13 | 2.92 | 4.1 | 3.71 | 3.56 | 1.59 | ER | ER | 2.8 | 3.7 | 4.28 | 3.8 | ER | ER | ER | ER | 4.12 | 4.41 | 4.08 | 3.83 | 4.02 | 3.76 | 3.96 | 3.99 | 3.96 | 3.95 | 3.59
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 5.36 | 5.44 | 7.34 | 7.37 | 7.27 | 7.32 | 7.4 | 7.35 | 7.15 | 7.38 | 7.58 | 7.4 | 7.32 | 7.33 | 7.14 | 7.22 | 4.62 | ER | ER | 2.02 | 7.94 | 7.45 | 7.53 | 8 | 7.49 | 7.47 | 7.63 | 8 | 7.66 | 7.42 | 7.18
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 53.96 | 57.78 | 60.08 | 59.98 | 59.47 | 59.57 | 59.4 | 54.13 | 56.31 | 59.12 | 71 | 59.8 | 60.1 | 56.77 | 54.5 | 55.47 | 58.06 | ER | ER | 54.02 | 65.03 | 56.25 | 54.84 | 57.82 | 55.73 | 78.7 | 56.39 | 56.6 | 56.22 | 54.97 | 54.5
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 33.47 | 33.47 | 37.83 | 38.51 | 38.39 | 36.69 | 38.62 | 38.15 | 37.84 | 38.15 | 25.61 | ER | 36.95 | 38.37 | 39.09 | 27.85 | ER | ER | ER | ER | 31.7 | 39.5 | 39 | 40.49 | 38.9 | 19.39 | 38.82 | 38.78 | 38.72 | 38.77 | 36.11
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 43.57 | 43.69 | 46.99 | 46.67 | 46.49 | 46.62 | 46.82 | 46.6 | 46.21 | 47.22 | 48.02 | 46.85 | 46.97 | 46.97 | 46.3 | 46.51 | 29.43 | ER | ER | 11.87 | 47.92 | 46.61 | 47.08 | 48.19 | 46.88 | 46.64 | 47.93 | 48.99 | 48 | 47.32 | 46.33
GTL DAILY LABORATORY ANALYSIS REPORT DATA
| RAW INFLUENT DATA |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
RAW TOTAL SUSPENDED SOLIDS | [5 empty] | 94 | 104 | 102 | 126 | 126 | 53 | 98 | 111 | 116 | 120 | 164 | 120 | 120 | 115 | 105 | 57 | 96 | 98 | 104 | 130 | 104 | 245 | 91 | 59 | 55 | 152 | 94 | 90 | 72 | 40 | 85
RAW FIXED SUSPENDED SOLIDS | [5 empty] | 8 | 14 | 8 | 4 | 24 | 11 | 2 | 17 | 20 | 26 | 24 | 4 | 24 | 11 | 14 | 3 | 17 | 10 | 12 | 18 | 9 | 64 | 10 | 4 | 5 | 13 | 7 | 7 | 6 | 6 | 12
RAW ALKILINITY | [5 empty] | 210 | 212 | 216 | 210 | 218 | 220 | 212 | 212 | 222 | 216 | 218 | 204 | 214 | 196 | 210 | 210 | 216 | 196 | 200 | 204 | 216 | 232 | 230 | 226 | 222 | 204 | 194 | 196 | 200 | 210 | 208
RAW CHLORIDES | [5 empty] | 670 | 680 | 710 | 760 | 770 | 740 | 600 | 600 | 770 | 730 | 730 | 650 | 660 | 620 | 650 | LS | 720 | 690 | 700 | 720 | 700 | 700 | 690 | 710 | 650 | 690 | 700 | 700 | 720 | 660 | 700
RAW COD | [5 empty] | 359 | 331 |  |  | 324 | 319 | 318 | 335 | 351 |  |  | 314 | 310 | 367 | 325 | 324 |  |  | 338 | 310 | 315 | 261 | 418 |  |  | 332 | 271 | 916 | 250 | 335
RAW CBOD | [5 empty] | 106.7 | 113 | 116.5 | 104 | 107 | 93 | 109.1 | 115 | 105 | 100.8 | 103.3 | 102 | 90.3 | 102.7 | 107.1 | 107 | 87.3 | 86.4 | 92.9 | 104 | 112.9 | 113.9 | 101.4 | 97.2 | 91 | 118 | 98 | 96 | 74 | 96 | 102
| EFFLUENT DATA |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
EFFLUENT TOTAL DISSOLVED SOLIDS | [5 empty] | 1218 | 1261 | 1377 | 1462 | 1548 | 1363 | 1582 | 1358 | 1296 | 1356 | 1255 | 1195 | 1267 | 1188 | 1276 | 1231 | 1276 | 1235 | 1315 | 1345 | 1240 | 1240 | 1157 | 1259 | 1234 | 1346 | 1378 | 1285 | 1239 | 1198 | 1284
EFFLUENT TOTAL SUSPENDED SOLIDS | [5 empty] | 14 | 13 | 8 | 10 | 13 | 13 | 10 | 7 | 10 | 17 | 17 | 12 | 18 | 7 | 11 | 14 | 23 | 14 | 15 | 27 | 16 | 20 | 23 | 18 | 18 | 20 | 14 | 13 | 12 | 9 | 14
EFFLUENT FIXED SUSPENDED SOLIDS | [5 empty] | 0 | 4 | 0 | 0 | 3 | 2 | 0 | 1 | 3 | 6 | 3 | 0 | 4 | 1 | 1 | 2 | 8 | 0 | 0 | 2 | 1 | 2 | 1 | 2 | 1 | 0 | 0 | 1 | 1 | 1 | 2
EFFLUENT ALKILINITY | [5 empty] | 188 | 188 | 192 | 190 | 196 | 196 | 186 | 190 | 190 | 194 | 196 | 186 | 192 | 188 | 192 | 194 | 186 | 176 | 184 | 186 | 206 | 196 | 194 | 190 | 184 | 186 | 184 | 182 | 180 | 192 | 190
EFFLUENT TURBIDITY | [5 empty] | 5.21 | 5.72 | 6.25 | 5.95 | 7.89 | 6.43 | 6.85 | 6.72 | 8.07 | 7.04 | 6.68 | 5.73 | 5.77 | 6.26 | 6.82 | 7.23 | 10.5 | 9.78 | 7.46 | 8.45 | 9.46 | 8.36 | 10.7 | 11.3 | 10.4 | 8.66 | 8.76 | 7.28 | 7.67 | 7.03 | 7.72
EFFLUENT CHLORIDES | [5 empty] | 640 | 640 | 700 | 730 | 760 | 730 | 680 | 650 | 680 | 750 | 640 | 630 | 630 | 600 | 610 | LS | 670 | 680 | 660 | 660 | 680 | 690 | 650 | 700 | 630 | 640 | 660 | 680 | 700 | 660 | 700
EFFLUENT CONDUCTIVITY | [5 empty] | 2550 | 2640 | 2760 | 2950 | 2850 | 2880 | 2750 | 2700 | 2730 | 2760 | 2630 | 2520 | 2440 | 2390 | 2540 | 2580 | 2600 | 2620 | 2600 | 2540 | 2580 | 2390 | 2340 | 2560 | 2460 | 2600 | 2590 | 2600 | 2600 | 2530 | 2630
EFFLUENT TOTAL BACTERIA COUNT | [5 empty] | 0 | 143 | 280 | 13600 | 4500 | 12000 | 220 | 71 | 125 | 54 | 2100 | 3000 | 63 | 48 | 54 | 610 | 25000 | 1259 | 2250 | 188 | 125 | 98 | 0 | 730 | 3600 | 230 | TNTC | 2250 | 634 | 45 | 3400
EFFLUENT FECAL BACTERIA COUNT | [5 empty] | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 9 | 0 | 0 | 18 | 0 | 0 | 0 | 260 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26000 | TNTC | 0 | 0 | 0
EFFLUENT COD | [5 empty] | 55.5 | 54.9 |  |  | 63.3 | 59 | 62.1 | 58.9 | 73.8 |  |  | 91 | 60.8 | 68.2 | 59.3 | 56.9 |  |  | 59.7 | 62.1 | 91.6 | 69.3 | 66.7 |  |  | 59.5 | 65.2 | 52.6 | 63.6 | 50.7
EFFLUENT CBOD | [5 empty] | 5.27 | 5.91 | 5.9 | 4.4 | 4.6 | 6.4 | 5.36 | 4.9 | 6.25 | 4.3 | 4.74 | 6 | 3.67 | 3.39 | 4.57 | 5.88 | 6.46 | 6.47 | 4.55 | 6.28 | 8.58 | 6.59 | 8.06 | 7.27 | 6.8 | 6 | 6 | 5 | 6 | 4 | 5
LABORATORY NUTRIENT DATA
RAW INFLUENT | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
RAW AMMONIA (PPM) | [5 empty] | 17.78 | 18.49 |  |  | 18.14 | 17.99 | 18.4 | 19.49 | 19.56 |  |  | 17.79 | 18.03 | 19.01 | 17.8 | 17.31 |  |  | 16.57 | 16.64 | 17.5 | 17.82 | 16.2 |  |  | 17.75 | 16.7 | 15.52 | 15.42 | 16.96
RAW NITRATES (PPM) | [6 empty] | 0.24 |  |  | 0.052 | 0.11 | 0.02 | 0.241 | 0.02 |  |  | 0.16 | 0.34 | 0.02 | 0.552 | 0.427 |  |  | 0.176 | 0.254 | 0.02 | 0.02 | 0.02 |  |  | 0.374 | 0.577 | 0.055 | 0.035 | 0.011
RAW TOTAL KNEDJAHL NITRIGEN | [5 empty] | 23.84 | 24.58 |  |  | 26.11 | 26.11 | 24.2 | 26.37 | 23.77 |  |  | 25.73 | 28.31 | 27.71 | 27.72 | 26.32 |  |  | 22.92 | 24.07 | 23.13 | 28.14 | 23.69 |  |  | 26.55 | 25.76 | 24.17 | 23.65 | 24.65
RAW TOTAL PHOSPHORUS | [5 empty] | 3.79 | 4 |  |  | 3.08 | 3.52 | 3.08 | 3.33 | 3.07 |  |  | 3.13 | 3.56 | 3.32 | 3.58 | 3.57 |  |  | 3.21 | 3.27 | 3.35 | 4.11 | 3.56 |  |  | 3.94 | 3.37 | 4.38 | 4.73 | 3.56
EFFLUENT | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
EFFLUENT AMMONIA (PPM) | [5 empty] | 13.68 | 14.11 |  |  | 14.77 | 15.11 | 14.26 | 13.67 | 13.34 |  |  | 14.09 | 14.12 | 14.49 | 13.81 | 13.09 |  |  | 13.54 | 15.19 | 16.31 | 14.35 | 13.51 |  |  | 13.93 | 13.9 | 12.71 | 12.67 | 12.26
EFFLUENT NITRATES (PPM) | [5 empty] | 0.537 | 0.528 |  |  | 0.489 | 0.404 | 0.701 | 0.681 | 0.575 |  |  | 0.281 | 0.355 | 0.334 | 0.352 | 0.388 |  |  | 0.111 | 0.118 | 0.2 | 0.221 | 0.255 |  |  | 0.399 | 0.475 | 0.522 | 0.469 | 0.391
EFFLUENT TOTAL KNEDJAHL NITRIGEN | [5 empty] | 18.19 | 17.79 |  |  | 20.73 | 21.96 | 21.54 | 21.02 | 18.79 |  |  | 20.45 | 21.5 | 22.9 | 21.84 | 19.67 |  |  | 18.32 | 21.73 | 22.41 | 19.96 | 0 |  |  | 18.9 | 20.93 | 19.28 | 19.33 | 18.02
EFFLUENT TOTAL PHOSPHORUS | [5 empty] | 1.33 | 0.991 |  |  | 1.12 | 1.03 | 1 | 1.21 | 1.29 |  |  | 1.46 | 1.06 | 1.46 | 1.72 | 1.27 |  |  | 1.33 | 1.65 | 1.6 | 1.72 | 1.53 |  |  | 1.52 | 1.93 | 1.94 | 2.03 | 1.14
LABORATORY REACTOR PROCESSES DATA
| REACTOR ONE TRAIN A |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MIXED-LIQUIR SUSPENDED SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
AVERAGE SETTLABLE SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
MIXED LIQUIR VOLITLE SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
| REACTOR ONE TRAIN B |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MIXED-LIQUIR SUSPENDED SOLIDS | [5 empty] | 3790 | 2940 | 3300 | 3510 | 3520 | 3730 | 3900 | 4200 | 3350 | 3500 | 3240 | 3660 | 3740 | 4690 | 3870 | 3730 | 3340 | 3500 | 2970 | 3690 | 3460 | 3540 | NS | 3680 | 3720 | 3460 | 3760 | 3690 | 3110 | 3470 | 3380
AVERAGE SETTLABLE SOLIDS | [5 empty] | 28 | 30 | 30 | 35 | 30 | 28 | 29 | 28 | 38 | 26 | 30 | 33 | 24 | 32 | 27 | 28 | 34 | 28 | 31 | 31 | 32 | 31 | 38 | 32 | 36 | 36 | 34 | 34 | 29 | 31 | 35
MIXED LIQUIR VOLITLE SOLIDS | [5 empty] | 3200 | 2480 | 2790 | 2920 | 2790 | 3030 | 3270 | 3410 | 2550 | 2880 | 2740 | 3200 | 3230 | 3910 | 3200 | 3070 | 2740 | 2980 | 2550 | 3120 | 2960 | 3000 | NS | 3060 | 3100 | 2950 | 3200 | 3150 | 2640 | 2920 | 2440
LABORATORY REACTOR PROCESSES DATA
CONTINUED
| REACTOR TWO TRAIN C |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MIXED-LIQUIR SUSPENDED SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
AVERAGE SETTLABLE SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
MIXED LIQUIR VOLITLE SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
| REACTOR TWO TRAIN D |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MIXED-LIQUIR SUSPENDED SOLIDS | [5 empty] | 3760 | 2860 | 3350 | 3030 | 3580 | 3650 | 3730 | 4420 | 3400 | 3220 | 2920 | 3100 | 3310 | 4500 | 3540 | 3430 | 3330 | 3220 | 2880 | 3610 | 4020 | 3880 | NS | 3290 | 3810 | 3480 | 3790 | 3700 | 3080 | 2980 | 3380
AVERAGE SETTLABLE SOLIDS | [5 empty] | 27 | 30 | 34 | 25 | 31 | 28 | 29 | 28 | 38 | 25 | 28 | 29 | 24 | 31 | 27 | 28 | 34 | 28 | 30 | 31 | 32 | 30 | 35 | 30 | 36 | 36 | 34 | 34 | 28 | 31 | 33
MIXED LIQUIR VOLITLE SOLIDS | [5 empty] | 3190 | 2410 | 2780 | 2530 | 2830 | 2970 | 3150 | 3520 | 2680 | 2680 | 2460 | 2700 | 2850 | 3770 | 2940 | 2830 | 2750 | 2730 | 2460 | 3050 | 3430 | 3310 | NS | 2750 | 3120 | 2940 | 3260 | 3160 | 2640 | 2570 | 2800
LABORATORY RETURN ACTIVATED SLUDGE AND WASTE SLUDGE DATA
| RETURN ACTIVATED SLUDGE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
PERCENT RETURN SLUDGE TOTAL SUSPENDED SOLIDS | [5 empty] | 0.46 | 1.2 | 1.22 | 1.22 | 1.15 | 1.05 | 1.15 | 1.24 | 1.25 | 1.25 | 1.19 | 0.88 | 0.95 | 1.3 | 1.2 | 1.16 | 1.09 | 1.13 | 1.13 | 0.28 | 1.31 | 1.15 | 0.91 | 0.95 | 1.06 | 1.07 | 1.01 | 1.04 | 0.99 | 1.07 | 0.4
PERCENT RETURN SLUDGE FIXED SUSPENDED SOLIDS | [5 empty] | 23.4 | 22.2 | 21.8 | 23.2 | 22.5 | 25 | 23.5 | 19.4 | 22 | 21.6 | 21.2 | 23.1 | 22.6 | 20.8 | 21.7 | 20 | 19.9 | 22.1 | 21.1 | 20.3 | 20.6 | 20.7 | 24.2 | 22.2 | 21.9 | 23 | 20.2 | 20 | 21.1 | 21.9 | 20.5
|  | WASTE SLUDGE |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
PERCENT WASTE FEED TOTAL SUSPENDED SOLDS | [5 empty] | 3: 1.64; 4: 1; 5: 1.1; 6: 1.52; 9: 1.75; 10: 1.4; 11: 1.45; 12: 1.07; 13: 1.54; 20: 1.43; 23: 1.36; 24: 1.43; 25: 1.07; 26: 1.33; 27: 1.08; 30: 1.2; 31: 1.51
PERCENT WASTE FEED FIXED SUSPENDED SOLIDS | [5 empty] | 3: 20.7; 4: 23; 5: 28.2; 6: 22.4; 9: 20.6; 10: 22.1; 11: 21.4; 12: 23.4; 13: 21.4; 20: 23.8; 23: 21.3; 24: 21.7; 25: 23.4; 26: 21.8; 27: 24.1; 30: 23.3; 31: 20.5
WASTE FEED SLUDGE pH | [5 empty] | 3: 6.73; 4: 6.83; 5: 6.93; 6: 6.88; 9: 6.82; 10: 6.68; 11: 6.74; 12: 6.73; 13: 6.74; 20: 6.8; 23: 6.47; 24: 6.8; 25: 6.79; 26: 6.89; 27: 6.92; 30: 6.74; 31: 7.02
DEWATERING FILTRATE TOTAL SUSPENDED SOLIDS | [5 empty] | 3: 0.22; 4: 0.21; 5: 0.22; 6: 0.21; 9: 0.23; 10: 0.21; 11: 0.21; 12: 0.21; 13: 0.23; 20: 0.26; 23: 0.24; 24: 0.19; 25: 0.2; 26: 0.2; 27: 0.23; 30: 0.2; 31: 0.17
DEWATERING FILTRATE FIXED SUSPENDED SOLIDS | [5 empty] | 3: 63.6; 4: 71.4; 5: 63.6; 6: 71.4; 9: 60.9; 10: 66.7; 11: 71.4; 12: 66.7; 13: 60.9; 20: 57.7; 23: 54.2; 24: 68.4; 25: 60; 26: 65; 27: 60.9; 30: 65; 31: 76.5
DEWATERING FILTRATE pH | [5 empty] | 3: 7.25; 4: 7.28; 5: 7.19; 6: 7.22; 9: 7.24; 10: 7.16; 11: 7.19; 12: 7.09; 13: 7.24; 20: 7.2; 23: 7.02; 24: 7.24; 25: 7.25; 26: 7.11; 27: 7.2; 30: 7.22; 31: 7.45
| DEWATERED CAKE SLUDGE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
PERCENT TOTAL SOLIDS PRESS CAKE | [5 empty] | 3: 17.22; 4: 18.01; 5: 18.42; 6: 17.88; 9: 17.86; 10: 17.64; 11: 17.89; 12: 17.2; 13: 17.42; 20: 17.13; 23: 17.15; 24: 17.64; 25: 17.1; 26: 17.4; 27: 16.61; 30: 16.74; 31: 17.34
PERCENT FIXED SOLIDS PRESS CAKE | [5 empty] | 3: 27.4; 4: 15.5; 5: 16.7; 6: 14.6; 9: 13.8; 10: 18.4; 11: 19.6; 12: 13.6; 13: 14.4; 20: 17.1; 23: 15.9; 24: 14.3; 25: 28.8; 26: 19.2; 27: 13.8; 30: 13.9; 31: 13.7
PERCENT TOTAL SOLIDS LIME CAKE
OTHER SLUDGE REMOVAL
[6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
GRIT (CU.YDS.) | [5 empty] | 21: 10
RAGS (CU.YDS.) | [5 empty] | 7: 10; 14: 10; 20: 10; 27: 10
VACUUM DEBRIS (EST. GAL) | [5 empty] | 31: 4500
MONITORING WELLS LABORATORY DATA
| MONITOR WELL ONE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
UPPER LEVEL
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
MONITORING WELLS LABORATORY DATA
| MONITOR WELL TWO |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
UPPER LEVEL
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
MONITORING WELLS LABORATORY DATA
| MONITOR WELL THREE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
FUTURE
UPPER LEVEL
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
MONITORING WELLS LABORATORY DATA
| REGIONAL MONITOR WELL ONE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
UPPER LEVEL
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
MARCH |  | 1 |  | 3
|  | 0 |  | 0
0
0
|  | 0 |  | 0
3
[5 empty] | 1st WEEK | 1: 2nd WEEK; 2: 3rd WEEK; 3: 4th WEEK
| 1 |  | 1 |  | 1 | 1: 8; 2: 15; 3: 23
| 2 |  | 2 |  | 2 | 1: 9; 2: 16; 3: 24
| 3 |  | 3 |  | 3 | 1: 10; 2: 17; 3: 25
| 4 |  | 4 |  | 4 | 1: 11; 2: 18; 3: 26
| 5 |  | 5 |  | 5 | 1: 12; 2: 19; 3: 27
| 6 |  | 6 |  | 6 | 1: 13; 2: 20; 3: 28
| 7 |  | 7 |  | 7 | 1: 14; 2: 21; 3: 29
| 8 |  | 8 |  |  | 2: 22; 3: 30
| 9 |  | 9 |  |  | 3: 31
| 10 |  | 10
| 11 |  | 11
| 12 |  | 12
| 13 |  | 13
| 14 |  | 14
| 15 |  | 15
| 16 |  | 16
| 17 |  | 17
| 18 |  | 18
| 19 |  | 19
| 20 |  | 20
| 21 |  | 21
| 22 |  | 22
| 23 |  | 23
| 24 |  | 24
| 25 |  | 25
| 26 |  | 26
| 27 |  | 27
| 28 |  | 28
29
30
31
| APRIL | MARCH | FEBRUARY
| AUGUST | JULY | JUNE
| DECEMBER | NOVEMBER | OCTOBER
| FEBRUARY | JANUARY | DECEMBER
| JANUARY | DECEMBER | NOVEMBER
| JUNE | MAY | APRIL
| JULY | JUNE | MAY | FEBRUARY
| MARCH | FEBRUARY | JANUARY | JANUARY
| MAY | APRIL | MARCH
| NOVEMBER | OCTOBER | SEPTEMBER
| OCTOBER | SEPTEMBER | AUGUST
| SEPTEMBER | AUGUST | JULY
| HYDROGEN PEROXIDE |  | 0.1395
| CHLORINE |  | 0.1475
| POLYMER |  | 0.61
| FPL |  | 0.055
[6 empty] | 1st WEEK |  |  | 2nd WEEK |  |  | 3rd WEEK |  |  | 4th WEEK
[7 empty] | G | H | I | J
[5 empty] | MW1 UP | 1: 311
312
313
314
315
316
317
318

## MONITOR DATA
UNDERGROUND INJECTION CONTROL SECTION
MONTHLY OPERATING REPORT DATA SUMMARY
FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT MONTH/YEAR |  |  | MARCH |  | 2003
I.D. NUMBER: 5006M02066 | [5 empty] | LEAD OPERATOR: |  |  |  | MIKE JUST
TELEPHONE NUMBER: (954) 523-1002
MONITORING WELL 1 DATA | [6 empty] | I.D. # 5006A11311
MW-1
PERMIT/CERTIFICATION NUMBER | [6 empty] | UO-06-279512
PERMIT EXPIRATION DATE |  | 2002-07-21
UPPER MONITORING INTERVAL | [6 empty] | 1,288' - 1,320' |  |  |  | Ft. bls.
Sample Date |  | 2003-03-04 |  | 2003-03-11 |  | 2003-03-18 |  | 2003-03-25
Submittal Date |  | 2003-03-05 |  | 2003-03-12 |  | 2003-03-19 |  | 2003-03-26
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 48.41 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 29.06 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 71 |  | 74 |  | 74 |  | 73 |  |  | degrees (F) |  | 73
TDS |  | 7456 |  | 7279 |  | 7431 |  | 73.21 |  |  | mg/l |  | 5559.8025
CHLORIDE |  | 3800 |  | 3750 |  | 3750 |  | 37.5 |  |  | mg/l |  | 2834.375
AMMONIA-N |  | 0.839 |  | 0.893 |  | 0.85 |  | 0.8 |  |  | mg/l |  | 0.8455
TKN |  | 1.22 |  | 1.33 |  | 1.53 |  | 1.44 |  |  | mg/l |  | 1.38
pH |  | 8.02 |  | 8 |  | 8.08 |  | 8 |  |  | Std units |  | 8.025
CONDUCTIVITY |  | 12900 |  | 12100 |  | 12070 |  | 12130 |  |  | umho/cm |  | 12300
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.05 | < | 0.05 | < | 0.05 | < | 0.05 |  |  | mg/l |  | 0.05
SULFATE |  | 850 |  | 750 |  | 850 |  | 850 |  |  | mg/l |  | 825
C.O.D. 'S |  | 190 |  | 180 |  | 150 |  | 150 |  |  | mg/l |  | 167.5
IRON |  | 0.56 |  | 0.51 |  | 2.9 |  | 0.59 |  |  | mg/l |  | 1.14
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
LOWER MONITORING INTERVAL | [6 empty] | 1,449' - 1,557' |  |  |  | Ft. bls
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 42.37 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 25.75 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 71 |  | 74 |  | 74 |  | 74 |  |  | degrees (F) |  | 73.25
TDS |  | 9750 |  | 9296 |  | 9318 |  | 9570 |  |  | mg/l |  | 9483.5
CHLORIDE |  | 5200 |  | 5100 |  | 5100 |  | 5100 |  |  | mg/l |  | 5125
AMMONIA-N |  | 9.31 |  | 9.35 |  | 9.34 |  | 8.94 |  |  | mg/l |  | 9.235
TKN |  | 13.2 |  | 12.7 |  | 12.99 |  | 12.55 |  |  | mg/l |  | 12.86
pH |  | 7.5 |  | 7.4 |  | 7.42 |  | 7.34 |  |  | Std units |  | 7.415
CONDUCTIVITY |  | 15840 |  | 15640 |  | 15650 |  | 15600 |  |  | umho/cm |  | 15682.5
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.05 | < | 0.05 | < | 0.05 | < | 0.05 |  |  | mg/l |  | 0.05
SULFATE |  | 800 |  | 800 |  | 900 |  | 750 |  |  | mg/l |  | 812.5
C.O.D. 'S |  | 270 |  | 290 |  | 240 |  | 240 |  |  | mg/l |  | 260
IRON |  | 0.01 |  | 0.01 |  | 0.01 |  | 0.01 |  |  | mg/l |  | 0.01
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
PAGE 24
UNDERGROUND INJECTION CONTROL SECTION
MONTHLY OPERATING REPORT DATA SUMMARY
FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT MONTH/YEAR |  |  | MARCH |  | 2003
I.D. NUMBER: 5006M02066 | [5 empty] | LEAD OPERATOR: |  |  |  | MIKE JUST
TELEPHONE NUMBER: (954) 523-1002
MONITORING WELL 2 DATA | [6 empty] | I.D. # 5006A11308 & 309
MW-2
PERMIT/CERTIFICATION NUMBER | [6 empty] | UO-06-279401 & 508
PERMIT EXPIRATION DATE |  | 2002-07-21
UPPER MONITORING INTERVAL | [6 empty] | 1,300' - 1,344' |  |  |  | Ft. bls.
Sample Date |  | 2003-03-04 |  | 2003-03-11 |  | 2003-03-18 |  | 2003-03-25
Submittal Date |  | 2003-03-05 |  | 2003-03-12 |  | 2003-03-19 |  | 2003-03-26
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 0 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 0 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 70 |  | 71 |  | 72 |  | 71 |  |  | degrees (F) |  | 71
TDS |  | 7704 |  | 31608 |  | 7385 |  | 7202 |  |  | mg/l |  | 13474.75
CHLORIDE |  | 3750 |  | 18200 |  | 3600 |  | 3700 |  |  | mg/l |  | 7312.5
AMMONIA-N |  | 0.85 |  | 1.2 |  | 0.871 |  | 0.811 |  |  | mg/l |  | 0.933
TKN |  | 1.55 |  | 2.03 |  | 1.62 |  | 1.53 |  |  | mg/l |  | 1.6825
pH |  | 8.08 |  | 7.41 |  | 8.06 |  | 8.08 |  |  | Std units |  | 7.9075
CONDUCTIVITY |  | 11850 |  | 47500 |  | 11850 |  | 11810 |  |  | umho/cm |  | 20752.5
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.05 | < | 0.05 | < | 0.05 | < | 0.05 |  |  | mg/l |  | 0.05
SULFATE |  | 850 |  | 2900 |  | 900 |  | 850 |  |  | mg/l |  | 1375
C.O.D. 'S |  | 170 |  | 950 |  | 140 |  | 150 |  |  | mg/l |  | 352.5
IRON |  | 1.01 |  | 0.03 |  | 4.2 |  | 10.55 |  |  | mg/l |  | 3.9475
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
LOWER MONITORING INTERVAL | [6 empty] | 1,970' - 2,025' |  |  |  | Ft. bls
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 42.27 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 26.64 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 70 |  | 70 |  | 70 |  | 70 |  |  | degrees (F) |  | 70
TDS |  | 31694 |  | 31608 |  | 31691 |  | 32219 |  |  | mg/l |  | 31803
CHLORIDE |  | 17650 |  | 18200 |  | 17100 |  | 19200 |  |  | mg/l |  | 18037.5
AMMONIA-N |  | 1.16 |  | 1.2 |  | 1.19 |  | 1.13 |  |  | mg/l |  | 1.17
TKN |  | 1.98 |  | 2.03 |  | 1.99 |  | 1.97 |  |  | mg/l |  | 1.9925
pH |  | 7.45 |  | 7.41 |  | 7.37 |  | 7.43 |  |  | Std units |  | 7.415
CONDUCTIVITY |  | 47500 |  | 47500 |  | 47600 |  | 47600 |  |  | umho/cm |  | 47550
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.05 | < | 0.05 | < | 0.05 | < | 0.05 |  |  | mg/l |  | 0.05
SULFATE |  | 2600 |  | 2900 |  | 3000 |  | 2600 |  |  | mg/l |  | 2775
C.O.D. 'S |  | 820 |  | 950 |  | 820 |  | 790 |  |  | mg/l |  | 845
IRON |  | 0.04 |  | 0.03 |  | 0.03 |  | 0.05 |  |  | mg/l |  | 0.0375
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
PAGE 25
UNDERGROUND INJECTION CONTROL SECTION
MONTHLY OPERATING REPORT DATA SUMMARY
FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT MONTH/YEAR |  |  | MARCH |  | 2003
I.D. NUMBER: 5006M02066 | [5 empty] | LEAD OPERATOR: |  |  |  | MIKE JUST
TELEPHONE NUMBER: (954) 523-1002
MONITORING WELL 2 DATA | [6 empty] | I.D. # 5006A11310
MW-3
PERMIT/CERTIFICATION NUMBER | [6 empty] | UO-06-279510
PERMIT EXPIRATION DATE |  | 2002-07-21
UPPER MONITORING INTERVAL | [6 empty] | 1,300' - 1,349' |  |  |  | Ft. bls.
Sample Date |  | 2003-03-04 |  | 2003-03-11 |  | 2003-03-18 |  | 2003-03-25
Submittal Date |  | 2003-03-05 |  | 2003-03-12 |  | 2003-03-19 |  | 2003-03-26
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 30.59 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 17.27 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 69 |  | 70 |  | 70 |  | 69 |  |  | degrees (F) |  | 69.5
TDS |  | 7478 |  | 7283 |  | 7254 |  | 7203 |  |  | mg/l |  | 7304.5
CHLORIDE |  | 3800 |  | 3700 |  | 3700 |  | 3750 |  |  | mg/l |  | 3737.5
AMMONIA-N |  | 0.84 |  | 0.929 |  | 0.871 |  | 0.784 |  |  | mg/l |  | 0.856
TKN |  | 1.31 |  | 1.58 |  | 1.41 |  | 1.43 |  |  | mg/l |  | 1.4325
pH |  | 8.12 |  | 8.13 |  | 8.15 |  | 8.24 |  |  | Std units |  | 8.16
CONDUCTIVITY |  | 11950 |  | 11990 |  | 11980 |  | 11920 |  |  | umho/cm |  | 11960
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.05 | < | 0.05 | < | 0.05 | < | 0.05 |  |  | mg/l |  | 0.05
SULFATE |  | 750 |  | 900 |  | 800 |  | 850 |  |  | mg/l |  | 825
C.O.D. 'S |  | 180 |  | 180 |  | 140 |  | 160 |  |  | mg/l |  | 165
IRON |  | 1.11 |  | 1.03 |  | 1.05 |  | 1.14 |  |  | mg/l |  | 1.0825
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
LOWER MONITORING INTERVAL | [6 empty] | 1,970' - 2,027' |  |  |  | Ft. bls
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 45.33 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 28.13 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 70 |  | 64 |  | 68 |  | 69 |  |  | degrees (F) |  | 67.75
TDS |  | 28860 |  | 29296 |  | 29263 |  | 29607 |  |  | mg/l |  | 29256.5
CHLORIDE |  | 15900 |  | 16200 |  | 16100 |  | 16000 |  |  | mg/l |  | 16050
AMMONIA-N |  | 2.15 |  | 2.14 |  | 2.11 |  | 2.05 |  |  | mg/l |  | 2.1125
TKN |  | 3.26 |  | 3.23 |  | 3.23 |  | 3.33 |  |  | mg/l |  | 3.2625
pH |  | 7.42 |  | 7.45 |  | 7.36 |  | 7.45 |  |  | Std units |  | 7.42
CONDUCTIVITY |  | 43800 |  | 44100 |  | 44100 |  | 44100 |  |  | umho/cm |  | 44025
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.05 | < | 0.05 | < | 0.05 | < | 0.05 |  |  | mg/l |  | 0.05
SULFATE |  | 2300 |  | 2400 |  | 2400 |  | 2400 |  |  | mg/l |  | 2375
C.O.D. 'S |  | 790 |  | 780 |  | 800 |  | 870 |  |  | mg/l |  | 810
IRON |  | 0.05 |  | 0.03 |  | 0.03 |  | 0.03 |  |  | mg/l |  | 0.035
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
PAGE 26
UNDERGROUND INJECTION CONTROL SECTION
MONTHLY OPERATING REPORT DATA SUMMARY
FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT MONTH/YEAR |  |  | MARCH |  | 2003
I.D. NUMBER: 5006M02066 | [5 empty] | LEAD OPERATOR: |  |  |  | MIKE JUST
TELEPHONE NUMBER: (954) 523-1002
REGIONAL MONITORING WELL DATA
RMW-1
PERMIT NUMBER | [6 empty] | UC06-249353
PERMIT EXPIRATION DATE |  | 1997-04-27
UPPER MONITORING INTERVAL | [6 empty] | 1300' - 1339' |  |  |  | Ft. bls.
Sample Date |  | 2003-03-04
Submittal Date |  | 2003-03-05
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 68.02 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 8.92 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 70 | [8 empty] | degrees (F) |  | 70
TDS |  | 5664 | [8 empty] | mg/l |  | 5664
CHLORIDE |  | 2900 | [8 empty] | mg/l |  | 2900
AMMONIA-N |  | 0.58 | [8 empty] | mg/l |  | 0.58
TKN |  | 1.07 | [8 empty] | mg/l |  | 1.07
pH |  | 8.08 | [8 empty] | Std units |  | 8.08
CONDUCTIVITY |  | 9420 | [8 empty] | umho/cm |  | 9420
FECAL COLIFORM |  | 0 | [8 empty] | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.05 | [8 empty] | mg/l |  | 0.05
SULFATE |  | 650 | [8 empty] | mg/l |  | 650
C.O.D. 'S |  | 140 | [8 empty] | mg/l |  | 140
IRON |  | 0.21 | [8 empty] | mg/l |  | 0.21
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
LOWER MONITORING INTERVAL | [6 empty] | 1500' - 1600' |  |  |  | Ft. bls
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 21.87 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 19.58 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 68 | [8 empty] | degrees (F) |  | 68
TDS |  | 26794 | [8 empty] | mg/l |  | 26794
CHLORIDE |  | 15600 | [8 empty] | mg/l |  | 15600
AMMONIA-N |  | 0.19 | [8 empty] | mg/l |  | 0.19
TKN |  | 0.646 | [8 empty] | mg/l |  | 0.646
pH |  | 7.7 | [8 empty] | Std units |  | 7.7
CONDUCTIVITY |  | 41400 | [8 empty] | umho/cm |  | 41400
FECAL COLIFORM |  | 0 | [8 empty] | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.05 | [8 empty] | mg/l |  | 0.05
SULFATE |  | 1650 | [8 empty] | mg/l |  | 1650
C.O.D. 'S |  | 690 | [8 empty] | mg/l |  | 690
IRON |  | 0.06 | [8 empty] | mg/l |  | 0.06
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
PAGE 27
Formulas:
LEAD OPERATOR: = [LEAD OPERATOR:, row above]+1

## WELL PRN DATA
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 1 |  |  | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90
60 | 10.91 | 5.33 | 8.38 | 54.19 | 40.5 | 47.37
61 | 12.1 | 5.47 | 8.41 | 57.73 | 40.42 | 47.46 |  |  | FLOW
62 | 12.8 | 4.07 | 8.19 | 60.11 | 38.02 | 47.36 | I |  | MAX | 10.91 | 12.1 | 12.8 | 12.39 | 11.74 | 12.77 | 12.85 | 11.12 | 11.96 | 12.65 | 12.77 | 12.9 | 12.82 | 10.19 | 11.05 | 11.2 | 12.09 | ER | ER | 11.03 | 14.65 | 11.56 | 11.37 | 13.03 | 11.31 | 11.38 | 11.75 | 11.85 | 11.68 | 11.33 | 11.25
63 | 12.39 | 4.59 | 8.21 | 60.59 | 38.63 | 46.98 | N |  | MIN | 5.33 | 5.47 | 4.07 | 4.59 | 4.52 | 3.36 | 4.51 | 4.06 | 4.03 | 2.53 | 0 | ER | ER | ER | 4.72 | 4.24 | ER | ER | ER | ER | 4.45 | 4.9 | 4.39 | 4.18 | 4.29 | 4.03 | 4.25 | 4.18 | 4.16 | 4.2 | 3.93
64 | 11.74 | 4.52 | 8.1 | 59.92 | 38.54 | 46.76 | J |  | TOT | 8.38 | 8.41 | 8.19 | 8.21 | 8.1 | 8.17 | 8.25 | 8.16 | 7.94 | 8.26 | 7.54 | 8.25 | 4.12 | 2.54 | 7.93 | 8.03 | 5.16 | ER | ER | 2.26 | 8.86 | 8.29 | 8.41 | 8.95 | 8.33 | 8.31 | 8.53 | 8.97 | 8.54 | 8.27 | 8.03
65 | 12.77 | 3.36 | 8.17 | 59.55 | 36.89 | 46.87 | E | INJECTION WELL ONE
66 | 12.85 | 4.51 | 8.25 | 60.17 | 38.74 | 47.09 | C |  | PSI
67 | 11.12 | 4.06 | 8.16 | 54.03 | 38.34 | 46.88 | T |  | MAX | 54.19 | 57.73 | 60.11 | 60.59 | 59.92 | 59.55 | 60.17 | 54.03 | 57.21 | 59.8 | 60.14 | 60.01 | 60.2 | 56.96 | 54.67 | 55.44 | 58.07 | ER | ER | 54.51 | 66.63 | 56.96 | 55.84 | 60.68 | 56.55 | 55.49 | 56.47 | 56.74 | 56.47 | 55.2 | 54.57
68 | 11.96 | 4.03 | 7.94 | 57.21 | 37.97 | 46.44 | O |  | MIN | 40.5 | 40.42 | 38.02 | 38.63 | 38.54 | 36.89 | 38.74 | 38.34 | 37.97 | 38.44 | 25.87 | ER | 0.06 | 33.26 | 39.4 | 28.32 | ER | ER | ER | ER | 21.01 | 40.23 | 39.42 | 40.89 | 39.13 | 38.7 | 38.95 | 38.88 | 38.82 | 38.86 | 36.86
69 | 12.65 | 2.53 | 8.26 | 59.8 | 38.44 | 47.46 | N |  | AVG | 47.37 | 47.46 | 47.36 | 46.98 | 46.76 | 46.87 | 47.09 | 46.88 | 46.44 | 47.46 | 46.69 | 47.12 | 46.81 | 47.15 | 46.65 | 46.77 | 29.37 | ER | ER | 12.03 | 48.72 | 47.62 | 47.92 | 48.93 | 47.58 | 47.56 | 48.04 | 49.15 | 48.17 | 47.47 | 46.33
70 | 12.77 | 0 | 7.54 | 60.14 | 25.87 | 46.69
71 | 12.9 | ER | 8.25 | 60.01 | ER | 47.12 | W
72 | 12.82 | ER | 4.12 | 60.2 | 0.06 | 46.81 | E
73 | 10.19 | ER | 2.54 | 56.96 | 33.26 | 47.15 | L
74 | 11.05 | 4.72 | 7.93 | 54.67 | 39.4 | 46.65 | L
75 | 11.2 | 4.24 | 8.03 | 55.44 | 28.32 | 46.77 | O
76 | 12.09 | ER | 5.16 | 58.07 | ER | 29.37 | N
77 | ER | ER | ER | ER | ER | ER | E
78 | ER | ER | ER | ER | ER | ER
79 | 11.03 | ER | 2.26 | 54.51 | ER | 12.03 | D
80 | 14.65 | 4.45 | 8.86 | 66.63 | 21.01 | 48.72 | A
81 | 11.56 | 4.9 | 8.29 | 56.96 | 40.23 | 47.62 | T
82 | 11.37 | 4.39 | 8.41 | 55.84 | 39.42 | 47.92 | A
83 | 13.03 | 4.18 | 8.95 | 60.68 | 40.89 | 48.93
84 | 11.31 | 4.29 | 8.33 | 56.55 | 39.13 | 47.58
85 | 11.38 | 4.03 | 8.31 | 55.49 | 38.7 | 47.56
86 | 11.75 | 4.25 | 8.53 | 56.47 | 38.95 | 48.04
87 | 11.85 | 4.18 | 8.97 | 56.74 | 38.88 | 49.15
88 | 11.68 | 4.16 | 8.54 | 56.47 | 38.82 | 48.17
89 | 11.33 | 4.2 | 8.27 | 55.2 | 38.86 | 47.47
90 | 11.25 | 3.93 | 8.03 | 54.57 | 36.86 | 46.33
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 2 |  |  | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90
60 | 10.97 | 5.2 | 8.39 | 53.29 | 39.72 | 46.49
61 | 12.14 | 5.35 | 8.44 | 56.77 | 39.65 | 46.58 |  |  | FLOW
62 | 12.94 | 3.71 | 8.16 | 59 | 37.29 | 46.47 | I |  | MAX | 10.97 | 12.14 | 12.94 | 12.52 | 11.78 | 12.76 | 12.93 | 11.15 | 12.07 | 12.74 | ER | 12.93 | 12.89 | 11.8 | 11.12 | 11.34 | 12.24 | ER | ER | 11.17 | 14.76 | 11.66 | 11.43 | 12.47 | 11.49 | 11.41 | 11.82 | 11.9 | 11.74 | 11.38 | 12.79
63 | 12.52 | 4.35 | 8.21 | 59.55 | 37.89 | 46.11 | N |  | MIN | 5.2 | 5.35 | 3.71 | 4.35 | 4.32 | 2.74 | 4.27 | 3.79 | 3.61 | 0.04 | 3.73 | ER | 2.5 | 3.76 | 4.53 | 3.96 | ER | ER | ER | ER | 4.31 | 4.63 | 4.27 | 4.91 | 4.11 | 3.84 | 4.12 | 4.18 | 4 | 4.1 | 3.63
64 | 11.78 | 4.32 | 8.09 | 58.76 | 37.81 | 45.88 | J |  | TOT | 8.39 | 8.44 | 8.16 | 8.21 | 8.09 | 8.16 | 8.27 | 8.19 | 7.95 | 8.24 | 9.13 | 8.29 | 8.16 | 8.2 | 7.99 | 8.09 | 5.17 | ER | ER | 2.3 | 8.93 | 8.33 | 8.38 | 8.76 | 8.37 | 8.35 | 8.57 | 9 | 8.6 | 8.32 | 8.08
65 | 12.76 | 2.74 | 8.16 | 58.43 | 36.19 | 46 | E | INJECTION WELL TWO
66 | 12.93 | 4.27 | 8.27 | 59 | 38.01 | 46.21 | C |  | PSI
67 | 11.15 | 3.79 | 8.19 | 53.12 | 37.59 | 45.97 | T |  | MAX | 53.29 | 56.77 | 59 | 59.55 | 58.76 | 58.43 | 59 | 53.12 | 56.21 | 58.63 | 89.5 | 58.84 | 59.05 | ER | 53.58 | 54.41 | 56.92 | ER | ER | 53.48 | 65.34 | 55.9 | 54.73 | 57.76 | 55.42 | 54.41 | 55.33 | 55.66 | 55.38 | 54.2 | 54.16
68 | 12.07 | 3.61 | 7.95 | 56.21 | 37.25 | 45.59 | I |  | MIN | 39.72 | 39.65 | 37.29 | 37.89 | 37.81 | 36.19 | 38.01 | 37.59 | 37.25 | 36.2 | 25.32 | ER | 36.4 | 37.83 | 38.66 | 27.77 | ER | ER | ER | ER | 30.57 | 39.48 | 38.67 | 40.31 | 38.33 | 37.95 | 38.19 | 38.12 | 38.06 | 38.09 | 35.24
69 | 12.74 | 0.04 | 8.24 | 58.63 | 36.2 | 46.5 | O |  | AVG | 46.49 | 46.58 | 46.47 | 46.11 | 45.88 | 46 | 46.21 | 45.97 | 45.59 | 46.5 | 48.87 | 46.23 | 46.35 | 46.35 | 45.78 | 45.87 | 28.98 | ER | ER | 11.8 | 47.83 | 46.75 | 47.01 | 48.01 | 46.64 | 46.65 | 47.11 | 48.18 | 47.25 | 46.54 | 45.44
70 | ER | 3.73 | 9.13 | 89.5 | 25.32 | 48.87 | N
71 | 12.93 | ER | 8.29 | 58.84 | ER | 46.23
72 | 12.89 | 2.5 | 8.16 | 59.05 | 36.4 | 46.35 | W
73 | 11.8 | 3.76 | 8.2 | 55.86 | 37.83 | 46.35 | E
74 | 11.12 | 4.53 | 7.99 | 53.58 | 38.66 | 45.78 | L
75 | 11.34 | 3.96 | 8.09 | 54.41 | 27.77 | 45.87 | L
76 | 12.24 | ER | 5.17 | 56.92 | ER | 28.98
77 | ER | ER | ER | ER | ER | ER | T
78 | ER | ER | ER | ER | ER | ER | W
79 | 11.17 | ER | 2.3 | 53.48 | ER | 11.8 | O
80 | 14.76 | 4.31 | 8.93 | 65.34 | 30.57 | 47.83
81 | 11.66 | 4.63 | 8.33 | 55.9 | 39.48 | 46.75 | D
82 | 11.43 | 4.27 | 8.38 | 54.73 | 38.67 | 47.01 | A
83 | 12.47 | 4.91 | 8.76 | 57.76 | 40.31 | 48.01 | T
84 | 11.49 | 4.11 | 8.37 | 55.42 | 38.33 | 46.64 | A
85 | 11.41 | 3.84 | 8.35 | 54.41 | 37.95 | 46.65
86 | 11.82 | 4.12 | 8.57 | 55.33 | 38.19 | 47.11
87 | 11.9 | 4.18 | 9 | 55.66 | 38.12 | 48.18
88 | 11.74 | 4 | 8.6 | 55.38 | 38.06 | 47.25
89 | 11.38 | 4.1 | 8.32 | 54.2 | 38.09 | 46.54
90 | 12.79 | 3.63 | 8.08 | 54.16 | 35.24 | 45.44
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 3 |  |  | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90
60 | 9.58 | 4.58 | 7.31 | 54.54 | 40.65 | 47.62
61 | 10.58 | 4.61 | 7.36 | 58.13 | 40.57 | 47.69 |  |  | FLOW
62 | 11.3 | 3.22 | 7.09 | 60.53 | 38.13 | 47.58 | I |  | MAX | 9.58 | 10.58 | 11.3 | 10.93 | 10.27 | 11.1 | 11.29 | 9.73 | 10.58 | 11.1 | 13.98 | 11.29 | 11.31 | 10.34 | 9.73 | 9.88 | 10.59 | ER | ER | ER | 10.29 | 10.42 | 10.17 | 11.59 | 10.2 | 10.12 | 10.43 | 10.52 | 10.39 | 10.03 | 9.9
63 | 10.93 | 3.7 | 7.12 | 61.03 | 38.75 | 47.22 | N |  | MIN | 4.58 | 4.61 | 3.22 | 3.7 | 3.64 | 2.47 | 3.67 | ER | 3.1 | 1.31 | ER | ER | ER | 3.26 | 3.82 | 3.35 | ER | ER | ER | ER | ER | 4.11 | 3.77 | ER | 3.66 | 3.37 | 3.6 | 3.63 | 3.58 | 3.55 | 3.25
64 | 10.27 | 3.64 | 7.01 | 60.32 | 38.66 | 46.98 | J |  | TOT | 7.31 | 7.36 | 7.09 | 7.12 | 7.01 | 7.09 | 7.16 | 6.25 | 6.89 | 7.16 | 7.42 | 7.2 | 6.79 | 7.12 | 6.9 | 6.98 | 4.48 | ER | ER | ER | ER | 7.38 | 7.47 | 6.93 | 7.41 | 7.39 | 7.56 | 7.94 | 7.57 | 7.3 | 7.1
65 | 11.1 | 2.47 | 7.09 | 59.97 | 36.97 | 47.09 | E | INJECTION WELL THREE
66 | 11.29 | 3.67 | 7.16 | 60.59 | 38.86 | 47.31 | C |  | PSI
67 | 9.73 | ER | 6.25 | 54.35 | 35.49 | 45.9 | T |  | MAX | 54.54 | 58.13 | 60.53 | 61.03 | 60.32 | 59.97 | 60.59 | 54.35 | 57.61 | 60.2 | 72.1 | 60.37 | 60.58 | 57.26 | 54.98 | 55.8 | 58.44 | ER | ER | 54.81 | 57.37 | 57.28 | 56.13 | 61.02 | 56.86 | 55.79 | 56.79 | 57.06 | 56.72 | 55.5 | 54.87
68 | 10.58 | 3.1 | 6.89 | 57.61 | 38.08 | 46.66 | I |  | MIN | 40.65 | 40.57 | 38.13 | 38.75 | 38.66 | 36.97 | 38.86 | 35.49 | 38.08 | 38.53 | 26 | ER | ER | 38.69 | 39.52 | 28.42 | ER | ER | ER | ER | 21.12 | 40.35 | 39.53 | 36.24 | 39.24 | 38.8 | 39.05 | 38.99 | 38.9 | 38.92 | 37.13
69 | 11.1 | 1.31 | 7.16 | 60.2 | 38.53 | 47.68 | O |  | AVG | 47.62 | 47.69 | 47.58 | 47.22 | 46.98 | 47.09 | 47.31 | 45.9 | 46.66 | 47.68 | 48.51 | 47.34 | 41.95 | 47.48 | 46.85 | 46.99 | 29.51 | ER | ER | 12.09 | 47.96 | 47.81 | 48.13 | 47.79 | 47.8 | 47.75 | 48.25 | 49.34 | 48.37 | 47.65 | 46.61
70 | 13.98 | ER | 7.42 | 72.1 | 26 | 48.51 | N
71 | 11.29 | ER | 7.2 | 60.37 | ER | 47.34
72 | 11.31 | ER | 6.79 | 60.58 | ER | 41.95 | W
73 | 10.34 | 3.26 | 7.12 | 57.26 | 38.69 | 47.48 | E
74 | 9.73 | 3.82 | 6.9 | 54.98 | 39.52 | 46.85 | L
75 | 9.88 | 3.35 | 6.98 | 55.8 | 28.42 | 46.99 | L
76 | 10.59 | ER | 4.48 | 58.44 | ER | 29.51
77 | ER | ER | ER | ER | ER | ER | T
78 | ER | ER | ER | ER | ER | ER | H
79 | ER | ER | ER | 54.81 | ER | 12.09 | R
80 | 10.29 | ER | ER | 57.37 | 21.12 | 47.96 | E
81 | 10.42 | 4.11 | 7.38 | 57.28 | 40.35 | 47.81 | E
82 | 10.17 | 3.77 | 7.47 | 56.13 | 39.53 | 48.13
83 | 11.59 | ER | 6.93 | 61.02 | 36.24 | 47.79 | D
84 | 10.2 | 3.66 | 7.41 | 56.86 | 39.24 | 47.8 | A
85 | 10.12 | 3.37 | 7.39 | 55.79 | 38.8 | 47.75 | T
86 | 10.43 | 3.6 | 7.56 | 56.79 | 39.05 | 48.25 | A
87 | 10.52 | 3.63 | 7.94 | 57.06 | 38.99 | 49.34
88 | 10.39 | 3.58 | 7.57 | 56.72 | 38.9 | 48.37
89 | 10.03 | 3.55 | 7.3 | 55.5 | 38.92 | 47.65
90 | 9.9 | 3.25 | 7.1 | 54.87 | 37.13 | 46.61
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 4 |  |  | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90
60 | 0.13 | 0.1 | 0.11 | 35.15 | 32.43 | 33.84
61 | 0.13 | 0.1 | 0.11 | 35.69 | 32.33 | 33.88 |  |  | FLOW
62 | 0.14 | 0.1 | 0.11 | 35.93 | 32.66 | 34.18 | I |  | MAX | 0.13 | 0.13 | 0.14 | 0.14 | 0.14 | 0.13 | 0.14 | 0.14 | 0.14 | 0.13 | 0.23 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.13 | ER | ER | 0.11 | 0.14 | 0.15 | 0.14 | 0.14 | 0.14 | 0.14 | 0.13 | 0.14 | 0.15 | 0.14 | 0.12
63 | 0.14 | 0.1 | 0.11 | 36.05 | 32.86 | 34.19 | N |  | MIN | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.11 | 0.1 | 0.1 | 0.1 | 0.05 | ER | 0.11 | 0.1 | 0.1 | 0.06 | ER | ER | ER | ER | 0.07 | 0.12 | 0.11 | 0.11 | 0.1 | 0.11 | 0.11 | 0.11 | 0.11 | 0.1 | 0.07
64 | 0.14 | 0.1 | 0.11 | 35.68 | 32.92 | 34.15 | J |  | TOT | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.12 | 0.12 | 0.12 | 0.11 | 0.11 | 0.12 | 0.12 | 0.12 | 0.12 | 0.11 | 0.07 | ER | ER | 0.02 | 0.12 | 0.13 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.13 | 0.12 | 0.1
65 | 0.13 | 0.1 | 0.11 | 35.87 | 32.45 | 34.13 | E | INJECTION WELL FOUR
66 | 0.14 | 0.11 | 0.12 | 36.49 | 32.83 | 34.66 | C |  | PSI
67 | 0.14 | 0.1 | 0.12 | 36.96 | 34.1 | 35.64 | T |  | MAX | 35.15 | 35.69 | 35.93 | 36.05 | 35.68 | 35.87 | 36.49 | 36.96 | 37.21 | 37.4 | 38.4 | 37.27 | 37.52 | 59.8 | 37.41 | 37.63 | 38.04 | ER | ER | 37.27 | 37.74 | 37.73 | 37.66 | 38.13 | 37.74 | 41.5 | 41.65 | 41.77 | 41.67 | 41.45 | 40.87
68 | 0.14 | 0.1 | 0.12 | 37.21 | 34.15 | 35.61 | I |  | MIN | 32.43 | 32.33 | 32.66 | 32.86 | 32.92 | 32.45 | 32.83 | 34.1 | 34.15 | 34.3 | 17.94 | ER | 34.27 | 34.75 | 35.24 | 22 | ER | ER | ER | ER | 23.51 | 35.26 | 35.14 | 35.13 | 35.2 | 35.84 | 39.23 | 39 | 38.94 | 38.88 | 34.04
69 | 0.13 | 0.1 | 0.11 | 37.4 | 34.3 | 35.68 | O |  | AVG | 33.84 | 33.88 | 34.18 | 34.19 | 34.15 | 34.13 | 34.66 | 35.64 | 35.61 | 35.68 | 35.74 | 35.49 | 35.84 | 36.21 | 36.31 | 36.29 | 22.62 | ER | ER | 8.65 | 36.4 | 36.44 | 36.52 | 36.63 | 36.66 | 39.81 | 40.45 | 40.59 | 40.39 | 40.17 | 39.59
70 | 0.23 | 0.05 | 0.11 | 38.4 | 17.94 | 35.74 | N
71 | 0.14 | ER | 0.12 | 37.27 | ER | 35.49
72 | 0.14 | 0.11 | 0.12 | 37.52 | 34.27 | 35.84 | W
73 | 0.14 | 0.1 | 0.12 | 37.39 | 34.75 | 36.21 | E
74 | 0.14 | 0.1 | 0.12 | 37.41 | 35.24 | 36.31 | L
75 | 0.14 | 0.06 | 0.11 | 37.63 | 22 | 36.29 | L
76 | 0.13 | ER | 0.07 | 38.04 | ER | 22.62
77 | ER | ER | ER | ER | ER | ER | F
78 | ER | ER | ER | ER | ER | ER | O
79 | 0.11 | ER | 0.02 | 37.27 | ER | 8.65 | U
80 | 0.14 | 0.07 | 0.12 | 37.74 | 23.51 | 36.4 | R
81 | 0.15 | 0.12 | 0.13 | 37.73 | 35.26 | 36.44
82 | 0.14 | 0.11 | 0.12 | 37.66 | 35.14 | 36.52 | D
83 | 0.14 | 0.11 | 0.12 | 38.13 | 35.13 | 36.63 | A
84 | 0.14 | 0.1 | 0.12 | 37.74 | 35.2 | 36.66 | T
85 | 0.14 | 0.11 | 0.12 | 41.5 | 35.84 | 39.81 | A
86 | 0.13 | 0.11 | 0.12 | 41.65 | 39.23 | 40.45
87 | 0.14 | 0.11 | 0.12 | 41.77 | 39 | 40.59
88 | 0.15 | 0.11 | 0.13 | 41.67 | 38.94 | 40.39
89 | 0.14 | 0.1 | 0.12 | 41.45 | 38.88 | 40.17
90 | 0.12 | 0.07 | 0.1 | 40.87 | 34.04 | 39.59
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 5 |  |  | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90
60 | 9.68 | ER | 5.36 | 53.96 | 33.47 | 43.57
61 | 10.67 | ER | 5.44 | 57.78 | 33.47 | 43.69 |  |  | FLOW
62 | 11.34 | 3.65 | 7.34 | 60.08 | 37.83 | 46.99 | I |  | MAX | 9.68 | 10.67 | 11.34 | 10.97 | 10.44 | 11.17 | 11.33 | 9.81 | 10.6 | 11.23 | 13.79 | 11.28 | 11.3 | 10.37 | 9.76 | 9.93 | 10.69 | ER | ER | 9.74 | 13.04 | 10.27 | 10.01 | 10.69 | 10.11 | 10 | 10.33 | 10.4 | 10.29 | 9.97 | 9.82
63 | 10.97 | 4.18 | 7.37 | 59.98 | 38.51 | 46.67 | N |  | MIN | ER | ER | 3.65 | 4.18 | 4.13 | 2.92 | 4.1 | 3.71 | 3.56 | 1.59 | ER | ER | 2.8 | 3.7 | 4.28 | 3.8 | ER | ER | ER | ER | 4.12 | 4.41 | 4.08 | 3.83 | 4.02 | 3.76 | 3.96 | 3.99 | 3.96 | 3.95 | 3.59
64 | 10.44 | 4.13 | 7.27 | 59.47 | 38.39 | 46.49 | J |  | TOT | 5.36 | 5.44 | 7.34 | 7.37 | 7.27 | 7.32 | 7.4 | 7.35 | 7.15 | 7.38 | 7.58 | 7.4 | 7.32 | 7.33 | 7.14 | 7.22 | 4.62 | ER | ER | 2.02 | 7.94 | 7.45 | 7.53 | 8 | 7.49 | 7.47 | 7.63 | 8 | 7.66 | 7.42 | 7.18
65 | 11.17 | 2.92 | 7.32 | 59.57 | 36.69 | 46.62 | E | INJECTION WELL FIVE
66 | 11.33 | 4.1 | 7.4 | 59.4 | 38.62 | 46.82 | C |  | PSI
67 | 9.81 | 3.71 | 7.35 | 54.13 | 38.15 | 46.6 | T |  | MAX | 53.96 | 57.78 | 60.08 | 59.98 | 59.47 | 59.57 | 59.4 | 54.13 | 56.31 | 59.12 | 71 | 59.8 | 60.1 | 56.77 | 54.5 | 55.47 | 58.06 | ER | ER | 54.02 | 65.03 | 56.25 | 54.84 | 57.82 | 55.73 | 78.7 | 56.39 | 56.6 | 56.22 | 54.97 | 54.5
68 | 10.6 | 3.56 | 7.15 | 56.31 | 37.84 | 46.21 | I |  | MIN | 33.47 | 33.47 | 37.83 | 38.51 | 38.39 | 36.69 | 38.62 | 38.15 | 37.84 | 38.15 | 25.61 | ER | 36.95 | 38.37 | 39.09 | 27.85 | ER | ER | ER | ER | 31.7 | 39.5 | 39 | 40.49 | 38.9 | 19.39 | 38.82 | 38.78 | 38.72 | 38.77 | 36.11
69 | 11.23 | 1.59 | 7.38 | 59.12 | 38.15 | 47.22 | O |  | AVG | 43.57 | 43.69 | 46.99 | 46.67 | 46.49 | 46.62 | 46.82 | 46.6 | 46.21 | 47.22 | 48.02 | 46.85 | 46.97 | 46.97 | 46.3 | 46.51 | 29.43 | ER | ER | 11.87 | 47.92 | 46.61 | 47.08 | 48.19 | 46.88 | 46.64 | 47.93 | 48.99 | 48 | 47.32 | 46.33
70 | 13.79 | ER | 7.58 | 71 | 25.61 | 48.02 | N
71 | 11.28 | ER | 7.4 | 59.8 | ER | 46.85
72 | 11.3 | 2.8 | 7.32 | 60.1 | 36.95 | 46.97 | W
73 | 10.37 | 3.7 | 7.33 | 56.77 | 38.37 | 46.97 | E
74 | 9.76 | 4.28 | 7.14 | 54.5 | 39.09 | 46.3 | L
75 | 9.93 | 3.8 | 7.22 | 55.47 | 27.85 | 46.51 | L
76 | 10.69 | ER | 4.62 | 58.06 | ER | 29.43
77 | ER | ER | ER | ER | ER | ER | F
78 | ER | ER | ER | ER | ER | ER | I
79 | 9.74 | ER | 2.02 | 54.02 | ER | 11.87 | V
80 | 13.04 | 4.12 | 7.94 | 65.03 | 31.7 | 47.92 | E
81 | 10.27 | 4.41 | 7.45 | 56.25 | 39.5 | 46.61
82 | 10.01 | 4.08 | 7.53 | 54.84 | 39 | 47.08 | D
83 | 10.69 | 3.83 | 8 | 57.82 | 40.49 | 48.19 | A
84 | 10.11 | 4.02 | 7.49 | 55.73 | 38.9 | 46.88 | T
85 | 10 | 3.76 | 7.47 | 78.7 | 19.39 | 46.64 | A
86 | 10.33 | 3.96 | 7.63 | 56.39 | 38.82 | 47.93
87 | 10.4 | 3.99 | 8 | 56.6 | 38.78 | 48.99
88 | 10.29 | 3.96 | 7.66 | 56.22 | 38.72 | 48
89 | 9.97 | 3.95 | 7.42 | 54.97 | 38.77 | 47.32
90 | 9.82 | 3.59 | 7.18 | 54.5 | 36.11 | 46.33

## RMW PRN DATA
julian | u-avg | u-min | u-max | l-avg | l-min | l-max
60 | 21.61 | 21.54 | 21.68 | 42.44 | 42.35 | 42.51 | R |  |  | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90
61 | 21.69 | 21.61 | 21.76 | 42.51 | 42.44 | 42.59 | E
62 | 20.83 | 19.83 | 21.77 | 36.72 | 32.05 | 42.57 | G |  | LOW
63 | 20.59 | 19.58 | 21 | ER | ER | 67.07 | I |  | MIN | 21.54 | 21.61 | 19.83 | 19.58 | 20.99 | 21.19 | 21.25 | 21.21 | 21.32 | 21.39 | 21.36 | 21.31 | 21.32 | 21.36 | 21.43 | 21.51 | 21.64 | 21.77 | 21.72 | 21.67 | 21.61 | 21.56 | 21.59 | 21.59 | 21.58 | 21.6 | 21.67 | 21.73 | 21.7 | 21.63 | 19.72
64 | 21.09 | 20.99 | 21.21 | ER | ER | 67.59 | O |  | MAX | 21.68 | 21.76 | 21.77 | 21 | 21.21 | 21.3 | 21.32 | 21.32 | 21.43 | 21.5 | 21.48 | 21.47 | 21.46 | 21.51 | 21.59 | 21.67 | 21.85 | 21.84 | 21.81 | 21.76 | 21.75 | 21.7 | 21.69 | 21.78 | 21.71 | 21.73 | 21.86 | 21.87 | 21.79 | 21.83 | 21.63
65 | 21.25 | 21.19 | 21.3 | ER | ER | 67.94 | N |  | AVG | 21.61 | 21.69 | 20.83 | 20.59 | 21.09 | 21.25 | 21.28 | 21.29 | 21.38 | 21.43 | 21.42 | 21.4 | 21.39 | 21.45 | 21.53 | 21.6 | 21.76 | 21.8 | 21.76 | 21.7 | 21.66 | 21.62 | 21.65 | 21.69 | 21.64 | 21.68 | 21.78 | 21.8 | 21.75 | 21.76 | 20.74
66 | 21.28 | 21.25 | 21.32 | ER | ER | 68.02 | A | RMW
67 | 21.29 | 21.21 | 21.32 | ER | ER | 67.78 | L |  | UP
68 | 21.38 | 21.32 | 21.43 | ER | ER | 67.05 |  |  | MIN | 42.35 | 42.44 | 32.05 | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | 8.95 | 8.97 | ER | ER | ER | ER | ER | ER | 8.98 | 8.97 | ER | 8.99 | 8.97 | 8.97 | ER | ER | 8.92
69 | 21.43 | 21.39 | 21.5 | ER | ER | 31.03 | M |  | MAX | 42.51 | 42.59 | 42.57 | 67.07 | 67.59 | 67.94 | 68.02 | 67.78 | 67.05 | 31.03 | 67.93 | 67.94 | 67.97 | 66.48 | 56.41 | 32.01 | 67.82 | 67.84 | 67.55 | 67.68 | 67.05 | 67 | 33.03 | 33.76 | 68 | 60.17 | 19.02 | 48.73 | 66.63 | 68.02 | 24.76
70 | 21.42 | 21.36 | 21.48 | ER | ER | 67.93 | O |  | AVG | 42.44 | 42.51 | 36.72 | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | 14.02 | 12.71 | ER | ER | ER | ER | ER | ER | 11.04 | 12.35 | ER | 16.17 | 10.84 | 15.69 | ER | ER | 10.56
71 | 21.4 | 21.31 | 21.47 | ER | ER | 67.94 | N
72 | 21.39 | 21.32 | 21.46 | ER | ER | 67.97 | I
73 | 21.45 | 21.36 | 21.51 | ER | ER | 66.48 | T
74 | 21.53 | 21.43 | 21.59 | 14.02 | 8.95 | 56.41 | O
75 | 21.6 | 21.51 | 21.67 | 12.71 | 8.97 | 32.01 | R
76 | 21.76 | 21.64 | 21.85 | ER | ER | 67.82
77 | 21.8 | 21.77 | 21.84 | ER | ER | 67.84 | W
78 | 21.76 | 21.72 | 21.81 | ER | ER | 67.55 | E
79 | 21.7 | 21.67 | 21.76 | ER | ER | 67.68 | L
80 | 21.66 | 21.61 | 21.75 | ER | ER | 67.05 | L
81 | 21.62 | 21.56 | 21.7 | ER | ER | 67
82 | 21.65 | 21.59 | 21.69 | 11.04 | 8.98 | 33.03
83 | 21.69 | 21.59 | 21.78 | 12.35 | 8.97 | 33.76 | R
84 | 21.64 | 21.58 | 21.71 | ER | ER | 68 | M
85 | 21.68 | 21.6 | 21.73 | 16.17 | 8.99 | 60.17 | W
86 | 21.78 | 21.67 | 21.86 | 10.84 | 8.97 | 19.02
87 | 21.8 | 21.73 | 21.87 | 15.69 | 8.97 | 48.73 | O
88 | 21.75 | 21.7 | 21.79 | ER | ER | 66.63 | N
89 | 21.76 | 21.63 | 21.83 | ER | ER | 68.02 | E
90 | 20.74 | 19.72 | 21.63 | 10.56 | 8.92 | 24.76
60 | 41.79 | 41.45 | 42.11 | 47.94 | 47.7 | 48.07 | M |  |  | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90
61 | 42.07 | 41.49 | 42.37 | 47.96 | 47.79 | 48.15 | O
62 | 35.03 | 29.97 | 41.71 | 47.32 | 46.5 | 48.11 | N |  | LOW
63 | 37.58 | 29.93 | 41.3 | 47.38 | 46.92 | 47.75 | I |  | MIN | 41.45 | 41.49 | 29.97 | 29.93 | 41.2 | 41.36 | 41.36 | 41.38 | 41.42 | 33.05 | 25.75 | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER
64 | 41.38 | 41.2 | 41.43 | 47.66 | 47.56 | 47.84 | T |  | MAX | 42.11 | 42.37 | 41.71 | 41.3 | 41.43 | 41.55 | 41.54 | 41.55 | 41.65 | 41.59 | 41.34 | 41.44 | 41.42 | ER | ER | ER | ER | ER | ER | 13.47 | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER
65 | 41.46 | 41.36 | 41.55 | 47.73 | 47.64 | 47.85 | O |  | AVG | 41.79 | 42.07 | 35.03 | 37.58 | 41.38 | 41.46 | 41.47 | 41.47 | 41.5 | 36.98 | 38.07 | 41.12 | ER | ER | ER | ER | ER | ER | 10.7 | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER
66 | 41.47 | 41.36 | 41.54 | 47.69 | 47.62 | 47.84 | R | MW-1
67 | 41.47 | 41.38 | 41.55 | 47.64 | 47.61 | 47.8 |  |  | UP
68 | 41.5 | 41.42 | 41.65 | 47.79 | 47.68 | 47.86 | W |  | MIN | 47.7 | 47.79 | 46.5 | 46.92 | 47.56 | 47.64 | 47.62 | 47.61 | 47.68 | 43.22 | 29.06 | ER | 47.39 | 47.75 | 47.82 | 33.32 | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER
69 | 36.98 | 33.05 | 41.59 | 45.67 | 43.22 | 47.91 | E |  | MAX | 48.07 | 48.15 | 48.11 | 47.75 | 47.84 | 47.85 | 47.84 | 47.8 | 47.86 | 47.91 | 48.2 | 47.98 | 47.97 | 48.07 | 48.17 | 48.28 | 48.41 | ER | ER | 14.86 | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER
70 | 38.07 | 25.75 | 41.34 | 46.37 | 29.06 | 48.2 | L |  | AVG | 47.94 | 47.96 | 47.32 | 47.38 | 47.66 | 47.73 | 47.69 | 47.64 | 47.79 | 45.67 | 46.37 | 47.53 | 47.86 | 47.95 | 48 | 47.89 | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER
71 | 41.12 | ER | 41.44 | 47.53 | ER | 47.98 | L
72 | ER | ER | 41.42 | 47.86 | 47.39 | 47.97
73 | ER | ER | ER | 47.95 | 47.75 | 48.07 | O
74 | ER | ER | ER | 48 | 47.82 | 48.17 | N
75 | ER | ER | ER | 47.89 | 33.32 | 48.28 | E
76 | ER | ER | ER | ER | ER | 48.41
77 | ER | ER | ER | ER | ER | ER | I
78 | 10.7 | ER | ER | ER | ER | ER | N
79 | ER | ER | 13.47 | ER | ER | 14.86 | J
80 | ER | ER | ER | ER | ER | ER | E
81 | ER | ER | ER | ER | ER | ER | C
82 | ER | ER | ER | ER | ER | ER | T
83 | ER | ER | ER | ER | ER | ER | I
84 | ER | ER | ER | ER | ER | ER | O
85 | ER | ER | ER | ER | ER | ER | N
86 | ER | ER | ER | ER | ER | ER
87 | ER | ER | ER | ER | ER | ER | W
88 | ER | ER | ER | ER | ER | ER | E
89 | ER | ER | ER | ER | ER | ER | L
90 | ER | ER | ER | ER | ER | ER | L
60 | 41.92 | 41.75 | 42 | ER | ER | ER | M |  |  | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90
61 | 41.98 | 41.88 | 42.11 | ER | ER | ER | O
62 | 35.83 | 30.92 | 42.08 | ER | ER | ER | N |  | LOW
63 | 38.05 | 30.87 | 41.62 | ER | ER | ER | I |  | MIN | 41.75 | 41.88 | 30.92 | 30.87 | 41.6 | 41.78 | 41.84 | 41.83 | 41.92 | 33.77 | 26.64 | ER | ER | 41.58 | 41.76 | 30.27 | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER
64 | 41.71 | 41.6 | 41.82 | ER | ER | ER | T |  | MAX | 42 | 42.11 | 42.08 | 41.62 | 41.82 | 41.89 | 41.9 | 41.92 | 42.02 | 42.06 | 41.52 | 41.73 | 41.77 | 41.88 | 42.02 | 42.15 | 42.27 | ER | ER | 36.17 | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER
65 | 41.9 | 41.78 | 41.89 | ER | ER | ER | O |  | AVG | 41.92 | 41.98 | 35.83 | 38.05 | 41.71 | 41.9 | 41.93 | 41.93 | 41.98 | 37.6 | 38.46 | 41.31 | 38.29 | 41.84 | 41.96 | 41.83 | 29.88 | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER
66 | 41.93 | 41.84 | 41.9 | ER | ER | ER | R | MW-2
67 | 41.93 | 41.83 | 41.92 | ER | ER | ER |  |  | UP
68 | 41.98 | 41.92 | 42.02 | ER | ER | ER | W |  | MIN | bar: 60 to 90
69 | 37.6 | 33.77 | 42.06 | ER | ER | ER | E |  | MAX | bar: 60 to 90
70 | 38.46 | 26.64 | 41.52 | ER | ER | ER | L |  | AVG | bar: 60 to 90
71 | 41.31 | ER | 41.73 | ER | ER | ER | L
72 | 38.29 | ER | 41.77 | ER | ER | ER
73 | 41.84 | 41.58 | 41.88 | ER | ER | ER | T
74 | 41.96 | 41.76 | 42.02 | ER | ER | ER | W
75 | 41.83 | 30.27 | 42.15 | ER | ER | ER | O
76 | 29.88 | ER | 42.27 | ER | ER | ER
77 | ER | ER | ER | ER | ER | ER | I
78 | ER | ER | ER | ER | ER | ER | N
79 | ER | ER | 36.17 | ER | ER | ER | J
80 | ER | ER | ER | ER | ER | ER | E
81 | ER | ER | ER | ER | ER | ER | C
82 | ER | ER | ER | ER | ER | ER | T
83 | ER | ER | ER | ER | ER | ER | I
84 | ER | ER | ER | ER | ER | ER | O
85 | ER | ER | ER | ER | ER | ER | N
86 | ER | ER | ER | ER | ER | ER
87 | ER | ER | ER | ER | ER | ER | W
88 | ER | ER | ER | ER | ER | ER | E
89 | ER | ER | ER | ER | ER | ER | L
90 | ER | ER | ER | ER | ER | ER | L
60 | 44.95 | 44.77 | 45 | 29.95 | 29.76 | 30.08 | M |  |  | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90
61 | 44.99 | 44.91 | 45.13 | 30 | 29.86 | 30.17 | O
62 | 40.92 | 37.66 | 45.09 | 25.93 | 22.68 | 30.12 | N |  | LOW
63 | 42.28 | 37.63 | 44.64 | 27.56 | 22.51 | 30.12 | I |  | MIN | 44.77 | 44.91 | 37.66 | 37.63 | 44.64 | 44.81 | 44.88 | 44.86 | 44.95 | 36.75 | 28.13 | ER | ER | 44.72 | 44.85 | 32.14 | ER | ER | ER | ER | 33.43 | 45.01 | 45.08 | 39.79 | 39.81 | 44.73 | 44.95 | 45.11 | 45.11 | 45.07 | 36.78
64 | 44.83 | 44.64 | 44.83 | 30.19 | 30.02 | 30.31 | T |  | MAX | 45 | 45.13 | 45.09 | 44.64 | 44.83 | 44.92 | 44.94 | 44.95 | 45.04 | 45.09 | 44.5 | 44.74 | 44.83 | 44.98 | 45.1 | 45.21 | 45.33 | ER | ER | 45.09 | 45.1 | 45.14 | 45.21 | 45.29 | 44.73 | 45.02 | 45.22 | 45.28 | 45.27 | 45.33 | 45.1
65 | 44.93 | 44.81 | 44.92 | 30.29 | 30.17 | 30.38 | O |  | AVG | 44.95 | 44.99 | 40.92 | 42.28 | 44.83 | 44.93 | 44.97 | 44.95 | 45 | 40.65 | 41.48 | 44.27 | 42.72 | 44.89 | 44.99 | 44.84 | 31.58 | ER | ER | 19.98 | 44.91 | 45.02 | 45.06 | 42.34 | 43.01 | 44.89 | 45.02 | 45.18 | 45.18 | 45.28 | 41.47
66 | 44.97 | 44.88 | 44.94 | 30.33 | 30.22 | 30.38 | R | MW-3
67 | 44.95 | 44.86 | 44.95 | 30.33 | 30.21 | 30.39 |  |  | UP
68 | 45 | 44.95 | 45.04 | 30.45 | 30.32 | 30.5 | W |  | MIN | 29.76 | 29.86 | 22.68 | 22.51 | 30.02 | 30.17 | 30.22 | 30.21 | 30.32 | 17.36 | 17.27 | ER | ER | 29.9 | 30.02 | 23.16 | ER | ER | ER | ER | 23.88 | 30.15 | 30.2 | 17.97 | 17.91 | 29.92 | 30.19 | 30.35 | 30.37 | 30.29 | 19.62
69 | 40.65 | 36.75 | 45.09 | 23.32 | 17.36 | 30.52 | E |  | MAX | 30.08 | 30.17 | 30.12 | 30.12 | 30.31 | 30.38 | 30.38 | 30.39 | 30.5 | 30.52 | 29.68 | 29.96 | 30.09 | 30.22 | 30.34 | 30.47 | 30.57 | ER | ER | 30.4 | 30.4 | 30.39 | 30.42 | 30.51 | 29.94 | 30.31 | 30.54 | 30.59 | 30.58 | 30.58 | 30.29
70 | 41.48 | 28.13 | 44.5 | 24.94 | 17.27 | 29.68 | L |  | AVG | 29.95 | 30 | 25.93 | 27.56 | 30.19 | 30.29 | 30.33 | 30.33 | 30.45 | 23.32 | 24.94 | 29.72 | 28.81 | 30.07 | 30.22 | 30.23 | 21.39 | ER | ER | 16.51 | 30.22 | 30.26 | 30.34 | 23.5 | 25.97 | 30.11 | 30.39 | 30.48 | 30.48 | 30.49 | 24.39
71 | 44.27 | ER | 44.74 | 29.72 | ER | 29.96 | L
72 | 42.72 | ER | 44.83 | 28.81 | ER | 30.09
73 | 44.89 | 44.72 | 44.98 | 30.07 | 29.9 | 30.22 | T
74 | 44.99 | 44.85 | 45.1 | 30.22 | 30.02 | 30.34 | H
75 | 44.84 | 32.14 | 45.21 | 30.23 | 23.16 | 30.47 | R
76 | 31.58 | ER | 45.33 | 21.39 | ER | 30.57 | E
77 | ER | ER | ER | ER | ER | ER | E
78 | ER | ER | ER | ER | ER | ER
79 | 19.98 | ER | 45.09 | 16.51 | ER | 30.4 | I
80 | 44.91 | 33.43 | 45.1 | 30.22 | 23.88 | 30.4 | N
81 | 45.02 | 45.01 | 45.14 | 30.26 | 30.15 | 30.39 | J
82 | 45.06 | 45.08 | 45.21 | 30.34 | 30.2 | 30.42 | E
83 | 42.34 | 39.79 | 45.29 | 23.5 | 17.97 | 30.51 | C
84 | 43.01 | 39.81 | 44.73 | 25.97 | 17.91 | 29.94 | T
85 | 44.89 | 44.73 | 45.02 | 30.11 | 29.92 | 30.31 | I
86 | 45.02 | 44.95 | 45.22 | 30.39 | 30.19 | 30.54 | O
87 | 45.18 | 45.11 | 45.28 | 30.48 | 30.35 | 30.59 | N
88 | 45.18 | 45.11 | 45.27 | 30.48 | 30.37 | 30.58
89 | 45.28 | 45.07 | 45.33 | 30.49 | 30.29 | 30.58 | W
90 | 41.47 | 36.78 | 45.1 | 24.39 | 19.62 | 30.29 | E
L
L

## SHIFT DATA
PERSONNEL LIST
|  | SHIFT CODE | OPERATOR NAME |  | CERTIFICATION NUMBER |  | SOCIAL SECURITY NUMBER
CHIEF OPERATORS
HOSTNICK, N. | CO# 3207-A | 3 | BAYLER, J. | 3 | CO# 4474-A | "A" |  | "A" | 4474 | 3207 | 2D | J. BAROFSKY | 5096-C
McGEARY, J. | CO# 4545-A | 1 | HOSTNICK, N. | 1 | CO# 3207-A | "A" |  | "A" | 3207 | 4545 | 5 | S. HULL | 5613-C
BAYLER, J. | CO# 4474-A | 2 | McGEARY, J. | 2 | CO# 4545-A | "A" |  | "A" | 4545 | 4474 | 4 | VACANT | X
VACANT | CO# XXXX-X | 5 | POMEROY, D. | 5 | CO# 421-B | "A" |  | "X" | 2052 | 421 | 3 | J. TINKER | 3291-C
POMEROY, D. | CO# 421-B | 4 | VACANT | 4 | CO# XXXX-X | "X" |  | "A" | 421 | 2052 | 1 | G. SLAYTON | 2606-B
[11 empty] | 2 | H. WALKER | 4700-A
OPERATOR II' S
BAROFSKY, J. | CO# 5096-C | 1 | BAROFSKY, J. | 1 | CO# 5096-C | [5 empty] | 5 | J. BENTLEY | X
THOMAS, P. | CO# 12833 C | 4 | BENTLEY, J. | 4 | CO# 9366-C | [5 empty] | 1D | S. CURMODE | X
JONES, K. | CO# 2466-B | 5 | CURMODE, S. | 5 | CO# 9379-A | [5 empty] | 4 | K. HENDERSON | 5087-B
BENTLEY, J. | CO# 9366-C | 2D | HULL, S. | 2D | CO# 5613-C | [5 empty] | 3D | K. JONES | 2466-C
CURMODE, S. | CO# 9379-A | 3 | JONES, K. | 3 | CO# 2466-B | [5 empty] | 3 | G. KLEYNHANS | 7367-C
HULL, S. | CO# 5613-C | 2 | THOMAS, P. | 2 | CO# 12833 C | [5 empty] | 2 | A. MORROW | 9164-C
[11 empty] | 1 | J. RAINFORTH | 2718-C
OPERATOR I' S
SANDERS, C. | CO# XXXX-X | 1D | FREIDLAND, M. | 1D | CO# XXXX-X
FREIDLAND, M. | CO# XXXX-X | 4 | HENDERSON, K. | 4 | CO# 5087-B
KOKLAS, D. | CO# XXXX-X | 2 | KOKLAS, D. | 2 | CO# XXXX-X
NOBERT, B. | CO# 9661-C | 3 | NOBERT, B. | 3 | CO# 9661-C
PEUGEOT, P. | CO# 12817-C | 3D | PEUGEOT, P. | 3D | CO# 12817-C
HENDERSON, K. | CO# 5087-B | 1 | SANDERS, C. | 1 | CO# XXXX-X
VERBOSH, R. | CO# 12667-C | 5 | VERBOSH, R. | 5 | CO# 12667-C

## COVER PAGE
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
|  | MARCH |  | 2003
| OPERATOR | TITLE | CERTIFICATE # | TOTAL COST |  |  | 67758.529
1 ST SHIFT | HOSTNICK, N. | CHIEF | CO# 3207-A | PEAK TO FLOW RATIO |  |  | 1.09
2230-0630 | BAROFSKY, J. | OP. II | CO# 5096-C
| SANDERS, C. | OP. I | CO# XXXX-X |  | TOTAL SUSPENDED SOLIDS
| FREIDLAND, M. | OP. I DEWAT | CO# XXXX-X |  |  |  | LBS/DAY
|  |  |  | RAW INFLUENT |  |  | 29003.3325
2 ND SHIFT |  |  |  | FINAL EFFLUENT |  |  | 4020.7947
0630-1430 | McGEARY, J. | CHIEF | CO# 4545-A |  | TOTAL CBOD
| THOMAS, P. | OP. II RELIEF | CO# 12833 C |  |  |  | LBS/DAY
| HULL, S. | OP. II DEWAT | CO# 5613-C | RAW INFLUENT |  |  | 28176.8358
| KOKLAS, D. | OP. I RELIEF | CO# XXXX-X | FINAL EFFLUENT |  |  | 1560.0683
CHEMICALS
3 RD SHIFT | BAYLER, J. | CHIEF | CO# 4474-A |  |  | COST | POUNDS
1430-2230 | JONES, K. | OP. II | CO# 2466-B | HYDROGEN PEROXIDE |  | 10544.805 | 75590
| NOBERT, B. | OP. I | CO# 9661-C | CHLORINE |  | 5464.875 | 37050
| PEUGEOT, P. | OP. I DEWAT | CO# 12817-C | POLYMER |  | 6537.309 | 10716.9
SLUDGE REMOVED
4 TH SHIFT | VACANT | CHIEF | CO# XXXX-X |  |  |  | TONS
WEEKEND | BENTLEY, J. | OP. II | CO# 9366-C | DRY TONS |  |  | 478.419
2230-1030 | HENDERSON, K. | OP. I | CO# 5087-B |  | ENERGY
[6 empty] | COST | KILOWATTS
5 TH SHIFT | POMEROY, D. | CHIEF | CO# 421-B | FPL CONSUMPTION |  | 45211.54 | 822028
WEEKEND | CURMODE, S. | OP. II | CO# 9379-A
1030-2230 | VERBOSH, R. | OP. I | CO# 12667-C | POPULATION EQUIVALENCE |  |  | 165746.093
This Monthly Operation Report prepared by: |  |  | BAYLER, J. | CO# 4474-A
State DEP Plant Classification: Class "A" Level "II"
I certify that I am familiar with the information contained in this report and that to the best of my knowledge and
belief, such information is true, complete and accurate.
Facilitiy Manager's Signature: ____________________________________ CO# __________________
Division Manager's Signature: ____________________________________ CO# __________________
Please direct all inquiries reguarding this report to the City Official Mailing Address:
Director of Public Services |  |  | Phone (954) 776-5151
City of Fort Lauderdale
P.O. Drawer 14250 |  |  | Copies mailed: Date ________________ To: DEP _____
Fort Lauderdale, Florida | [5 empty] | DNRP _____
33302
PAGE 1

## PRINT PAGES
UNDERGROUND INJECTION CONTROL SECTION
[28 empty] | MONTHLY OPERATING REPORT DATA SUMMARY | [13 empty] | DEP From # 17-801.900 (1) | [11 empty] | DEP From # 17-801.900 (1) | [19 empty] | DAILY SAMPLE RESULTS - PART B
[25 empty] | FACILITY: GEORGE T. LOHMEYER WWTP |  |  |  |  | REPORT DATE: |  | MARCH | 2003 | [8 empty] | Form Title:Domestic Wastewater Treatment | [11 empty] | Form Title:Domestic Wastewater Treatment
[25 empty] | I.D. NUMBER: 5006M02066 |  |  |  | CHIEF OPERATOR: |  |  | BAYLER, J. | CO# 4474-A | [8 empty] | Plant Monthly Operating Report | [11 empty] | Plant Monthly Operating Report | [15 empty] | Permit Number: |  | FLA041378 |  |  |  |  | Three-month Average Daily Flow: | [5 empty] | 32.2143
[25 empty] | TELEPHONE NUMBER: (954) 523-1002 | [16 empty] | Effective Date: July 1, 1991 | [11 empty] | Effective Date: July 1, 1991 | [15 empty] | Monitoring Period |  | From: | 2003-03-01 | To: | 2003-03-31 |  | (TMADF):/Permitted Capacity)x100: | [5 empty] | 74.92%
[19 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [8 empty] | INJECTION WELL DATA | [13 empty] | DEP Application No. __________________ | [11 empty] | DEP Application No. __________________ | [11 empty] | Department of Natural Resource Protection
[5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [13 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [6 empty] | IW-1 | IW-2 | IW-3 |  | IW-4 | IW-5 | [35 empty] | Laboratory/Licensing/Enforcement |  |  |  | Flow | Flow | Flow | Flow | Flow | Flow | CBOD5 | CBOD5 | TSS | TSS | pH | pH | TDS | NH-3 | TKN | pH | cond. | temp. | TP
[5 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [13 empty] | MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING | [5 empty] | PERMIT/CERTIFICATION NUMBER: | UO-06-279401 | UO-06-279508 | UO-06-279510 |  | UC 06-264391 | UO-06-2795112 | [19 empty] | DOMESTIC WASTEWATER TREATMENT PLANT | [11 empty] | BROWARD COUNTY DEPARTMENT OF NATURAL RESOURCE PROTECTION | [5 empty] | 218 S. W. 1st Avenue |  |  | (MGD) | (MGD) | (MGD) | (MGD) | (MGD) | (mg/l) | (mg/l) | (mg/l) | (mg/l) | (Min) | (Max) | mg/L | mg/L | mg/L | units | umho/ | F | mg/L
[5 empty] | MONTHLY OPERATIONAL REPORT | [13 empty] | MONITORING WELL ONE |  |  |  | 7/21/97 thru 7/21/02 |  | PERMIT EXPIRATION DATE: | 2002-07-27 | 2002-07-27 | 2002-07-27 |  | 2000-11-30 | 2002-07-27 | [19 empty] | MONTHLY OPERATING REPORT | [11 empty] | WASTEWATER TREATMENT PLANT | [5 empty] | Fort Lauderdale, FL 33301 | [17 empty] | cm
[5 empty] | PROCESS DATA | [11 empty] | MW-1 | I.D. #: 5066A11311 |  |  | PERMIT/CERT. #: UO-06-279512 |  |  |  | CASING DEPTH | 2799' | 2798' | 2800' |  | 2804' | 2818' | [8 empty] | DOMESTIC WASTEWATER TREATMENT PLANT |  |  |  |  | (34) | [8 empty] | MONTH: | MARCH |  | YEAR: | 2003 |  |  |  |  | MONTHLY SLUDGE REPORTS | [5 empty] | Tel. No. (954) 765-4804 | Code | 50050 | 50050 | 50050 | 50050 | 50050 | 50050 | 80082 | 80082 | 00530 | 00530 | 00400 | 00400
| RUN DATE | [14 empty] | RUN DATE | [8 empty] | TOTAL DEPTH | 3513' | 3518' | 3977' |  | 3305' | 3462' | [8 empty] | MONTHLY OPERATING REPORT |  |  |  |  | DAY OF | FLOW | CHLORINE | CHLORINE | CBOD5 | TSS | CBOD5 | TSS | PH |  |  | EFFLUENT NUTRIENTS (MG/L) |  |  | I. | [10 empty] | Mon. Site | INF-001 | EFF-002 | EFF-003 | EFF-004 | EFF-005 | EFF-006 | INF-002 | EFF-001 | INF-002 | EFF-001 | EFF-001 | EFF-001
| 2026-07-30 | [14 empty] | 2026-07-30 |  | UPPER MONITOR ZONE |  |  |  |  | LOWER MONITOR ZONE |  | AVERAGE DAILY FLOW: | 7.6341 | 8.0386 | 7.0881 |  | 0.11172 | 7.0269 | MGD | [7 empty] | Part II - General Information |  |  |  |  | THE |  | RESIDUAL | RESIDUAL | INFLUENT | INFLUENT | EFFLUENT | EFFLUENT | EFFLUENT | TKN | NH3-N | NITRATE | TOTAL | FECAL | Plant Name: | GEORGE T. LOHMEYER WASTEWATER TREATMENT FACILITY | [6 empty] | MONTH: | MARCH |  | 1 | 31.303 | 8.38 | 8.39 | 7.31 | 0.11 | 5.36 | 106.7 | 5.27 | 94 | 14 | 6.4 | 6.4 | 1218 | 13.68 | 18.19 | 6.4 | 2550 | 79 | 1.33
[17 empty] | MIN | MAX | AVG |  |  | MIN | MAX | AVG | **MAX DAILY FLOW PER MO (mg): | 8.97 | 9.13 | 7.94 |  | 0.13 | 8 | MG | [12 empty] | MONTH | (MGD) | AFTER | AFTER DE- | [8 empty] | P | COLIFORM | II. | [7 empty] | YEAR: | 2003 |  | 2 | 31.465 | 8.41 | 8.44 | 7.36 | 0.11 | 5.44 | 113 | 5.91 | 104 | 13 | 6.3 | 6.3 | 1261 | 14.11 | 17.79 | 6.4 | 2640 | 79 | 0.991
| MARCH | INFLUENT | HOURLY | INFLUENT | INFLUENT | RAS | PERCENT | WAS | RAIN | SPARE | [5 empty] | MARCH | FT HEAD | FT HEAD | FT HEAD |  |  | FT HEAD | FT HEAD | FT HEAD | ** PEAK HR FLOW (MGD) ON MAX DAY: | 10.5722 | 11.1465 | 9.8534 |  | 0.15498 | 9.7348 | MGD |  | (1) Month: |  | MARCH |  | Year: | 2003 |  | Parameter | Units | STORET | Value |  |  | CONTACT | CHLORINATION | MG/L | MG/L | MG/L | MG/L | [6 empty] | A) | Sludge Treatment Provided: |  |  |  |  | B) | Sludge Dewater Processes |  |  |  | 3 | 32.224 | 8.19 | 8.16 | 7.09 | 0.11 | 7.34 | 116.5 | 5.9 | 102 | 8 | 6.4 | 6.5 | 1377 |  |  | 6.4 | 2760 | 80
| 2003 | FLOW | MAXIMUM | MAXIMUM | MINIMUM | FLOW | RAS | FLOW | INCHES | [6 empty] | 2003 | ABOVE | ABOVE | ABOVE |  |  | ABOVE | ABOVE | ABOVE | MAX SUSTAINED INJECTION PRESSURE: | 66.63 | 89.5 | 72.1 |  | 59.8 | 78.7 | PSIG |  | (2) Plant's DEP Identification Number: |  |  |  |  | 5006M02066 |  |  |  | Code |  | 1 | 31.303 | 1.1 |  | 106.7 | 94 | 5.27 | 14 | 6.4 | 18.19 | 13.68 | 0.537 | 1.33 | 0 |  |  | Aerobic Digestion | [5 empty] | Thickner |  |  | 4 | 32.434 | 8.21 | 8.21 | 7.12 | 0.11 | 7.37 | 104 | 4.4 | 126 | 10 | 6.4 | 6.6 | 1462 |  |  | 6.5 | 2950 | 80
|  | MGD | MGD | MGD | MGD | MGD |  | MGD | [8 empty] | NGVD | NGVD | NGVD |  |  | NGVD | NGVD | NGVD | MONTHLY AVG. INJECTION PRESSURE: | 45.5431 | 44.8083 | 45.5141 |  | 35.0607 | 45.0238 | PSIG |  | (3) Plant Name: |  |  |  | George T. Lohmeyer Regional Wastewater |  |  | (16) Monthly average daily flow | mgd | 050053 | 33.212 | 2 | 31.465 | 1 |  | 113 | 104 | 5.91 | 13 | 6.4 | 17.79 | 14.11 | 0.528 | 0.991 | 0 |  |  | Anaerobic Digestion | [5 empty] | DGA___X___Filter Press |  |  | 5 | 32.068 | 8.1 | 8.09 | 7.01 | 0.11 | 7.27 | 107 | 4.6 | 126 | 13 | 6.3 | 6.4 | 1548 | 14.77 | 20.73 | 6.4 | 2850 | 80 | 1.12
| 1 | 31.303 | 1.722 | 52.656 | 0.594 | 12.556 | 40.11% | 0 | 0 |  |  | 1 |  |  |  | 1 | 47.7 | 48.07 | 48.15 |  |  | 41.45 | 42.11 | 41.79 | *** MAX INJECTION PRESSURE PERMITTED: | 99 | 99 | 99 |  | 99 | 99 | PSIG |  |  |  |  | Treatment Facility |  |  |  | (17) Permitted capacity | mgd | - | 43 | 3 | 32.224 | 0.8 |  | 116.5 | 102 | 5.9 | 8 | 6.4 |  |  |  |  | 0 |  |  | Other | [5 empty] | Centrifuge Drying Beds, Bed #______ |  |  | 6 | 32.35 | 8.17 | 8.16 | 7.09 | 0.11 | 7.32 | 93 | 6.4 | 53 | 13 | 6.3 | 6.5 | 1363 | 15.11 | 21.96 | 6.4 | 2880 | 80 | 1.03
| 2 | 31.465 | 1.715 | 53.688 | 0.594 | 12.491 | 39.7% | 0.19797 | 0 |  |  | 2 |  |  |  | 2 | 47.79 | 48.15 | 47.94 |  |  | 41.49 | 42.37 | 42.07 | ***NOTE: (INJECTION PRESSURE NOT TO EXCEED 66% TESTED PRESSURE | [8 empty] | (4) Plant Address: |  |  | 1765 S.E. 18th Street at |  |  |  | (18) Three-month average daily flow | mgd | - | 32.2143 | 4 | 32.434 | 0.9 |  | 104 | 126 | 4.4 | 10 | 6.5 |  |  |  |  | 0 | [8 empty] | Heat Treatment____No Treatment |  |  | 7 | 32.283 | 8.25 | 8.27 | 7.16 | 0.12 | 7.4 | 109.1 | 5.36 | 98 | 10 | 6.3 | 6.4 | 1582 | 14.26 | 21.54 | 6.3 | 2750 | 80 | 1
| 3 | 32.224 | 1.736 | 51.531 | 0.313 | 12.339 | 38.29% | 0.55866 | 0 |  |  | 3 |  |  |  | 3 | 46.5 | 48.11 | 47.32 |  |  | 29.97 | 41.71 | 35.03 | TESTED CASING PRESSURE DURING MIT | 150 | 150 | 150 |  | 150 | 150 | PSIG |  |  |  |  | Eisenhower Boulevard |  |  |  | (19) Percent of permitted capacity | % | - | 74.92% | 5 | 32.068 | 0.9 |  | 107 | 126 | 4.6 | 13 | 6.4 | 20.73 | 14.77 | 0.489 | 1.12 | 9 | [7 empty] | x | Other: | LIME STABILIZATION |  | 8 | 31.8 | 8.16 | 8.19 | 6.25 | 0.12 | 7.35 | 115 | 4.9 | 111 | 7 | 6.3 | 6.4 | 1358 | 13.67 | 21.02 | 6.3 | 2700 | 80 | 1.21
| 4 | 32.434 | 1.706 | 52.25 | 1 | 12.7 | 39.16% | 0.55326 | 0 |  |  | 4 |  |  |  | 4 | 46.92 | 47.75 | 47.38 |  |  | 29.93 | 41.3 | 37.58 | [9 empty] | (5) City: |  | Fort Lauderdale |  |  |  |  | (20) CBOD5 Effluent | mg/L | 080082 | 5.6323 | 6 | 32.35 | 0.9 |  | 93 | 53 | 6.4 | 13 | 6.4 | 21.96 | 15.11 | 0.404 | 1.03 | 0 | [9 empty] | CLASS "AA" |  | 9 | 31.931 | 7.94 | 7.95 | 6.89 | 0.12 | 7.15 | 105 | 6.25 | 116 | 10 | 6.3 | 6.4 | 1296 | 13.34 | 18.79 | 6.4 | 2730 | 80 | 1.29
| 5 | 32.068 | 1.683 | 53.094 | 0.438 | 13.149 | 41% | 0.56425 | 0 |  |  | 5 |  |  |  | 5 | 47.56 | 47.84 | 47.66 |  |  | 41.2 | 41.43 | 41.38 |  |  | MONITORING WELL DATA | [6 empty] | (6) County: |  | Broward |  |  |  |  | (21) CBOD5 Effluent | lbs/day | - | 1560.0683 | 7 | 32.283 | 1.1 |  | 109.1 | 98 | 5.36 | 10 | 6.3 | 21.54 | 14.26 | 0.701 | 1 | 0 | III. | Final Sludge Disposal: | [7 empty] | RMF-Azurix (Nutri-Cycle) |  | 10 | 32.743 | 8.26 | 8.24 | 7.16 | 0.11 | 7.38 | 100.8 | 4.3 | 120 | 17 | 6.3 | 6.4 | 1356 |  |  | 6.4 | 2760 | 80
| 6 | 32.35 | 1.692 | 49.438 | 0.563 | 13.232 | 40.9% | 0.54754 | 0 |  |  | 6 |  |  |  | 6 | 47.64 | 47.85 | 47.73 |  |  | 41.36 | 41.55 | 41.46 |  | MW-1 | MW-2 | MW-3 |  | RMW-1 |  |  |  | (7) Phone Number: |  |  | (954) 523-1002 |  |  |  | (22) TSS Effluent | mg/L | 900201 | 14.5161 | 8 | 31.8 | 1.1 |  | 115 | 111 | 4.9 | 7 | 6.3 | 21.02 | 13.67 | 0.681 | 1.21 | 9 | A) | Liquid Sludge Disposal: | [9 empty] | 11 | 33.859 | 7.54 | 9.13 | 7.42 | 0.11 | 7.58 | 103.3 | 4.74 | 164 | 17 | 6.4 | 6.4 | 1255 |  |  | 6.4 | 2630 | 80
| 7 | 32.283 | 1.675 | 50.781 | 0.906 | 13.228 | 40.98% | 0.17834 | 0 |  |  | 7 |  |  |  | 7 | 47.62 | 47.84 | 47.69 |  |  | 41.36 | 41.54 | 41.47 | PERMIT NUMBER | UO-06-279512 | UO-06-279401 | UO-06-279510 |  | UC06-249353 |  |  |  | (8) Permit Number: |  |  | FLA041378 |  |  |  | (23) TSS Effluent | lbs/day | - | 4020.7947 | 9 | 31.931 | 1.1 |  | 105 | 116 | 6.25 | 10 | 6.4 | 18.79 | 13.34 | 0.575 | 1.29 | 0 |  | WEEK OF | MARCH | GALLONS | % SOLIDS |  |  | HAULERS |  |  | DISPOSAL SITE | 12 | 32.93 | 8.25 | 8.29 | 7.2 | 0.12 | 7.4 | 102 | 6 | 120 | 12 | 6.4 | 6.4 | 1195 | 14.09 | 20.45 | 6.4 | 2520 | 80 | 1.46
| 8 | 31.8 | 1.703 | 51.563 | 0.625 | 12.401 | 39% | 0 | 0 |  |  | 8 |  |  |  | 8 | 47.61 | 47.8 | 47.64 |  |  | 41.38 | 41.55 | 41.47 | UPPER MONITORING INTERVAL | 1288'-1320' | 1300'-1344' | 1300'-1349' |  | 1300'-1339' |  | Ft. bls. |  | (9) Plant Type: |  |  | Oxygen Activated Sludge |  |  |  | (24) Minimum pH |  | - | 6.2 | 10 | 32.743 | 1 |  | 100.8 | 120 | 4.3 | 17 | 6.4 |  |  |  |  | 9 | [11 empty] | 13 | 32.074 | 4.12 | 8.16 | 6.79 | 0.12 | 7.32 | 90.3 | 3.67 | 120 | 18 | 6.2 | 6.5 | 1267 | 14.12 | 21.5 | 6.3 | 2440 | 80 | 1.06
| 9 | 31.931 | 1.714 | 52.219 | 1.094 | 12.633 | 39.56% | 0.148 | 0 |  |  | 9 |  |  |  | 9 | 47.68 | 47.86 | 47.79 |  |  | 41.42 | 41.65 | 41.5 | MONTHLY MAX DAILY PRESSURE | 48.41 | 0 | 30.59 |  | 68.02 |  | FT. HEAD |  | (10) Test Site Identification Number: |  |  |  |  | 5006X10744 |  | (25) Maximum pH |  | - | 6.6 | 11 | 33.859 | 0.9 |  | 103.3 | 164 | 4.74 | 17 | 6.4 |  |  |  |  | 0 |  | FIRST THRU SEVENTH | [9 empty] | 14 | 31.677 | 2.54 | 8.2 | 7.12 | 0.12 | 7.33 | 102.7 | 3.39 | 115 | 7 | 6.2 | 6.4 | 1267 | 14.49 | 22.9 | 6.3 | 2390 | 80 | 1.46
| 10 | 32.743 | 1.671 | 51.281 | 1.156 | 13.131 | 40.1% | 0.52059 | 0.05 |  |  | 10 |  |  |  | 10 | 43.22 | 47.91 | 45.67 |  |  | 33.05 | 41.59 | 36.98 | MONTHLY MIN DAILY PRESSURE | 29.06 | 0 | 17.27 |  | 8.92 |  | FT. HEAD |  | (11) Fecal Coliform Method | [6 empty] | (26) Total N | mg/L | 000600 | 19.7294 | 12 | 32.93 | 1 |  | 102 | 120 | 6 | 12 | 6.4 | 20.45 | 14.09 | 0.281 | 1.46 | 0 | [11 empty] | 15 | 31.615 | 7.93 | 7.99 | 6.9 | 0.12 | 7.14 | 107.1 | 4.57 | 105 | 11 | 6.3 | 6.4 | 1276 | 13.81 | 21.84 | 6.4 | 2540 | 81 | 1.72
| 11 | 33.859 | 1.707 | 51.656 | 1.158 | 13.14 | 38.81% | 0.52 | 1.2 |  |  | 11 |  |  |  | 11 | 29.06 | 48.2 | 46.37 |  |  | 25.75 | 41.34 | 38.07 | TDS (MONTHLY AVERAGE) | 5559.8025 | 13474.75 | 7304.5 |  | 5664 |  | mg/l |  |  | XX | Membrane Filter |  |  |  |  | (27) TKN | mg/L | 000625 | 19.33 | 13 | 32.074 | 0.9 |  | 90.3 | 120 | 3.67 | 18 | 6.3 | 21.5 | 14.12 | 0.355 | 1.06 | 18 |  | EIGHT THRU FORTEENTH | [9 empty] | 16 | 32.063 | 8.03 | 8.09 | 6.98 | 0.11 | 7.22 | 107 | 5.88 | 57 | 14 | 6.2 | 6.4 | 1231 | 13.09 | 19.67 | 6.3 | 2580 | 80 | 1.27
| 12 | 32.93 | 1.719 | 52.469 | 0.875 | 12.934 | 39.28% | 0.507 | 0 |  |  | 12 |  |  |  | 12 | ER | 47.98 | 47.53 |  |  | ER | 41.44 | 41.12 | CHLORIDE (MONTHLY AVERAGE) | 2834.375 | 7312.5 | 3737.5 |  | 2900 |  | mg/l |  |  |  | Most Probable Number |  |  |  |  | (28) Ammonia (NH3 - N) | mg/L | 000610 | 13.9505 | 14 | 31.677 | 1 |  | 102.7 | 115 | 3.39 | 7 | 6.3 | 22.9 | 14.49 | 0.334 | 1.46 | 0 |  | FIFTHTEENTH THRU | [9 empty] | 17 | 35.171 | 5.16 | 5.17 | 4.48 | 0.07 | 4.62 | 87.3 | 6.46 | 96 | 23 | 6.3 | 6.5 | 1276 |  |  | 6.4 | 2600 | 80
| 13 | 32.074 | 1.671 | 51.344 | 1 | 12.647 | 39.43% | 0.57 | 0 |  |  | 13 |  |  |  | 13 | 47.39 | 47.97 | 47.86 |  |  | ER | 41.42 | ER | AMMONIA-N (MONTHLY AVERAGE) | 0.8455 | 0.933 | 0.856 |  | 0.58 |  | mg/l |  | (12) Type of Effluent Disposal or Reclaimed Water Reuse | [6 empty] | (29) Nitrate | mg/L | 071850 | 0.39936 | 15 | 31.615 | 1 |  | 107.1 | 105 | 4.57 | 11 | 6.4 | 21.84 | 13.81 | 0.352 | 1.72 | 0 |  | TWENTY SECOND | [9 empty] | 18 | 36.093 | ER | ER | ER | ER | ER | 86.4 | 6.47 | 98 | 14 | 6.3 | 6.5 | 1235 |  |  | 6.4 | 2620 | 80
| 14 | 31.677 | 1.674 | 51.594 | 0.781 | 13.535 | 42.73% | 0.16569 | 0 |  |  | 14 |  |  |  | 14 | 47.75 | 48.07 | 47.95 |  |  | ER | ER | ER | TKN (MONTHLY AVERAGE) | 1.38 | 1.6825 | 1.4325 |  | 1.07 |  | mg/l |  |  |  | Deep Well Injection |  |  |  |  | (30) Total Phosphorus | mg/L | 000665 | 1.4241 | 16 | 32.063 | 0.8 |  | 107 | 57 | 5.88 | 14 | 6.3 | 19.67 | 13.09 | 0.388 | 1.27 | 0 |  | TWENTY THIRD THRU | [9 empty] | 19 | 36.2 | ER | ER | ER | ER | ER | 92.9 | 4.55 | 104 | 15 | 6.4 | 6.6 | 1315 | 13.54 | 18.32 | 6.5 | 2600 | 80 | 1.33
| 15 | 31.615 | 1.748 | 52.688 | 0.531 | 12.58 | 39.79% | 0 | 0.25 |  |  | 15 |  |  |  | 15 | 47.82 | 48.17 | 48 |  |  | ER | ER | ER | pH (MONTHLY AVERAGE) | 8.025 | 7.9075 | 8.16 |  | 8.08 |  | Std units |  | (13) Limited Wet Wheather Discharge Activated | [6 empty] | (31) Minimum Chlorine Residual | mg/L | - | 0.8 | 17 | 35.171 | 0.9 |  | 87.3 | 96 | 6.46 | 23 | 6.4 |  |  |  |  | 260 |  | THIRTY FIRST | [9 empty] | 20 | 35.581 | 2.26 | 2.3 | ER | 0.02 | 2.02 | 104 | 6.28 | 130 | 27 | 6.4 | 6.6 | 1345 | 15.19 | 21.73 | 6.5 | 2540 | 81 | 1.65
| 16 | 32.063 | 1.728 | 53.063 | 0.813 | 12.792 | 39.9% | 0 | 0 |  |  | 16 |  |  |  | 16 | 33.32 | 48.28 | 47.89 |  |  | ER | ER | ER | CONDUCTIVITY (MONTHLY AVERAGE) | 12300 | 20752.5 | 11960 |  | 9420 |  | umho/cm |  |  |  | YES |  | XX | Not Applicable |  | (32) Maximum Chlorine Residual | mg/L | - | 1.2 | 18 | 36.093 | 0.8 |  | 86.4 | 98 | 6.47 | 14 | 6.4 |  |  |  |  | 9 | [11 empty] | 21 | 34.452 | 8.86 | 8.93 | ER | 0.12 | 7.94 | 112.9 | 8.58 | 104 | 16 | 6.3 | 6.5 | 1240 | 16.31 | 22.41 | 6.4 | 2580 | 81 | 1.6
| 17 | 35.171 | 1.802 | 56.313 | 1.9094 | 13.616 | 38.71% | 0 | 0.86 |  |  | 17 |  |  |  | 17 | ER | 48.41 | ER |  |  | ER | ER | ER | FECAL COLIFORM (MONTHLY AVERAGE) | 0 | 0 | 0 |  | 0 |  | # col/100ml |  |  |  | NO |  |  |  |  | (33) Other Effluent Parameters |  |  |  | 19 | 36.2 | 0.9 |  | 92.9 | 104 | 4.55 | 15 | 6.5 | 18.32 | 13.54 | 0.111 | 1.33 | 0 | B) | Solid Sludge Hauled from Plant: | [9 empty] | 22 | 33.509 | 8.29 | 8.33 | 7.38 | 0.13 | 7.45 | 113.9 | 6.59 | 245 | 20 | 6.3 | 6.5 | 1240 | 14.35 | 19.96 | 6.4 | 2390 | 81 | 1.72
| 18 | 36.093 | 1.893 | 53.438 | 11.781 | 13.906 | 38.53% | 0 | 0 |  |  | 18 |  |  |  | 18 | ER | ER | ER |  |  | ER | ER | ER | TEMPERATURE (MONTHLY AVERAGE) | 73 | 71 | 69.5 |  | 70 |  | deg. F | [12 empty] | 20 | 35.581 | 0.8 |  | 104 | 130 | 6.28 | 27 | 6.5 | 21.73 | 15.19 | 0.118 | 1.65 | 0 |  | WEEK OF | MARCH | TONS |  | % SOLIDS |  | HAULERS |  |  | DISPOSAL SITE | 23 | 33.525 | 8.41 | 8.38 | 7.47 | 0.12 | 7.53 | 101.4 | 8.06 | 91 | 23 | 6.3 | 6.4 | 1157 | 13.51 | 0 | 6.4 | 2340 | 81 | 1.53
| 19 | 36.2 | 1.883 | 55.938 | 0.813 | 13.239 | 36.57% | 0.24 | 0 |  |  | 19 |  |  |  | 19 | ER | ER | ER |  |  | ER | ER | 10.7 | TOTAL PHOSPHOROUS (MONTHLY AVG.) | 0.05 | 0.05 | 0.05 |  | 0.05 |  | mg/l |  | (14) Cumulative Days of Wet Wheather Discharge | [10 empty] | 21 | 34.452 | 0.8 |  | 112.9 | 104 | 8.58 | 16 | 6.4 | 22.41 | 16.31 | 0.2 | 1.6 | 0 | [10 empty] | Nutri-Cylcle Inc. | 24 | 34.625 | 8.95 | 8.76 | 6.93 | 0.12 | 8 | 97.2 | 7.27 | 59 | 18 | 6.3 | 6.5 | 1259 |  |  | 6.4 | 2560 | 80
| 20 | 35.581 | 1.836 | 54.063 | 1.094 | 13.598 | 38.22% | 0.63 | 0 |  |  | 20 |  |  |  | 20 | ER | 14.86 | ER |  |  | ER | 13.47 | ER | SULFATE (MONTHLY AVERAGE) | 825 | 1375 | 825 |  | 650 |  | mg/l |  |  |  | N/A | [8 empty] | 22 | 33.509 | 0.8 |  | 113.9 | 245 | 6.59 | 20 | 6.4 | 19.96 | 14.35 | 0.221 | 1.72 | 0 |  | FIRST THRU SEVENTH |  | 725 |  | 17.8825 |  | AZURIX |  |  | Arcadia, FL | 25 | 33.396 | 8.33 | 8.37 | 7.41 | 0.12 | 7.49 | 91 | 6.8 | 55 | 18 | 6.4 | 6.4 | 1234 |  |  | 6.4 | 2460 | 80
| 21 | 34.452 | 1.775 | 53.625 | 1.125 | 13.459 | 39.07% | 0.36563 | 0 |  |  | 21 |  |  |  | 21 | ER | ER | ER |  |  | ER | ER | ER | C.O.D. (MONTHLY AVERAGE) | 167.5 | 352.5 | 165 |  | 140 |  | mg/l |  | (15) Plant Staffing: | [10 empty] | 23 | 33.525 | 0.9 |  | 101.4 | 91 | 8.06 | 23 | 6.4 | 0 | 13.51 | 0.255 | 1.53 | 0 | [10 empty] | Nutri-Cylcle Inc. | 26 | 33.14 | 8.31 | 8.35 | 7.39 | 0.12 | 7.47 | 118 | 6 | 152 | 20 | 6.4 | 6.4 | 1346 | 13.93 | 18.9 | 6.4 | 2600 | 80 | 1.52
| 22 | 33.509 | 1.774 | 53.906 | 8.344 | 12.414 | 37.05% | 0 | 0 |  |  | 22 |  |  |  | 22 | ER | ER | ER |  |  | ER | ER | ER | IRON (MONTHLY AVERAGE) | 1.14 | 3.9475 | 1.0825 |  | 0.21 |  | mg/l | [12 empty] | 24 | 34.625 | 0.9 |  | 97.2 | 59 | 7.27 | 18 | 6.4 |  |  |  |  | 0 |  | EIGHT THRU FORTEENTH |  | 725 |  | 17.602 |  | AZURIX |  |  | Arcadia, FL | 27 | 33.979 | 8.53 | 8.57 | 7.56 | 0.12 | 7.63 | 98 | 6 | 94 | 14 | 6.3 | 6.4 | 1378 | 13.9 | 20.93 | 6.3 | 2590 | 80 | 1.93
| 23 | 33.525 | 1.736 | 51.219 | 10.344 | 12.512 | 37.32% | 0.22671 | 0.21 |  |  | 23 |  |  |  | 23 | ER | ER | ER |  |  | ER | ER | ER | SULFIDE (MONTHLY AVERAGE) | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! |  | mg/l |  |  | Day Shift Operator: |  |  | Class | "A" | Cert. No. | 4545 |  |  |  | 25 | 33.396 | 0.9 |  | 91 | 55 | 6.8 | 18 | 6.4 |  |  |  |  | 0 |  | FIFTHTEENTH THRU | [8 empty] | Nutri-Cylcle Inc. | 28 | 35.305 | 8.97 | 9 | 7.94 | 0.12 | 8 | 96 | 5 | 90 | 13 | 6.2 | 6.4 | 1285 | 12.71 | 19.28 | 6.3 | 2600 | 80 | 1.94
| 24 | 34.625 | 1.78 | 53.781 | 10.281 | 13.045 | 37.68% | 0.663 | 0 |  |  | 24 |  |  |  | 24 | ER | ER | ER |  |  | ER | ER | ER | LOWER MONITORING INTERVAL | 1449'-1557' | 1970'-2025' | 1970'-2027' |  | 1500'-1600' |  | Ft. bls | [12 empty] | 26 | 33.14 | 1 |  | 118 | 152 | 6 | 20 | 6.4 | 18.9 | 13.93 | 0.399 | 1.52 | 0 |  | TWENTY SECOND |  | 350 |  | 17.602 |  | AZURIX |  |  | Arcadia, FL | 29 | 34.501 | 8.54 | 8.6 | 7.57 | 0.13 | 7.66 | 74 | 6 | 72 | 12 | 6.3 | 6.4 | 1239 | 12.67 | 19.33 | 6.4 | 2600 | 81 | 2.03
| 25 | 33.396 | 1.755 | 52.656 | 12.031 | 13.76 | 41.2% | 0.582 | 0 |  |  | 25 |  |  |  | 25 | ER | ER | ER |  |  | ER | ER | ER | MONTHLY MAX DAILY PRESSURE | 42.37 | 42.27 | 45.33 |  | 21.87 |  | FT. HEAD |  |  | Evening Shift Operator: |  |  | Class | "A" | Cert. No. | 4474 |  |  |  | 27 | 33.979 | 0.8 |  | 98 | 94 | 6 | 14 | 6.3 | 20.93 | 13.9 | 0.475 | 1.93 | 26000 |  | TWENTY THIRD THRU | [8 empty] | Nutri-Cylcle Inc. | 30 | 33.07 | 8.27 | 8.32 | 7.3 | 0.12 | 7.42 | 96 | 4 | 40 | 9 | 6.3 | 6.4 | 1198 | 12.26 | 18.02 | 6.4 | 2530 | 80 | 1.14
| 26 | 33.14 | 1.742 | 51.031 | 1.031 | 13.675 | 41.26% | 0.595 | 0 |  |  | 26 |  |  |  | 26 | ER | ER | ER |  |  | ER | ER | ER | MONTHLY MIN DAILY PRESSURE | 25.75 | 26.64 | 28.13 |  | 19.58 |  | FT. HEAD | [12 empty] | 28 | 35.305 | 0.9 |  | 96 | 90 | 5 | 13 | 6.3 | 19.28 | 12.71 | 0.522 | 1.94 | TNTC |  | THIRTY FIRST |  | 1025 |  | 17.14 |  | AZURIX |  |  | Arcadia, FL | 31 | 32.206 | 8.03 | 8.08 | 7.1 | 0.1 | 7.18 | 102 | 5 | 85 | 14 | 6.3 | 6.4 | 1284 |  |  | 6.4 | 2630 | 79
| 27 | 33.979 | 1.808 | 54.25 | 11.906 | 13.991 | 41.18% | 0.599 | 0.75 |  |  | 27 |  |  |  | 27 | ER | ER | ER |  |  | ER | ER | ER | TDS (MONTHLY AVERAGE) | 9483.5 | 31803 | 29256.5 |  | 26794 |  | mg/l |  |  | Night Shift Operator: |  |  | Class | "A" | Cert. No. | 3207 |  |  |  | 29 | 34.501 | 1.2 |  | 74 | 72 | 6 | 12 | 6.4 | 19.33 | 12.67 | 0.469 | 2.03 | 0 | C) | Monthly quantities of solid sludge stockpiled at plant.Solid Sludge Hauled from Plant: | [9 empty] | TOT | 1029.572 | 221.39 | 233.12 | 191.38 | 3.24 | 203.78 | 3153.5 | 174.6 | 3246 | 450 | 195.8 | 199.7 | 40343 | 306.91 | 425.26 | 198 | 80910 | 2483 | 31.331
| 28 | 35.305 | 1.901 | 57.969 | 4.5 | 13.787 | 39.05% | 0.31678 | 0 |  |  | 28 |  |  |  | 28 | ER | ER | ER |  |  | ER | ER | ER | CHLORIDE (MONTHLY AVERAGE) | 5125 | 18037.5 | 16050 |  | 15600 |  | mg/l | [12 empty] | 30 | 33.07 | 1.1 |  | 96 | 40 | 4 | 9 | 6.4 | 18.02 | 12.26 | 0.391 | 1.14 | 0 |  | 1) | Additions |  |  | Cubic Yards | [5 empty] | AVG | 33.212 | 7.6341 | 8.0386 | 7.0881 | 0.11172 | 7.0269 | 101.7258 | 5.6323 | 104.7097 | 14.5161 | 6.3161 | 6.4419 | 1301.3871 | 13.9505 | 19.33 | 6.3871 | 2610 | 80.0968 | 1.4241
| 29 | 34.501 | 1.854 | 53.375 | 9.781 | 12.877 | 37.32% | 0 | 0 |  |  | 29 |  |  |  | 29 | ER | ER | ER |  |  | ER | ER | ER | AMMONIA-N (MONTHLY AVERAGE) | 9.235 | 1.17 | 2.1125 |  | 0.19 |  | mg/l |  |  | Lead Operator:_________________________________ | [9 empty] | 31 | 32.206 | 1 |  | 102 | 85 | 5 | 14 | 6.4 |  |  |  |  | 0 | [5 empty] | Tons | [5 empty] | MAX | 36.2 | 8.97 | 9.13 | 7.94 | 0.13 | 8 | 118 | 8.58 | 245 | 27 | 6.4 | 6.6 | 1582 | 16.31 | 22.9 | 6.5 | 2950 | 81 | 2.03
| 30 | 33.07 | 1.73 | 52.688 | 0.719 | 12.682 | 38.35% | 0.32697 | 0 |  |  | 30 |  |  |  | 30 | ER | ER | ER |  |  | ER | ER | ER | TKN (MONTHLY AVERAGE) | 12.86 | 1.9925 | 3.2625 |  | 0.646 |  | mg/l | [5 empty] | Signature |  | Cert. No. |  |  |  |  | Lead Operator : This is to certify that I am familar with the information contained on this report and that to the best of | [14 empty] | 2) | Removals |  |  | Cubic Yards | [5 empty] | MIN | 31.303 | 2.26 | 2.3 | 4.48 | 0.02 | 2.02 | 74 | 3.39 | 40 | 7 | 6.2 | 6.3 | 1157 | 12.26 | 0 | 6.3 | 2340 | 79 | 0.991
| 31 | 32.206 | 1.736 | 50.469 | 2.063 | 12.912 | 40.09% | 0.515 | 0.05 |  |  | 31 |  |  |  | 31 | ER | ER | ER |  |  | ER | ER | ER | pH (MONTHLY AVERAGE) | 7.415 | 7.415 | 7.42 |  | 7.7 |  | Std units | [12 empty] | my knowledge and belief, this information is true, complete and accuate. | [16 empty] | X |  | Tons | [6 empty] | item #1 | 10.5722 | 11.1465 | 9.8534 | 0.15498 | 9.7348 | MAX HOURLY FLOW (MG) = |  |  |  | 1.901 | ON THE | 28 | DAY OF THIS MONTH
| TOTAL | 1029.572 | 54.269 | 1636.036 | 100.1634 | 404.961 |  | 10.0914 | 3.37 | [6 empty] | TOTAL | 675.58 | 831.12 | 760.57 |  |  | 408.36 | 554.47 | 490.62 | CONDUCTIVITY (MONTHLY AVERAGE) | 15682.5 | 47550 | 44025 |  | 41400 |  | umho/cm | [33 empty] | Signature |  |  |  |  | item #2 | 45.5431 | 44.8083 | 45.5141 | 35.0607 | 45.0238
| AVERAGE | 33.212 | 1.7506 | 52.7754 | 3.2311 | 13.0633 | 39.33% | 0.43876 | 0.10871 | [6 empty] | AVERAGE | 45.0387 | 46.1733 | 47.5356 |  |  | 37.1236 | 39.605 | 37.74 | FECAL COLIFORM (MONTHLY AVERAGE) | 0 | 0 | 0 |  | 0 |  | # col/100ml | [12 empty] | Signed: ____________________________ Date: ___________________ | [20 empty] | Title |  |  |  |  | item #3 | 36.1 | 36.3 | 37.1 | 34.8 | 35.3
[16 empty] | MAXIMUM | 47.82 | 48.41 | 48.15 |  |  | 41.49 | 42.37 | 42.07 | TEMPERATURE (MONTHLY AVERAGE) | 73.25 | 70 | 67.75 |  | 68 |  | deg. F | [33 empty] | Date |  |  |  | item #1 | =monthly maximum of the daily flows (MG), with peakhour flow (MGD) on the day of the month with maximum flow = | [14 empty] | 1.901 | MG/hour multiplied by
[16 empty] | MINIMUM | 29.06 | 14.86 | 45.67 |  |  | 25.75 | 13.47 | 10.7 | TOTAL PHOSPHOROUS (MONTHLY AVG.) | 0.05 | 0.05 | 0.05 |  | 0.05 |  | mg/l | [12 empty] | Name: Michael A. Just | [14 empty] | * Sludge Reports should be submitted along with the monthly operating reports to Broward County Department | [10 empty] | the % of average % of TOTAL RAW FLOW to each Injection well.
[25 empty] | SULFATE (MONTHLY AVERAGE) | 812.5 | 2775 | 2375 |  | 1650 |  | mg/l | [27 empty] | of Natural Resource Protection, 218 S. W. 1st Avenue, Fort Lauderdale, Florida 33301 | [9 empty] | item #2 | =monthly average injection well pressure at injection well (psig)
[25 empty] | C.O.D. (MONTHLY AVERAGE) | 260 | 845 | 810 |  | 690 |  | mg/l | [12 empty] | Company Name: City of Fort Lauderdale Telephone No. (954) 523-1002 | [24 empty] | item #3 | =monthly wellhead pressure with no flow (shut-in pressure,psig)
[25 empty] | IRON (MONTHLY AVERAGE) | 0.01 | 0.0375 | 0.035 |  | 0.06 |  | mg/l | [37 empty] | PLANT STAFFING
[5 empty] | PAGE 2 | [19 empty] | SULFIDE (MONTHLY AVERAGE) | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! |  | mg/l | [37 empty] | Day Shift Operator |  |  | Class: | "A" | Certificate No. | 4545 | Name: |  | McGEARY, J.
[70 empty] | Evening Shift Operator |  |  | Class: | "A" | Certificate No. | 4474 | Name: |  | BAYLER, J.
[20 empty] | PAGE 20 | [49 empty] | Night Shift Operator |  |  | Class: | "A" | Certificate No. | 3207 | Name: |  | HOSTNICK, N.
[70 empty] | Lead Operator |  |  | Class: | "A" | Certificate No. | 2769 | Name: |  | JUST, M.
[70 empty] | Type of Effluent Disposal or Reclaimed Water Reuse: |  |  |  |  | DEEPWELL INJECTION
[70 empty] | Permited Wet Weather Discharge Activated: |  |  |  | YES: |  | NO: |  |  | Not Applicable |  | X
If Yes, cumulative days of wet weather:
Attach additional sheets if necessary to list all certified operators. See page 1 "COVER PAGE" of supplental attachements.
DEP form 62-620.910(10), effective November 29, 1994
[19 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [46 empty] | Department of Natural Resource Protection
[5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [13 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [46 empty] | Division of Pollution Prevention and Remediation Programs
[5 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [13 empty] | MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING | [49 empty] | 218 S. W. 1st Avenue
[5 empty] | MONTHLY OPERATIONAL REPORT | [13 empty] | MONITORING WELL TWO |  |  |  | 7/21/97 thru 7/21/02 | [38 empty] | SLUDGE HAULERS MONTHLY REPORT | [6 empty] | Fort Lauderdale, FL 33301
[5 empty] | INFLUENT DATA | [11 empty] | MW-2 | I.D. #: 5066A11308 & 09 |  |  | PERMIT/CERT. #: UO-06-279401 & 508 | [40 empty] | BROWARD COUNTY CODE SECTION 27-356 (d)(4)(1) | [5 empty] | Tel. No. (954) 523-1002
| RUN DATE | [14 empty] | RUN DATE | [51 empty] | *FAX (954) 519-1245
| 2026-07-30 | [14 empty] | 2026-07-30 |  | UPPER MONITOR ZONE |  |  |  |  | LOWER MONITOR ZONE
[17 empty] | MIN | MAX | AVG |  |  | MIN | MAX | AVG | [34 empty] | Plant Name: | GEORGE T. LOHMEYER WASTEWATER TREATMENT FACILITY
| MARCH | RAW | RAW TSS | RAW SS | RAW | RAW | RAW | RAW | RAW | RAW | [5 empty] | MARCH | FT HEAD | FT HEAD | FT HEAD |  |  | FT HEAD | FT HEAD | FT HEAD | [34 empty] | Address: | 1765 S.E. 18th Street at Eisenhower Boulevard | [6 empty] | MONTH: | MARCH
| 2003 | CBOD | TOTAL | FIXED | COD | pH | CL_ | ALK. | H2S | TEMP.(F) | [5 empty] | 2003 | ABOVE | ABOVE | ABOVE |  |  | ABOVE | ABOVE | ABOVE | [34 empty] | Phone: | (954) 523-1002 * FAX (954) 468-1577 | [6 empty] | YEAR: | 2003
[17 empty] | NGVD | NGVD | NGVD |  |  | NGVD | NGVD | NGVD
| 1 | 106.7 | 94 | 8 | 359 | 7.2 | 670 | 210 | 8 | 80 | [5 empty] | 1 | ER | ER | ER |  |  | 41.75 | 42 | 41.92 | [34 empty] | a) | WEEK OF | MARCH |  | Type of Sludge |  |  | Disopsal Site |  |  | Cubic Yards
| 2 | 113 | 104 | 14 | 331 | 7.2 | 680 | 212 | 7 | 83 | [5 empty] | 2 | ER | ER | ER |  |  | 41.88 | 42.11 | 41.98
| 3 | 116.5 | 102 | 8 |  | 7.2 | 710 | 216 | 6 | 80 | [5 empty] | 3 | ER | ER | ER |  |  | 30.92 | 42.08 | 35.83 | [35 empty] | FIRST THRU SEVENTH |  |  | GRIT |  |  | Central Landfill |  |  | 0
| 4 | 104 | 126 | 4 |  | 7.2 | 760 | 210 | 6 | 80 | [5 empty] | 4 | ER | ER | ER |  |  | 30.87 | 41.62 | 38.05
| 5 | 107 | 126 | 24 | 324 | 7.2 | 770 | 218 | 6 | 81 | [5 empty] | 5 | ER | ER | ER |  |  | 41.6 | 41.82 | 41.71 | [35 empty] | EIGHT THRU FORTEENTH |  |  | GRIT |  |  | Central Landfill |  |  | 0
| 6 | 93 | 53 | 11 | 319 | 7.2 | 740 | 220 | 8 | 81 | [5 empty] | 6 | ER | ER | ER |  |  | 41.78 | 41.89 | 41.9 | [35 empty] | FIFTHTEENTH THRU
| 7 | 109.1 | 98 | 2 | 318 | 7.2 | 600 | 212 | 5 | 81 | [5 empty] | 7 | ER | ER | ER |  |  | 41.84 | 41.9 | 41.93 | [35 empty] | TWENTY SECOND |  |  | GRIT |  |  | Central Landfill |  |  | 10
| 8 | 115 | 111 | 17 | 335 | 7.2 | 600 | 212 | 7 | 81 | [5 empty] | 8 | ER | ER | ER |  |  | 41.83 | 41.92 | 41.93 | [35 empty] | TWENTY THIRD THRU
| 9 | 105 | 116 | 20 | 351 | 6.4 | 770 | 222 | 8 | 82 | [5 empty] | 9 | ER | ER | ER |  |  | 41.92 | 42.02 | 41.98 | [35 empty] | THIRTY FIRST |  |  | GRIT |  |  | Central Landfill |  |  | 0
| 10 | 100.8 | 120 | 26 |  | 7.2 | 730 | 216 | 7 | 81 | [5 empty] | 10 | ER | ER | ER |  |  | 33.77 | 42.06 | 37.6
| 11 | 103.3 | 164 | 24 |  | 7.2 | 730 | 218 | 6 | 81 | [5 empty] | 11 | ER | ER | ER |  |  | 26.64 | 41.52 | 38.46 | [34 empty] | b) | WEEK OF | MARCH |  | Type of Sludge |  |  | Disopsal Site |  |  | Cubic Yards
| 12 | 102 | 120 | 4 | 314 | 7.2 | 650 | 204 | 6 | 81 | [5 empty] | 12 | ER | ER | ER |  |  | ER | 41.73 | 41.31
| 13 | 90.3 | 120 | 24 | 310 | 7.2 | 660 | 214 | 6 | 81 | [5 empty] | 13 | ER | ER | ER |  |  | ER | 41.77 | 38.29 | [35 empty] | FIRST THRU SEVENTH |  |  | RAGS |  |  | Central Landfill |  |  | 10
| 14 | 102.7 | 115 | 11 | 367 | 7.2 | 620 | 196 | 7 | 81 | [5 empty] | 14 | ER | ER | ER |  |  | 41.58 | 41.88 | 41.84
| 15 | 107.1 | 105 | 14 | 325 | 7.2 | 650 | 210 | 7 | 81 | [5 empty] | 15 | ER | ER | ER |  |  | 41.76 | 42.02 | 41.96 | [35 empty] | EIGHT THRU FORTEENTH |  |  | RAGS |  |  | Central Landfill |  |  | 10
| 16 | 107 | 57 | 3 | 324 | 7.1 | LS | 210 | 5 | 81 | [5 empty] | 16 | ER | ER | ER |  |  | 30.27 | 42.15 | 41.83 | [35 empty] | FIFTHTEENTH THRU
| 17 | 87.3 | 96 | 17 |  | 7.2 | 720 | 216 | 6 | 80 | [5 empty] | 17 | ER | ER | ER |  |  | ER | 42.27 | 29.88 | [35 empty] | TWENTY SECOND |  |  | RAGS |  |  | Central Landfill |  |  | 10
| 18 | 86.4 | 98 | 10 |  | 7.2 | 690 | 196 | 4 | 81 | [5 empty] | 18 | ER | ER | ER |  |  | ER | ER | ER | [35 empty] | TWENTY THIRD THRU
| 19 | 92.9 | 104 | 12 | 338 | 7.2 | 700 | 200 | 5 | 81 | [5 empty] | 19 | ER | ER | ER |  |  | ER | ER | ER | [35 empty] | THIRTY FIRST |  |  | RAGS |  |  | Central Landfill |  |  | 10
| 20 | 104 | 130 | 18 | 310 | 7.2 | 720 | 204 | 5 | 81 | [5 empty] | 20 | ER | ER | ER |  |  | ER | 36.17 | ER | [35 empty] | BCSR = Broward County Septage Receiving
| 21 | 112.9 | 104 | 9 | 315 | 7.3 | 700 | 216 | 6 | 81 | [5 empty] | 21 | ER | ER | ER |  |  | ER | ER | ER | [34 empty] | c) | WEEK OF | MARCH |  | Type of Sludge |  |  | Disopsal Site |  |  | Gallons
| 22 | 113.9 | 245 | 64 | 261 | 7.2 | 700 | 232 | 7 | 81 | [5 empty] | 22 | ER | ER | ER |  |  | ER | ER | ER
| 23 | 101.4 | 91 | 10 | 418 | 7.2 | 690 | 230 | 7 | 81 | [5 empty] | 23 | ER | ER | ER |  |  | ER | ER | ER | [35 empty] | FIRST THRU SEVENTH |  |  | VAC/Plastic & Rags |  |  | BCSR |  |  | 0
| 24 | 97.2 | 59 | 4 |  | 7.2 | 710 | 226 | 7 | 80 | [5 empty] | 24 | ER | ER | ER |  |  | ER | ER | ER
| 25 | 91 | 55 | 5 |  | 7 | 650 | 222 | 6 | 77 | [5 empty] | 25 | ER | ER | ER |  |  | ER | ER | ER | [35 empty] | EIGHT THRU FORTEENTH |  |  | VAC/Plastic & Rags |  |  | BCSR |  |  | 0
| 26 | 118 | 152 | 13 | 332 | 7 | 690 | 204 | 5 | 81 | [5 empty] | 26 | ER | ER | ER |  |  | ER | ER | ER | [35 empty] | FIFTHTEENTH THRU
| 27 | 98 | 94 | 7 | 271 | 7.1 | 700 | 194 | 6 | 79 | [5 empty] | 27 | ER | ER | ER |  |  | ER | ER | ER | [35 empty] | TWENTY SECOND |  |  | VAC/Plastic & Rags |  |  | BSCR |  |  | 0
| 28 | 96 | 90 | 7 | 916 | 7.2 | 700 | 196 | 5 | 78 | [5 empty] | 28 | ER | ER | ER |  |  | ER | ER | ER | [35 empty] | TWENTY THIRD THRU
| 29 | 74 | 72 | 6 | 250 | 7.2 | 720 | 200 | 6 | 80 | [5 empty] | 29 | ER | ER | ER |  |  | ER | ER | ER | [35 empty] | THIRTY FIRST |  |  | VAC/Plastic & Rags |  |  | BSCR |  |  | 4500
| 30 | 96 | 40 | 6 | 335 | 7.2 | 660 | 210 | 7 | 81 | [5 empty] | 30 | ER | ER | ER |  |  | ER | ER | ER | [34 empty] | TOTALS
| 31 | 102 | 85 | 12 |  | 7.2 | 700 | 208 | 7 | 80 | [5 empty] | 31 | ER | ER | ER |  |  | ER | ER | ER | [35 empty] | a) | 10 | cu.yds |  | GRIT |  | Signature
| TOTAL | 3153.5 | 3246 | 414 | 7723 | 221.9 | 20790 | 6554 | 194 | 2498 | [5 empty] | TOTAL | 0 | 0 | 0 |  |  | 528.41 | 748.93 | 678.4 | [35 empty] | b) | 40 | cu.yds |  | RAGS |  | Title
| AVERAGE | 101.7258 | 104.7097 | 13.3548 | 351.0455 | 7.1581 | 693 | 211.4194 | 6.2581 | 80.5806 | [5 empty] | AVERAGE | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 37.7436 | 41.6072 | 39.9059 | [35 empty] | c) | 4500 | gal. |  | VAC/Plastic & Rags |  | Date
[16 empty] | MAXIMUM | 0 | 0 | 0 |  |  | 41.92 | 42.27 | 41.98
[16 empty] | MINIMUM | 0 | 0 | 0 |  |  | 26.64 | 36.17 | 29.88 | [35 empty] | * Sludge Reports should be submitted along with the monthly operating reports to Broward County Department
of Natural Resource Protection, 218 S. W. 1st Avenue, Fort Lauderdale, Florida 33301
PAGE 3
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
[5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [13 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
[5 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [13 empty] | MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
[5 empty] | MONTHLY OPERATIONAL REPORT | [13 empty] | MONITORING WELL THREE |  |  |  | 7/21/97 thru 7/21/02
[5 empty] | EFFLUENT DATA PART 1 | [11 empty] | MW-3 | I.D. #: 5066A11310 |  |  | PERMIT/CERT. #: UO-06-279510
RUN DATE
[16 empty] | 2026-07-30 |  | UPPER MONITOR ZONE |  |  |  |  | LOWER MONITOR ZONE
| RUN DATE | [15 empty] | MIN | MAX | AVG |  |  | MIN | MAX | AVG
| 2026-07-30 | [14 empty] | MARCH | FT HEAD | FT HEAD | FT HEAD |  |  | FT HEAD | FT HEAD | FT HEAD
[14 empty] | BOD | TSS | 2003 | ABOVE | ABOVE | ABOVE |  |  | ABOVE | ABOVE | ABOVE
| MARCH | EFFLUENT | EFFL. TSS | EFFL. SS | EFFLUENT | EFFL. | EFFL. | EFFL. | EFFL. | EFFL. | TDS |  |  | MONTHLY AVG OVER 30 | MONTHLY AVG OVER 30 |  | NGVD | NGVD | NGVD |  |  | NGVD | NGVD | NGVD
| 2003 | CBOD | TOTAL | FIXED | COD | CL_ | ALK. | TURB. | COND. | TEMP.(F) |  |  |  | 0 | 0 | 1 | 29.76 | 30.08 | 29.95 |  |  | 44.77 | 45 | 44.95
[14 empty] | WEKKLY OVER 45 | WEKKLY OVER 45 | 2 | 29.86 | 30.17 | 30 |  |  | 44.91 | 45.13 | 44.99
| 1 | 5.27 | 14 | 0 | 55.5 | 640 | 188 | 5.21 | 2550 | 79 | 1218 | 1 |  | 0 | 0 | 3 | 22.68 | 30.12 | 25.93 |  |  | 37.66 | 45.09 | 40.92
| 2 | 5.91 | 13 | 4 | 54.9 | 640 | 188 | 5.72 | 2640 | 79 | 1261 | 1 |  | SINGLE DAY OVER 60 | SINGLE DAY OVER 60 | 4 | 22.51 | 30.12 | 27.56 |  |  | 37.63 | 44.64 | 42.28
| 3 | 5.9 | 8 | 0 |  | 700 | 192 | 6.25 | 2760 | 80 | 1377 | 1 |  | 0 | 0 | 5 | 30.02 | 30.31 | 30.19 |  |  | 44.64 | 44.83 | 44.83
| 4 | 4.4 | 10 | 0 |  | 730 | 190 | 5.95 | 2950 | 80 | 1462 | 1 |  | 0 | 0 | 6 | 30.17 | 30.38 | 30.29 |  |  | 44.81 | 44.92 | 44.93
| 5 | 4.6 | 13 | 3 | 63.3 | 760 | 196 | 7.89 | 2850 | 80 | 1548 | 1 |  |  |  | 7 | 30.22 | 30.38 | 30.33 |  |  | 44.88 | 44.94 | 44.97
| 6 | 6.4 | 13 | 2 | 59 | 730 | 196 | 6.43 | 2880 | 80 | 1363 | 1 |  |  |  | 8 | 30.21 | 30.39 | 30.33 |  |  | 44.86 | 44.95 | 44.95
| 7 | 5.36 | 10 | 0 | 62.1 | 680 | 186 | 6.85 | 2750 | 80 | 1582 | 1 | 5.4057 | 5.4057 | 11.5714 | 9 | 30.32 | 30.5 | 30.45 |  |  | 44.95 | 45.04 | 45
| 8 | 4.9 | 7 | 1 | 58.9 | 650 | 190 | 6.72 | 2700 | 80 | 1358 | 1 |  | 5.3529 | 10.5714 | 10 | 17.36 | 30.52 | 23.32 |  |  | 36.75 | 45.09 | 40.65
| 9 | 6.25 | 10 | 3 | 73.8 | 680 | 190 | 8.07 | 2730 | 80 | 1296 | 1 |  | 5.4014 | 10.1429 | 11 | 17.27 | 29.68 | 24.94 |  |  | 28.13 | 44.5 | 41.48
| 10 | 4.3 | 17 | 6 |  | 750 | 194 | 7.04 | 2760 | 80 | 1356 | 1 |  | 5.1729 | 11.4286 | 12 | ER | 29.96 | 29.72 |  |  | ER | 44.74 | 44.27
| 11 | 4.74 | 17 | 3 |  | 640 | 196 | 6.68 | 2630 | 80 | 1255 | 1 |  | 5.2214 | 12.4286 | 13 | ER | 30.09 | 28.81 |  |  | ER | 44.83 | 42.72
| 12 | 6 | 12 | 0 | 91 | 630 | 186 | 5.73 | 2520 | 80 | 1195 | 1 |  | 5.4214 | 12.2857 | 14 | 29.9 | 30.22 | 30.07 |  |  | 44.72 | 44.98 | 44.89
| 13 | 3.67 | 18 | 4 | 60.8 | 630 | 192 | 5.77 | 2440 | 80 | 1267 | 1 |  | 5.0314 | 13 | 15 | 30.02 | 30.34 | 30.22 |  |  | 44.85 | 45.1 | 44.99
| 14 | 3.39 | 7 | 1 | 68.2 | 600 | 188 | 6.26 | 2390 | 80 | 1267 | 1 | 4.75 | 4.75 | 12.5714 | 16 | 23.16 | 30.47 | 30.23 |  |  | 32.14 | 45.21 | 44.84
| 15 | 4.57 | 11 | 1 | 59.3 | 610 | 192 | 6.82 | 2540 | 81 | 1276 | 1 |  | 4.7029 | 13.1429 | 17 | ER | 30.57 | 21.39 |  |  | ER | 45.33 | 31.58
| 16 | 5.88 | 14 | 2 | 56.9 | LS | 194 | 7.23 | 2580 | 80 | 1231 | 1 |  | 4.65 | 13.7143 | 18 | ER | ER | ER |  |  | ER | ER | ER
| 17 | 6.46 | 23 | 8 |  | 670 | 186 | 10.5 | 2600 | 80 | 1276 | 1 |  | 4.9586 | 14.5714 | 19 | ER | ER | ER |  |  | ER | ER | ER
| 18 | 6.47 | 14 | 0 |  | 680 | 176 | 9.78 | 2620 | 80 | 1235 | 1 |  | 5.2057 | 14.1429 | 20 | ER | 30.4 | 16.51 |  |  | ER | 45.09 | 19.98
| 19 | 4.55 | 15 | 0 | 59.7 | 660 | 184 | 7.46 | 2600 | 80 | 1315 | 1 |  | 4.9986 | 14.5714 | 21 | 23.88 | 30.4 | 30.22 |  |  | 33.43 | 45.1 | 44.91
| 20 | 6.28 | 27 | 2 | 62.1 | 660 | 186 | 8.45 | 2540 | 81 | 1345 | 1 |  | 5.3714 | 15.8571 | 22 | 30.15 | 30.39 | 30.26 |  |  | 45.01 | 45.14 | 45.02
| 21 | 8.58 | 16 | 1 | 91.6 | 680 | 206 | 9.46 | 2580 | 81 | 1240 | 1 | 6.1129 | 6.1129 | 17.1429 | 23 | 30.2 | 30.42 | 30.34 |  |  | 45.08 | 45.21 | 45.06
| 22 | 6.59 | 20 | 2 | 69.3 | 690 | 196 | 8.36 | 2390 | 81 | 1240 | 1 |  | 6.4014 | 18.4286 | 24 | 17.97 | 30.51 | 23.5 |  |  | 39.79 | 45.29 | 42.34
| 23 | 8.06 | 23 | 1 | 66.7 | 650 | 194 | 10.7 | 2340 | 81 | 1157 | 1 |  | 6.7129 | 19.7143 | 25 | 17.91 | 29.94 | 25.97 |  |  | 39.81 | 44.73 | 43.01
| 24 | 7.27 | 18 | 2 |  | 700 | 190 | 11.3 | 2560 | 80 | 1259 | 1 |  | 6.8286 | 19 | 26 | 29.92 | 30.31 | 30.11 |  |  | 44.73 | 45.02 | 44.89
| 25 | 6.8 | 18 | 1 |  | 630 | 184 | 10.4 | 2460 | 80 | 1234 | 1 |  | 6.8757 | 19.5714 | 27 | 30.19 | 30.54 | 30.39 |  |  | 44.95 | 45.22 | 45.02
| 26 | 6 | 20 | 0 | 59.5 | 640 | 186 | 8.66 | 2600 | 80 | 1346 | 1 |  | 7.0829 | 20.2857 | 28 | 30.35 | 30.59 | 30.48 |  |  | 45.11 | 45.28 | 45.18
| 27 | 6 | 14 | 0 | 65.2 | 660 | 184 | 8.76 | 2590 | 80 | 1378 | 1 |  | 7.0429 | 18.4286 | 29 | 30.37 | 30.58 | 30.48 |  |  | 45.11 | 45.27 | 45.18
| 28 | 5 | 13 | 1 | 52.6 | 680 | 182 | 7.28 | 2600 | 80 | 1285 | 1 |  | 6.5314 | 18 | 30 | 30.29 | 30.58 | 30.49 |  |  | 45.07 | 45.33 | 45.28
| 29 | 6 | 12 | 1 | 63.6 | 700 | 180 | 7.67 | 2600 | 81 | 1239 | 1 |  | 6.4471 | 16.8571 | 31 | 19.62 | 30.29 | 24.39 |  |  | 36.78 | 45.1 | 41.47
| 30 | 4 | 9 | 1 | 50.7 | 660 | 192 | 7.03 | 2530 | 80 | 1198 | 1 |  | 5.8671 | 14.8571 | TOTAL | 664.31 | 879.25 | 816.87 |  |  | 1040.57 | 1306.1 | 1240.58
| 31 | 5 | 14 | 2 |  | 700 | 190 | 7.72 | 2630 | 79 | 1284 | 1 | 6.072 | 5.5429 | 14.2857 | AVERAGE | 26.5724 | 30.319 | 28.1679 |  |  | 41.6228 | 45.0379 | 42.7786
| TOTAL | 174.6 | 450 | 52 | 1404.7 | 20130 | 5874 | 238.15 | 80910 | 2483 | 40343 |  |  |  |  | MAXIMUM | 30.37 | 30.59 | 30.49 |  |  | 45.11 | 45.33 | 45.28
| AVERAGE | 5.6323 | 14.5161 | 2.3636 | 63.85 | 671 | 189.4839 | 7.6823 | 2610 | 80.0968 | 1301.3871 |  |  | 5.7236 | 15.0629 | MINIMUM | 17.27 | 29.68 | 16.51 |  |  | 28.13 | 44.5 | 19.98
| MAXIMUM | 8.58 | 27
[5 empty] | PAGE 4 | [14 empty] | PAGE 22
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
[5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [13 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
[5 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [13 empty] | MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
[5 empty] | MONTHLY OPERATIONAL REPORT | [13 empty] | REGIONAL MONITORING WELL ONE
[5 empty] | EFFLUENT DATA PART 2 | [13 empty] | RMW-1
[16 empty] | RUN DATE |  |  | UC06-249353
[16 empty] | 2026-07-30 |  | UPPER MONITOR ZONE |  |  |  |  | LOWER MONITOR ZONE
RUN DATE | [16 empty] | MIN | MAX | AVG |  |  | MIN | MAX | AVG
2026-07-30 | [15 empty] | MARCH | FT HEAD | FT HEAD | FT HEAD |  |  | FT HEAD | FT HEAD | FT HEAD
[16 empty] | 2003 | ABOVE | ABOVE | ABOVE |  |  | ABOVE | ABOVE | ABOVE
| MARCH | EFF. BACT. | EFF. BACT. | FREE | TOTAL | EFFL. | EFF PH | EFF PH | EFF. SAP | AVG. | [6 empty] | NGVD | NGVD | NGVD |  |  | NGVD | NGVD | NGVD
| 2003 | TOTAL | FECAL | CL2 | CL2 | pH | MIN | MAX | TEMP.(C) | BLK. | [5 empty] | 1 | 42.35 | 42.51 | 42.44 |  |  | 21.54 | 21.68 | 21.61
[16 empty] | 2 | 42.44 | 42.59 | 42.51 |  |  | 21.61 | 21.76 | 21.69
| 1 | 0 | 0 | 0 | 1.1 | 6.4 | 6.4 | 6.4 | 2 | 49 | [5 empty] | 3 | 32.05 | 42.57 | 36.72 |  |  | 19.83 | 21.77 | 20.83
| 2 | 143 | 0 | 0 | 1 | 6.4 | 6.3 | 6.3 | 5 | 41 | [5 empty] | 4 | ER | 67.07 | ER |  |  | 19.58 | 21 | 20.59
| 3 | 280 | 0 | 0 | 0.8 | 6.4 | 6.4 | 6.5 | 3 | 43 | [5 empty] | 5 | ER | 67.59 | ER |  |  | 20.99 | 21.21 | 21.09
| 4 | 13600 | 0 | 0 | 0.9 | 6.5 | 6.4 | 6.6 | 0 | 44 | [5 empty] | 6 | ER | 67.94 | ER |  |  | 21.19 | 21.3 | 21.25
| 5 | 4500 | 9 | 0 | 0.9 | 6.4 | 6.3 | 6.4 | 0.5 | 34 | [5 empty] | 7 | ER | 68.02 | ER |  |  | 21.25 | 21.32 | 21.28
| 6 | 12000 | 0 | 0 | 0.9 | 6.4 | 6.3 | 6.5 | 5 | 33 | [5 empty] | 8 | ER | 67.78 | ER |  |  | 21.21 | 21.32 | 21.29
| 7 | 220 | 0 | 0 | 1.1 | 6.3 | 6.3 | 6.4 | 2 | 34 | [5 empty] | 9 | ER | 67.05 | ER |  |  | 21.32 | 21.43 | 21.38
| 8 | 71 | 9 | 0 | 1.1 | 6.3 | 6.3 | 6.4 | 2 | 48 | [5 empty] | 10 | ER | 31.03 | ER |  |  | 21.39 | 21.5 | 21.43
| 9 | 125 | 0 | 0 | 1.1 | 6.4 | 6.3 | 6.4 | 0 | 46 | [5 empty] | 11 | ER | 67.93 | ER |  |  | 21.36 | 21.48 | 21.42
| 10 | 54 | 9 | 0 | 1 | 6.4 | 6.3 | 6.4 | 0 | 58 | [5 empty] | 12 | ER | 67.94 | ER |  |  | 21.31 | 21.47 | 21.4
| 11 | 2100 | 0 | 0 | 0.9 | 6.4 | 6.4 | 6.4 | 4 | 58 | [5 empty] | 13 | ER | 67.97 | ER |  |  | 21.32 | 21.46 | 21.39
| 12 | 3000 | 0 | 0 | 1 | 6.4 | 6.4 | 6.4 | 5 | 40 | [5 empty] | 14 | ER | 66.48 | ER |  |  | 21.36 | 21.51 | 21.45
| 13 | 63 | 18 | 0 | 0.9 | 6.3 | 6.2 | 6.5 | 5 | 36 | [5 empty] | 15 | 8.95 | 56.41 | 14.02 |  |  | 21.43 | 21.59 | 21.53
| 14 | 48 | 0 | 0 | 1 | 6.3 | 6.2 | 6.4 | 3 | 38 | [5 empty] | 16 | 8.97 | 32.01 | 12.71 |  |  | 21.51 | 21.67 | 21.6
| 15 | 54 | 0 | 0 | 1 | 6.4 | 6.3 | 6.4 | 2 | 57 | [5 empty] | 17 | ER | 67.82 | ER |  |  | 21.64 | 21.85 | 21.76
| 16 | 610 | 0 | 0 | 0.8 | 6.3 | 6.2 | 6.4 | 5 | 51 | [5 empty] | 18 | ER | 67.84 | ER |  |  | 21.77 | 21.84 | 21.8
| 17 | 25000 | 260 | 0 | 0.9 | 6.4 | 6.3 | 6.5 | 5 | 71 | [5 empty] | 19 | ER | 67.55 | ER |  |  | 21.72 | 21.81 | 21.76
| 18 | 1259 | 9 | 0 | 0.8 | 6.4 | 6.3 | 6.5 | 5 | 59 | [5 empty] | 20 | ER | 67.68 | ER |  |  | 21.67 | 21.76 | 21.7
| 19 | 2250 | 0 | 0 | 0.9 | 6.5 | 6.4 | 6.6 | 5 | 44 | [5 empty] | 21 | ER | 67.05 | ER |  |  | 21.61 | 21.75 | 21.66
| 20 | 188 | 0 | 0 | 0.8 | 6.5 | 6.4 | 6.6 | 5 | 63 | [5 empty] | 22 | ER | 67 | ER |  |  | 21.56 | 21.7 | 21.62
| 21 | 125 | 0 | 0 | 0.8 | 6.4 | 6.3 | 6.5 | 4 | 63 | [5 empty] | 23 | 8.98 | 33.03 | 11.04 |  |  | 21.59 | 21.69 | 21.65
| 22 | 98 | 0 | 0 | 0.8 | 6.4 | 6.3 | 6.5 | 3 | 89 | [5 empty] | 24 | 8.97 | 33.76 | 12.35 |  |  | 21.59 | 21.78 | 21.69
| 23 | 0 | 0 | 0 | 0.9 | 6.4 | 6.3 | 6.4 | 0.5 | 69 | [5 empty] | 25 | ER | 68 | ER |  |  | 21.58 | 21.71 | 21.64
| 24 | 730 | 0 | 0 | 0.9 | 6.4 | 6.3 | 6.5 | 5 | 71 | [5 empty] | 26 | 8.99 | 60.17 | 16.17 |  |  | 21.6 | 21.73 | 21.68
| 25 | 3600 | 0 | 0 | 0.9 | 6.4 | 6.4 | 6.4 | 5 | 67 | [5 empty] | 27 | 8.97 | 19.02 | 10.84 |  |  | 21.67 | 21.86 | 21.78
| 26 | 230 | 0 | 0 | 1 | 6.4 | 6.4 | 6.4 | 5 | 59 | [5 empty] | 28 | 8.97 | 48.73 | 15.69 |  |  | 21.73 | 21.87 | 21.8
| 27 | TNTC | 26000 | 0 | 0.8 | 6.3 | 6.3 | 6.4 | 5 | 52 | [5 empty] | 29 | ER | 66.63 | ER |  |  | 21.7 | 21.79 | 21.75
| 28 | 2250 | TNTC | 0 | 0.9 | 6.3 | 6.2 | 6.4 | 0 | 64 | [5 empty] | 30 | ER | 68.02 | ER |  |  | 21.63 | 21.83 | 21.76
| 29 | 634 | 0 | 0 | 1.2 | 6.4 | 6.3 | 6.4 | 1 | 63 | [5 empty] | 31 | 8.92 | 24.76 | 10.56 |  |  | 19.72 | 21.63 | 20.74
| 30 | 45 | 0 | 0 | 1.1 | 6.4 | 6.3 | 6.4 | 5 | 59 | [5 empty] | TOTAL | 188.56 | 1749.95 | 225.05 |  |  | 660.98 | 670.07 | 666.02
| 31 | 3400 | 0 | 0 | 1 | 6.4 | 6.3 | 6.4 | 5 | 56 | [5 empty] | AVERAGE | 17.1418 | 56.45 | 20.4591 |  |  | 21.3219 | 21.6152 | 21.4845
| TOTAL | 76677 | 26314 | 0 | 29.2 | 198 | 195.8 | 199.7 | 102 | 1659 | [5 empty] | MAXIMUM | 42.44 | 68.02 | 42.51 |  |  | 21.77 | 21.87 | 21.8
| AVERAGE | 2555.9 | 877.1333 | 0 | 0.94194 | 6.3871 | 6.3161 | 6.4419 | 3.2903 | 53.5161 | [5 empty] | MINIMUM | 8.92 | 19.02 | 10.56 |  |  | 19.58 | 21 | 20.59
[7 empty] | 6.2 | 6.6
[7 empty] | MIN | MAX
PAGE 5
PAGE 23
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
NUTRIENTS
RUN DATE
| 2026-07-30 |  | INFLUENT | [5 empty] | EFFLUENT
| MARCH | INFLUENT | INFLUENT | INFLUENT | INFLUENT |  | EFFL. | EFFL. | EFFL. | EFFL.
| 2003 | NH-3 | N03-N | TKN | TOT P |  | NH-3 | N03-N | TKN | TOT P
| 1 | 17.78 |  | 23.84 | 3.79 |  | 13.68 | 0.537 | 18.19 | 1.33
| 2 | 18.49 | 0.24 | 24.58 | 4 |  | 14.11 | 0.528 | 17.79 | 0.991
3
4
| 5 | 18.14 | 0.052 | 26.11 | 3.08 |  | 14.77 | 0.489 | 20.73 | 1.12
| 6 | 17.99 | 0.11 | 26.11 | 3.52 |  | 15.11 | 0.404 | 21.96 | 1.03
| 7 | 18.4 | 0.02 | 24.2 | 3.08 |  | 14.26 | 0.701 | 21.54 | 1
| 8 | 19.49 | 0.241 | 26.37 | 3.33 |  | 13.67 | 0.681 | 21.02 | 1.21
| 9 | 19.56 | 0.02 | 23.77 | 3.07 |  | 13.34 | 0.575 | 18.79 | 1.29
10
11
| 12 | 17.79 | 0.16 | 25.73 | 3.13 |  | 14.09 | 0.281 | 20.45 | 1.46
| 13 | 18.03 | 0.34 | 28.31 | 3.56 |  | 14.12 | 0.355 | 21.5 | 1.06
| 14 | 19.01 | 0.02 | 27.71 | 3.32 |  | 14.49 | 0.334 | 22.9 | 1.46
| 15 | 17.8 | 0.552 | 27.72 | 3.58 |  | 13.81 | 0.352 | 21.84 | 1.72
| 16 | 17.31 | 0.427 | 26.32 | 3.57 |  | 13.09 | 0.388 | 19.67 | 1.27
17
18
| 19 | 16.57 | 0.176 | 22.92 | 3.21 |  | 13.54 | 0.111 | 18.32 | 1.33
| 20 | 16.64 | 0.254 | 24.07 | 3.27 |  | 15.19 | 0.118 | 21.73 | 1.65
| 21 | 17.5 | 0.02 | 23.13 | 3.35 |  | 16.31 | 0.2 | 22.41 | 1.6
| 22 | 17.82 | 0.02 | 28.14 | 4.11 |  | 14.35 | 0.221 | 19.96 | 1.72
| 23 | 16.2 | 0.02 | 23.69 | 3.56 |  | 13.51 | 0.255 | 0 | 1.53
24
25
| 26 | 17.75 | 0.374 | 26.55 | 3.94 |  | 13.93 | 0.399 | 18.9 | 1.52
| 27 | 16.7 | 0.577 | 25.76 | 3.37 |  | 13.9 | 0.475 | 20.93 | 1.93
| 28 | 15.52 | 0.055 | 24.17 | 4.38 |  | 12.71 | 0.522 | 19.28 | 1.94
| 29 | 15.42 | 0.035 | 23.65 | 4.73 |  | 12.67 | 0.469 | 19.33 | 2.03
| 30 | 16.96 | 0.011 | 24.65 | 3.56 |  | 12.26 | 0.391 | 18.02 | 1.14
31
| TOTAL | 386.87 | 3.724 | 557.5 | 78.51 | TOT. | 306.91 | 8.786 | 425.26 | 31.331
| AVERAGE | 17.585 | 0.17733 | 25.3409 | 3.5686 | AVG. | 13.9505 | 0.39936 | 19.33 | 1.4241
PAGE 6
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
REACTOR ONE PROCESS
RUN DATE
| 2026-07-30 |  | TRAIN "A" | [5 empty] | TRAIN "B"
| MARCH | MLSS | MLVSS | SS | SVI |  | MLSS | MLVSS | SS | SVI
| 2003 | "A" | "A" | "A" | "A" |  | "B" | "B" | "B" | "B"
| 1 | O/S | O/S | O/S |  |  | 3790 | 3200 | 28 | 73.8786
| 2 | O/S | O/S | O/S |  |  | 2940 | 2480 | 30 | 102.0408
| 3 | O/S | O/S | O/S |  |  | 3300 | 2790 | 30 | 90.9091
| 4 | O/S | O/S | O/S |  |  | 3510 | 2920 | 35 | 99.7151
| 5 | O/S | O/S | O/S |  |  | 3520 | 2790 | 30 | 85.2273
| 6 | O/S | O/S | O/S |  |  | 3730 | 3030 | 28 | 75.067
| 7 | O/S | O/S | O/S |  |  | 3900 | 3270 | 29 | 74.359
| 8 | O/S | O/S | O/S |  |  | 4200 | 3410 | 28 | 66.6667
| 9 | O/S | O/S | O/S |  |  | 3350 | 2550 | 38 | 113.4328
| 10 | O/S | O/S | O/S |  |  | 3500 | 2880 | 26 | 74.2857
| 11 | O/S | O/S | O/S |  |  | 3240 | 2740 | 30 | 92.5926
| 12 | O/S | O/S | O/S |  |  | 3660 | 3200 | 33 | 90.1639
| 13 | O/S | O/S | O/S |  |  | 3740 | 3230 | 24 | 64.1711
| 14 | O/S | O/S | O/S |  |  | 4690 | 3910 | 32 | 68.2303
| 15 | O/S | O/S | O/S |  |  | 3870 | 3200 | 27 | 69.7674
| 16 | O/S | O/S | O/S |  |  | 3730 | 3070 | 28 | 75.067
| 17 | O/S | O/S | O/S |  |  | 3340 | 2740 | 34 | 101.7964
| 18 | O/S | O/S | O/S |  |  | 3500 | 2980 | 28 | 80
| 19 | O/S | O/S | O/S |  |  | 2970 | 2550 | 31 | 104.3771
| 20 | O/S | O/S | O/S |  |  | 3690 | 3120 | 31 | 84.0108
| 21 | O/S | O/S | O/S |  |  | 3460 | 2960 | 32 | 92.4855
| 22 | O/S | O/S | O/S |  |  | 3540 | 3000 | 31 | 87.5706
| 23 | O/S | O/S | O/S |  |  | NS | NS | 38
| 24 | O/S | O/S | O/S |  |  | 3680 | 3060 | 32 | 86.9565
| 25 | O/S | O/S | O/S |  |  | 3720 | 3100 | 36 | 96.7742
| 26 | O/S | O/S | O/S |  |  | 3460 | 2950 | 36 | 104.0462
| 27 | O/S | O/S | O/S |  |  | 3760 | 3200 | 34 | 90.4255
| 28 | O/S | O/S | O/S |  |  | 3690 | 3150 | 34 | 92.1409
| 29 | O/S | O/S | O/S |  |  | 3110 | 2640 | 29 | 93.2476
| 30 | O/S | O/S | O/S |  |  | 3470 | 2920 | 31 | 89.3372
| 31 | O/S | O/S | O/S |  |  | 3380 | 2440 | 35 | 103.5503
| TOTAL | 0 | 0 | 0 |  |  | 107440 | 89480 | 968
| AVERAGE | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 3581.3333 | 2982.6667 | 31.2258 | 87.1904
PAGE 7
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
REACTOR TWO PROCESS
RUN DATE
| 2026-07-30 |  | TRAIN "C" | [5 empty] | TRAIN "D"
| MARCH | MLSS | MLVSS | SS | SVI |  | MLSS | MLVSS | SS | SVI
| 2003 | "C" | "C" | "C" | "C" |  | "D" | "D" | "D" | "D"
| 1 | O/S | O/S | O/S |  |  | 3760 | 3190 | 27 | 71.8085
| 2 | O/S | O/S | O/S |  |  | 2860 | 2410 | 30 | 104.8951
| 3 | O/S | O/S | O/S |  |  | 3350 | 2780 | 34 | 101.4925
| 4 | O/S | O/S | O/S |  |  | 3030 | 2530 | 25 | 82.5083
| 5 | O/S | O/S | O/S |  |  | 3580 | 2830 | 31 | 86.5922
| 6 | O/S | O/S | O/S |  |  | 3650 | 2970 | 28 | 76.7123
| 7 | O/S | O/S | O/S |  |  | 3730 | 3150 | 29 | 77.748
| 8 | O/S | O/S | O/S |  |  | 4420 | 3520 | 28 | 63.3484
| 9 | O/S | O/S | O/S |  |  | 3400 | 2680 | 38 | 111.7647
| 10 | O/S | O/S | O/S |  |  | 3220 | 2680 | 25 | 77.6398
| 11 | O/S | O/S | O/S |  |  | 2920 | 2460 | 28 | 95.8904
| 12 | O/S | O/S | O/S |  |  | 3100 | 2700 | 29 | 93.5484
| 13 | O/S | O/S | O/S |  |  | 3310 | 2850 | 24 | 72.5076
| 14 | O/S | O/S | O/S |  |  | 4500 | 3770 | 31 | 68.8889
| 15 | O/S | O/S | O/S |  |  | 3540 | 2940 | 27 | 76.2712
| 16 | O/S | O/S | O/S |  |  | 3430 | 2830 | 28 | 81.6327
| 17 | O/S | O/S | O/S |  |  | 3330 | 2750 | 34 | 102.1021
| 18 | O/S | O/S | O/S |  |  | 3220 | 2730 | 28 | 86.9565
| 19 | O/S | O/S | O/S |  |  | 2880 | 2460 | 30 | 104.1667
| 20 | O/S | O/S | O/S |  |  | 3610 | 3050 | 31 | 85.8726
| 21 | O/S | O/S | O/S |  |  | 4020 | 3430 | 32 | 79.602
| 22 | O/S | O/S | O/S |  |  | 3880 | 3310 | 30 | 77.3196
| 23 | O/S | O/S | O/S |  |  | NS | NS | 35
| 24 | O/S | O/S | O/S |  |  | 3290 | 2750 | 30 | 91.1854
| 25 | O/S | O/S | O/S |  |  | 3810 | 3120 | 36 | 94.4882
| 26 | O/S | O/S | O/S |  |  | 3480 | 2940 | 36 | 103.4483
| 27 | O/S | O/S | O/S |  |  | 3790 | 3260 | 34 | 89.7098
| 28 | O/S | O/S | O/S |  |  | 3700 | 3160 | 34 | 91.8919
| 29 | O/S | O/S | O/S |  |  | 3080 | 2640 | 28 | 90.9091
| 30 | O/S | O/S | O/S |  |  | 2980 | 2570 | 31 | 104.0268
| 31 | O/S | O/S | O/S |  |  | 3380 | 2800 | 33 | 97.6331
| TOTAL | 0 | 0 | 0 |  |  | 104250 | 87260 | 944
| AVERAGE | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 3475 | 2908.6667 | 30.4516 | 87.6305
PAGE 8
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
RAS SUMMARY
RUN DATE
2026-07-30
| MARCH | R-1 | R-2 | TOTAL | F/M | TOTAL | SLUDGE | % TOT | % FIX | % VOL.
| 2003 | TOT. RAS | TOT. RAS | MLVSS | RATIO | MLSS | AGE | RAS | RAS | RAS
|  | MGD | MGD
| 1 | 6.532 | 6.024 | 6390 | 0.61494 | 7550 | 2.181 | 0.46 | 23.4 | 76.6
| 2 | 6.562 | 5.929 | 4890 | 0.85542 | 5800 | 1.5066 | 1.2 | 22.2 | 77.8
| 3 | 6.468 | 5.872 | 5570 | 0.79292 | 6650 | 1.7197 | 1.22 | 21.8 | 78.2
| 4 | 6.476 | 6.232 | 5450 | 0.72815 | 6540 | 1.3603 | 1.22 | 23.2 | 76.8
| 5 | 6.483 | 6.666 | 5620 | 0.71829 | 7100 | 1.4936 | 1.15 | 22.5 | 77.5
| 6 | 6.46 | 6.772 | 6000 | 0.58991 | 7380 | 3.6587 | 1.05 | 25 | 75
| 7 | 6.433 | 6.785 | 6420 | 0.64542 | 7630 | 2.05 | 1.15 | 23.5 | 76.5
| 8 | 6.432 | 5.97 | 6930 | 0.62083 | 8620 | 2.0758 | 1.24 | 19.4 | 80.6
| 9 | 6.464 | 6.17 | 5230 | 0.75419 | 6750 | 1.549 | 1.25 | 22 | 78
| 10 | 6.389 | 6.748 | 5560 | 0.69837 | 6720 | 1.4537 | 1.25 | 21.6 | 78.4
| 11 | 6.456 | 6.685 | 5200 | 0.79132 | 6160 | 0.94293 | 1.19 | 21.2 | 78.8
| 12 | 6.492 | 6.442 | 5900 | 0.66976 | 6760 | 1.4541 | 0.88 | 23.1 | 76.9
| 13 | 6.6 | 6.047 | 6080 | 0.56043 | 7050 | 1.5569 | 0.95 | 22.6 | 77.4
| 14 | 6.686 | 6.848 | 7680 | 0.49835 | 9190 | 2.1443 | 1.3 | 20.8 | 79.2
| 15 | 6.447 | 6.133 | 6140 | 0.64878 | 7410 | 1.8974 | 1.2 | 21.7 | 78.3
| 16 | 6.507 | 6.285 | 5900 | 0.6841 | 7160 | 3.3301 | 1.16 | 20 | 80
| 17 | 6.68 | 6.936 | 5490 | 0.65797 | 6670 | 1.6791 | 1.09 | 19.9 | 80.1
| 18 | 6.491 | 7.415 | 5710 | 0.64251 | 6720 | 1.6149 | 1.13 | 22.1 | 77.9
| 19 | 6.432 | 6.808 | 5010 | 0.78971 | 5850 | 1.3208 | 1.13 | 21.1 | 78.9
| 20 | 6.528 | 7.071 | 6170 | 0.70558 | 7300 | 1.3415 | 0.28 | 20.3 | 79.7
| 21 | 6.468 | 6.991 | 6390 | 0.71612 | 7480 | 1.7745 | 1.31 | 20.6 | 79.4
| 22 | 6.431 | 5.933 | 6310 | 0.7116 | 7420 | 0.76824 | 1.15 | 20.7 | 79.3
| 23 | 6.373 | 6.138 |  |  |  |  | 0.91 | 24.2 | 75.8
| 24 | 6.425 | 6.621 | 5810 | 0.68149 | 6970 | 2.9001 | 0.95 | 22.2 | 77.8
| 25 | 6.481 | 7.278 | 6220 | 0.57481 | 7530 | 3.4846 | 1.06 | 21.9 | 78.1
| 26 | 6.475 | 7.201 | 5890 | 0.78109 | 6940 | 1.1711 | 1.07 | 23 | 77
| 27 | 6.597 | 7.395 | 6460 | 0.60644 | 7550 | 2.0092 | 1.01 | 20.2 | 79.8
| 28 | 6.502 | 7.284 | 6310 | 0.63192 | 7390 | 1.9769 | 1.04 | 20 | 80
| 29 | 6.544 | 6.333 | 5280 | 0.56887 | 6190 | 2.1181 | 0.99 | 21.1 | 78.9
| 30 | 6.539 | 6.142 | 5490 | 0.68032 | 6450 | 4.1446 | 1.07 | 21.9 | 78.1
| 31 | 6.489 | 6.424 | 5240 | 0.73754 | 6760 | 2.099 | 0.4 | 20.5 | 79.5
| TOTAL | 201.342 | 203.578 | 176740 |  | 211690 |  | 32.46 | 673.7 | 2426.3
| AVERAGE | 6.4949 | 6.567 | 5891.3333 | 0.67467 | 7056.3333 | 1.7247 | 1.0471 | 21.7323 | 78.2677
PAGE 9
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
DEWATERING DATA
RUN DATE
| 2026-07-30 |  | FEED SLUDGE |  |  |  |  | FILTRATE RETURN
| MARCH | % TOT. | % FIX. | % VOL. | pH |  | % TOT. | % FIX. | % VOL. | pH
| 2003 | FEED | FEED | FEED |  |  | FILT. | FILT. | FILT.
1
2
| 3 | 1.64 | 20.7 | 79.3 | 6.73 |  | 0.22 | 63.6 | 36.4 | 7.25
| 4 | 1 | 23 | 77 | 6.83 |  | 0.21 | 71.4 | 28.6 | 7.28
| 5 | 1.1 | 28.2 | 71.8 | 6.93 |  | 0.22 | 63.6 | 36.4 | 7.19
| 6 | 1.52 | 22.4 | 77.6 | 6.88 |  | 0.21 | 71.4 | 28.6 | 7.22
7
8
| 9 | 1.75 | 20.6 | 79.4 | 6.82 |  | 0.23 | 60.9 | 39.1 | 7.24
| 10 | 1.4 | 22.1 | 77.9 | 6.68 |  | 0.21 | 66.7 | 33.3 | 7.16
| 11 | 1.45 | 21.4 | 78.6 | 6.74 |  | 0.21 | 71.4 | 28.6 | 7.19
| 12 | 1.07 | 23.4 | 76.6 | 6.73 |  | 0.21 | 66.7 | 33.3 | 7.09
| 13 | 1.54 | 21.4 | 78.6 | 6.74 |  | 0.23 | 60.9 | 39.1 | 7.24
14
15
16
17
18
19
| 20 | 1.43 | 23.8 | 76.2 | 6.8 |  | 0.26 | 57.7 | 42.3 | 7.2
21
22
| 23 | 1.36 | 21.3 | 78.7 | 6.47 |  | 0.24 | 54.2 | 45.8 | 7.02
| 24 | 1.43 | 21.7 | 78.3 | 6.8 |  | 0.19 | 68.4 | 31.6 | 7.24
| 25 | 1.07 | 23.4 | 76.6 | 6.79 |  | 0.2 | 60 | 40 | 7.25
| 26 | 1.33 | 21.8 | 78.2 | 6.89 |  | 0.2 | 65 | 35 | 7.11
| 27 | 1.08 | 24.1 | 75.9 | 6.92 |  | 0.23 | 60.9 | 39.1 | 7.2
28
29
| 30 | 1.2 | 23.3 | 76.7 | 6.74 |  | 0.2 | 65 | 35 | 7.22
| 31 | 1.51 | 20.5 | 79.5 | 7.02 |  | 0.17 | 76.5 | 23.5 | 7.45
| TOTAL | 22.88 | 383.1 | 1316.9 | 115.51 |  | 3.64 | 1104.3 | 595.7 | 122.55
| AVERAGE | 1.3459 | 22.5353 | 77.4647 | 6.7947 |  | 0.21412 | 64.9588 | 35.0412 | 7.2088
PAGE 10
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
SLUDGE VOLUME REMOVED
RUN DATE
2026-07-30
|  | MARCH | TRAILERS | TONS | DRY TONS | % LIME | % TOT. | % FIX. | % VOL.
|  | 2003 | REMOVED | SLUDGE | REMOVED | CAKE | CAKE | CAKE | CAKE
|  | 1 | 0 | 0
|  | 2 | 1 | 25
|  | 3 | 6 | 150 | 38.2058 |  | 17.22 | 27.4 | 72.6
|  | 4 | 5 | 125 | 23.0708 |  | 18.01 | 15.5 | 84.5
|  | 5 | 6 | 150 | 25.8823 |  | 18.42 | 16.7 | 83.3
|  | 6 | 8 | 200 | 34.7054 |  | 17.88 | 14.6 | 85.4
|  | 7 | 3 | 75
|  | 8 | 0 | 0
|  | 9 | 1 | 25 | 10.8005 |  | 17.86 | 13.8 | 86.2
|  | 10 | 6 | 150 | 30.3922 |  | 17.64 | 18.4 | 81.6
|  | 11 | 6 | 150 | 31.4418 |  | 17.89 | 19.6 | 80.4
|  | 12 | 6 | 150 | 22.6218 |  | 17.2 | 13.6 | 86.4
|  | 13 | 6 | 150 | 36.6043 |  | 17.42 | 14.4 | 85.6
|  | 14 | 4 | 100
|  | 15 | 0 | 0
|  | 16 | 0 | 0
|  | 17 | 0 | 0
|  | 18 | 0 | 0
|  | 19 | 2 | 50
|  | 20 | 7 | 175 | 37.5675 |  | 17.13 | 17.1 | 82.9
|  | 21 | 5 | 125
|  | 22 | 0 | 0
|  | 23 | 2 | 50 | 12.8573 |  | 17.15 | 15.9 | 84.1
|  | 24 | 7 | 175 | 39.5354 |  | 17.64 | 14.3 | 85.7
|  | 25 | 6 | 150 | 25.9683 |  | 17.1 | 28.8 | 71.2
|  | 26 | 7 | 175 | 32.9993 |  | 17.4 | 19.2 | 80.8
|  | 27 | 6 | 150 | 26.9766 |  | 16.61 | 13.8 | 86.2
|  | 28 | 5 | 125
|  | 29 | 0 | 0
|  | 30 | 2 | 50 | 16.3618 |  | 16.74 | 13.9 | 86.1
|  | 31 | 6 | 150 | 32.428 |  | 17.34 | 13.7 | 86.3
|  | TOTAL | 113 | 2825 | 478.419 | 0 | 296.65 | 290.7 | 1409.3
|  | AVERAGE | 3.6452 | 91.129 | 28.1423 | #DIV/0! | 17.45 | 17.1 | 82.9
PAGE 11
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
CHEMICAL USEAGE
RUN DATE
2026-07-30
| MARCH | H2O2 | CL2 | POLYMER | POLYMER | LIME | GOX | O2 % | LOX | FPL
| 2003 | POUNDS | POUNDS | GALLONS | POUNDS | DELV. | TONS | PURITY | TONS | KW
| 1 | 2495 | 1180 | 0 | 0 | 0 | 34.7 | 99.5% | 152 | 22742
| 2 | 2435 | 1180 | 34 | 283.56 | 0 | 36.6 | 99.2% | 152 | 24511
| 3 | 2017 | 1220 | 83 | 692.22 | 0 | 37.3 | 99.2% | 154 | 27200
| 4 | 1388 | 1140 | 138 | 1150.92 | 0 | 36 | 99.4% | 156 | 27100
| 5 | 1178 | 1340 | 77 | 642.18 | 0 | 37.4 | 99.1% | 156 | 26845
| 6 | 2356 | 1220 | 0 | 0 | 0 | 37.8 | 99.1% | 157 | 25999
| 7 | 2545 | 1300 | 33 | 275.22 | 0 | 37.8 | 99.1% | 157 | 23807
| 8 | 2695 | 1260 | 0 | 0 | 0 | 36 | 99.6% | 157 | 21868
| 9 | 2843 | 1140 | 22 | 183.48 | 0 | 37.4 | 99.3% | 156 | 25937
| 10 | 2994 | 1360 | 70 | 583.8 | 0 | 38 | 99% | 156 | 25813
| 11 | 3004 | 1180 | 123 | 1025.82 | 0 | 39 | 99.3% | 157 | 28210
| 12 | 3114 | 1160 | 9 | 75.06 | 0 | 38.9 | 99.3% | 158 | 25730
| 13 | 3263 | 1320 | 68 | 567.12 | 0 | 38.9 | 99.2% | 159 | 25012
| 14 | 3064 | 1300 | 20 | 166.8 | 0 | 39.9 | 99% | 158 | 21583
| 15 | 3164 | 1120 | 0 | 0 | 0 | 40.2 | 98.9% | 158 | 22656
| 16 | 2834 | 1170 | 2 | 16.68 | 0 | 38.4 | 99.3% | 158 | 23994
| 17 | 2944 | 1260 | 9 | 75.06 | 0 | 39.5 | 99% | 158 | 25679
| 18 | 2824 | 1040 | 15 | 125.1 | 0 | 42.3 | 98.5% | 159 | 24569
| 19 | 3463 | 1200 | 24 | 200.16 | 0 | 45.8 | 99.2% | 157 | 27239
| 20 | 2155 | 1240 | 0 | 0 | 0 | 41.2 | 99% | 160 | 23948
| 21 | 1308 | 1180 | 123 | 1025.82 | 0 | 39.7 | 98.2% | 160 | 24947
| 22 | 1408 | 1100 | 0 | 0 | 0 | 42.1 | 98.2% | 160 | 22121
| 23 | 419 | 1420 | 45 | 375.3 | 0 | 34.5 | #VALUE! | 160 | 23788
| 24 | 1977 | 1160 | 59 | 492.06 | 0 | 36.7 | 99.7% | 161 | 30152
| 25 | 2924 | 1160 | 42 | 350.28 | 0 | 38 | 99.1% | 161 | 27012
| 26 | 2435 | 1180 | 66 | 550.44 | 0 | 38 | 98.9% | 162 | 22059
| 27 | 2575 | 1240 | 65 | 542.1 | 0 | 37.6 | 98.7% | 163 | 33189
| 28 | 2455 | 1120 | 25 | 208.5 | 0 | 39.6 | 98% | 157 | 38295
| 29 | 2584 | 1100 | 0 | 0 | 0 | 42.7 | 97.6% | 115 | 35192
| 30 | 2565 | 940 | 81 | 675.54 | 0 | 42.4 | 97.9% | 117 | 36507
| 31 | 2165 | 1120 | 52 | 433.68 | 0 | 39.4 | 98.9% | 116 | 28324
| TOTAL | 75590 | 37050 | 1285 | 10716.9 | 0 | 1203.8 |  | 4767 | 822028
| AVERAGE | 2438.3871 | 1195.1613 | 41.4516 | 345.7065 | 0 | 38.8323 | #VALUE! | 153.7742 | 26517.0323
PAGE 12
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL ONE
|  | RUN DATE |  |  | PERMIT NUMBER UO-06-279401
|  | 2026-07-30 |  |  | 7/21/97 thru 7/21/02 |  |  | I.D. #:5006A11308
|  | MARCH | % INFL. | MAX | MIN | WELL 1 | MAX | MIN | AVG
|  | 2003 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 26.77% | 10.91 | 5.33 | 8.38 | 54.19 | 40.5 | 47.37
|  | 2 | 26.73% | 12.1 | 5.47 | 8.41 | 57.73 | 40.42 | 47.46
|  | 3 | 25.42% | 12.8 | 4.07 | 8.19 | 60.11 | 38.02 | 47.36
|  | 4 | 25.31% | 12.39 | 4.59 | 8.21 | 60.59 | 38.63 | 46.98
|  | 5 | 25.26% | 11.74 | 4.52 | 8.1 | 59.92 | 38.54 | 46.76
|  | 6 | 25.26% | 12.77 | 3.36 | 8.17 | 59.55 | 36.89 | 46.87
|  | 7 | 25.56% | 12.85 | 4.51 | 8.25 | 60.17 | 38.74 | 47.09
|  | 8 | 25.66% | 11.12 | 4.06 | 8.16 | 54.03 | 38.34 | 46.88
|  | 9 | 24.87% | 11.96 | 4.03 | 7.94 | 57.21 | 37.97 | 46.44
|  | 10 | 25.23% | 12.65 | 2.53 | 8.26 | 59.8 | 38.44 | 47.46
|  | 11 | 22.27% | 12.77 | 0 | 7.54 | 60.14 | 25.87 | 46.69
|  | 12 | 25.05% | 12.9 | ER | 8.25 | 60.01 | ER | 47.12
|  | 13 | 12.85% | 12.82 | ER | 4.12 | 60.2 | 0.06 | 46.81
|  | 14 | 8.018% | 10.19 | ER | 2.54 | 56.96 | 33.26 | 47.15
|  | 15 | 25.08% | 11.05 | 4.72 | 7.93 | 54.67 | 39.4 | 46.65
|  | 16 | 25.04% | 11.2 | 4.24 | 8.03 | 55.44 | 28.32 | 46.77
|  | 17 | 14.67% | 12.09 | ER | 5.16 | 58.07 | ER | 29.37
|  | 18 |  | ER | ER | ER | ER | ER | ER
|  | 19 |  | ER | ER | ER | ER | ER | ER
|  | 20 | 6.352% | 11.03 | ER | 2.26 | 54.51 | ER | 12.03
|  | 21 | 25.72% | 14.65 | 4.45 | 8.86 | 66.63 | 21.01 | 48.72
|  | 22 | 24.74% | 11.56 | 4.9 | 8.29 | 56.96 | 40.23 | 47.62
|  | 23 | 25.09% | 11.37 | 4.39 | 8.41 | 55.84 | 39.42 | 47.92
|  | 24 | 25.85% | 13.03 | 4.18 | 8.95 | 60.68 | 40.89 | 48.93
|  | 25 | 24.94% | 11.31 | 4.29 | 8.33 | 56.55 | 39.13 | 47.58
|  | 26 | 25.08% | 11.38 | 4.03 | 8.31 | 55.49 | 38.7 | 47.56
|  | 27 | 25.1% | 11.75 | 4.25 | 8.53 | 56.47 | 38.95 | 48.04
|  | 28 | 25.41% | 11.85 | 4.18 | 8.97 | 56.74 | 38.88 | 49.15
|  | 29 | 24.75% | 11.68 | 4.16 | 8.54 | 56.47 | 38.82 | 48.17
|  | 30 | 25.01% | 11.33 | 4.2 | 8.27 | 55.2 | 38.86 | 47.47
|  | 31 | 24.93% | 11.25 | 3.93 | 8.03 | 54.57 | 36.86 | 46.33
|  | TOTAL | 672% | 346.5 | 98.39 | 221.39 | 1674.9 | 925.15 | 1320.75
|  | AVERAGE | 23.17% | 11.9483 | 4.0996 | 7.6341 | 57.7552 | 35.5827 | 45.5431
|  | MAXIMUM | 26.77% | 14.65 | 5.47 | 8.97 | 66.63 | 40.89 | 49.15
|  | MINIMUM | 6.352% | 10.19 | 0 | 2.26 | 54.03 | 0.06 | 12.03
PAGE 13
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL TWO
|  | RUN DATE |  |  | PERMIT NUMBER UO-06-279508
|  | 2026-07-30 |  |  | 7/21/97 thru 7/21/02 |  |  | I.D. #:5006A11309
|  | MARCH | % INFL. | MAX | MIN | WELL 2 | MAX | MIN | AVG
|  | 2003 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 26.8% | 10.97 | 5.2 | 8.39 | 53.29 | 39.72 | 46.49
|  | 2 | 26.82% | 12.14 | 5.35 | 8.44 | 56.77 | 39.65 | 46.58
|  | 3 | 25.32% | 12.94 | 3.71 | 8.16 | 59 | 37.29 | 46.47
|  | 4 | 25.31% | 12.52 | 4.35 | 8.21 | 59.55 | 37.89 | 46.11
|  | 5 | 25.23% | 11.78 | 4.32 | 8.09 | 58.76 | 37.81 | 45.88
|  | 6 | 25.22% | 12.76 | 2.74 | 8.16 | 58.43 | 36.19 | 46
|  | 7 | 25.62% | 12.93 | 4.27 | 8.27 | 59 | 38.01 | 46.21
|  | 8 | 25.75% | 11.15 | 3.79 | 8.19 | 53.12 | 37.59 | 45.97
|  | 9 | 24.9% | 12.07 | 3.61 | 7.95 | 56.21 | 37.25 | 45.59
|  | 10 | 25.17% | 12.74 | 0.04 | 8.24 | 58.63 | 36.2 | 46.5
|  | 11 | 26.96% | ER | 3.73 | 9.13 | 89.5 | 25.32 | 48.87
|  | 12 | 25.17% | 12.93 | ER | 8.29 | 58.84 | ER | 46.23
|  | 13 | 25.44% | 12.89 | 2.5 | 8.16 | 59.05 | 36.4 | 46.35
|  | 14 | 25.89% | 11.8 | 3.76 | 8.2 | ER | 37.83 | 46.35
|  | 15 | 25.27% | 11.12 | 4.53 | 7.99 | 53.58 | 38.66 | 45.78
|  | 16 | 25.23% | 11.34 | 3.96 | 8.09 | 54.41 | 27.77 | 45.87
|  | 17 | 14.7% | 12.24 | ER | 5.17 | 56.92 | ER | 28.98
|  | 18 |  | ER | ER | ER | ER | ER | ER
|  | 19 |  | ER | ER | ER | ER | ER | ER
|  | 20 | 6.464% | 11.17 | ER | 2.3 | 53.48 | ER | 11.8
|  | 21 | 25.92% | 14.76 | 4.31 | 8.93 | 65.34 | 30.57 | 47.83
|  | 22 | 24.86% | 11.66 | 4.63 | 8.33 | 55.9 | 39.48 | 46.75
|  | 23 | 25% | 11.43 | 4.27 | 8.38 | 54.73 | 38.67 | 47.01
|  | 24 | 25.3% | 12.47 | 4.91 | 8.76 | 57.76 | 40.31 | 48.01
|  | 25 | 25.06% | 11.49 | 4.11 | 8.37 | 55.42 | 38.33 | 46.64
|  | 26 | 25.2% | 11.41 | 3.84 | 8.35 | 54.41 | 37.95 | 46.65
|  | 27 | 25.22% | 11.82 | 4.12 | 8.57 | 55.33 | 38.19 | 47.11
|  | 28 | 25.49% | 11.9 | 4.18 | 9 | 55.66 | 38.12 | 48.18
|  | 29 | 24.93% | 11.74 | 4 | 8.6 | 55.38 | 38.06 | 47.25
|  | 30 | 25.16% | 11.38 | 4.1 | 8.32 | 54.2 | 38.09 | 46.54
|  | 31 | 25.09% | 12.79 | 3.63 | 8.08 | 54.16 | 35.24 | 45.44
|  | TOTAL | 708.5% | 338.34 | 101.96 | 233.12 | 1616.83 | 956.59 | 1299.44
|  | AVERAGE | 24.43% | 12.0836 | 3.9215 | 8.0386 | 57.7439 | 36.7919 | 44.8083
|  | MAXIMUM | 26.96% | 14.76 | 5.35 | 9.13 | 89.5 | 40.31 | 48.87
|  | MINIMUM | 6.464% | 10.97 | 0.04 | 2.3 | 53.12 | 25.32 | 11.8
PAGE 14
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL THREE
|  | RUN DATE |  |  | PERMIT NUMBER UO-06-279510
|  | 2026-07-30 |  |  | 7/21/97 thru 7/21/02 |  |  | I.D. #:5006A11310
|  | MARCH | % INFL. | MAX | MIN | WELL 3 | MAX | MIN | AVG
|  | 2003 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 23.35% | 9.58 | 4.58 | 7.31 | 54.54 | 40.65 | 47.62
|  | 2 | 23.39% | 10.58 | 4.61 | 7.36 | 58.13 | 40.57 | 47.69
|  | 3 | 22% | 11.3 | 3.22 | 7.09 | 60.53 | 38.13 | 47.58
|  | 4 | 21.95% | 10.93 | 3.7 | 7.12 | 61.03 | 38.75 | 47.22
|  | 5 | 21.86% | 10.27 | 3.64 | 7.01 | 60.32 | 38.66 | 46.98
|  | 6 | 21.92% | 11.1 | 2.47 | 7.09 | 59.97 | 36.97 | 47.09
|  | 7 | 22.18% | 11.29 | 3.67 | 7.16 | 60.59 | 38.86 | 47.31
|  | 8 | 19.65% | 9.73 | ER | 6.25 | 54.35 | 35.49 | 45.9
|  | 9 | 21.58% | 10.58 | 3.1 | 6.89 | 57.61 | 38.08 | 46.66
|  | 10 | 21.87% | 11.1 | 1.31 | 7.16 | 60.2 | 38.53 | 47.68
|  | 11 | 21.91% | 13.98 | ER | 7.42 | 72.1 | 26 | 48.51
|  | 12 | 21.86% | 11.29 | ER | 7.2 | 60.37 | ER | 47.34
|  | 13 | 21.17% | 11.31 | ER | 6.79 | 60.58 | ER | 41.95
|  | 14 | 22.48% | 10.34 | 3.26 | 7.12 | 57.26 | 38.69 | 47.48
|  | 15 | 21.83% | 9.73 | 3.82 | 6.9 | 54.98 | 39.52 | 46.85
|  | 16 | 21.77% | 9.88 | 3.35 | 6.98 | 55.8 | 28.42 | 46.99
|  | 17 | 12.74% | 10.59 | ER | 4.48 | 58.44 | ER | 29.51
|  | 18 |  | ER | ER | ER | ER | ER | ER
|  | 19 |  | ER | ER | ER | ER | ER | ER
|  | 20 |  | ER | ER | ER | 54.81 | ER | 12.09
|  | 21 |  | 10.29 | ER | ER | 57.37 | 21.12 | 47.96
|  | 22 | 22.02% | 10.42 | 4.11 | 7.38 | 57.28 | 40.35 | 47.81
|  | 23 | 22.28% | 10.17 | 3.77 | 7.47 | 56.13 | 39.53 | 48.13
|  | 24 | 20.01% | 11.59 | ER | 6.93 | 61.02 | 36.24 | 47.79
|  | 25 | 22.19% | 10.2 | 3.66 | 7.41 | 56.86 | 39.24 | 47.8
|  | 26 | 22.3% | 10.12 | 3.37 | 7.39 | 55.79 | 38.8 | 47.75
|  | 27 | 22.25% | 10.43 | 3.6 | 7.56 | 56.79 | 39.05 | 48.25
|  | 28 | 22.49% | 10.52 | 3.63 | 7.94 | 57.06 | 38.99 | 49.34
|  | 29 | 21.94% | 10.39 | 3.58 | 7.57 | 56.72 | 38.9 | 48.37
|  | 30 | 22.07% | 10.03 | 3.55 | 7.3 | 55.5 | 38.92 | 47.65
|  | 31 | 22.05% | 9.9 | 3.25 | 7.1 | 54.87 | 37.13 | 46.61
|  | TOTAL | 583.1% | 297.64 | 73.25 | 191.38 | 1687 | 925.59 | 1319.91
|  | AVERAGE | 21.6% | 10.63 | 3.4881 | 7.0881 | 58.1724 | 37.0236 | 45.5141
|  | MAXIMUM | 23.39% | 13.98 | 4.61 | 7.94 | 72.1 | 40.65 | 49.34
|  | MINIMUM | 12.74% | 9.58 | 1.31 | 4.48 | 54.35 | 21.12 | 12.09
PAGE 15
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL FOUR
|  | RUN DATE |  |  | PERMIT NUMBER UC-06-264391 (IW-4)
2026-07-30
|  | MARCH | % INFL. | MAX | MIN | WELL 4 | MAX | MIN | AVG
|  | 2003 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 0.3514% | 0.13 | 0.1 | 0.11 | 35.15 | 32.43 | 33.84
|  | 2 | 0.3496% | 0.13 | 0.1 | 0.11 | 35.69 | 32.33 | 33.88
|  | 3 | 0.3414% | 0.14 | 0.1 | 0.11 | 35.93 | 32.66 | 34.18
|  | 4 | 0.3392% | 0.14 | 0.1 | 0.11 | 36.05 | 32.86 | 34.19
|  | 5 | 0.343% | 0.14 | 0.1 | 0.11 | 35.68 | 32.92 | 34.15
|  | 6 | 0.34% | 0.13 | 0.1 | 0.11 | 35.87 | 32.45 | 34.13
|  | 7 | 0.3717% | 0.14 | 0.11 | 0.12 | 36.49 | 32.83 | 34.66
|  | 8 | 0.3774% | 0.14 | 0.1 | 0.12 | 36.96 | 34.1 | 35.64
|  | 9 | 0.3758% | 0.14 | 0.1 | 0.12 | 37.21 | 34.15 | 35.61
|  | 10 | 0.3359% | 0.13 | 0.1 | 0.11 | 37.4 | 34.3 | 35.68
|  | 11 | 0.3249% | 0.23 | 0.05 | 0.11 | 38.4 | 17.94 | 35.74
|  | 12 | 0.3644% | 0.14 | ER | 0.12 | 37.27 | ER | 35.49
|  | 13 | 0.3741% | 0.14 | 0.11 | 0.12 | 37.52 | 34.27 | 35.84
|  | 14 | 0.3788% | 0.14 | 0.1 | 0.12 | 59.8 | 34.75 | 36.21
|  | 15 | 0.3796% | 0.14 | 0.1 | 0.12 | 37.41 | 35.24 | 36.31
|  | 16 | 0.3431% | 0.14 | 0.06 | 0.11 | 37.63 | 22 | 36.29
|  | 17 | 0.199% | 0.13 | ER | 0.07 | 38.04 | ER | 22.62
|  | 18 |  | ER | ER | ER | ER | ER | ER
|  | 19 |  | ER | ER | ER | ER | ER | ER
|  | 20 | 0.05621% | 0.11 | ER | 0.02 | 37.27 | ER | 8.65
|  | 21 | 0.3483% | 0.14 | 0.07 | 0.12 | 37.74 | 23.51 | 36.4
|  | 22 | 0.388% | 0.15 | 0.12 | 0.13 | 37.73 | 35.26 | 36.44
|  | 23 | 0.3579% | 0.14 | 0.11 | 0.12 | 37.66 | 35.14 | 36.52
|  | 24 | 0.3466% | 0.14 | 0.11 | 0.12 | 38.13 | 35.13 | 36.63
|  | 25 | 0.3593% | 0.14 | 0.1 | 0.12 | 37.74 | 35.2 | 36.66
|  | 26 | 0.3621% | 0.14 | 0.11 | 0.12 | 41.5 | 35.84 | 39.81
|  | 27 | 0.3532% | 0.13 | 0.11 | 0.12 | 41.65 | 39.23 | 40.45
|  | 28 | 0.3399% | 0.14 | 0.11 | 0.12 | 41.77 | 39 | 40.59
|  | 29 | 0.3768% | 0.15 | 0.11 | 0.13 | 41.67 | 38.94 | 40.39
|  | 30 | 0.3629% | 0.14 | 0.1 | 0.12 | 41.45 | 38.88 | 40.17
|  | 31 | 0.3105% | 0.12 | 0.07 | 0.1 | 40.87 | 34.04 | 39.59
|  | TOTAL | 9.851% | 4.06 | 2.55 | 3.24 | 1123.68 | 865.4 | 1016.76
|  | AVERAGE | 0.3397% | 0.14 | 0.098077 | 0.11172 | 38.7476 | 33.2846 | 35.0607
|  | MAXIMUM | 0.388% | 0.23 | 0.12 | 0.13 | 59.8 | 39.23 | 40.59
|  | MINIMUM | 0.05621% | 0.11 | 0.05 | 0.02 | 35.15 | 17.94 | 8.65
PAGE 16
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL FIVE
|  | RUN DATE |  |  | PERMIT NUMBER UO-06-279512
|  | 2026-07-30 |  |  | 7/21/97 thru 7/21/02 |  |  | I.D. #:5006A11311
|  | MARCH | % INFL. | MAX | MIN | WELL 5 | MAX | MIN | AVG
|  | 2003 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 17.12% | 9.68 | ER | 5.36 | 53.96 | 33.47 | 43.57
|  | 2 | 17.29% | 10.67 | ER | 5.44 | 57.78 | 33.47 | 43.69
|  | 3 | 22.78% | 11.34 | 3.65 | 7.34 | 60.08 | 37.83 | 46.99
|  | 4 | 22.72% | 10.97 | 4.18 | 7.37 | 59.98 | 38.51 | 46.67
|  | 5 | 22.67% | 10.44 | 4.13 | 7.27 | 59.47 | 38.39 | 46.49
|  | 6 | 22.63% | 11.17 | 2.92 | 7.32 | 59.57 | 36.69 | 46.62
|  | 7 | 22.92% | 11.33 | 4.1 | 7.4 | 59.4 | 38.62 | 46.82
|  | 8 | 23.11% | 9.81 | 3.71 | 7.35 | 54.13 | 38.15 | 46.6
|  | 9 | 22.39% | 10.6 | 3.56 | 7.15 | 56.31 | 37.84 | 46.21
|  | 10 | 22.54% | 11.23 | 1.59 | 7.38 | 59.12 | 38.15 | 47.22
|  | 11 | 22.39% | 13.79 | ER | 7.58 | 71 | 25.61 | 48.02
|  | 12 | 22.47% | 11.28 | ER | 7.4 | 59.8 | ER | 46.85
|  | 13 | 22.82% | 11.3 | 2.8 | 7.32 | 60.1 | 36.95 | 46.97
|  | 14 | 23.14% | 10.37 | 3.7 | 7.33 | 56.77 | 38.37 | 46.97
|  | 15 | 22.58% | 9.76 | 4.28 | 7.14 | 54.5 | 39.09 | 46.3
|  | 16 | 22.52% | 9.93 | 3.8 | 7.22 | 55.47 | 27.85 | 46.51
|  | 17 | 13.14% | 10.69 | ER | 4.62 | 58.06 | ER | 29.43
|  | 18 |  | ER | ER | ER | ER | ER | ER
|  | 19 |  | ER | ER | ER | ER | ER | ER
|  | 20 | 5.677% | 9.74 | ER | 2.02 | 54.02 | ER | 11.87
|  | 21 | 23.05% | 13.04 | 4.12 | 7.94 | 65.03 | 31.7 | 47.92
|  | 22 | 22.23% | 10.27 | 4.41 | 7.45 | 56.25 | 39.5 | 46.61
|  | 23 | 22.46% | 10.01 | 4.08 | 7.53 | 54.84 | 39 | 47.08
|  | 24 | 23.1% | 10.69 | 3.83 | 8 | 57.82 | 40.49 | 48.19
|  | 25 | 22.43% | 10.11 | 4.02 | 7.49 | 55.73 | 38.9 | 46.88
|  | 26 | 22.54% | 10 | 3.76 | 7.47 | 78.7 | 19.39 | 46.64
|  | 27 | 22.46% | 10.33 | 3.96 | 7.63 | 56.39 | 38.82 | 47.93
|  | 28 | 22.66% | 10.4 | 3.99 | 8 | 56.6 | 38.78 | 48.99
|  | 29 | 22.2% | 10.29 | 3.96 | 7.66 | 56.22 | 38.72 | 48
|  | 30 | 22.44% | 9.97 | 3.95 | 7.42 | 54.97 | 38.77 | 47.32
|  | 31 | 22.29% | 9.82 | 3.59 | 7.18 | 54.5 | 36.11 | 46.33
|  | TOTAL | 618.8% | 309.03 | 86.09 | 203.78 | 1696.57 | 939.17 | 1305.69
|  | AVERAGE | 21.34% | 10.6562 | 3.743 | 7.0269 | 58.5024 | 36.1219 | 45.0238
|  | MAXIMUM | 23.14% | 13.79 | 4.41 | 8 | 78.7 | 40.49 | 48.99
|  | MINIMUM | 5.677% | 9.68 | 1.59 | 2.02 | 53.96 | 19.39 | 11.87
PAGE 17
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
INJECTION WELL SUMMARY
RUN DATE
2026-07-30
| MARCH | INFLUENT | EFFLUENT | EFFLUENT | IW-1 | IW-2 | IW-3 | IW-4 | IW-5 | TOTAL
| 2003 | FLOW | FLOW | SS | LBS SS | LBS SS | LBS SS | LBS SS | LBS SS | LBS SS
|  | MGD | MGD
| 1 | 31.303 | 29.461 | 14 | 978.4488 | 979.6164 | 853.5156 | 12.8436 | 625.8336 | 3437.4144
| 2 | 31.465 | 29.665 | 13 | 911.8122 | 915.0648 | 797.9712 | 11.9262 | 589.8048 | 3214.653
| 3 | 32.224 | 30.868 | 8 | 546.4368 | 544.4352 | 473.0448 | 7.3392 | 489.7248 | 2053.6416
| 4 | 32.434 | 30.986 | 10 | 684.714 | 684.714 | 593.808 | 9.174 | 614.658 | 2577.894
| 5 | 32.068 | 30.495 | 13 | 878.202 | 877.1178 | 760.0242 | 11.9262 | 788.2134 | 3303.5574
| 6 | 32.35 | 30.705 | 13 | 885.7914 | 884.7072 | 768.6978 | 11.9262 | 793.6344 | 3332.8308
| 7 | 32.283 | 31.113 | 10 | 688.05 | 689.718 | 597.144 | 10.008 | 617.16 | 2592.072
| 8 | 31.8 | 29.962 | 7 | 476.3808 | 478.1322 | 364.875 | 7.0056 | 429.093 | 1748.481
| 9 | 31.931 | 29.95 | 10 | 662.196 | 663.03 | 574.626 | 10.008 | 596.31 | 2496.162
| 10 | 32.743 | 31.095 | 17 | 1171.1028 | 1168.2672 | 1015.1448 | 15.5958 | 1046.3364 | 4400.8512
| 11 | 33.859 | 31.632 | 17 | 1069.0212 | 1294.4514 | 1052.0076 | 15.5958 | 1074.6924 | 4490.1726
| 12 | 32.93 | 31.505 | 12 | 825.66 | 829.6632 | 720.576 | 12.0096 | 740.592 | 3116.4912
| 13 | 32.074 | 30.475 | 18 | 618.4944 | 1224.9792 | 1019.3148 | 18.0144 | 1098.8784 | 3961.6668
| 14 | 31.677 | 30.542 | 7 | 148.2852 | 478.716 | 415.6656 | 7.0056 | 427.9254 | 1470.5922
| 15 | 31.615 | 28.96 | 11 | 727.4982 | 733.0026 | 633.006 | 11.0088 | 655.0236 | 2748.5304
| 16 | 32.063 | 30.459 | 14 | 937.5828 | 944.5884 | 814.9848 | 12.8436 | 843.0072 | 3540.1632
| 17 | 35.171 | 34.621 | 23 | 989.7912 | 991.7094 | 859.3536 | 13.4274 | 886.2084 | 3727.0626
| 18 | 36.093 | 34.749 | 14
| 19 | 36.2 | 34.937 | 15
| 20 | 35.581 | 34.521 | 27 | 508.9068 | 517.914 |  | 4.5036 | 454.8636
| 21 | 34.452 | 34.299 | 16 | 1182.2784 | 1191.6192 |  | 16.0128 | 1059.5136
| 22 | 33.509 | 31.519 | 20 | 1382.772 | 1389.444 | 1230.984 | 21.684 | 1242.66 | 5245.86
| 23 | 33.525 | 31.804 | 23 | 1613.2062 | 1607.4516 | 1432.8954 | 23.0184 | 1444.4046 | 6097.9578
| 24 | 34.625 | 32.716 | 18 | 1343.574 | 1315.0512 | 1040.3316 | 18.0144 | 1200.96 | 4899.9168
| 25 | 33.396 | 31.646 | 18 | 1250.4996 | 1256.5044 | 1112.3892 | 18.0144 | 1124.3988 | 4743.792
| 26 | 33.14 | 31.573 | 20 | 1386.108 | 1392.78 | 1232.652 | 20.016 | 1245.996 | 5257.536
| 27 | 33.979 | 32.397 | 14 | 995.9628 | 1000.6332 | 882.7056 | 14.0112 | 890.8788 | 3770.1804
| 28 | 35.305 | 33.876 | 13 | 972.5274 | 975.78 | 860.8548 | 13.0104 | 867.36 | 3676.5222
| 29 | 34.501 | 32.378 | 12 | 854.6832 | 860.688 | 757.6056 | 13.0104 | 766.6128 | 3239.5896
| 30 | 33.07 | 31.377 | 9 | 620.7462 | 624.4992 | 547.938 | 9.0072 | 556.9452 | 2350.1286
| 31 | 32.206 | 30.387 | 14 | 937.5828 | 943.4208 | 828.996 | 11.676 | 838.3368 | 3548.3364
| TOTAL | 1029.572 | 980.673 | 450 | 26248.3152 | 27457.6986 | 22241.112 | 379.6368 | 24010.026 | 95042.0562
| AVERAGE | 33.212 | 31.6346 | 14.5161 | 905.1143 | 946.8172 | 823.7449 | 13.0909 | 827.9319 | 3520.0762
PAGE 18
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
| RUN DATE |  |  |  | SOLIDS REMOVAL INVENTORY DATA SHEET
2026-07-30
| MARCH | TONS | CAKE |  |  |  | MARCH | RAGS | GRIT | OTHER
| 2003 | SLUDGE | TSS |  |  |  | 2003 |  |  | (vac)
| 1st - 7th | [5 empty] | 1st - 7th
| 1 | 0 |  |  |  |  | 1
| 2 | 25 |  |  |  |  | 2
| 3 | 150 | 17.22 |  |  |  | 3
| 4 | 125 | 18.01 |  |  |  | 4
| 5 | 150 | 18.42 |  |  |  | 5
| 6 | 200 | 17.88 |  |  |  | 6
| 7 | 75 |  |  |  |  | 7 | 10
| TOTAL = | 725 | 17.8825 | = AVG. |  |  | TOTAL = | 10 | 0 | 0
| 8th - 14th | [5 empty] | 8th - 14th
| 8 | 0 |  |  |  |  | 8
| 9 | 25 | 17.86 |  |  |  | 9
| 10 | 150 | 17.64 |  |  |  | 10
| 11 | 150 | 17.89 |  |  |  | 11
| 12 | 150 | 17.2 |  |  |  | 12
| 13 | 150 | 17.42 |  |  |  | 13
| 14 | 100 |  |  |  |  | 14 | 10
| TOTAL = | 725 | 17.602 | = AVG. |  |  | TOTAL = | 10 | 0 | 0
| 15th - 22nd | [5 empty] | 15th-22nd
| 15 | 0 |  |  |  |  | 15
| 16 | 0 |  |  |  |  | 16
| 17 | 0 |  |  |  |  | 17
| 18 | 0 |  |  |  |  | 18
| 19 | 50 |  |  |  |  | 19
| 20 | 175 | 17.13 |  |  |  | 20 | 10
| 21 | 125 |  |  |  |  | 21 |  | 10
| 22 | 0 |  |  |  |  | 22
| TOTAL = | 350 | 17.13 | = AVG. |  |  | TOTAL = | 10 | 10 | 0
| 23rd - 31st | [5 empty] | 23rd-31st
| 23 | 50 | 17.15 |  |  |  | 23
| 24 | 175 | 17.64 |  |  |  | 24
| 25 | 150 | 17.1 |  |  |  | 25
| 26 | 175 | 17.4 |  |  |  | 26
| 27 | 150 | 16.61 |  |  |  | 27 | 10
| 28 | 125 |  |  |  |  | 28
| 29 | 0 |  |  |  |  | 29
| 30 | 50 | 16.74 |  |  |  | 30
| 31 | 150 | 17.34 |  |  |  | 31 |  |  | 4500
| TOTAL = | 1025 | 17.14 | = AVG. |  |  | TOTAL = | 10 | 0 | 4500
PAGE 19

## INJECTION PAGES
|  |  |  | UNDERGROUND INJECTION CONTROL | [10 empty] | UNDERGROUND INJECTION CONTROL | [10 empty] | UNDERGROUND INJECTION CONTROL
[15 empty] | MONTHLY OPERATING REPORT | [10 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES |  |  |  |  | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES |  |  |  |  | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [10 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [10 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-1 | [7 empty] | Wet Well Description: |  |  | Effuent Wet Well for IW-1, IW-2, IW3, IW-4 and IW-5 | [7 empty] | Monitoring Well Decription: |  |  | UPPER ZONE OF MONITORING WELL MW-1
Permit #: |  | UO-06-279401 |  |  |  |  | Date of Issuance: |  | 1997-07-21 |  | Facility ID #: |  | 5006M02066 |  |  |  | Permit Number: |  |  | FLA041378 |  | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | UO-06-279512
[22 empty] | Monitoring Well ID #: |  |  | 5006A11311
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2002-07-21 | [7 empty] | Issue Date: |  |  | 1999-10-18 |  | As Identified in Permit: |  | Monitor Well MW-1 Upper Monitor Zone |  |  |  | Issue Date: |  |  | 1997-07-21
[22 empty] | Monitoring Well Interval: |  |  | 1288' to 1320'
Injection Well ID #: |  | 5006A11308 | [8 empty] | Wet Well ID #: |  | Well Facility U-001 |  |  |  | Expiration Date: |  |  | 2004-10-17 |  | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.3 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24 | Associated Injection Well(s):
Injection Interval: |  |  | 2799' to 3513' | [18 empty] | 500A11311 |  |  | INJECTION WELL IW-5
[11 empty] | Injection Well ID #: |  |  | Injection Well Description
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s): | [10 empty] | 5006A11308 |  |  | INJECTION WELL IW-1
[11 empty] | 5006A11309 |  |  | INJECTION WELL IW-2 | [7 empty] | REPORT MONTH / YEAR: |  | 2003-03-01 | DATE OF SAP / RECORDING: |  |  | 2003-03-04 | 2003-03-11 | 2003-03-18 | 2003-03-25
Monitoring Zone ID #: | [5 empty] | Description |  |  |  |  | 5006A11310 |  |  | INJECTION WELL IW-3
[11 empty] | N/A |  |  | INJECTION WELL IW-4 | [7 empty] | OPERATOR'S NAME: |  |  | BAYLER, J.
UO-06-279401 |  | UPPER ZONE OF MONITORING WELL MW-2 | [8 empty] | 5006A11311 |  |  | INJECTION WELL IW-5
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A
UO-06-279401 |  | LOWER ZONE OF MONITORING WELL MW-2
[11 empty] | THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [10 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [10 empty] | REPORT MONTH / YEAR: |  | 2003-03-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous |  |  | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2003-03-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous |  |  | OPERATOR'S NAME: |  |  | BAYLER, J.
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
OPERATOR'S NAME: |  |  | BAYLER, J. | [7 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A | [7 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4474-A | [7 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: |  |  |  | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 48.41 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 29.06 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: |  |  |  | PARAMETER |  |  |  | Sampling Frequency |  |  |  | VALUE |  | UNITS | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 47.5356 | PSIG
[11 empty] | Nitrogen, Total as N |  |  |  |  | Daily/Monthly Average |  |  | 19.7294 |  | mg/L as N | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[11 empty] | Nitrogen, Nitrate, Total as N |  |  |  |  | Daily/Monthly Average |  |  | 0.39936 |  | mg/L as N | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 5559.8025 | mg/l
Total monthly flow | [7 empty] | 221.39 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 2834.375 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [7 empty] | Nitrogen, Total Kjeildahl as N |  |  |  |  | Daily/Monthly Average |  |  | 19.33 |  | mg/L as N | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.8455 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 14.65 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.38 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 66.63 |  | PSIG | pH |  |  |  |  | Daily/Monthly Average |  |  | 6.3871 |  | s.u. | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 8.025 | Std units
Monthly average of the daily flow rates | [7 empty] | 7.6341 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 12300 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 10.5722 |  | MG | Phosphorus, Total as P |  |  |  |  | Daily/Monthly Average |  |  | 1.4241 |  | mg/L as P | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 1.901 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 73 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [10 empty] | Total Dissolved Solids (TDS) |  |  |  |  | Daily/Monthly Average |  |  | 1301.3871 |  | mg/L | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.05 | mg/l
Monthly average pressure | [7 empty] | 45.5431 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 825 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 36.1 |  | PSIG | Residue, Total filterable (TSS dried at 180 C) |  |  |  |  | Daily/Monthly Average |  |  | 14.5161 |  | mg/L | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 167.5 | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.14 | mg/l
[11 empty] | Specific Conductance (Temperature Compensated) |  |  |  |  | Daily/Monthly Average |  |  | 2610 |  | umhos/cm | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just | [6 empty] | Temperature, Water |  |  |  |  | Daily/Monthly Average |  |  | 80.0968 |  | deg C
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [9 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just |  |  | Date: |  |  |  |  | (Signature):
Date:
(Signature):
|  |  |  | UNDERGROUND INJECTION CONTROL | [21 empty] | UNDERGROUND INJECTION CONTROL
|  |  |  | MONTHLY OPERATING REPORT | [21 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES | [15 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [21 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-2 | [18 empty] | Monitoring Well Decription: |  |  | LOWER ZONE OF MONITORING WELL MW-1
Permit #: |  | UO-06-279508 |  |  |  |  | Date of Issuance: |  | 1997-07-21 | [12 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | UO-06-279512
[22 empty] | Monitoring Well ID #: |  |  | 5006A11311
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2002-07-21 | [12 empty] | As Identified in Permit: |  | Monitor Well MW-1 Lower Monitor Zone |  |  |  | Issue Date: |  |  | 1997-07-21
[22 empty] | Monitoring Well Interval: |  |  | 1449' to 1557'
Injection Well ID #: |  | 5006A11309 | [19 empty] | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.3 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24
Injection Interval: |  |  | 2798' to 3518' | [18 empty] | 500A11311 |  |  | INJECTION WELL IW-5
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s):
[22 empty] | REPORT MONTH / YEAR: |  | 2003-03-01 | DATE OF SAP / RECORDING: |  |  | 2003-03-04 | 2003-03-11 | 2003-03-18 | 2003-03-25
Monitoring Zone ID #: | [5 empty] | Description
[22 empty] | OPERATOR'S NAME: |  |  | BAYLER, J.
UO-06-279401 |  | UPPER ZONE OF MONITORING WELL MW-2
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A
UO-06-279401 |  | LOWER ZONE OF MONITORING WELL MW-2
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [21 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2003-03-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
OPERATOR'S NAME: |  |  | BAYLER, J. | [18 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4474-A | [18 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 42.37 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 25.75 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: | [14 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 37.74 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 9483.5 | mg/l
Total monthly flow | [7 empty] | 233.12 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 5125 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [18 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 9.235 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 14.76 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 12.86 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 89.5 |  | PSIG | [11 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7.415 | Std units
Monthly average of the daily flow rates | [7 empty] | 8.0386 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 15682.5 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 11.1465 |  | MG | [11 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 1.901 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 73.25 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [21 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.05 | mg/l
Monthly average pressure | [7 empty] | 44.8083 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 812.5 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 36.3 |  | PSIG | [11 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 260 | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.01 | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [21 empty] | (Signature):
Date:
|  |  |  | UNDERGROUND INJECTION CONTROL | [21 empty] | UNDERGROUND INJECTION CONTROL
|  |  |  | MONTHLY OPERATING REPORT | [21 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES | [15 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [21 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-3 | [18 empty] | Monitoring Well Decription: |  |  | UPPER ZONE OF MONITORING WELL MW-2
Permit #: |  | UO-06-279510 |  |  |  |  | Date of Issuance: |  | 1997-07-21 | [12 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | UC-06-279401 & 508
[22 empty] | Monitoring Well ID #: |  |  | 5006A11308 & 309
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2002-07-21 | [12 empty] | As Identified in Permit: |  | Monitor Well MW-2 Upper Monitor Zone |  |  |  | Issue Date: |  |  | 1997-07-21
[22 empty] | Monitoring Well Interval: |  |  | 1300' to 1344'
Injection Well ID #: |  | 5006A11310 | [19 empty] | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.3 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24
Injection Interval: |  |  | 2800' to 3977' | [18 empty] | 5006A11308 |  |  | INJECTION WELL IW-1
[22 empty] | 5006A11309 |  |  | INJECTION WELL IW-2
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s):
[22 empty] | REPORT MONTH / YEAR: |  | 2003-03-01 | DATE OF SAP / RECORDING: |  |  | 2003-03-04 | 2003-03-11 | 2003-03-18 | 2003-03-25
Monitoring Zone ID #: | [5 empty] | Description
[22 empty] | OPERATOR'S NAME: |  |  | BAYLER, J.
UO-06-279510 |  | UPPER ZONE OF MONITORING WELL MW-3
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A
UO-06-279510 |  | LOWER ZONE OF MONITORING WELL MW-3
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [21 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2003-03-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
OPERATOR'S NAME: |  |  | BAYLER, J. | [18 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4474-A | [18 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 0 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 0 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: | [14 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | #DIV/0! | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 13474.75 | mg/l
Total monthly flow | [7 empty] | 191.38 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7312.5 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [18 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.933 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 13.98 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.6825 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 72.1 |  | PSIG | [11 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7.9075 | Std units
Monthly average of the daily flow rates | [7 empty] | 7.0881 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 20752.5 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 9.8534 |  | MG | [11 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 1.901 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 71 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [21 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.05 | mg/l
Monthly average pressure | [7 empty] | 45.5141 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1375 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 37.1 |  | PSIG | [11 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 352.5 | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 3.9475 | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [21 empty] | (Signature):
Date:
|  |  |  | UNDERGROUND INJECTION CONTROL | [21 empty] | UNDERGROUND INJECTION CONTROL
|  |  |  | MONTHLY OPERATING REPORT | [21 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES | [15 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [21 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-4 | [18 empty] | Monitoring Well Decription: |  |  | LOWER ZONE OF MONITORING WELL MW-2
Permit #: |  | UC-06-264391 |  |  |  |  | Date of Issuance: |  | N/A | [12 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | UC-06-279401 & 508
[22 empty] | Monitoring Well ID #: |  |  | 5006A11308 & 309
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2000-11-30 | [12 empty] | As Identified in Permit: |  | Monitor Well MW-2 Lower Monitor Zone |  |  |  | Issue Date: |  |  | 1997-07-21
[22 empty] | Monitoring Well Interval: |  |  | 1970' to 2025'
Injection Well ID #: |  | N/A | [19 empty] | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24
Injection Interval: |  |  | 2804' to 3977' | [18 empty] | 5006A11308 |  |  | INJECTION WELL IW-1
[22 empty] | 5006A11309 |  |  | INJECTION WELL IW-2
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s):
[22 empty] | REPORT MONTH / YEAR: |  | 2003-03-01 | DATE OF SAP / RECORDING: |  |  | 2003-03-04 | 2003-03-11 | 2003-03-18 | 2003-03-25
Monitoring Zone ID #: | [5 empty] | Description
[22 empty] | OPERATOR'S NAME: |  |  | BAYLER, J.
UO-06-279510 |  | UPPER ZONE OF MONITORING WELL MW-3
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A
UO-06-279510 |  | LOWER ZONE OF MONITORING WELL MW-3
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [21 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2003-03-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
OPERATOR'S NAME: |  |  | BAYLER, J. | [18 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4474-A | [18 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 42.27 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 26.64 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: | [14 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 39.9059 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 31803 | mg/l
Total monthly flow | [7 empty] | 3.24 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 18037.5 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [18 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.17 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 0.23 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.9925 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 59.8 |  | PSIG | [11 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7.415 | Std units
Monthly average of the daily flow rates | [7 empty] | 0.11172 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 47550 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 0.15498 |  | MG | [11 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 1.901 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 70 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [21 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.05 | mg/l
Monthly average pressure | [7 empty] | 35.0607 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 2775 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 34.8 |  | PSIG | [11 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 845 | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.0375 | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [21 empty] | (Signature):
Date:
|  |  |  | UNDERGROUND INJECTION CONTROL | [21 empty] | UNDERGROUND INJECTION CONTROL
|  |  |  | MONTHLY OPERATING REPORT | [21 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES | [15 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [21 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-5 | [18 empty] | Monitoring Well Decription: |  |  | UPPER ZONE OF MONITORING WELL MW-3
Permit #: |  | UO-06-279512 |  |  |  |  | Date of Issuance: |  | 1997-07-21 | [12 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | UO-06-279510
[22 empty] | Monitoring Well ID #: |  |  | 5006A11310
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2002-07-21 | [12 empty] | As Identified in Permit: |  | Monitor Well MW-3 Upper Monitor Zone |  |  |  | Issue Date: |  |  | 1997-07-21
[22 empty] | Monitoring Well Interval: |  |  | 1300' to 1349'
Injection Well ID #: |  | 5006A11311 | [19 empty] | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.3 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24
Injection Interval: |  |  | 2818' to 3462' | [18 empty] | 5006A11310 |  |  | INJECTION WELL IW-3
[22 empty] | N/A |  |  | INJECTION WELL IW-4
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s):
[22 empty] | REPORT MONTH / YEAR: |  | 2003-03-01 | DATE OF SAP / RECORDING: |  |  | 2003-03-04 | 2003-03-11 | 2003-03-18 | 2003-03-25
Monitoring Zone ID #: | [5 empty] | Description
[22 empty] | OPERATOR'S NAME: |  |  | BAYLER, J.
UO-06-279512 |  | UPPER ZONE OF MONITORING WELL MW-1
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A
UO-06-279512 |  | LOWER ZONE OF MONITORING WELL MW-1
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [21 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2003-03-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
OPERATOR'S NAME: |  |  | BAYLER, J. | [18 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4474-A | [18 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 30.59 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 17.27 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: | [14 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 28.1679 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7304.5 | mg/l
Total monthly flow | [7 empty] | 203.78 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 3737.5 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [18 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.856 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 13.79 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.4325 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 78.7 |  | PSIG | [11 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 8.16 | Std units
Monthly average of the daily flow rates | [7 empty] | 7.0269 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 11960 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 9.7348 |  | MG | [11 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 1.901 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 69.5 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [21 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.05 | mg/l
Monthly average pressure | [7 empty] | 45.0238 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 825 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 35.3 |  | PSIG | [11 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 165 | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.0825 | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [21 empty] | (Signature):
Date:
UNDERGROUND INJECTION CONTROL
MONTHLY OPERATING REPORT
[22 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
[22 empty] | Monitoring Well Decription: |  |  | LOWER ZONE OF MONITORING WELL MW-3
[22 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | UO-06-279510
[22 empty] | Monitoring Well ID #: |  |  | 5006A11310
[22 empty] | As Identified in Permit: |  | Monitor Well MW-3 Lower Monitor Zone |  |  |  | Issue Date: |  |  | 1997-07-21
[22 empty] | Monitoring Well Interval: |  |  | 1970 to 2027'
Associated Injection Well(s):
[22 empty] | Injection Well ID #: |  |  | Injection Well Description
[22 empty] | 5006A11310 |  |  | INJECTION WELL IW-3
[22 empty] | N/A |  |  | INJECTION WELL IW-4
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
[22 empty] | REPORT MONTH / YEAR: |  | 2003-03-01 | DATE OF SAP / RECORDING: |  |  | 2003-03-04 | 2003-03-11 | 2003-03-18 | 2003-03-25
[22 empty] | OPERATOR'S NAME: |  |  | BAYLER, J.
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
[22 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
[22 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
[22 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 45.33 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 28.13 | PSIG
[22 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 42.7786 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
[22 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 29256.5 | mg/l
[22 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 16050 | mg/l
[22 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 2.1125 | mg/l
[22 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 3.2625 | mg/l
[22 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7.42 | Std units
[22 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 44025 | umho/cm
[22 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
[22 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 67.75 | deg. F
[22 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.05 | mg/l
[22 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 2375 | mg/l
[22 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 810 | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.035 | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
Date:

## DEP FORMS
Department of Environmental Protection Discharge Monitoring Report - Part A
When Completed mail this report to: Department of Environmental Protection, Wastewater Facilities Management Section, MS 3551, 2600 Blair Stone Road, Tallahassee, FL 32399-2400
PERMITEE NAME: | City of Fort Lauderdale |  |  |  |  | PERMIT NUMBER: |  | FLA041378 |  | REPORT: | Monthly
MAILING ADDRESS: | 949 NW 38th Street |  |  |  |  | LIMIT: |  | Final |  | GROUP: | Domestic
| Fort Lauderdale, FL 33309 |  |  |  |  | CLASS SIZE: |  | N/A |  | GMS TEST SITE
[6 empty] | GMS ID NO. |  | 5006M02066 |  | NO:
FACILITY: | City of Fort Lauderdale G. T. Lohmeyer WWTF |  |  |  |  | MONITORING GROUP NUMBER: |  | U-001
LOCATION: | 1765 SE 18th Street |  |  |  |  | PLANT SIZE/TREATMENT TYPE: |  | IIA
Fort Lauderdale, FL 33316
COUNTY: | Broward | [5 empty] | MONITORING PERIOD: |  |  | 2003-03-01
Parameter |  | Quantity of Loading |  | Units |  | Quality or Concentration |  | Units | No. Ex. | Frequency of Analysis | Sample Type
Flow | Sample Measurement | 10.5722 | 7.6341 | [5 empty] | 0
PARM Code 50050 1 Mon.Site No. EFF-002 | Permit Requirement | 18.3 (Peak Hour.) | Report (Mo. Avg.) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
Flow | Sample Measurement | 11.1465 | 8.0386 | [5 empty] | 0
PARM Code 50050 1 Mon.Site No. EFF-003 | Permit Requirement | 18.3 (Peak Hour.) | Report (Mo. Avg.) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
Flow | Sample Measurement | 9.8534 | 7.0881 | [5 empty] | 0
PARM Code 50050 1 Mon.Site No. EFF-004 | Permit Requirement | 18.3 (Peak Hour.) | Report (Mo. Avg.) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
Flow | Sample Measurement | 0.15498 | 0.11172 | [5 empty] | 0
PARM Code 50050 1 Mon.Site No. EFF-005 | Permit Requirement | 18.0 (Peak Hour.) | Report (Mo. Avg.) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
Flow | Sample Measurement | 9.7348 | 7.0269 | [5 empty] | 0
PARM Code 50050 1 Mon.Site No. EFF-006 | Permit Requirement | 18.3 (Peak Hour.) | Report (Mo. Avg.) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
I certify under penalty of law that I have personally examined and am familiar with the informantion submitted herein; and based on my inquiry of those individuals immeadiately responsible for obtaining the information, I believe the submitted
information is true, accurate and complete. I am aware that there are significant penalties for submitting false information including the possiblity of fine and imprisonment.
NAME/TITLE OF PRINCIPAL EXECUTIVE OFFICER OR AUTHORIZED AGENT |  |  |  | SIGNATURE OF PRINCIPAL EXECUTIVE OFFICER OR AUTHORIZED AGENT |  |  |  |  | TELEPHONE |  | DATE (YY/MM/DD)
954-523-1002 ext 2021
REGIONAL WASTEWATER FACILITIES MANAGER
COMMENTS AND EXPLANATION OF ANY VIOLATIONS (Reference all attachments here):
Version 8/13/99
Department of Environmental Protection Discharge Monitoring Report - Part A (Continued)
[12 empty] | PERMITEE NAME: | City of Fort Lauderdale G. T. Lohmeyer WWTF |  |  |  | PERMIT NUMBER: |  | FLA041378 | MONITORING GROUP NUMBER: U-001 |  |  | REPORT: | Monthly
[20 empty] | MONITORING PERIOD: |  |  |  | 2003-03-01
[12 empty] | Parameter |  |  | Quantity of Loading |  | Units |  | Quality or Concentration |  | Units | No. Ex. | Frequency of Analysis | Sample Type
[12 empty] | BOD, Carbonaceous 5 day, 20C |  | Sample Measurement |  |  |  | 4.2 |  |  |  | 0
[12 empty] | PARM Code 80082 Y Mon.Site No. EFF-001 |  | Permit Requirement |  |  |  | 20.0 (An.Avg.) |  |  | mg/l |  | Daily | 24-hour FPC
[12 empty] | BOD, Carbonaceous 5 day, 20C |  | Sample Measurement |  |  |  | 5.6323 | 5.7236 | 8.58 |  | 0
[12 empty] | PARM Code 80082 1 Mon.Site No. EFF-001 |  | Permit Requirement |  |  |  | 30.0 (Mo.Avg.) | 45.0 (Week.Avg.) | 60.0 (Max.) | mg/l |  | Daily | 24-hour FPC
[12 empty] | Solids, Total Suspended |  | Sample Measurement |  |  |  | 13.4 |  |  |  | 0
[12 empty] | PARM Code 00530 Y Mon.Site No. EFF-001 |  | Permit Requirement |  |  |  | 20.0 (An.Avg.) |  |  | mg/l |  | Daily | 24-hour FPC
[12 empty] | Solids, Total Suspended |  | Sample Measurement |  |  |  | 14.5161 | 15.0629 | 27 |  | 0
[12 empty] | PARM Code 00530 1 Mon.Site No. EFF-001 |  | Permit Requirement |  |  |  | 30.0 (Mo.Avg.) | 45.0 (Week.Avg.) | 60.0 (Max.) | mg/l |  | Daily | 24-hour FPC
[12 empty] | pH |  | Sample Measurement |  |  |  | 6.2 |  |  |  | 0
[12 empty] | PARM Code 00400 1 Mon.Site No. EFF-001 |  | Permit Requirement |  |  |  | 6.0 (Min.) |  |  | s.u. |  | Continuous | Meter
[12 empty] | Flow |  | Sample Measurement | 32.2143 | 33.212 | [5 empty] | 0
[12 empty] | PARM Code 50050 G Mon.Site No. INF-001 |  | Permit Requirement | 43.0 (3-Mo.Avg.) | Report (Mo.Avg.) | mgd | [5 empty] | Continuous | Flow meters with 24-hour recording chart
[12 empty] | BOD, Carbonaceous 5 day, 20C |  | Sample Measurement |  |  |  | 101.7258 |  |  |  | N/A
[12 empty] | PARM Code 80082 G Mon.Site No. INF-002 |  | Permit Requirement |  |  |  | Report (Mo.Avg.) |  |  | mg/l |  | Daily | 24-hour FPC
[12 empty] | Solids, Total Suspended |  | Sample Measurement |  |  |  | 104.7097 |  |  |  | N/A
[12 empty] | PARM Code 00530 G Mon.Site No. INF-002 |  | Permit Requirement |  |  |  | Report (Mo.Avg.) |  |  | mg/l |  | Daily | 24-hour FPC
Version 8/13/99

## JULIAN CONVERT
2003-03-01 | 37681 | 1999-01-01 | 1520
FROM DATE ON "DATA INPUT" PAGE | [5 empty] | 2003-03-01
1999
MONTHYY.PAR RANGE TO COMPILE (JULIAN DAY VALUES) FOR SPLIT PROGRAM ARE | [7 empty] | 60 | THROUGH | 1552
|  | 3 | MARCH
[5 empty] | 2003-03-01 | 2003-03-01 | 3
2003-03-01 |  |  |  |  | 1 | JANUARY |  | 1995 | 1995-01-01
[5 empty] | 2 | FEBRUARY |  | 1996 | 1996-01-01
[5 empty] | 3 | MARCH |  | 1997 | 1997-01-01
MARCH |  | 1 |  | 3 | 4 | APRIL |  | 1998 | 1998-01-01
|  | 0 |  | 0 | 5 | MAY |  | 1999 | 1999-01-01
|  | 0 |  |  | 6 | JUNE |  | 2000 | 2000-01-01
|  | 0 |  |  | 7 | JULY |  | 2001 | 2001-01-01
|  | 0 |  | 0 | 8 | AUGUST |  | 2002 | 2002-01-01
|  |  |  | 3 | 9 | SEPTEMBER |  | 2003 | 2003-01-01
[5 empty] | 10 | OCTOBER |  | 2004 | 2004-01-01
[5 empty] | 11 | NOVEMBER |  | 2005 | 2005-01-01
2003 |  |  |  |  | 12 | DECEMBER |  | 2006 | 2006-01-01
37681 | [6 empty] | MARCH | 2007 | 2007-01-01
37622 | [7 empty] | 2008 | 2008-01-01
59 | 1 |  | 1 | 60 | Saturday
| 2 |  | 2 | 61 | Sunday
| 3 |  | 3 | 62 | Monday
| 4 |  | 4 | 63 | Tuesday
| 5 |  | 5 | 64 | Wednesday
| 6 |  | 6 | 65 | Thursday
| 7 |  | 7 | 66 | Friday
| 8 |  | 8 | 67 | Saturday
| 9 |  | 9 | 68 | Sunday
| 10 |  | 10 | 69 | Monday
| 11 |  | 11 | 70 | Tuesday
| 12 |  | 12 | 71 | Wednesday
| 13 |  | 13 | 72 | Thursday
| 14 |  | 14 | 73 | Friday
| 15 |  | 15 | 74 | Saturday
| 16 |  | 16 | 75 | Sunday
| 17 |  | 17 | 76 | Monday
| 18 |  | 18 | 77 | Tuesday
| 19 |  | 19 | 78 | Wednesday
| 20 |  | 20 | 79 | Thursday
| 21 |  | 21 | 80 | Friday
| 22 |  | 22 | 81 | Saturday
| 23 |  | 23 | 82 | Sunday
| 24 |  | 24 | 83 | Monday
| 25 |  | 25 | 84 | Tuesday
| 26 |  | 26 | 85 | Wednesday
| 27 |  | 27 | 86 | Thursday
| 28 |  | 28 | 87 | Friday
| 29 |  | 29 | 88 | Saturday
| 30 |  | 30 | 89 | Sunday
| 31 |  | 31 | 90 | Monday
31