## DATA INPUT
ENTER THE AVERAGE MONTHLY INFLUENT FLOW
INTO THE CORROSPONDING BOXES BELOW:
MAY | 33.744 | APRIL | 33.273
ENTER THE PRESENT MONTH AND YEAR IN BOX BELOW (A5) | [5 empty] | JUNE
2005-06-01 | [5 empty] | 2005
IW-1 | IW-2 | IW-3 | IW-4 | IW-5
36.14 | 36.72 | 37.65 | 38.22 | 36.64 | 2005-06-14
|  | ENTER INJECTION WELL SHUT-IN PRESSURE ABOVE |  |  | ENTER DATE OF SHUT-IN READINGS
ENTER SLUDGE DISPOSAL SITE FOR EACH WEEK BELOW
| WEEK 1 | WEEK 2 | WEEK 3 | WEEK 4
1 st | Central Sanitary Landfill | Central Sanitary Landfill | Central Sanitary Landfill | Central Sanitary Landfill
2 nd | Pompano Beach, FL | Pompano Beach, FL | Pompano Beach, FL | Pompano Beach, FL
RAW DATA REPORT ENTRY CATEGORIES
GTL PLANT DAILY PROCESS SUMMARY
[6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
TOTAL RAW INFLUENT FLOW (MGD) | [5 empty] | 42.712 | 46.568 | 47.958 | 45.725 | 48.199 | 48.32 | 44.575 | 42.458 | 41.712 | 42.112 | 51.15 | 49.335 | 45.518 | 42.822 | 40.675 | 40.132 | 42.276 | 45.26 | 45.708 | 45.815 | 47.854 | 45.069 | 46.868 | 57.594 | 52.491 | 48.201 | 48.385 | 50.065 | 52.667 | 49.039
TOTAL EFFLUENT FLOW (MGD) | [5 empty] | 42.258 | 46.344 | 48.351 | 45.119 | 46.856 | 47.233 | 44.157 | 42.319 | 41.63 | 41.833 | 49.977 | 48.848 | 45.477 | 42.77 | 39.974 | 39.552 | 42.865 | 45.212 | 45.151 | 44.925 | 46.964 | 44.967 | 46.928 | 57.462 | 51.617 | 46.987 | 48.647 | 50.085 | 52.267 | 48.179
MAXIMUM HOURLY RAW INFLUENT FLOW (MGD) | [5 empty] | 2.323 | 2.34 | 2.345 | 2.15 | 2.473 | 2.281 | 2.116 | 1.987 | 1.95 | 2.011 | 2.544 | 2.294 | 2.142 | 2.07 | 1.885 | 1.952 | 2.137 | 2.157 | 2.189 | 2.172 | 2.304 | 2.187 | 2.985 | 2.632 | 2.431 | 2.194 | 2.282 | 2.304 | 2.394 | 2.459
MAXIMUM INSTANANEOUS PEAK RAW INFUENT FLOW (MGD) | [5 empty] | 63.12 | 61.903 | 62.223 | 59.692 | 64.883 | 63.505 | 58.346 | 54.405 | 55.302 | 55.494 | 68.054 | 62.544 | 59.083 | 56.936 | 56.071 | 57.609 | 57.801 | 60.237 | 58.186 | 59.66 | 61.486 | 59.019 | 76.289 | 68.919 | 63.922 | 61.743 | 60.076 | 62.832 | 65.139 | 66.229
MINIMUM INSTANANEOUS PEAK RAW INFUENT FLOW (MGD) | [5 empty] | 12.239 | 24.735 | 29.349 | 23.299 | 22.396 | 28.74 | 25.023 | 20.665 | 23.613 | 20.089 | 26.273 | 33.513 | 25.087 | 26.497 | 17.717 | 20.121 | 18.807 | 24.382 | 26.85 | 25.6 | 31.785 | 23.177 | 25.023 | 44.088 | 35.821 | 30.951 | 28.676 | 28.292 | 37.551 | 27.875
TOTAL RETURN ACTIVATED SLUDGE FLOW (MGD) | [5 empty] | 13.621 | 13.202 | 13.58 | 13.206 | 12.227 | 12.636 | 13.747 | 14.153 | 14.263 | 14.23 | 13.054 | 12.712 | 13.955 | 14.073 | 13.268 | 13.525 | 13.743 | 13.018 | 13.088 | 13.239 | 12.669 | 12.563 | 12.546 | 12.785 | 12.645 | 12.913 | 13.745 | 12.982 | 12.869 | 13.634
TOTAL WASTE FLOW TO DEWATERING PROCESS (MG) | [5 empty] | 0.679 | 0.633 | 0.198 | 0 | 0.698 | 0.481 | 0.216 | 0.451 | 0.765 | 0.159 | 0 | 0.225 | 0.638 | 0.491 | 0.482 | 0.544 | 0.277 | 0 | 0.211 | 0.582 | 0.604 | 0.604 | 0.598 | 0.237 | 0 | 0.154 | 0.458 | 0.53 | 0.581 | 0.414
TOTAL DAILY RAINFALL | [5 empty] | 1.45 | 0.84 | 0.03 | 0.5 | 0.209 | 0 | 0.03 | 0.28 | 0.04 | 0.89 | 0.82 | 0 | 0 | 0.19 | 0 | 0.66 | 0.9 | 0.32 | 0.28 | 0.98 | 0.82 | 0.43 | 1.22 | 0.02 | 0 | 0 | 1.43 | 0.77 | 0.05 | 0.58
RAW INFLUENT pH | [5 empty] | 7 | 7 | 7.1 | 7 | NR | 7 | 7.1 | 7 | 7 | 7 | 7.1 | 7.2 | 7.1 | 7 | 7 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.2 | 7.2 | 7.1 | 7.1 | 7.1 | 7 | 7 | 7
RAW INFLUENT HYDROGEN SULFIDE (PPM) | [5 empty] | 6 | 3 | 3 | 5 | NR | 4 | 4 | 4 | 4 | 3 | 3 | 4 | 3 | 3 | 2 | 2 | 2 | 3 | 2 | 3 | 2 | 2 | 3 | 3 | 2 | 8 | 3 | 2 | 2 | 3
RAW INFLUENT TEMPERATURE (F ) | [5 empty] | 81.7 | 82 | 81 | 80 | NR | 80 | 81 | 80 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 82 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 80 | 81 | 82 | 81 | 81 | 80 | 82
TOTAL DAILY KILOWATTS (FPL POWER CONSUMPTION) | [5 empty] | 33078 | 33090 | 32310 | 32126 | 32310 | 31976 | 32742 | 32737 | 29159 | 29965 | 32686 | 32224 | 32249 | 32567 | 32565 | 32393 | 31995 | 32099 | 32430 | 32551 | 32337 | 32352 | 32004 | 32336 | 32182 | 32376 | 32348 | 32418 | 32000 | 32011
GTL PLANT DAILY PROCESS SUMMARY
(CONTINUED)
[6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
FINAL EFFLUENT FREE CHLORINE RESIDUAL (PPM) | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0
FINAL EFFLUENT TOTAL CHLORINE RESIDUAL (PPM) | [5 empty] | 0.8 | 0.8 | 1.5 | 1.3 | 1.1 | 1.2 | 1 | 1 | 1 | 1.1 | 1.3 | 1.2 | 1 | 0.9 | 1 | 1.1 | 0.8 | 1.2 | 1.2 | 0.9 | 0.9 | 0.9 | 1.4 | 1 | 1.1 | 1.3 | 1 | 1 | 0.8 | 1
FINAL EFFLUENT pH (daily average) | [5 empty] | 6.6 | 6.6 | 6.6 | 6.5 | 6.5 | 6.7 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.7 | 6.7 | 6.6 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7
FINAL EFFLUENT pH (daily minimum) | [5 empty] | 6.5 | 6.5 | 6.6 | 6.5 | 6.5 | 6.6 | 6.6 | 6.6 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.5 | 6.5 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
FINAL EFFLUENT pH (daily maximum) | [5 empty] | 6.7 | 6.7 | 6.7 | 6.6 | 6.6 | 6.8 | 6.8 | 6.6 | 6.7 | 6.6 | 6.7 | 6.6 | 6.6 | 6.7 | 6.7 | 6.7 | 6.7 | 6.6 | 6.6 | 6.7 | 6.6 | 6.6 | 6.8 | 6.8 | 6.8 | 7 | 6.7 | 6.7 | 6.7 | 6.8
FINAL EFFLUENT TEMPARTURE (F ) | [5 empty] | 84 | 84 | 84 | 84 | 84 | 84 | 83.8 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 85 | 85 | 84 | 84.1 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84
AVERAGE CLARIFIER BLANKET DEPTH (INCHES) | [5 empty] | 41 | 33 | 38 | 55 | 44 | 33 | 40 | 33 | 30 | 35 | 49 | 16 | 32 | 26 | 24 | 22 | 23 | 34 | 28 | 25 | 20 | 17 | 0 | 19 | 23 | 20 | 21 | 14 | 12 | 14
FINAL EFFLUENT SAMPLE TEMPARTURE (C ) | [5 empty] | 2 | 3 | 5 | 5 | 2 | 3 | 3 | 3 | 3 | 1.2 | 3.3 | 3 | 3 | 3 | 3 | 2 | 0.5 | 1.6 | 3 | 3 | 3 | 2 | 0 | 0 | 2.5 | 0 | 3 | 3 | 3 | 2
TOTAL RETURN ACTIVATED SLUDGE FLOW TO REACTOR ONE (MGD) | [5 empty] | 6.187 | 6.278 | 6.305 | 6.441 | 6.189 | 6.148 | 6.344 | 6.388 | 6.417 | 6.37 | 6.358 | 6.231 | 6.548 | 6.46 | 6.234 | 6.183 | 6.33 | 6.281 | 6.132 | 6.235 | 6.397 | 6.496 | 6.447 | 6.459 | 6.343 | 6.294 | 6.121 | 6.237 | 6.369 | 6.259
TOTAL RETURN ACTIVATED SLUDGE FLOW TO REACTOR TWO (MGD) | [5 empty] | 7.434 | 6.925 | 7.276 | 6.765 | 6.037 | 6.488 | 7.403 | 7.765 | 7.846 | 7.86 | 6.696 | 6.48 | 7.408 | 7.613 | 7.034 | 7.342 | 7.413 | 6.736 | 6.907 | 7.004 | 6.272 | 6.067 | 6.099 | 6.326 | 6.302 | 6.618 | 7.624 | 6.745 | 6.499 | 7.375
GTL PLANT DAILY PROCESS SUMMARY
CONTINUED
[6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
TOTAL DAILY TRUCKING LOAD OF DEWATERED SLUDGE REMOVED | [5 empty] | 4 | 6 | 4 | 0 | 0 | 2 | 5 | 4 | 6 | 5 | 0 | 0 | 4 | 6 | 3 | 3 | 5 | 0 | 0 | 5 | 5 | 6 | 5 | 5 | 0 | 0 | 5 | 5 | 4 | 3
TOTAL DAILY HYDROGEN PEROXIDE CONSUMED (LBS) | [5 empty] | 1357 | 150 | 319 | 190 | 200 | 0 | 0 | 0 | 978 | 1787 | 1497 | 1946 | 1677 | 1866 | 1677 | 1148 | 1327 | 639 | 170 | 1397 | 279 | 529 | 568 | 180 | 0 | 0 | 390 | 0 | 0 | 0
TOTAL DAILY CHLORINE CONSUMED (LBS) | [5 empty] | 1400 | 1640 | 1360 | 1420 | 1520 | 1400 | 1240 | 680 | 1540 | 1580 | 1520 | 1520 | 1360 | 840 | 1280 | 1440 | 1260 | 1380 | 1500 | 1360 | 1480 | 1320 | 1600 | 1400 | 1460 | 900 | 1560 | 1420 | 1400 | 1480
TOTAL DAILY POLYMER CONSUMED (GALS) | [5 empty] | 38 | 85 | 16 | 17 | 68 | 87 | 39 | 51 | 168 | 45 | 0 | 32 | 143 | 105 | 17 | 103 | 51 | 0 | 68 | 43 | 83 | 109 | 113 | 0 | 0 | 0 | 84 | 107 | 66 | 96
TOTAL TONS OF LIME DELIVERED DAILY | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTAL DAILY GASIOUS OXYGEN PRODUCED (TONS) | [5 empty] | 34.2 | 27.8 | 24.5 | 24.8 | 30.5 | 29.9 | 31.7 | 31.4 | 30.3 | 29.6 | 32 | 33.3 | 32.2 | 30.1 | 22.7 | 22.3 | 22.7 | 24.3 | 29.2 | 27.6 | 22.8 | 22 | 24.2 | 18.5 | 19.3 | 24.5 | 20.5 | 27.6 | 23.2 | 19.8
AVERAGE PERCENT OXYGEN PRODUCT PURITY | [5 empty] | 99 | 100 | 100 | 100 | 99 | 99 | 99 | 99 | 96 | 100 | 98 | 95 | 99 | 100 | 100 | 100 | 100 | 99 | 99 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
TOTAL DAILY LIQUID OXYGEN IN STORAGE (TONS) | [5 empty] | 97.7 | 99.8 | 98.7 | 96.9 | 96.5 | 96.4 | 97.1 | 97.7 | 96.4 | 94.8 | 94.6 | 93.4 | 93.6 | 93.2 | 93.2 | 93.5 | 94.3 | 94.6 | 94.9 | 95.4 | 95.4 | 95.9 | 96.1 | 96.3 | 97.7 | 98.5 | 98.6 | 100 | 101.4 | 101.5
MONITORING WELL PRESSURE DATA
MONITORING WELL ONE UPPER/LOWER LEVEL
| MW-1 |  | UPPER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
MINIMUM | [5 empty] | 48.09 | 48.09 | 48.18 | 48.19 | 48.25 | 40.7 | 41.07 | 48.52 | 48.58 | 48.68 | 48.75 | 48.77 | 43.02 | 43.47 | 48.78 | 48.82 | ER | 48.85 | 48.83 | 44.13 | 44.43 | 48.77 | 48.87 | 49.09 | 49.13 | 49.07 | 41.69 | 42.13 | 49.05 | 49.1
MAXIMUM | [5 empty] | 48.39 | 48.44 | 48.54 | 48.56 | 48.59 | 48.52 | 49.01 | 48.83 | 48.85 | 48.92 | 48.96 | 48.96 | 48.98 | 49.16 | 49 | 49.09 | 49.15 | 49.18 | 49.16 | 49.06 | 49.29 | 49.18 | 49.33 | 49.46 | 49.46 | 49.41 | 49.33 | 49.37 | 49.36 | 49.45
AVERAGE | [5 empty] | 48.24 | 48.29 | 48.38 | 48.39 | 48.44 | 43.36 | 46.4 | 48.68 | 48.68 | 48.77 | 48.91 | 48.92 | 44.81 | 47.39 | 48.93 | 48.95 | 48.86 | 49 | 49 | 46.08 | 47.51 | 48.97 | 49.09 | 49.21 | 49.29 | 49.19 | 44.27 | 47 | 49.19 | 49.29
| MW-1 |  | LOWER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
MINIMUM | [5 empty] | 40.67 | 40.69 | 41.99 | 41.53 | 41.46 | 38.15 | 37.1 | 40.22 | 41.94 | 42.05 | 42.37 | 42.8 | 39 | 38.41 | 41.12 | 41.05 | ER | 42.79 | 41.87 | 39.02 | 38.41 | 40.76 | 41.33 | 42.32 | 42.98 | 43.38 | 39.2 | 38.68 | 40.46 | 41.83
MAXIMUM | [5 empty] | 43.53 | 44.33 | 45.18 | 44.13 | 45.19 | 44.77 | 40.83 | 44.3 | 44.11 | 43.47 | 45.37 | 46.05 | 43.94 | 42.94 | 44.62 | 46.59 | 45.69 | 46.19 | 46.89 | 43.32 | 42.52 | 43.37 | 45.98 | 46.11 | 46.65 | 45.97 | 45.23 | 42.92 | 44.75 | 45.77
AVERAGE | [5 empty] | 41.8 | 42.37 | 43.46 | 42.97 | 42.88 | 41.65 | 39.22 | 42.16 | 42.77 | 42.81 | 43.52 | 44.03 | 42.3 | 40.79 | 42.93 | 43.15 | 43.31 | 43.81 | 43.79 | 41.44 | 40.4 | 42.01 | 43.55 | 44.03 | 44.48 | 44.27 | 42.23 | 40.76 | 42.75 | 43.62
MONITORING WELL TWO UPPER/LOWER LEVEL
| MW-2 |  | UPPER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
MINIMUM | [5 empty] | 28.7 | 28.65 | 29.22 | 29.16 | 29.26 | 25.15 | 24.9 | 29.55 | 29.99 | 29.86 | 30.1 | 30.45 | 25.59 | 25.41 | 30.29 | 30.04 | ER | 30.74 | 30.47 | 25.22 | 25 | 30.12 | 30.37 | 30.66 | 30.96 | 31.23 | 25.8 | 25.92 | 30.66 | 31.14
MAXIMUM | [5 empty] | 29.86 | 30.15 | 30.78 | 30.26 | 30.53 | 30.05 | 30.49 | 30.76 | 30.77 | 30.51 | 31.2 | 31.5 | 30.66 | 31.18 | 31.65 | 32.11 | 32.06 | 32.04 | 31.99 | 30.86 | 30.88 | 31.22 | 31.69 | 32.07 | 32.59 | 32.4 | 31.56 | 31.99 | 32.17 | 32.68
AVERAGE | [5 empty] | 29.22 | 29.37 | 29.88 | 29.77 | 29.74 | 27.06 | 28.52 | 30.2 | 30.34 | 30.23 | 30.54 | 30.85 | 27.65 | 29.17 | 30.87 | 30.9 | 30.96 | 31.19 | 31.12 | 27.68 | 28.93 | 30.6 | 31.01 | 31.38 | 31.76 | 31.76 | 28.27 | 29.68 | 31.44 | 31.65
| MW-2 |  | LOWER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
MINIMUM | [5 empty] | 42.56 | 42.62 | 42.77 | 42.78 | 42.86 | 37.09 | 37.06 | 42.7 | 42.88 | 43.02 | 43.1 | 43.13 | 37.85 | 37.83 | 42.89 | 43.03 | ER | 43.18 | 43.22 | 35.69 | 35.63 | 42.82 | 43.05 | 43.26 | 43.36 | 43.33 | 35.06 | 35.04 | 42.99 | 43.14
MAXIMUM | [5 empty] | 42.76 | 42.84 | 42.96 | 42.98 | 43.01 | 43.01 | 42.71 | 42.94 | 43.04 | 43.17 | 43.2 | 43.22 | 43.26 | 42.89 | 43.08 | 43.24 | 43.31 | 43.37 | 43.37 | 43.34 | 42.84 | 43.09 | 43.29 | 43.46 | 43.47 | 43.48 | 43.47 | 42.99 | 43.22 | 43.35
AVERAGE | [5 empty] | 42.58 | 42.81 | 42.89 | 42.91 | 42.96 | 38.95 | 40.89 | 42.85 | 42.97 | 43.01 | 43.08 | 43.12 | 39.41 | 41.37 | 42.99 | 43.03 | 43.08 | 43.35 | 43.37 | 38.74 | 40.51 | 42.94 | 43.11 | 43.36 | 43.47 | 43.46 | 37.73 | 40.48 | 43.02 | 43.35
MONITORING WELL THREE UPPER/LOWER LEVEL
| MW-3 |  | UPPER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
MINIMUM | [5 empty] | 32.92 | 33.09 | 33.3 | 33.35 | 33.45 | 17.9 | 17.82 | 32.87 | 33.09 | 33.21 | 33.3 | 33.4 | 17.99 | 17.92 | 33.08 | 33.23 | ER | 33.4 | 33.44 | 17.98 | 17.93 | 33.16 | 33.4 | 33.66 | 33.79 | 33.72 | 18.08 | 18.03 | 33.4 | 33.59
MAXIMUM | [5 empty] | 33.29 | 33.43 | 33.61 | 33.67 | 33.72 | 33.65 | 32.95 | 33.23 | 33.32 | 33.45 | 33.56 | 33.58 | 33.61 | 33.09 | 33.34 | 33.51 | 33.63 | 33.7 | 33.7 | 33.6 | 33.25 | 33.55 | 33.81 | 34.04 | 34.04 | 34 | 33.94 | 33.41 | 33.74 | 33.91
AVERAGE | [5 empty] | 33.09 | 33.31 | 33.42 | 33.46 | 33.52 | 22.81 | 28.18 | 32.97 | 33.17 | 33.31 | 33.45 | 33.49 | 22.08 | 28.42 | 33.17 | 33.39 | 33.43 | 33.53 | 33.54 | 23.78 | 28.16 | 33.31 | 33.53 | 33.79 | 33.95 | 33.88 | 22.95 | 28.47 | 33.53 | 33.79
| MW-3 |  | LOWER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
MINIMUM | [5 empty] | 45.23 | 45.33 | 45.47 | 45.51 | 45.6 | 36.44 | 36.44 | 45.37 | 45.59 | 45.73 | 45.83 | 45.86 | 38.01 | 38.02 | 45.56 | 45.73 | ER | 45.89 | 45.98 | 35.51 | 35.49 | 45.52 | 45.76 | 45.99 | 46.1 | 46.09 | 36.83 | 36.87 | 45.7 | 45.86
MAXIMUM | [5 empty] | 45.44 | 45.53 | 45.65 | 45.7 | 45.73 | 45.73 | 45.37 | 45.62 | 45.73 | 45.86 | 45.91 | 45.95 | 45.99 | 45.56 | 45.79 | 45.95 | 46.04 | 46.13 | 46.11 | 46.08 | 45.52 | 45.79 | 46 | 46.17 | 46.2 | 46.21 | 46.2 | 45.7 | 45.94 | 46.09
AVERAGE | [5 empty] | 45.39 | 45.47 | 45.52 | 45.52 | 45.58 | 39.37 | 42.57 | 45.47 | 45.58 | 45.81 | 45.91 | 45.95 | 40.11 | 43.22 | 45.65 | 45.88 | 45.82 | 46 | 46.02 | 39.45 | 42.27 | 45.64 | 45.87 | 46 | 46.08 | 46.09 | 39.82 | 42.79 | 45.87 | 45.98
MONITORING WELL RMW-1 UPPER/LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
[5 empty] | JULIAN DATE | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180 | 181
| RMW-1 |  | UPPER LEVEL
MINIMUM | [5 empty] | 1 152: 44.54
MAXIMUM | [5 empty] | 1 152: 44.64
AVERAGE | [5 empty] | 1 152: 44.59
| RMW-1 |  | LOWER LEVEL
MINIMUM | [5 empty] | 1 152: 22.53
MAXIMUM | [5 empty] | 1 152: 22.68
AVERAGE | [5 empty] | 1 152: 22.63
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
| INJECTION WELL ONE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 14.73 | 12.5 | 15.22 | 14.26 | 15.29 | 14.29 | 12.64 | 14.44 | 13.99 | 13.46 | 15.16 | 13.12 | 14.52 | 14.49 | 13.98 | 12.61 | 9.63 | 14.7 | 13.91 | 14.44 | 14.82 | 12.99 | 15.92 | 14.81 | 14.66 | 14.38 | 10.85 | 15.23 | 14.94 | 15.96
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 5.87 | 0 | 0 | 4.87 | 7.98 | 7.6 | 0 | 0.01 | 0.01 | 7.94 | 8.67 | 0.01 | 0.01 | 0 | 6.32 | 6.6 | 0 | 0 | 8.08 | 7.89 | 8.72 | 0 | 0 | 9.47 | 8.3 | 7.51 | 0 | 0 | 10.53 | 0.01
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 10.99 | 5.18 | 10.54 | 11.63 | 12.09 | 12.07 | 2.65 | 9.08 | 10.13 | 11.18 | 12.62 | 0.96 | 10.87 | 9.41 | 10.63 | 10.36 | 0.16 | 9.89 | 11.85 | 12.03 | 12.08 | 3.02 | 10.63 | 12.28 | 11.94 | 11.92 | 0.67 | 12.28 | 13.5 | 12.06
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 70.8 | 60.6 | 71 | 67.34 | 72.7 | 68.18 | 61.19 | 67.91 | 65.13 | 64.71 | 72 | 64.43 | 68.28 | 69.61 | 66.86 | 62.06 | 55.76 | 69.44 | 65.72 | 68.77 | 71 | 63.23 | 76 | 70.8 | 70.2 | 68.47 | 56.12 | 70.5 | 70 | 73.5
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 42.37 | 36.13 | 36.41 | 45.68 | 47.4 | 46.73 | 36.06 | 35.62 | 35.6 | 47.39 | 50.33 | 36.21 | 36.54 | 35.85 | 44.01 | 44.74 | 0 | 36.15 | 48.34 | 46.7 | 48.89 | 36.61 | 35.9 | 53.13 | 48.17 | 47.44 | 36.25 | 36.78 | 54.91 | 36.88
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 56.45 | 45.8 | 56.61 | 58.23 | 59.74 | 59.84 | 41.36 | 53.13 | 54.21 | 56.75 | 62.37 | 38.92 | 57.43 | 53.64 | 55.28 | 54.56 | 37.5 | 55.76 | 58.9 | 59.3 | 60 | 42.46 | 57.36 | 61.45 | 60.05 | 59.82 | 38.35 | 62.26 | 64.78 | 60.91
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
| INJECTION WELL TWO |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 15 | 15.21 | 14.29 | 14.72 | 15.57 | 14.55 | 14.38 | 13.69 | 13.04 | 13.69 | 15.36 | 15.45 | 12.12 | 14.87 | 12.63 | 12.82 | 15.43 | 13.27 | 14.26 | 14.8 | 15.11 | 15.59 | 16.06 | 15.09 | 14.88 | 14.54 | 15.47 | 12.22 | 15.11 | 16.01
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 5.89 | 8.29 | 0.05 | 0.05 | 0.05 | 7.61 | 9.47 | 0.05 | 0.05 | 0.05 | 8.93 | 8.39 | 0.05 | 0.05 | 0.05 | 6.71 | 0 | 0.05 | 0.05 | 0.05 | 8.83 | 8.24 | 0.05 | 8.76 | 8.43 | 7.53 | 9.23 | 0.05 | 0.05 | 0.05
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 11.21 | 12.27 | 4.7 | 10.55 | 10.1 | 12.3 | 12.37 | 2.71 | 8.75 | 9.32 | 12.85 | 13.36 | 0.74 | 9.03 | 8.72 | 10.56 | 12.97 | 2.6 | 10.11 | 10.02 | 12.31 | 12.47 | 3.04 | 12.43 | 12.13 | 12.14 | 13.35 | 0.81 | 12.5 | 12.25
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 69.64 | 68.19 | 63.97 | 66.17 | 71.4 | 66.95 | 64.62 | 61.54 | 60.61 | 63.56 | 70.8 | 69.31 | 58.76 | 69.19 | 60.13 | 60.76 | 69.32 | 61.36 | 64.7 | 67.76 | 69.88 | 70.9 | 74.8 | 69.6 | 69.07 | 67.42 | 69.14 | 58.05 | 68.38 | 71.2
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 41.75 | 46.79 | 36.65 | 36.93 | 36.57 | 46.1 | 50.12 | 37.06 | 35.88 | 36.71 | 49.63 | 48.5 | 37.2 | 36.46 | 36.97 | 44.06 | 0 | 36.88 | 37.27 | 36.84 | 48.26 | 47.96 | 36.5 | 52.21 | 47.41 | 46.68 | 49.27 | 37.31 | 37.86 | 38.43
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 55.6 | 58.5 | 45.14 | 55.02 | 55.25 | 59.02 | 58.06 | 41.5 | 50.83 | 52.6 | 61.38 | 62.06 | 39.01 | 51.96 | 50.87 | 53.58 | 60.51 | 42.07 | 54.48 | 54.66 | 59 | 58.96 | 43.52 | 60.33 | 59.04 | 58.88 | 61.78 | 39.4 | 61.33 | 59.88
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
| INJECTION WELL THREE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 13.94 | 13.56 | 14.06 | 11.82 | 14.65 | 13.57 | 12.94 | 13.31 | 13.95 | 12.95 | 14.22 | 14.02 | 13.48 | 13.31 | 12.03 | 12.06 | 13.9 | 13.69 | 10.78 | 13.93 | 14.06 | 14.09 | 14.86 | 13.66 | 14.02 | 13.62 | 13.94 | 14.12 | 12.58 | 15.97
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 5.98 | 8.04 | 7.09 | ER | ER | 4.72 | 9.1 | 8.74 | ER | ER | ER | 7.97 | 8.74 | ER | ER | ER | 0 | 7.74 | ER | ER | ER | 8.1 | 7.73 | ER | ER | ER | 8.61 | 9.66 | ER | ER
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 10.64 | 11.31 | 11.26 | 0.64 | 9.13 | 11.58 | 11.37 | 10.98 | 1.46 | 8.49 | 11.87 | 12.13 | 11.43 | 2.6 | 7.96 | 8.27 | 11.74 | 11.27 | 0.61 | 9.08 | 9.36 | 11.51 | 11.47 | 9.6 | 11.22 | 11.37 | 12.16 | 12.64 | 0.74 | 10
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 71 | 69.46 | 71.1 | 61.53 | 73 | 68.25 | 65.78 | 67.69 | 69.72 | 64.93 | 72.3 | 70.6 | 68.37 | 67.28 | 61.4 | 61.97 | 70.6 | 69.66 | 57.67 | 69.29 | 71.3 | 72.2 | 76.4 | 70.2 | 70.5 | 68.76 | 70.4 | 70.7 | 64.18 | 79.2
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 42.58 | 47.74 | 46.39 | 37.56 | 37.13 | 44.78 | 51.14 | 50.41 | 37.45 | 37.14 | 37.7 | 49.45 | 50.79 | 37.79 | 37.54 | 37.05 | 0 | 48.66 | 38.07 | 37.54 | 37.38 | 48.94 | 47.68 | 39.85 | 39.86 | 38.06 | 50.24 | 53.06 | 38.9 | 37.87
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 56.73 | 59.65 | 59.63 | 39.69 | 55.8 | 60.13 | 59.19 | 57.79 | 41.08 | 53.09 | 62.22 | 63.19 | 60.09 | 43.7 | 51.37 | 51.73 | 61.53 | 59.7 | 39.97 | 55.25 | 55.88 | 60.07 | 60.4 | 57.15 | 59.7 | 59.72 | 62.96 | 64.87 | 41.21 | 58.13
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
FUTURE
| INJECTION WELL FOUR |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 14.6 | 13.88 | 14.29 | 13.98 | 12.82 | 14 | 13.09 | 13.49 | 14.03 | 12.51 | 14.84 | 14.56 | 13.75 | 14.12 | 13.57 | 12.66 | 14.06 | 13.8 | 13.54 | 13.72 | 14.47 | 14.31 | 15.06 | 14.34 | 12.67 | 14.04 | 14.23 | 14.15 | 14.49 | 15.95
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 0.04 | 0.04 | 7.23 | 8.6 | 0.03 | 0.04 | 0.04 | 8.84 | 7.31 | 0.04 | 0.04 | 4.98 | 8.94 | 6.24 | 0.04 | 0.04 | 0 | 7.82 | 8.25 | 0.04 | 0.03 | 0.04 | 7.78 | 9.3 | 0.05 | 0.05 | 6.14 | 9.7 | 10.46 | 0.04
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 9.47 | 9.48 | 11.43 | 11.49 | 4.53 | 10.08 | 9.37 | 11.11 | 10.97 | 2.48 | 9.87 | 12.28 | 11.58 | 11.19 | 2.55 | 8.26 | 11.93 | 11.41 | 11.63 | 2.68 | 9.11 | 9.53 | 11.57 | 11.84 | 5.04 | 9.9 | 12.36 | 12.74 | 13.11 | 2.45
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 71.3 | 69.93 | 71.6 | 68.14 | 62.87 | 68.73 | 66.34 | 68.24 | 70.2 | 62.28 | 72.7 | 71.1 | 68.77 | 64.71 | 67.52 | 62.37 | 71.2 | 70.2 | 66.65 | 66.62 | 71.8 | 72.7 | 76.9 | 71.6 | 64.58 | 69.25 | 70.8 | 71.2 | 70.9 | 79.6
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 36.32 | 36.75 | 47.05 | 49.59 | 37.57 | 36.89 | 36.8 | 51.03 | 46.84 | 37.7 | 37.2 | 46.28 | 51.38 | 46.74 | 37.87 | 37.16 | 0 | 49.32 | 49.22 | 38.07 | 37.19 | 37.15 | 48.36 | 53.9 | 38.98 | 37.35 | 45.57 | 53.7 | 55.74 | 38.03
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 54.85 | 56.39 | 60.27 | 59.29 | 46.6 | 57.21 | 55.74 | 58.38 | 57.18 | 42.58 | 58.27 | 63.58 | 60.68 | 58.52 | 42.86 | 51.66 | 62.26 | 60.37 | 59.78 | 43.26 | 55.45 | 56.72 | 61 | 62.19 | 47.88 | 56.83 | 63.37 | 65.44 | 65.7 | 44.18
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
| INJECTION WELL FIVE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 8.51 | 12.94 | 13.42 | 13.02 | 14.17 | 11.1 | 12.3 | 12.68 | 13.19 | 12.52 | 12.01 | 13.19 | 12.78 | 13.18 | 12.63 | 11.75 | 13.17 | 12.95 | 12.65 | 13.47 | 13.01 | 13.44 | 14.11 | 13.37 | 13.48 | 12.51 | 13.18 | 13.28 | 13.48 | 14.33
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | ER | ER | ER | 8.09 | 7.91 | ER | ER | ER | 6.91 | 7.81 | ER | ER | 5.26 | 6.67 | 6.29 | ER | 0 | ER | 7.75 | 7.56 | ER | ER | 6.23 | 8.79 | 7.83 | ER | ER | 6.58 | 9.8 | 0.18
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 0.29 | 8.43 | 10.34 | 10.75 | 11.22 | 1.16 | 8.35 | 8.53 | 10.28 | 10.51 | 3.08 | 10.04 | 10.83 | 10.53 | 10.07 | 2.19 | 11.06 | 10.14 | 10.87 | 11.23 | 4.17 | 8.46 | 10.85 | 11.12 | 11.05 | 1.59 | 10.24 | 11.93 | 12.24 | 11.49
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 57.32 | 69.01 | 70.7 | 67.06 | 72.4 | 59 | 65.29 | 67.25 | 69.34 | 64.38 | 65.07 | 70 | 67.91 | 69.13 | 66.5 | 60.44 | 70.2 | 69.19 | 65.52 | 68.7 | 65.75 | 71.7 | 76 | 70.5 | 69.89 | 63.68 | 69.97 | 70.2 | 69.87 | 73.7
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 34.75 | 34.95 | 37.26 | 48.56 | 47.39 | 35.88 | 35.42 | 36.6 | 45.82 | 47.6 | 36.13 | 37.1 | 46.87 | 48.39 | 43.9 | 36.81 | 0 | 37.59 | 48.23 | 46.58 | 36.85 | 35.49 | 47.35 | 52.96 | 48.11 | 36.34 | 36.87 | 49.62 | 54.74 | 37.76
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 37.23 | 54.64 | 58.39 | 58.25 | 59.67 | 39.48 | 53.9 | 53.88 | 56.12 | 56.6 | 43.82 | 59.55 | 59.57 | 57.57 | 54.98 | 40.81 | 60.99 | 58.19 | 58.75 | 59.2 | 45.53 | 54.8 | 59.91 | 61.18 | 59.81 | 40.65 | 60 | 64.35 | 64.61 | 61.42
GTL DAILY LABORATORY ANALYSIS REPORT DATA
| RAW INFLUENT DATA |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
RAW TOTAL SUSPENDED SOLIDS | [5 empty] | 200 | 90 | 38 | 70 | 68 | 78 | 84 | 78 | 42 | 60 | 118 | 80 | 108 | 84 | 100 | 108 | 94 | 76 | 74 | 114 | 98 | 88 | 70 | 118 | 16 | 68 | 78 | 70 | 42 | 40
RAW FIXED SUSPENDED SOLIDS | [5 empty] | 22 | 14 | 15 | 16 | 4 | 2 | 4 | 16 | 0 | 0 | 24 | 8 | 12 | 16 | 16 | 18 | 8 | 14 | 10 | 32 | 28 | 6 | 12 | 22 | 14 | 8 | 2 | 0 | 30 | 0
RAW ALKILINITY | [5 empty] | 202 | 194 | 202 | 190 | 192 | 192 | 202 | 210 | 192 | 189 | 190 | 212 | 218 | 218 | 222 | 210 | 192 | 206 | 208 | 206 | 208 | 202 | 202 | 206 | 198 | 7.28 | 194 | 184 | 202 | 190
RAW CHLORIDES | [5 empty] | 720 | 660 | 620 | 630 | 580 | 620 | 620 | 680 | 600 | 530 | 420 | 440 | 480 | 500 | 580 | 530 | 500 | 510 | 610 | 610 | 580 | 460 | 510 | 400 | 430 | 430 | 450 | 410 | 370 | 360
RAW COD | [5 empty] | 129 | 113 | 93 | 132 | 102 | 93 | 98 | 107 | 100 | 110 | 99 | 95 | 102 | 116 | 115 | 162 | 173 | 167 | 311 | 106 | 97 | 98 | 103 | 111 | 96 | 129 | 102 | 94 | 106 | 97
RAW CBOD | [5 empty] | 79.5 | 61 | 74.36 | 52.28 | 22.47 | 38.53 | 44 | 53.8 | 71.8 | 86.4 | 48.8 | 72.28 | 81.6 | 83.6 | 92.7 | 89.9 | 85.8 | 87.3 | 83.1 | 44.4 | 69.5 | 44.6 | 41.2 | 67 | 34.4 | 34 | LS | 11 | 34 | 10
RAW SUFATES | [5 empty] | 132.5 | 131 | 130.5 | 137.8 | 135.5 | 131.3 | 133.5 | 144 | 129 | 112.5 | 103.3 | 105.5 | 108.5 | 120 | 113 | 122.8 | 128.3 | 122 | 131.8 | 117 | 111.3 | 107 | 107.3 | 97.3 | 99.5 | 109 | 108.8 | 108 | 102.8 | 104
| EFFLUENT DATA |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
EFFLUENT TOTAL DISSOLVED SOLIDS | [5 empty] | 1591 | 1326 | 1251 | 1294 | 1253 | 1148 | 1210 | 1304 | 1231 | 1084 | 979 | 938 | 1076 | 1054 | 1222 | 1084 | 1171 | 1105 | 1311 | 1375 | 1211 | 996 | 990 | 888 | 877 | 963 | 960 | 926 | 759 | 778
EFFLUENT TOTAL SUSPENDED SOLIDS | [5 empty] | 11 | 15 | 6 | 17 | 10 | 8 | 13 | 3 | 9 | 14 | 22 | 9 | 10 | 10 | 11 | 12 | 8 | 12 | 12 | 18 | 21 | 12 | 5 | 12 | 4 | 8 | 11 | 8 | 10 | 2
EFFLUENT FIXED SUSPENDED SOLIDS | [5 empty] | 0 | 2 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 1 | 2 | 5 | 4 | 2 | 0 | 2 | 2 | 7 | 9 | 0 | 1 | 2 | 11 | 0 | 0 | 0 | 9 | 0
EFFLUENT ALKILINITY | [5 empty] | 190 | 186 | 184 | 186 | 184 | 178 | 188 | 198 | 186 | 184 | 178 | 182 | 194 | 196 | 192 | 196 | 200 | 198 | 194 | 192 | 194 | 188 | 186 | 188 | 189 | 178 | 216 | 180 | 190 | 186
EFFLUENT TURBIDITY | [5 empty] | 7.9 | 6.4 | 6.23 | 8.32 | 6.75 | 4.85 | 5.16 | 3.32 | 5.08 | 5.34 | 5.6 | 3.75 | 4.94 | 8.63 | 3.5 | 4.54 | 4.8 | 4.63 | 4.78 | 4.16 | 6.5 | 4.58 | 3.31 | 6.95 | 5.48 | 4.98 | 4.86 | 5.47 | 6.05 | 6.31
EFFLUENT CHLORIDES | [5 empty] | 800 | 680 | 620 | 630 | 610 | 600 | 610 | 630 | 630 | 540 | 490 | 420 | 490 | 500 | 510 | 520 | 520 | 490 | 600 | 630 | 560 | 510 | 480 | 390 | 400 | 440 | 450 | 430 | 370 | 380
EFFLUENT CONDUCTIVITY | [5 empty] | 3110 | 2690 | 2520 | 2550 | 2490 | 2380 | 2450 | 2500 | 2490 | 2250 | 1988 | 1869 | 2020 | 2110 | 2110 | 2150 | 2170 | 2160 | 2410 | 2580 | 2320 | 2050 | 2040 | 1682 | 1803 | 1912 | 1936 | 1866 | 1672 | 1726
EFFLUENT TOTAL BACTERIA COUNT | [5 empty] | 170 | TNTC | 300 | 0 | 18 | 410 | 4200 | TNTC | TNTC | 64 | 41 | 9 | 9 | TNTC | 0 | 9 | TNTC | 0 | 16 | 18 | 0 | TNTC | 0 | 117 | 455 | 0 | 9 | 9 | 18 | 63
EFFLUENT FECAL BACTERIA COUNT | [5 empty] | 0 | 179 | 0 | 0 | 0 | 0 | 18 | TNTC | TNTC | 0 | 0 | 0 | 0 | TNTC | 0 | 0 | TNTC | 0 | 0 | 0 | 0 | 26 | 0 | 9 | 0 | 9 | 0 | 0 | 0 | 9
EFFLUENT COD | [5 empty] | 22.1 | 38.9 | 40.8 | 37.8 | 36.5 | 36.5 | 37.5 | 25.3 | 39.9 | 41.5 | 39.3 | 37.6 | 39.1 | 39.2 | 43.2 | 44.5 | 41.7 | 44.6 | 54.6 | 39.7 | 42.7 | 40.7 | 48.4 | 22.2 | 38.5 | 38.6 | 40.3 | 40.8 | 40.9 | 39.3
EFFLUENT CBOD | [5 empty] | 3.94 | 2.64 | 3.69 | 2.35 | 2 | 2.33 | 2 | 2.3 | 2.21 | 2 | 1.99 | 2.22 | 2.23 | 2.64 | 2 | 2.19 | 2.91 | 2.71 | 2.43 | 2 | 2.8 | 2 | 2 | 2.85 | 2 | 2 | LS | 2 | 2 | 5
EFFLUENT SULFATES | [5 empty] | 134.5 | 123.5 | 124.3 | 120 | 110.8 | 121 | 108.5 | 106.8 | 122 | 126 | 110.5 | 95.5 | 109.8 | 108.8 | 97.8 | 106 | 111.5 | 112.3 | 120 | 113.5 | 107.8 | 99 | 96.8 | 92.3 | 89.8 | 81.8 | 96.3 | 100.3 | 85.5 | 85.5
LABORATORY NUTRIENT DATA
RAW INFLUENT | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
RAW AMMONIA (PPM) | [5 empty] | 11 | 11 | 11 | 12 | 11 | 10 | 12 | 13 | 12 | 12 | 7.8 | 6.5 | 11 | 11 | 12 | 13 | 12 | 12 | 13 | 13 | 11 | 12 | 12 | 8.8 | 9.4 | 9.4 | 10 | 9.2 | 9.2 | 11
RAW NITRATES (PPM) | [5 empty] | 0.02 | 0.057 | 0.06 | 0.02 | 0.055 | 0.063 | 0.071 | 0.072 | 0.074 | 0.071 | 0.02 | 0.07 | 0.11 | 0.11 | 0.091 | 0.02 | 0.02 | 0.02 | 0.02 | 0.14 | 0.15 | 0.11 | 0.14 | 0.02 | 0.02 | 0.02 | 0.12 | 0.15 | 0.12 | 0.11
RAW TOTAL KNEDJAHL NITRIGEN | [5 empty] | 43 | 47 | 45 | 32 | 32 | 17 | 15 | 20 | 19 | 17 | 12 | 14 | 16 | 19 | 21 | 20 | 19 | 17 | 21 | 16 | 15 | 17 | 16 | 14 | 12 | 16 | 12 | 12 | 12 | 13
RAW TOTAL PHOSPHORUS | [5 empty] | 2.3 | 2.4 | 2.1 | 2.2 | 2.2 | 2 | 2.2 | 2.5 | 2.3 | 2.3 | 2.1 | 2.1 | 2.4 | 2.3 | 2.6 | 2.5 | 2.4 | 1.9 | 4.3 | 2.3 | 2 | 2.4 | 2.2 | 1.8 | 1.5 | 2.1 | 1.8 | 1.8 | 1.7 | 1.9
EFFLUENT | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
EFFLUENT AMMONIA (PPM) | [5 empty] | 8 | 8.5 | 8.3 | 8 | 7.1 | 8.8 | 10 | 9.4 | 9.8 | 7.7 | 9.2 | 5 | 8.6 | 8.8 | 8.9 | 7.3 | 8.5 | 6 | 6 | 9.6 | 8.7 | 9.5 | 10 | 7.9 | 5.4 | 6.7 | 6.3 | 6.6 | 7.7 | 6.9
EFFLUENT NITRATES (PPM) | [5 empty] | 0.32 | 0.25 | 0.36 | 0.44 | 0.044 | 0.14 | 0.13 | 0.24 | 0.21 | 0.3 | 0.24 | 0.24 | 0.25 | 0.23 | 0.02 | 0.23 | 0.31 | 0.24 | 0.25 | 0.31 | 0.34 | 0.3 | 0.21 | 0.36 | 0.058 | 0.32 | 0.32 | 0.29 | 0.36 | 0.31
EFFLUENT TOTAL KNEDJAHL NITRIGEN | [5 empty] | 20 | 18 | 16 | 17 | 19 | 9 | 11 | 10 | 12 | 12 | 9.2 | 8.4 | 11 | 11 | 12 | 13 | 13 | 9.9 | 10 | 10 | 10 | 9.9 | 0 | 7.9 | 8.2 | 8.4 | 8.6 | 8 | 7.8 | 8.1
EFFLUENT TOTAL PHOSPHORUS | [5 empty] | 0.56 | 0.57 | 0.57 | 0.86 | 1.8 | 0.43 | 0.41 | 0.47 | 0.71 | 0.98 | 0.77 | 0.6 | 0.49 | 0.52 | 0.65 | 0.6 | 0.76 | 0.79 | 0.61 | 0.43 | 0.59 | 0.89 | 1.9 | 0.96 | 0.7 | 0.52 | 0.71 | 1.2 | 1.2 | 1.3
LABORATORY REACTOR PROCESSES DATA
| REACTOR ONE TRAIN A |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
MIXED-LIQUIR SUSPENDED SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
AVERAGE SETTLABLE SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
MIXED LIQUIR VOLITLE SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
| REACTOR ONE TRAIN B |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
MIXED-LIQUIR SUSPENDED SOLIDS | [5 empty] | 2300 | 2540 | 2710 | 2580 | 1870 | 2740 | 2730 | 2900 | 2930 | 3280 | 2450 | 2340 | 2690 | 2480 | 2550 | 2880 | 4270 | 2630 | 2280 | 2180 | 1990 | 2110 | 1490 | 1910 | 2540 | 2220 | 1750 | 1370 | 1210 | 1260
AVERAGE SETTLABLE SOLIDS | [5 empty] | 24 | 21 | 23 | 29 | 25 | 24 | 24 | 25 | 23 | 25 | 25 | 22 | 22 | 21 | 20 | 20 | 21 | 26 | 25 | 20 | 18 | 18 | 16 | 15 | 19 | 18 | 20 | 15 | 12 | 11
MIXED LIQUIR VOLITLE SOLIDS | [5 empty] | 1960 | 2090 | 2250 | 2090 | 1570 | 2270 | 2250 | 2380 | 2450 | 2770 | 2020 | 1960 | 2250 | 2020 | 2100 | 2360 | 3280 | 2140 | 1890 | 1710 | 1560 | 1700 | 1170 | 1520 | 2080 | 1870 | 1440 | 1180 | 900 | 1160
LABORATORY REACTOR PROCESSES DATA
CONTINUED
| REACTOR TWO TRAIN C |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
MIXED-LIQUIR SUSPENDED SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
AVERAGE SETTLABLE SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
MIXED LIQUIR VOLITLE SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
| REACTOR TWO TRAIN D |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
MIXED-LIQUIR SUSPENDED SOLIDS | [5 empty] | 2100 | 2120 | 2420 | 2010 | 1890 | 2350 | 2460 | 2790 | 3390 | 2900 | 2380 | 2260 | 2140 | 2580 | 2480 | 2290 | 3360 | 2480 | 2100 | 2380 | 1970 | 1810 | 1480 | 2250 | 3240 | 1900 | 1840 | 1260 | 1170 | 1380
AVERAGE SETTLABLE SOLIDS | [5 empty] | 24 | 22 | 23 | 28 | 25 | 24 | 25 | 25 | 24 | 26 | 25 | 22 | 23 | 22 | 21 | 20 | 21 | 26 | 25 | 20 | 18 | 18 | 16 | 15 | 19 | 18 | 20 | 15 | 12 | 10
MIXED LIQUIR VOLITLE SOLIDS | [5 empty] | 1810 | 1770 | 1970 | 1640 | 1590 | 1910 | 2030 | 2260 | 2790 | 2510 | 1960 | 1860 | 1790 | 2090 | 2040 | 1870 | 2690 | 2040 | 1760 | 1890 | 1540 | 1510 | 1170 | 1710 | 2640 | 1590 | 1530 | 1110 | 860 | 1280
LABORATORY RETURN ACTIVATED SLUDGE AND WASTE SLUDGE DATA
| RETURN ACTIVATED SLUDGE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
PERCENT RETURN SLUDGE TOTAL SUSPENDED SOLIDS | [5 empty] | 0.62 | 0.93 | 0.94 | 0.99 | 0.89 | 0.91 | 0.97 | 0.7 | 0.75 | 1.07 | 1.12 | 0.91 | 1.1 | 0.9 | 0.98 | 0.94 | 1.26 | 1.13 | 1.05 | 0.91 | 0.71 | 0.67 | 0.85 | 0.79 | 0.96 | 0.79 | 0.68 | 0.61 | 0.65 | 0.47
PERCENT RETURN SLUDGE FIXED SUSPENDED SOLIDS | [5 empty] | 29.76 | 28.85 | 27.66 | 28.28 | 26.97 | 27.47 | 26.4 | 31.43 | 29.25 | 24.3 | 23.74 | 24.3 | 25.22 | 27.88 | 21.33 | 27.66 | 23.02 | 26.55 | 23.81 | 27.03 | 32.04 | 31.34 | 29.41 | 24.76 | 25 | 25.3 | 19.12 | 29.51 | 29.23 | 29.03
|  | WASTE SLUDGE |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
PERCENT WASTE FEED TOTAL SUSPENDED SOLDS | [5 empty] | 1.41 | 1.42 |  |  | 1.54 | 1.1 | 1.3 | 1.11 | 1.3 |  |  | 1.17 | 1.15 | 1.52 | 1.19 | 1.57 |  |  | 1.71 | 1.1 | 0.83 | 0.56 | 0.55 |  |  | 1 | 1.11 | 1.21 | 0.46 | 0.13
PERCENT WASTE FEED FIXED SUSPENDED SOLIDS | [5 empty] | 21.99 | 23.24 |  |  | 22.73 | 26.36 | 25.38 | 26.13 | 25.38 |  |  | 23.08 | 23.48 | 22.37 | 14.29 | 22.29 |  |  | 21.05 | 26.36 | 34.94 | 33.93 | 32.73 |  |  | 25 | 25.23 | 23.97 | 32.61 | 69.23
WASTE FEED SLUDGE pH | [5 empty] | 6.43 | 6.42 |  |  | 6.38 | 6.54 | 6.43 | 6.74 | 6.5 |  |  | 6.23 | 6.38 | 6.2 | 6.41 | 6.22 |  |  | 6.22 | 6.62 | 6.48 | 6.42 | 6.49 |  |  | 6.04 | 6.28 | 6.11 | 6.36 | 6.64
DEWATERING FILTRATE TOTAL SUSPENDED SOLIDS | [5 empty] | 0.3 | 0.31 |  |  | 0.19 | 0.26 | 0.22 | 0.26 | 0.23 |  |  | 0.22 | 0.25 | 0.25 | 0.34 | 0.31 |  |  | 0.23 | 0.23 | 0.2 | 0.16 | 0.17 |  |  | 0.13 | 0.12 | 0.14 | 0.13 | 0.39
DEWATERING FILTRATE FIXED SUSPENDED SOLIDS | [5 empty] | 50 | 51.61 |  |  | 63.16 | 53.85 | 59.09 | 57.69 | 60.87 |  |  | 54.55 | 52 | 52 | 41.18 | 48.39 |  |  | 56.52 | 60.87 | 70 | 68.75 | 64.71 |  |  | 61.54 | 83.33 | 71.43 | 92.31 | 30.77
DEWATERING FILTRATE pH | [5 empty] | 7.03 | 7.11 |  |  | 6.91 | 6.88 | 6.94 | 7.14 | 6.89 |  |  | 6.61 | 6.64 | 6.74 | 6.69 | 6.8 |  |  | 6.73 | 6.87 | 6.82 | 6.75 | 6.75 |  |  | 6.67 | 6.8 | 6.8 | 6.71 | 6.47
| DEWATERED CAKE SLUDGE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
PERCENT TOTAL SOLIDS PRESS CAKE | [5 empty] | 17.18 | 18.1 |  |  | 17.21 | 18.06 | 18.43 | 17.88 | 18.21 |  |  | 17.44 | 18.29 | 18.03 | 18.7 | 16.26 |  |  | 21.17 | 18.04 | 18.9 | 19.05 | 19.03 |  |  | 18.26 | 18.31 | 18.91 | 19.35 | 18.74
PERCENT FIXED SOLIDS PRESS CAKE | [5 empty] | 13.68 | 14.48 |  |  | 15.75 | 17.05 | 16.39 | 16.5 | 18.51 |  |  | 21.56 | 22.64 | 23.24 | 21.28 | 17.59 |  |  | 21.68 | 23.28 | 18.73 | 18.74 | 19.76 |  |  | 19.5 | 18.22 | 19.83 | 20.41 | 20.6
PERCENT TOTAL SOLIDS LIME CAKE
OTHER SLUDGE REMOVAL
[6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
GRIT (CU.YDS.) | [5 empty] | 3: 10; 7: 10; 22: 10; 28: 10; 30: 10
RAGS (CU.YDS.) | [5 empty] | 3: 10; 14: 10; 17: 10
VACUUM DEBRIS (EST. GAL) | [5 empty] | 16: 4500
MONITORING WELLS LABORATORY DATA
| MONITOR WELL ONE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
UPPER LEVEL
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
MONITORING WELLS LABORATORY DATA
| MONITOR WELL TWO |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
UPPER LEVEL
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
MONITORING WELLS LABORATORY DATA
| MONITOR WELL THREE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
FUTURE
UPPER LEVEL
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
MONITORING WELLS LABORATORY DATA
| REGIONAL MONITOR WELL ONE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
UPPER LEVEL
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
JUNE |  | 0 |  | 0
|  | 1 |  | 2
0
0
|  | 0 |  | 0
2
[5 empty] | 1st WEEK | 1: 2nd WEEK; 2: 3rd WEEK; 3: 4th WEEK
| 1 |  | 1 |  | 1 | 1: 8; 2: 15; 3: 23
| 2 |  | 2 |  | 2 | 1: 9; 2: 16; 3: 24
| 3 |  | 3 |  | 3 | 1: 10; 2: 17; 3: 25
| 4 |  | 4 |  | 4 | 1: 11; 2: 18; 3: 26
| 5 |  | 5 |  | 5 | 1: 12; 2: 19; 3: 27
| 6 |  | 6 |  | 6 | 1: 13; 2: 20; 3: 28
| 7 |  | 7 |  | 7 | 1: 14; 2: 21; 3: 29
| 8 |  | 8 |  |  | 2: 22; 3: 30
| 9 |  | 9
| 10 |  | 10
| 11 |  | 11
| 12 |  | 12
| 13 |  | 13
| 14 |  | 14
| 15 |  | 15
| 16 |  | 16
| 17 |  | 17
| 18 |  | 18
| 19 |  | 19
| 20 |  | 20
| 21 |  | 21
| 22 |  | 22
| 23 |  | 23
| 24 |  | 24
| 25 |  | 25
| 26 |  | 26
| 27 |  | 27
| 28 |  | 28
29
30
| APRIL | MARCH | FEBRUARY
| AUGUST | JULY | JUNE
| DECEMBER | NOVEMBER | OCTOBER
| FEBRUARY | JANUARY | DECEMBER
| JANUARY | DECEMBER | NOVEMBER
| JUNE | MAY | APRIL
| JULY | JUNE | MAY | MAY
| MARCH | FEBRUARY | JANUARY | APRIL
| MAY | APRIL | MARCH
| NOVEMBER | OCTOBER | SEPTEMBER
| OCTOBER | SEPTEMBER | AUGUST
| SEPTEMBER | AUGUST | JULY
| HYDROGEN PEROXIDE |  | 0.1465
| CHLORINE |  | 0.295
| POLYMER |  | 0.61
| FPL |  | 0.055
[6 empty] | 1st WEEK |  |  | 2nd WEEK |  |  | 3rd WEEK |  |  | 4th WEEK
[7 empty] | G | H | I | J
[5 empty] | MW1 UP | 1: 311
312
313
314
315
316
317
318

## MONITOR DATA
UNDERGROUND INJECTION CONTROL SECTION
MONTHLY OPERATING REPORT DATA SUMMARY
FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT MONTH/YEAR |  |  | JUNE |  | 2005
I.D. NUMBER: 5006M02066 | [5 empty] | LEAD OPERATOR: |  |  |  | MIKE JUST
TELEPHONE NUMBER: (954) 523-1002
MONITORING WELL 1 DATA | [6 empty] | I.D. # 5006A11311
MW-1
PERMIT/CERTIFICATION NUMBER | [6 empty] | 0054569-142-UO
PERMIT EXPIRATION DATE |  | 2009-01-06
UPPER MONITORING INTERVAL | [6 empty] | 1,288' - 1,320' |  |  |  | Ft. bls.
Sample Date |  | 2005-06-07 |  | 2005-06-14 |  | 2005-06-21 |  | 2005-06-28
Submittal Date |  | 2005-06-08 |  | 2005-06-15 |  | 2005-06-22 |  | 2005-06-29
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 49.46 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 40.7 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 73 |  | 76 |  | 77 |  | 78 |  |  | degrees (F) |  | 76
TDS |  | 7489 |  | 7893 |  | 7840 |  | 7275 |  |  | mg/l |  | 7624.25
CHLORIDE |  | 3850 |  | 3800 |  | 3800 |  | 3750 |  |  | mg/l |  | 3800
AMMONIA-N |  | 0.93 |  | 0.86 |  | 0.96 |  | 0.9 |  |  | mg/l |  | 0.9125
TKN |  | 1 |  | 0.95 |  | 0.96 |  | 0.93 |  |  | mg/l |  | 0.96
pH |  | 7.83 |  | 7.92 |  | 8.12 |  | 7.91 |  |  | Std units |  | 7.945
CONDUCTIVITY |  | 12170 |  | 12230 |  | 12260 |  | 12200 |  |  | umho/cm |  | 12215
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.01 | < | 0.01 | < | 0.01 | < | 0.01 |  |  | mg/l |  | 0.01
SULFATE |  | 945 |  | 955 |  | 990 |  | LS |  |  | mg/l |  | 963.3333
C.O.D. 'S | [10 empty] | mg/l |  | #DIV/0!
IRON | [10 empty] | mg/l |  | #DIV/0!
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
LOWER MONITORING INTERVAL | [6 empty] | 1,449' - 1,557' |  |  |  | Ft. bls
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 46.89 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 37.1 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 74 |  | 76 |  | 78 |  | 78 |  |  | degrees (F) |  | 76.5
TDS |  | 9459 |  | 9837 |  | 9669 |  | 9236 |  |  | mg/l |  | 9550.25
CHLORIDE |  | 5200 |  | 5000 |  | 5000 |  | 5000 |  |  | mg/l |  | 5050
AMMONIA-N |  | 9.6 |  | 7.5 |  | 11 |  | 8.7 |  |  | mg/l |  | 9.2
TKN |  | 9.9 |  | 10 |  | 11 |  | 9.3 |  |  | mg/l |  | 10.05
pH |  | 7.38 |  | 7.49 |  | 7.49 |  | 7.29 |  |  | Std units |  | 7.4125
CONDUCTIVITY |  | 15650 |  | 15670 |  | 15700 |  | 15670 |  |  | umho/cm |  | 15672.5
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.01 | < | 0.01 | < | 0.01 | < | 0.01 |  |  | mg/l |  | 0.01
SULFATE |  | 810 |  | 883 |  | 915 |  | LS |  |  | mg/l |  | 869.3333
C.O.D. 'S | [10 empty] | mg/l |  | #DIV/0!
IRON | [10 empty] | mg/l |  | #DIV/0!
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
PAGE 24
UNDERGROUND INJECTION CONTROL SECTION
MONTHLY OPERATING REPORT DATA SUMMARY
FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT MONTH/YEAR |  |  | JUNE |  | 2005
I.D. NUMBER: 5006M02066 | [5 empty] | LEAD OPERATOR: |  |  |  | MIKE JUST
TELEPHONE NUMBER: (954) 523-1002
MONITORING WELL 2 DATA | [6 empty] | I.D. # 5006A11308 & 309
MW-2
PERMIT/CERTIFICATION NUMBER | [6 empty] | 0054569-142-UO
PERMIT EXPIRATION DATE |  | 2009-01-06
UPPER MONITORING INTERVAL | [6 empty] | 1,300' - 1,344' |  |  |  | Ft. bls.
Sample Date |  | 2005-06-07 |  | 2005-06-14 |  | 2005-06-21 |  | 2005-06-28
Submittal Date |  | 2005-06-08 |  | 2005-06-15 |  | 2005-06-22 |  | 2005-06-29
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 32.68 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 24.9 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 72 |  | 76 |  | 75 |  | 75 |  |  | degrees (F) |  | 74.5
TDS |  | 7173 |  | 7625 |  | 7569 |  | 7180 |  |  | mg/l |  | 7386.75
CHLORIDE |  | 3700 |  | 3650 |  | 3600 |  | 3650 |  |  | mg/l |  | 3650
AMMONIA-N |  | 0.88 |  | 0.8 |  | 0.96 |  | 0.91 |  |  | mg/l |  | 0.8875
TKN |  | 1.1 |  | 0.93 |  | 1 |  | 0.92 |  |  | mg/l |  | 0.9875
pH |  | 7.98 |  | 7.97 |  | 8.11 |  | 8.06 |  |  | Std units |  | 8.03
CONDUCTIVITY |  | 11910 |  | 11930 |  | 11970 |  | 11910 |  |  | umho/cm |  | 11930
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.01 | < | 0.01 | < | 0.01 |  | 0.015 |  |  | mg/l |  | 0.01125
SULFATE |  | 985 |  | 985 |  | 993 |  | LS |  |  | mg/l |  | 987.6667
C.O.D. 'S | [10 empty] | mg/l |  | #DIV/0!
IRON | [10 empty] | mg/l |  | #DIV/0!
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
LOWER MONITORING INTERVAL | [6 empty] | 1,970' - 2,025' |  |  |  | Ft. bls
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 43.48 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 35.04 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 70 |  | 74 |  | 74 |  | 74 |  |  | degrees (F) |  | 73
TDS |  | 31761 |  | 32657 |  | 33196 |  | 30257 |  |  | mg/l |  | 31967.75
CHLORIDE |  | 17600 |  | 17600 |  | 17400 |  | 17600 |  |  | mg/l |  | 17550
AMMONIA-N |  | 1.4 |  | 1.3 |  | 1.5 |  | 1.4 |  |  | mg/l |  | 1.4
TKN |  | 2 |  | 1.9 |  | 1.7 |  | 1.4 |  |  | mg/l |  | 1.75
pH |  | 7.62 |  | 7.62 |  | 7.6 |  | 7.54 |  |  | Std units |  | 7.595
CONDUCTIVITY |  | 47000 |  | 47100 |  | 47100 |  | 47000 |  |  | umho/cm |  | 47050
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.01 | < | 0.01 | < | 0.01 | < | 0.01 |  |  | mg/l |  | 0.01
SULFATE |  | 3230 |  | 3240 |  | 3130 |  | LS |  |  | mg/l |  | 3200
C.O.D. 'S | [10 empty] | mg/l |  | #DIV/0!
IRON | [10 empty] | mg/l |  | #DIV/0!
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
PAGE 25
UNDERGROUND INJECTION CONTROL SECTION
MONTHLY OPERATING REPORT DATA SUMMARY
FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT MONTH/YEAR |  |  | JUNE |  | 2005
I.D. NUMBER: 5006M02066 | [5 empty] | LEAD OPERATOR: |  |  |  | MIKE JUST
TELEPHONE NUMBER: (954) 523-1002
MONITORING WELL 2 DATA | [6 empty] | I.D. # 5006A11310
MW-3
PERMIT/CERTIFICATION NUMBER | [6 empty] | 0054569-142-UO
PERMIT EXPIRATION DATE |  | 2009-01-06
UPPER MONITORING INTERVAL | [6 empty] | 1,300' - 1,349' |  |  |  | Ft. bls.
Sample Date |  | 2005-06-07 |  | 2005-06-14 |  | 2005-06-21 |  | 2005-06-28
Submittal Date |  | 2005-06-08 |  | 2005-06-15 |  | 2005-06-22 |  | 2005-06-29
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 34.04 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 17.82 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 70 |  | 74 |  | 74 |  | 74 |  |  | degrees (F) |  | 73
TDS |  | 7370 |  | 7726 |  | 7964 |  | 7390 |  |  | mg/l |  | 7612.5
CHLORIDE |  | 3700 |  | 3700 |  | 3650 |  | 3750 |  |  | mg/l |  | 3700
AMMONIA-N |  | 0.92 |  | 0.77 |  | 0.95 |  | 0.9 |  |  | mg/l |  | 0.885
TKN |  | 0.99 |  | 1.3 |  | 0.95 |  | 0.92 |  |  | mg/l |  | 1.04
pH |  | 8.21 |  | 7.99 |  | 8.14 |  | 8.28 |  |  | Std units |  | 8.155
CONDUCTIVITY |  | 12080 |  | 12060 |  | 12060 |  | 12080 |  |  | umho/cm |  | 12070
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS |  | 0.013 | < | 0.01 | < | 0.01 | < | 0.01 |  |  | mg/l |  | 0.01075
SULFATE |  | 968 |  | 808 |  | 1010 |  | LS |  |  | mg/l |  | 928.6667
C.O.D. 'S | [10 empty] | mg/l |  | #DIV/0!
IRON | [10 empty] | mg/l |  | #DIV/0!
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
LOWER MONITORING INTERVAL | [6 empty] | 1,970' - 2,027' |  |  |  | Ft. bls
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 46.21 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 35.49 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 68 |  | 73 |  | 74 |  | 74 |  |  | degrees (F) |  | 72.25
TDS |  | 28176 |  | 29975 |  | 29771 |  | 27792 |  |  | mg/l |  | 28928.5
CHLORIDE |  | 15600 |  | 15800 |  | 15800 |  | 15800 |  |  | mg/l |  | 15750
AMMONIA-N |  | 2.5 |  | 2.2 |  | 2.6 |  | 2.3 |  |  | mg/l |  | 2.4
TKN |  | 2.8 |  | 3.1 |  | 2.7 |  | 2.4 |  |  | mg/l |  | 2.75
pH |  | 7.44 |  | 7.58 |  | 7.53 |  | 7.52 |  |  | Std units |  | 7.5175
CONDUCTIVITY |  | 43000 |  | 43200 |  | 43300 |  | 43100 |  |  | umho/cm |  | 43150
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS |  | 0.018 |  | 0.081 | < | 0.01 | < | 0.01 |  |  | mg/l |  | 0.02975
SULFATE |  | 3160 |  | 3280 |  | 3020 |  | LS |  |  | mg/l |  | 3153.3333
C.O.D. 'S | [10 empty] | mg/l |  | #DIV/0!
IRON | [10 empty] | mg/l |  | #DIV/0!
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
PAGE 26
UNDERGROUND INJECTION CONTROL SECTION
MONTHLY OPERATING REPORT DATA SUMMARY
FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT MONTH/YEAR |  |  | JUNE |  | 2005
I.D. NUMBER: 5006M02066 | [5 empty] | LEAD OPERATOR: |  |  |  | MIKE JUST
TELEPHONE NUMBER: (954) 523-1002
REGIONAL MONITORING WELL DATA
RMW-1
PERMIT NUMBER | [6 empty] | 0054569-142-UO
PERMIT EXPIRATION DATE |  | 2009-01-06
UPPER MONITORING INTERVAL | [6 empty] | 1300' - 1339' |  |  |  | Ft. bls.
Sample Date |  | 2005-06-07
Submittal Date |  | 2005-06-08
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 44.64 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 44.54 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 70 | [8 empty] | degrees (F) |  | 70
TDS |  | 5589 | [8 empty] | mg/l |  | 5589
CHLORIDE |  | 2800 | [8 empty] | mg/l |  | 2800
AMMONIA-N |  | 0.68 | [8 empty] | mg/l |  | 0.68
TKN |  | 0.8 | [8 empty] | mg/l |  | 0.8
pH |  | 8.2 | [8 empty] | Std units |  | 8.2
CONDUCTIVITY |  | 9370 | [8 empty] | umho/cm |  | 9370
FECAL COLIFORM |  | 0 | [8 empty] | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.01 | [8 empty] | mg/l |  | 0.01
SULFATE |  | 808 | [8 empty] | mg/l |  | 808
C.O.D. 'S | [10 empty] | mg/l |  | #DIV/0!
IRON | [10 empty] | mg/l |  | #DIV/0!
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
LOWER MONITORING INTERVAL | [6 empty] | 1500' - 1600' |  |  |  | Ft. bls
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 22.68 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 22.53 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 66 | [8 empty] | degrees (F) |  | 66
TDS |  | 25230 | [8 empty] | mg/l |  | 25230
CHLORIDE |  | 14800 | [8 empty] | mg/l |  | 14800
AMMONIA-N |  | 0.38 | [8 empty] | mg/l |  | 0.38
TKN |  | 0.73 | [8 empty] | mg/l |  | 0.73
pH |  | 7.54 | [8 empty] | Std units |  | 7.54
CONDUCTIVITY |  | 40000 | [8 empty] | umho/cm |  | 40000
FECAL COLIFORM |  | 0 | [8 empty] | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.01 | [8 empty] | mg/l |  | 0.01
SULFATE |  | 2140 | [8 empty] | mg/l |  | 2140
C.O.D. 'S | [10 empty] | mg/l |  | #DIV/0!
IRON | [10 empty] | mg/l |  | #DIV/0!
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
PAGE 27
Formulas:
LEAD OPERATOR: = [LEAD OPERATOR:, row above]+1

## WELL PRN DATA
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 1 |  |  | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180 | 181
152 | 14.73 | 5.87 | 10.99 | 70.8 | 42.37 | 56.45
153 | 12.5 | 0 | 5.18 | 60.6 | 36.13 | 45.8 |  |  | FLOW
154 | 15.22 | 0 | 10.54 | 71 | 36.41 | 56.61 | I |  | MAX | 14.73 | 12.5 | 15.22 | 14.26 | 15.29 | 14.29 | 12.64 | 14.44 | 13.99 | 13.46 | 15.16 | 13.12 | 14.52 | 14.49 | 13.98 | 12.61 | 9.63 | 14.7 | 13.91 | 14.44 | 14.82 | 12.99 | 15.92 | 14.81 | 14.66 | 14.38 | 10.85 | 15.23 | 14.94 | 15.96
155 | 14.26 | 4.87 | 11.63 | 67.34 | 45.68 | 58.23 | N |  | MIN | 5.87 | 0 | 0 | 4.87 | 7.98 | 7.6 | 0 | 0.01 | 0.01 | 7.94 | 8.67 | 0.01 | 0.01 | 0 | 6.32 | 6.6 | 0 | 0 | 8.08 | 7.89 | 8.72 | 0 | 0 | 9.47 | 8.3 | 7.51 | 0 | 0 | 10.53 | 0.01
156 | 15.29 | 7.98 | 12.09 | 72.7 | 47.4 | 59.74 | J |  | TOT | 10.99 | 5.18 | 10.54 | 11.63 | 12.09 | 12.07 | 2.65 | 9.08 | 10.13 | 11.18 | 12.62 | 0.96 | 10.87 | 9.41 | 10.63 | 10.36 | 0.16 | 9.89 | 11.85 | 12.03 | 12.08 | 3.02 | 10.63 | 12.28 | 11.94 | 11.92 | 0.67 | 12.28 | 13.5 | 12.06
157 | 14.29 | 7.6 | 12.07 | 68.18 | 46.73 | 59.84 | E | INJECTION WELL ONE
158 | 12.64 | 0 | 2.65 | 61.19 | 36.06 | 41.36 | C |  | PSI
159 | 14.44 | 0.01 | 9.08 | 67.91 | 35.62 | 53.13 | T |  | MAX | 70.8 | 60.6 | 71 | 67.34 | 72.7 | 68.18 | 61.19 | 67.91 | 65.13 | 64.71 | 72 | 64.43 | 68.28 | 69.61 | 66.86 | 62.06 | 55.76 | 69.44 | 65.72 | 68.77 | 71 | 63.23 | 76 | 70.8 | 70.2 | 68.47 | 56.12 | 70.5 | 70 | 73.5
160 | 13.99 | 0.01 | 10.13 | 65.13 | 35.6 | 54.21 | O |  | MIN | 42.37 | 36.13 | 36.41 | 45.68 | 47.4 | 46.73 | 36.06 | 35.62 | 35.6 | 47.39 | 50.33 | 36.21 | 36.54 | 35.85 | 44.01 | 44.74 | 0 | 36.15 | 48.34 | 46.7 | 48.89 | 36.61 | 35.9 | 53.13 | 48.17 | 47.44 | 36.25 | 36.78 | 54.91 | 36.88
161 | 13.46 | 7.94 | 11.18 | 64.71 | 47.39 | 56.75 | N |  | AVG | 56.45 | 45.8 | 56.61 | 58.23 | 59.74 | 59.84 | 41.36 | 53.13 | 54.21 | 56.75 | 62.37 | 38.92 | 57.43 | 53.64 | 55.28 | 54.56 | 37.5 | 55.76 | 58.9 | 59.3 | 60 | 42.46 | 57.36 | 61.45 | 60.05 | 59.82 | 38.35 | 62.26 | 64.78 | 60.91
162 | 15.16 | 8.67 | 12.62 | 72 | 50.33 | 62.37
163 | 13.12 | 0.01 | 0.96 | 64.43 | 36.21 | 38.92 | W
164 | 14.52 | 0.01 | 10.87 | 68.28 | 36.54 | 57.43 | E
165 | 14.49 | 0 | 9.41 | 69.61 | 35.85 | 53.64 | L
166 | 13.98 | 6.32 | 10.63 | 66.86 | 44.01 | 55.28 | L
167 | 12.61 | 6.6 | 10.36 | 62.06 | 44.74 | 54.56 | O
168 | 9.63 | 0 | 0.16 | 55.76 | 0 | 37.5 | N
169 | 14.7 | 0 | 9.89 | 69.44 | 36.15 | 55.76 | E
170 | 13.91 | 8.08 | 11.85 | 65.72 | 48.34 | 58.9
171 | 14.44 | 7.89 | 12.03 | 68.77 | 46.7 | 59.3 | D
172 | 14.82 | 8.72 | 12.08 | 71 | 48.89 | 60 | A
173 | 12.99 | 0 | 3.02 | 63.23 | 36.61 | 42.46 | T
174 | 15.92 | 0 | 10.63 | 76 | 35.9 | 57.36 | A
175 | 14.81 | 9.47 | 12.28 | 70.8 | 53.13 | 61.45
176 | 14.66 | 8.3 | 11.94 | 70.2 | 48.17 | 60.05
177 | 14.38 | 7.51 | 11.92 | 68.47 | 47.44 | 59.82
178 | 10.85 | 0 | 0.67 | 56.12 | 36.25 | 38.35
179 | 15.23 | 0 | 12.28 | 70.5 | 36.78 | 62.26
180 | 14.94 | 10.53 | 13.5 | 70 | 54.91 | 64.78
181 | 15.96 | 0.01 | 12.06 | 73.5 | 36.88 | 60.91
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 2 |  |  | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180 | 181
152 | 15 | 5.89 | 11.21 | 69.64 | 41.75 | 55.6
153 | 15.21 | 8.29 | 12.27 | 68.19 | 46.79 | 58.5 |  |  | FLOW
154 | 14.29 | 0.05 | 4.7 | 63.97 | 36.65 | 45.14 | I |  | MAX | 15 | 15.21 | 14.29 | 14.72 | 15.57 | 14.55 | 14.38 | 13.69 | 13.04 | 13.69 | 15.36 | 15.45 | 12.12 | 14.87 | 12.63 | 12.82 | 15.43 | 13.27 | 14.26 | 14.8 | 15.11 | 15.59 | 16.06 | 15.09 | 14.88 | 14.54 | 15.47 | 12.22 | 15.11 | 16.01
155 | 14.72 | 0.05 | 10.55 | 66.17 | 36.93 | 55.02 | N |  | MIN | 5.89 | 8.29 | 0.05 | 0.05 | 0.05 | 7.61 | 9.47 | 0.05 | 0.05 | 0.05 | 8.93 | 8.39 | 0.05 | 0.05 | 0.05 | 6.71 | 0 | 0.05 | 0.05 | 0.05 | 8.83 | 8.24 | 0.05 | 8.76 | 8.43 | 7.53 | 9.23 | 0.05 | 0.05 | 0.05
156 | 15.57 | 0.05 | 10.1 | 71.4 | 36.57 | 55.25 | J |  | TOT | 11.21 | 12.27 | 4.7 | 10.55 | 10.1 | 12.3 | 12.37 | 2.71 | 8.75 | 9.32 | 12.85 | 13.36 | 0.74 | 9.03 | 8.72 | 10.56 | 12.97 | 2.6 | 10.11 | 10.02 | 12.31 | 12.47 | 3.04 | 12.43 | 12.13 | 12.14 | 13.35 | 0.81 | 12.5 | 12.25
157 | 14.55 | 7.61 | 12.3 | 66.95 | 46.1 | 59.02 | E | INJECTION WELL TWO
158 | 14.38 | 9.47 | 12.37 | 64.62 | 50.12 | 58.06 | C |  | PSI
159 | 13.69 | 0.05 | 2.71 | 61.54 | 37.06 | 41.5 | T |  | MAX | 69.64 | 68.19 | 63.97 | 66.17 | 71.4 | 66.95 | 64.62 | 61.54 | 60.61 | 63.56 | 70.8 | 69.31 | 58.76 | 69.19 | 60.13 | 60.76 | 69.32 | 61.36 | 64.7 | 67.76 | 69.88 | 70.9 | 74.8 | 69.6 | 69.07 | 67.42 | 69.14 | 58.05 | 68.38 | 71.2
160 | 13.04 | 0.05 | 8.75 | 60.61 | 35.88 | 50.83 | I |  | MIN | 41.75 | 46.79 | 36.65 | 36.93 | 36.57 | 46.1 | 50.12 | 37.06 | 35.88 | 36.71 | 49.63 | 48.5 | 37.2 | 36.46 | 36.97 | 44.06 | 0 | 36.88 | 37.27 | 36.84 | 48.26 | 47.96 | 36.5 | 52.21 | 47.41 | 46.68 | 49.27 | 37.31 | 37.86 | 38.43
161 | 13.69 | 0.05 | 9.32 | 63.56 | 36.71 | 52.6 | O |  | AVG | 55.6 | 58.5 | 45.14 | 55.02 | 55.25 | 59.02 | 58.06 | 41.5 | 50.83 | 52.6 | 61.38 | 62.06 | 39.01 | 51.96 | 50.87 | 53.58 | 60.51 | 42.07 | 54.48 | 54.66 | 59 | 58.96 | 43.52 | 60.33 | 59.04 | 58.88 | 61.78 | 39.4 | 61.33 | 59.88
162 | 15.36 | 8.93 | 12.85 | 70.8 | 49.63 | 61.38 | N
163 | 15.45 | 8.39 | 13.36 | 69.31 | 48.5 | 62.06
164 | 12.12 | 0.05 | 0.74 | 58.76 | 37.2 | 39.01 | W
165 | 14.87 | 0.05 | 9.03 | 68.34 | 36.46 | 51.96 | E
166 | 12.63 | 0.05 | 8.72 | 60.13 | 36.97 | 50.87 | L
167 | 12.82 | 6.71 | 10.56 | 60.76 | 44.06 | 53.58 | L
168 | 15.43 | 0 | 12.97 | 69.32 | 0 | 60.51
169 | 13.27 | 0.05 | 2.6 | 61.36 | 36.88 | 42.07 | T
170 | 14.26 | 0.05 | 10.11 | 64.7 | 37.27 | 54.48 | W
171 | 14.8 | 0.05 | 10.02 | 67.76 | 36.84 | 54.66 | O
172 | 15.11 | 8.83 | 12.31 | 69.88 | 48.26 | 59
173 | 15.59 | 8.24 | 12.47 | 70.9 | 47.96 | 58.96 | D
174 | 16.06 | 0.05 | 3.04 | 74.8 | 36.5 | 43.52 | A
175 | 15.09 | 8.76 | 12.43 | 69.6 | 52.21 | 60.33 | T
176 | 14.88 | 8.43 | 12.13 | 69.07 | 47.41 | 59.04 | A
177 | 14.54 | 7.53 | 12.14 | 67.42 | 46.68 | 58.88
178 | 15.47 | 9.23 | 13.35 | 69.14 | 49.27 | 61.78
179 | 12.22 | 0.05 | 0.81 | 58.05 | 37.31 | 39.4
180 | 15.11 | 0.05 | 12.5 | 68.38 | 37.86 | 61.33
181 | 16.01 | 0.05 | 12.25 | 71.2 | 38.43 | 59.88
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 3 |  |  | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180 | 181
152 | 13.94 | 5.98 | 10.64 | 71 | 42.58 | 56.73
153 | 13.56 | 8.04 | 11.31 | 69.46 | 47.74 | 59.65 |  |  | FLOW
154 | 14.06 | 7.09 | 11.26 | 71.1 | 46.39 | 59.63 | I |  | MAX | 13.94 | 13.56 | 14.06 | 11.82 | 14.65 | 13.57 | 12.94 | 13.31 | 13.95 | 12.95 | 14.22 | 14.02 | 13.48 | 13.31 | 12.03 | 12.06 | 13.9 | 13.69 | 10.78 | 13.93 | 14.06 | 14.09 | 14.86 | 13.66 | 14.02 | 13.62 | 13.94 | 14.12 | 12.58 | 15.97
155 | 11.82 | ER | 0.64 | 61.53 | 37.56 | 39.69 | N |  | MIN | 5.98 | 8.04 | 7.09 | ER | ER | 4.72 | 9.1 | 8.74 | ER | ER | ER | 7.97 | 8.74 | ER | ER | ER | 0 | 7.74 | ER | ER | ER | 8.1 | 7.73 | ER | ER | ER | 8.61 | 9.66 | ER | ER
156 | 14.65 | ER | 9.13 | 73 | 37.13 | 55.8 | J |  | TOT | 10.64 | 11.31 | 11.26 | 0.64 | 9.13 | 11.58 | 11.37 | 10.98 | 1.46 | 8.49 | 11.87 | 12.13 | 11.43 | 2.6 | 7.96 | 8.27 | 11.74 | 11.27 | 0.61 | 9.08 | 9.36 | 11.51 | 11.47 | 9.6 | 11.22 | 11.37 | 12.16 | 12.64 | 0.74 | 10
157 | 13.57 | 4.72 | 11.58 | 68.25 | 44.78 | 60.13 | E | INJECTION WELL THREE
158 | 12.94 | 9.1 | 11.37 | 65.78 | 51.14 | 59.19 | C |  | PSI
159 | 13.31 | 8.74 | 10.98 | 67.69 | 50.41 | 57.79 | T |  | MAX | 71 | 69.46 | 71.1 | 61.53 | 73 | 68.25 | 65.78 | 67.69 | 69.72 | 64.93 | 72.3 | 70.6 | 68.37 | 67.28 | 61.4 | 61.97 | 70.6 | 69.66 | 57.67 | 69.29 | 71.3 | 72.2 | 76.4 | 70.2 | 70.5 | 68.76 | 70.4 | 70.7 | 64.18 | 79.2
160 | 13.95 | ER | 1.46 | 69.72 | 37.45 | 41.08 | I |  | MIN | 42.58 | 47.74 | 46.39 | 37.56 | 37.13 | 44.78 | 51.14 | 50.41 | 37.45 | 37.14 | 37.7 | 49.45 | 50.79 | 37.79 | 37.54 | 37.05 | 0 | 48.66 | 38.07 | 37.54 | 37.38 | 48.94 | 47.68 | 39.85 | 39.86 | 38.06 | 50.24 | 53.06 | 38.9 | 37.87
161 | 12.95 | ER | 8.49 | 64.93 | 37.14 | 53.09 | O |  | AVG | 56.73 | 59.65 | 59.63 | 39.69 | 55.8 | 60.13 | 59.19 | 57.79 | 41.08 | 53.09 | 62.22 | 63.19 | 60.09 | 43.7 | 51.37 | 51.73 | 61.53 | 59.7 | 39.97 | 55.25 | 55.88 | 60.07 | 60.4 | 57.15 | 59.7 | 59.72 | 62.96 | 64.87 | 41.21 | 58.13
162 | 14.22 | ER | 11.87 | 72.3 | 37.7 | 62.22 | N
163 | 14.02 | 7.97 | 12.13 | 70.6 | 49.45 | 63.19
164 | 13.48 | 8.74 | 11.43 | 68.37 | 50.79 | 60.09 | W
165 | 13.31 | ER | 2.6 | 67.28 | 37.79 | 43.7 | E
166 | 12.03 | ER | 7.96 | 61.4 | 37.54 | 51.37 | L
167 | 12.06 | ER | 8.27 | 61.97 | 37.05 | 51.73 | L
168 | 13.9 | 0 | 11.74 | 70.6 | 0 | 61.53
169 | 13.69 | 7.74 | 11.27 | 69.66 | 48.66 | 59.7 | T
170 | 10.78 | ER | 0.61 | 57.67 | 38.07 | 39.97 | H
171 | 13.93 | ER | 9.08 | 69.29 | 37.54 | 55.25 | R
172 | 14.06 | ER | 9.36 | 71.3 | 37.38 | 55.88 | E
173 | 14.09 | 8.1 | 11.51 | 72.2 | 48.94 | 60.07 | E
174 | 14.86 | 7.73 | 11.47 | 76.4 | 47.68 | 60.4
175 | 13.66 | ER | 9.6 | 70.2 | 39.85 | 57.15 | D
176 | 14.02 | ER | 11.22 | 70.5 | 39.86 | 59.7 | A
177 | 13.62 | ER | 11.37 | 68.76 | 38.06 | 59.72 | T
178 | 13.94 | 8.61 | 12.16 | 70.4 | 50.24 | 62.96 | A
179 | 14.12 | 9.66 | 12.64 | 70.7 | 53.06 | 64.87
180 | 12.58 | ER | 0.74 | 64.18 | 38.9 | 41.21
181 | 15.97 | ER | 10 | 79.2 | 37.87 | 58.13
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 4 |  |  | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180 | 181
152 | 14.6 | 0.04 | 9.47 | 71.3 | 36.32 | 54.85
153 | 13.88 | 0.04 | 9.48 | 69.93 | 36.75 | 56.39 |  |  | FLOW
154 | 14.29 | 7.23 | 11.43 | 71.6 | 47.05 | 60.27 | I |  | MAX | 14.6 | 13.88 | 14.29 | 13.98 | 12.82 | 14 | 13.09 | 13.49 | 14.03 | 12.51 | 14.84 | 14.56 | 13.75 | 14.12 | 13.57 | 12.66 | 14.06 | 13.8 | 13.54 | 13.72 | 14.47 | 14.31 | 15.06 | 14.34 | 12.67 | 14.04 | 14.23 | 14.15 | 14.49 | 15.95
155 | 13.98 | 8.6 | 11.49 | 68.14 | 49.59 | 59.29 | N |  | MIN | 0.04 | 0.04 | 7.23 | 8.6 | 0.03 | 0.04 | 0.04 | 8.84 | 7.31 | 0.04 | 0.04 | 4.98 | 8.94 | 6.24 | 0.04 | 0.04 | 0 | 7.82 | 8.25 | 0.04 | 0.03 | 0.04 | 7.78 | 9.3 | 0.05 | 0.05 | 6.14 | 9.7 | 10.46 | 0.04
156 | 12.82 | 0.03 | 4.53 | 62.87 | 37.57 | 46.6 | J |  | TOT | 9.47 | 9.48 | 11.43 | 11.49 | 4.53 | 10.08 | 9.37 | 11.11 | 10.97 | 2.48 | 9.87 | 12.28 | 11.58 | 11.19 | 2.55 | 8.26 | 11.93 | 11.41 | 11.63 | 2.68 | 9.11 | 9.53 | 11.57 | 11.84 | 5.04 | 9.9 | 12.36 | 12.74 | 13.11 | 2.45
157 | 14 | 0.04 | 10.08 | 68.73 | 36.89 | 57.21 | E | INJECTION WELL FOUR
158 | 13.09 | 0.04 | 9.37 | 66.34 | 36.8 | 55.74 | C |  | PSI
159 | 13.49 | 8.84 | 11.11 | 68.24 | 51.03 | 58.38 | T |  | MAX | 71.3 | 69.93 | 71.6 | 68.14 | 62.87 | 68.73 | 66.34 | 68.24 | 70.2 | 62.28 | 72.7 | 71.1 | 68.77 | 64.71 | 67.52 | 62.37 | 71.2 | 70.2 | 66.65 | 66.62 | 71.8 | 72.7 | 76.9 | 71.6 | 64.58 | 69.25 | 70.8 | 71.2 | 70.9 | 79.6
160 | 14.03 | 7.31 | 10.97 | 70.2 | 46.84 | 57.18 | I |  | MIN | 36.32 | 36.75 | 47.05 | 49.59 | 37.57 | 36.89 | 36.8 | 51.03 | 46.84 | 37.7 | 37.2 | 46.28 | 51.38 | 46.74 | 37.87 | 37.16 | 0 | 49.32 | 49.22 | 38.07 | 37.19 | 37.15 | 48.36 | 53.9 | 38.98 | 37.35 | 45.57 | 53.7 | 55.74 | 38.03
161 | 12.51 | 0.04 | 2.48 | 62.28 | 37.7 | 42.58 | O |  | AVG | 54.85 | 56.39 | 60.27 | 59.29 | 46.6 | 57.21 | 55.74 | 58.38 | 57.18 | 42.58 | 58.27 | 63.58 | 60.68 | 58.52 | 42.86 | 51.66 | 62.26 | 60.37 | 59.78 | 43.26 | 55.45 | 56.72 | 61 | 62.19 | 47.88 | 56.83 | 63.37 | 65.44 | 65.7 | 44.18
162 | 14.84 | 0.04 | 9.87 | 72.7 | 37.2 | 58.27 | N
163 | 14.56 | 4.98 | 12.28 | 71.1 | 46.28 | 63.58
164 | 13.75 | 8.94 | 11.58 | 68.77 | 51.38 | 60.68 | W
165 | 14.12 | 6.24 | 11.19 | 70.4 | 46.74 | 58.52 | E
166 | 13.57 | 0.04 | 2.55 | 67.52 | 37.87 | 42.86 | L
167 | 12.66 | 0.04 | 8.26 | 62.37 | 37.16 | 51.66 | L
168 | 14.06 | 0 | 11.93 | 71.2 | 0 | 62.26
169 | 13.8 | 7.82 | 11.41 | 70.2 | 49.32 | 60.37 | F
170 | 13.54 | 8.25 | 11.63 | 66.65 | 49.22 | 59.78 | O
171 | 13.72 | 0.04 | 2.68 | 66.62 | 38.07 | 43.26 | U
172 | 14.47 | 0.03 | 9.11 | 71.8 | 37.19 | 55.45 | R
173 | 14.31 | 0.04 | 9.53 | 72.7 | 37.15 | 56.72
174 | 15.06 | 7.78 | 11.57 | 76.9 | 48.36 | 61 | D
175 | 14.34 | 9.3 | 11.84 | 71.6 | 53.9 | 62.19 | A
176 | 12.67 | 0.05 | 5.04 | 64.58 | 38.98 | 47.88 | T
177 | 14.04 | 0.05 | 9.9 | 69.25 | 37.35 | 56.83 | A
178 | 14.23 | 6.14 | 12.36 | 70.8 | 45.57 | 63.37
179 | 14.15 | 9.7 | 12.74 | 71.2 | 53.7 | 65.44
180 | 14.49 | 10.46 | 13.11 | 70.9 | 55.74 | 65.7
181 | 15.95 | 0.04 | 2.45 | 79.6 | 38.03 | 44.18
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 5 |  |  | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180 | 181
152 | 8.51 | ER | 0.29 | 57.32 | 34.75 | 37.23
153 | 12.94 | ER | 8.43 | 69.01 | 34.95 | 54.64 |  |  | FLOW
154 | 13.42 | ER | 10.34 | 70.7 | 37.26 | 58.39 | I |  | MAX | 8.51 | 12.94 | 13.42 | 13.02 | 14.17 | 11.1 | 12.3 | 12.68 | 13.19 | 12.52 | 12.01 | 13.19 | 12.78 | 13.18 | 12.63 | 11.75 | 13.17 | 12.95 | 12.65 | 13.47 | 13.01 | 13.44 | 14.11 | 13.37 | 13.48 | 12.51 | 13.18 | 13.28 | 13.48 | 14.33
155 | 13.02 | 8.09 | 10.75 | 67.06 | 48.56 | 58.25 | N |  | MIN | ER | ER | ER | 8.09 | 7.91 | ER | ER | ER | 6.91 | 7.81 | ER | ER | 5.26 | 6.67 | 6.29 | ER | 0 | ER | 7.75 | 7.56 | ER | ER | 6.23 | 8.79 | 7.83 | ER | ER | 6.58 | 9.8 | 0.18
156 | 14.17 | 7.91 | 11.22 | 72.4 | 47.39 | 59.67 | J |  | TOT | 0.29 | 8.43 | 10.34 | 10.75 | 11.22 | 1.16 | 8.35 | 8.53 | 10.28 | 10.51 | 3.08 | 10.04 | 10.83 | 10.53 | 10.07 | 2.19 | 11.06 | 10.14 | 10.87 | 11.23 | 4.17 | 8.46 | 10.85 | 11.12 | 11.05 | 1.59 | 10.24 | 11.93 | 12.24 | 11.49
157 | 11.1 | ER | 1.16 | 59 | 35.88 | 39.48 | E | INJECTION WELL FIVE
158 | 12.3 | ER | 8.35 | 65.29 | 35.42 | 53.9 | C |  | PSI
159 | 12.68 | ER | 8.53 | 67.25 | 36.6 | 53.88 | T |  | MAX | 57.32 | 69.01 | 70.7 | 67.06 | 72.4 | 59 | 65.29 | 67.25 | 69.34 | 64.38 | 65.07 | 70 | 67.91 | 69.13 | 66.5 | 60.44 | 70.2 | 69.19 | 65.52 | 68.7 | 65.75 | 71.7 | 76 | 70.5 | 69.89 | 63.68 | 69.97 | 70.2 | 69.87 | 73.7
160 | 13.19 | 6.91 | 10.28 | 69.34 | 45.82 | 56.12 | I |  | MIN | 34.75 | 34.95 | 37.26 | 48.56 | 47.39 | 35.88 | 35.42 | 36.6 | 45.82 | 47.6 | 36.13 | 37.1 | 46.87 | 48.39 | 43.9 | 36.81 | 0 | 37.59 | 48.23 | 46.58 | 36.85 | 35.49 | 47.35 | 52.96 | 48.11 | 36.34 | 36.87 | 49.62 | 54.74 | 37.76
161 | 12.52 | 7.81 | 10.51 | 64.38 | 47.6 | 56.6 | O |  | AVG | 37.23 | 54.64 | 58.39 | 58.25 | 59.67 | 39.48 | 53.9 | 53.88 | 56.12 | 56.6 | 43.82 | 59.55 | 59.57 | 57.57 | 54.98 | 40.81 | 60.99 | 58.19 | 58.75 | 59.2 | 45.53 | 54.8 | 59.91 | 61.18 | 59.81 | 40.65 | 60 | 64.35 | 64.61 | 61.42
162 | 12.01 | ER | 3.08 | 65.07 | 36.13 | 43.82 | N
163 | 13.19 | ER | 10.04 | 70 | 37.1 | 59.55
164 | 12.78 | 5.26 | 10.83 | 67.91 | 46.87 | 59.57 | W
165 | 13.18 | 6.67 | 10.53 | 69.13 | 48.39 | 57.57 | E
166 | 12.63 | 6.29 | 10.07 | 66.5 | 43.9 | 54.98 | L
167 | 11.75 | ER | 2.19 | 60.44 | 36.81 | 40.81 | L
168 | 13.17 | 0 | 11.06 | 70.2 | 0 | 60.99
169 | 12.95 | ER | 10.14 | 69.19 | 37.59 | 58.19 | F
170 | 12.65 | 7.75 | 10.87 | 65.52 | 48.23 | 58.75 | I
171 | 13.47 | 7.56 | 11.23 | 68.7 | 46.58 | 59.2 | V
172 | 13.01 | ER | 4.17 | 65.75 | 36.85 | 45.53 | E
173 | 13.44 | ER | 8.46 | 71.7 | 35.49 | 54.8
174 | 14.11 | 6.23 | 10.85 | 76 | 47.35 | 59.91 | D
175 | 13.37 | 8.79 | 11.12 | 70.5 | 52.96 | 61.18 | A
176 | 13.48 | 7.83 | 11.05 | 69.89 | 48.11 | 59.81 | T
177 | 12.51 | ER | 1.59 | 63.68 | 36.34 | 40.65 | A
178 | 13.18 | ER | 10.24 | 69.97 | 36.87 | 60
179 | 13.28 | 6.58 | 11.93 | 70.2 | 49.62 | 64.35
180 | 13.48 | 9.8 | 12.24 | 69.87 | 54.74 | 64.61
181 | 14.33 | 0.18 | 11.49 | 73.7 | 37.76 | 61.42

## RMW PRN DATA
julian | u-avg | u-min | u-max | l-avg | l-min | l-max
152 | 22.63 | 22.53 | 22.68 | 44.59 | 44.54 | 44.64 | R |  |  | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180 | 181
E
[7 empty] | G |  | LOW
[7 empty] | I |  | MIN | 152: 22.53
[7 empty] | O |  | MAX | 152: 22.68
[7 empty] | N |  | AVG | 152: 22.63
[7 empty] | A | RMW
[7 empty] | L |  | UP
[9 empty] | MIN | 152: 44.54
[7 empty] | M |  | MAX | 152: 44.64
[7 empty] | O |  | AVG | 152: 44.59
N
I
T
O
R
W
E
L
L
R
M
W
O
N
E
152 | 41.8 | 40.67 | 43.53 | 48.24 | 48.09 | 48.39 | M |  |  | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180 | 181
153 | 42.37 | 40.69 | 44.33 | 48.29 | 48.09 | 48.44 | O
154 | 43.46 | 41.99 | 45.18 | 48.38 | 48.18 | 48.54 | N |  | LOW
155 | 42.97 | 41.53 | 44.13 | 48.39 | 48.19 | 48.56 | I |  | MIN | 40.67 | 40.69 | 41.99 | 41.53 | 41.46 | 38.15 | 37.1 | 40.22 | 41.94 | 42.05 | 42.37 | 42.8 | 39 | 38.41 | 41.12 | 41.05 | ER | 42.79 | 41.87 | 39.02 | 38.41 | 40.76 | 41.33 | 42.32 | 42.98 | 43.38 | 39.2 | 38.68 | 40.46 | 41.83
156 | 42.88 | 41.46 | 45.19 | 48.44 | 48.25 | 48.59 | T |  | MAX | 43.53 | 44.33 | 45.18 | 44.13 | 45.19 | 44.77 | 40.83 | 44.3 | 44.11 | 43.47 | 45.37 | 46.05 | 43.94 | 42.94 | 44.62 | 46.59 | 45.69 | 46.19 | 46.89 | 43.32 | 42.52 | 43.37 | 45.98 | 46.11 | 46.65 | 45.97 | 45.23 | 42.92 | 44.75 | 45.77
157 | 41.65 | 38.15 | 44.77 | 43.36 | 40.7 | 48.52 | O |  | AVG | 41.8 | 42.37 | 43.46 | 42.97 | 42.88 | 41.65 | 39.22 | 42.16 | 42.77 | 42.81 | 43.52 | 44.03 | 42.3 | 40.79 | 42.93 | 43.15 | 43.31 | 43.81 | 43.79 | 41.44 | 40.4 | 42.01 | 43.55 | 44.03 | 44.48 | 44.27 | 42.23 | 40.76 | 42.75 | 43.62
158 | 39.22 | 37.1 | 40.83 | 46.4 | 41.07 | 49.01 | R | MW-1
159 | 42.16 | 40.22 | 44.3 | 48.68 | 48.52 | 48.83 |  |  | UP
160 | 42.77 | 41.94 | 44.11 | 48.68 | 48.58 | 48.85 | W |  | MIN | 48.09 | 48.09 | 48.18 | 48.19 | 48.25 | 40.7 | 41.07 | 48.52 | 48.58 | 48.68 | 48.75 | 48.77 | 43.02 | 43.47 | 48.78 | 48.82 | ER | 48.85 | 48.83 | 44.13 | 44.43 | 48.77 | 48.87 | 49.09 | 49.13 | 49.07 | 41.69 | 42.13 | 49.05 | 49.1
161 | 42.81 | 42.05 | 43.47 | 48.77 | 48.68 | 48.92 | E |  | MAX | 48.39 | 48.44 | 48.54 | 48.56 | 48.59 | 48.52 | 49.01 | 48.83 | 48.85 | 48.92 | 48.96 | 48.96 | 48.98 | 49.16 | 49 | 49.09 | 49.15 | 49.18 | 49.16 | 49.06 | 49.29 | 49.18 | 49.33 | 49.46 | 49.46 | 49.41 | 49.33 | 49.37 | 49.36 | 49.45
162 | 43.52 | 42.37 | 45.37 | 48.91 | 48.75 | 48.96 | L |  | AVG | 48.24 | 48.29 | 48.38 | 48.39 | 48.44 | 43.36 | 46.4 | 48.68 | 48.68 | 48.77 | 48.91 | 48.92 | 44.81 | 47.39 | 48.93 | 48.95 | 48.86 | 49 | 49 | 46.08 | 47.51 | 48.97 | 49.09 | 49.21 | 49.29 | 49.19 | 44.27 | 47 | 49.19 | 49.29
163 | 44.03 | 42.8 | 46.05 | 48.92 | 48.77 | 48.96 | L
164 | 42.3 | 39 | 43.94 | 44.81 | 43.02 | 48.98
165 | 40.79 | 38.41 | 42.94 | 47.39 | 43.47 | 49.16 | O
166 | 42.93 | 41.12 | 44.62 | 48.93 | 48.78 | 49 | N
167 | 43.15 | 41.05 | 46.59 | 48.95 | 48.82 | 49.09 | E
168 | 43.31 | ER | 45.69 | 48.86 | ER | 49.15
169 | 43.81 | 42.79 | 46.19 | 49 | 48.85 | 49.18 | I
170 | 43.79 | 41.87 | 46.89 | 49 | 48.83 | 49.16 | N
171 | 41.44 | 39.02 | 43.32 | 46.08 | 44.13 | 49.06 | J
172 | 40.4 | 38.41 | 42.52 | 47.51 | 44.43 | 49.29 | E
173 | 42.01 | 40.76 | 43.37 | 48.97 | 48.77 | 49.18 | C
174 | 43.55 | 41.33 | 45.98 | 49.09 | 48.87 | 49.33 | T
175 | 44.03 | 42.32 | 46.11 | 49.21 | 49.09 | 49.46 | I
176 | 44.48 | 42.98 | 46.65 | 49.29 | 49.13 | 49.46 | O
177 | 44.27 | 43.38 | 45.97 | 49.19 | 49.07 | 49.41 | N
178 | 42.23 | 39.2 | 45.23 | 44.27 | 41.69 | 49.33
179 | 40.76 | 38.68 | 42.92 | 47 | 42.13 | 49.37 | W
180 | 42.75 | 40.46 | 44.75 | 49.19 | 49.05 | 49.36 | E
181 | 43.62 | 41.83 | 45.77 | 49.29 | 49.1 | 49.45 | L
L
152 | 42.58 | 42.56 | 42.76 | 29.22 | 28.7 | 29.86 | M |  |  | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180 | 181
153 | 42.81 | 42.62 | 42.84 | 29.37 | 28.65 | 30.15 | O
154 | 42.89 | 42.77 | 42.96 | 29.88 | 29.22 | 30.78 | N |  | LOW
155 | 42.91 | 42.78 | 42.98 | 29.77 | 29.16 | 30.26 | I |  | MIN | 42.56 | 42.62 | 42.77 | 42.78 | 42.86 | 37.09 | 37.06 | 42.7 | 42.88 | 43.02 | 43.1 | 43.13 | 37.85 | 37.83 | 42.89 | 43.03 | ER | 43.18 | 43.22 | 35.69 | 35.63 | 42.82 | 43.05 | 43.26 | 43.36 | 43.33 | 35.06 | 35.04 | 42.99 | 43.14
156 | 42.96 | 42.86 | 43.01 | 29.74 | 29.26 | 30.53 | T |  | MAX | 42.76 | 42.84 | 42.96 | 42.98 | 43.01 | 43.01 | 42.71 | 42.94 | 43.04 | 43.17 | 43.2 | 43.22 | 43.26 | 42.89 | 43.08 | 43.24 | 43.31 | 43.37 | 43.37 | 43.34 | 42.84 | 43.09 | 43.29 | 43.46 | 43.47 | 43.48 | 43.47 | 42.99 | 43.22 | 43.35
157 | 38.95 | 37.09 | 43.01 | 27.06 | 25.15 | 30.05 | O |  | AVG | 42.58 | 42.81 | 42.89 | 42.91 | 42.96 | 38.95 | 40.89 | 42.85 | 42.97 | 43.01 | 43.08 | 43.12 | 39.41 | 41.37 | 42.99 | 43.03 | 43.08 | 43.35 | 43.37 | 38.74 | 40.51 | 42.94 | 43.11 | 43.36 | 43.47 | 43.46 | 37.73 | 40.48 | 43.02 | 43.35
158 | 40.89 | 37.06 | 42.71 | 28.52 | 24.9 | 30.49 | R | MW-2
159 | 42.85 | 42.7 | 42.94 | 30.2 | 29.55 | 30.76 |  |  | UP
160 | 42.97 | 42.88 | 43.04 | 30.34 | 29.99 | 30.77 | W |  | MIN | 28.7 | 28.65 | 29.22 | 29.16 | 29.26 | 25.15 | 24.9 | 29.55 | 29.99 | 29.86 | 30.1 | 30.45 | 25.59 | 25.41 | 30.29 | 30.04 | ER | 30.74 | 30.47 | 25.22 | 25 | 30.12 | 30.37 | 30.66 | 30.96 | 31.23 | 25.8 | 25.92 | 30.66 | 31.14
161 | 43.01 | 43.02 | 43.17 | 30.23 | 29.86 | 30.51 | E |  | MAX | 29.86 | 30.15 | 30.78 | 30.26 | 30.53 | 30.05 | 30.49 | 30.76 | 30.77 | 30.51 | 31.2 | 31.5 | 30.66 | 31.18 | 31.65 | 32.11 | 32.06 | 32.04 | 31.99 | 30.86 | 30.88 | 31.22 | 31.69 | 32.07 | 32.59 | 32.4 | 31.56 | 31.99 | 32.17 | 32.68
162 | 43.08 | 43.1 | 43.2 | 30.54 | 30.1 | 31.2 | L |  | AVG | 29.22 | 29.37 | 29.88 | 29.77 | 29.74 | 27.06 | 28.52 | 30.2 | 30.34 | 30.23 | 30.54 | 30.85 | 27.65 | 29.17 | 30.87 | 30.9 | 30.96 | 31.19 | 31.12 | 27.68 | 28.93 | 30.6 | 31.01 | 31.38 | 31.76 | 31.76 | 28.27 | 29.68 | 31.44 | 31.65
163 | 43.12 | 43.13 | 43.22 | 30.85 | 30.45 | 31.5 | L
164 | 39.41 | 37.85 | 43.26 | 27.65 | 25.59 | 30.66
165 | 41.37 | 37.83 | 42.89 | 29.17 | 25.41 | 31.18 | T
166 | 42.99 | 42.89 | 43.08 | 30.87 | 30.29 | 31.65 | W
167 | 43.03 | 43.03 | 43.24 | 30.9 | 30.04 | 32.11 | O
168 | 43.08 | ER | 43.31 | 30.96 | ER | 32.06
169 | 43.35 | 43.18 | 43.37 | 31.19 | 30.74 | 32.04 | I
170 | 43.37 | 43.22 | 43.37 | 31.12 | 30.47 | 31.99 | N
171 | 38.74 | 35.69 | 43.34 | 27.68 | 25.22 | 30.86 | J
172 | 40.51 | 35.63 | 42.84 | 28.93 | 25 | 30.88 | E
173 | 42.94 | 42.82 | 43.09 | 30.6 | 30.12 | 31.22 | C
174 | 43.11 | 43.05 | 43.29 | 31.01 | 30.37 | 31.69 | T
175 | 43.36 | 43.26 | 43.46 | 31.38 | 30.66 | 32.07 | I
176 | 43.47 | 43.36 | 43.47 | 31.76 | 30.96 | 32.59 | O
177 | 43.46 | 43.33 | 43.48 | 31.76 | 31.23 | 32.4 | N
178 | 37.73 | 35.06 | 43.47 | 28.27 | 25.8 | 31.56
179 | 40.48 | 35.04 | 42.99 | 29.68 | 25.92 | 31.99 | W
180 | 43.02 | 42.99 | 43.22 | 31.44 | 30.66 | 32.17 | E
181 | 43.35 | 43.14 | 43.35 | 31.65 | 31.14 | 32.68 | L
L
152 | 45.39 | 45.23 | 45.44 | 33.09 | 32.92 | 33.29 | M |  |  | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180 | 181
153 | 45.47 | 45.33 | 45.53 | 33.31 | 33.09 | 33.43 | O
154 | 45.52 | 45.47 | 45.65 | 33.42 | 33.3 | 33.61 | N |  | LOW
155 | 45.52 | 45.51 | 45.7 | 33.46 | 33.35 | 33.67 | I |  | MIN | 45.23 | 45.33 | 45.47 | 45.51 | 45.6 | 36.44 | 36.44 | 45.37 | 45.59 | 45.73 | 45.83 | 45.86 | 38.01 | 38.02 | 45.56 | 45.73 | ER | 45.89 | 45.98 | 35.51 | 35.49 | 45.52 | 45.76 | 45.99 | 46.1 | 46.09 | 36.83 | 36.87 | 45.7 | 45.86
156 | 45.58 | 45.6 | 45.73 | 33.52 | 33.45 | 33.72 | T |  | MAX | 45.44 | 45.53 | 45.65 | 45.7 | 45.73 | 45.73 | 45.37 | 45.62 | 45.73 | 45.86 | 45.91 | 45.95 | 45.99 | 45.56 | 45.79 | 45.95 | 46.04 | 46.13 | 46.11 | 46.08 | 45.52 | 45.79 | 46 | 46.17 | 46.2 | 46.21 | 46.2 | 45.7 | 45.94 | 46.09
157 | 39.37 | 36.44 | 45.73 | 22.81 | 17.9 | 33.65 | O |  | AVG | 45.39 | 45.47 | 45.52 | 45.52 | 45.58 | 39.37 | 42.57 | 45.47 | 45.58 | 45.81 | 45.91 | 45.95 | 40.11 | 43.22 | 45.65 | 45.88 | 45.82 | 46 | 46.02 | 39.45 | 42.27 | 45.64 | 45.87 | 46 | 46.08 | 46.09 | 39.82 | 42.79 | 45.87 | 45.98
158 | 42.57 | 36.44 | 45.37 | 28.18 | 17.82 | 32.95 | R | MW-3
159 | 45.47 | 45.37 | 45.62 | 32.97 | 32.87 | 33.23 |  |  | UP
160 | 45.58 | 45.59 | 45.73 | 33.17 | 33.09 | 33.32 | W |  | MIN | 32.92 | 33.09 | 33.3 | 33.35 | 33.45 | 17.9 | 17.82 | 32.87 | 33.09 | 33.21 | 33.3 | 33.4 | 17.99 | 17.92 | 33.08 | 33.23 | ER | 33.4 | 33.44 | 17.98 | 17.93 | 33.16 | 33.4 | 33.66 | 33.79 | 33.72 | 18.08 | 18.03 | 33.4 | 33.59
161 | 45.81 | 45.73 | 45.86 | 33.31 | 33.21 | 33.45 | E |  | MAX | 33.29 | 33.43 | 33.61 | 33.67 | 33.72 | 33.65 | 32.95 | 33.23 | 33.32 | 33.45 | 33.56 | 33.58 | 33.61 | 33.09 | 33.34 | 33.51 | 33.63 | 33.7 | 33.7 | 33.6 | 33.25 | 33.55 | 33.81 | 34.04 | 34.04 | 34 | 33.94 | 33.41 | 33.74 | 33.91
162 | 45.91 | 45.83 | 45.91 | 33.45 | 33.3 | 33.56 | L |  | AVG | 33.09 | 33.31 | 33.42 | 33.46 | 33.52 | 22.81 | 28.18 | 32.97 | 33.17 | 33.31 | 33.45 | 33.49 | 22.08 | 28.42 | 33.17 | 33.39 | 33.43 | 33.53 | 33.54 | 23.78 | 28.16 | 33.31 | 33.53 | 33.79 | 33.95 | 33.88 | 22.95 | 28.47 | 33.53 | 33.79
163 | 45.95 | 45.86 | 45.95 | 33.49 | 33.4 | 33.58 | L
164 | 40.11 | 38.01 | 45.99 | 22.08 | 17.99 | 33.61
165 | 43.22 | 38.02 | 45.56 | 28.42 | 17.92 | 33.09 | T
166 | 45.65 | 45.56 | 45.79 | 33.17 | 33.08 | 33.34 | H
167 | 45.88 | 45.73 | 45.95 | 33.39 | 33.23 | 33.51 | R
168 | 45.82 | ER | 46.04 | 33.43 | ER | 33.63 | E
169 | 46 | 45.89 | 46.13 | 33.53 | 33.4 | 33.7 | E
170 | 46.02 | 45.98 | 46.11 | 33.54 | 33.44 | 33.7
171 | 39.45 | 35.51 | 46.08 | 23.78 | 17.98 | 33.6 | I
172 | 42.27 | 35.49 | 45.52 | 28.16 | 17.93 | 33.25 | N
173 | 45.64 | 45.52 | 45.79 | 33.31 | 33.16 | 33.55 | J
174 | 45.87 | 45.76 | 46 | 33.53 | 33.4 | 33.81 | E
175 | 46 | 45.99 | 46.17 | 33.79 | 33.66 | 34.04 | C
176 | 46.08 | 46.1 | 46.2 | 33.95 | 33.79 | 34.04 | T
177 | 46.09 | 46.09 | 46.21 | 33.88 | 33.72 | 34 | I
178 | 39.82 | 36.83 | 46.2 | 22.95 | 18.08 | 33.94 | O
179 | 42.79 | 36.87 | 45.7 | 28.47 | 18.03 | 33.41 | N
180 | 45.87 | 45.7 | 45.94 | 33.53 | 33.4 | 33.74
181 | 45.98 | 45.86 | 46.09 | 33.79 | 33.59 | 33.91 | W
E
L
L

## SHIFT DATA
PERSONNEL LIST
[6 empty] | CERTIFICATION NUMBER |  | SOCIAL SECURITY NUMBER
CHIEF OPERATORS
McGEARY, J. | CO# 4545-A | [5 empty] | "A" |  | 2D | J. BAROFSKY | 5096-C
BAYLER, J. | CO# 4474-A | [5 empty] | "A" |  | 5 | S. HULL | 5613-C
[9 empty] | 4 | VACANT | X
[9 empty] | 3 | J. TINKER | 3291-C
[9 empty] | 1 | G. SLAYTON | 2606-B
[9 empty] | 2 | H. WALKER | 4700-A
OPERATOR II' S
BAROFSKY, J. | CO# 5096-C | 1 |  | BAROFSKY, J. | 1 | CO# 5096-C |  |  | 5 | J. BENTLEY | X
JVACANT | CO# XXXX-X | 4 |  | BENTLEY, J. | 4 | CO# 9366-C |  |  | 1D | S. CURMODE | X
THOMAS, P. | CO# 12833 C | 5 |  | CURMODE, S. | 5 | CO# 9379-A |  |  | 4 | K. HENDERSON | 5087-B
BENTLEY, J. | CO# 9366-C | 2D |  | HULL, S. | 2D | CO# 5613-C |  |  | 3D | K. JONES | 2466-C
CURMODE, S. | CO# 9379-A | 2 |  | JVACANT | 2 | CO# XXXX-X |  |  | 3 | G. KLEYNHANS | 7367-C
HULL, S. | CO# 5613-C | 3 |  | THOMAS, P. | 3 | CO# 12833 C |  |  | 2 | A. MORROW | 9164-C
[9 empty] | 1 | J. RAINFORTH | 2718-C
OPERATOR I' S
PEUGEOT, P. | CO# 12817-C | 5A |  | DESHIELDS, D | 5A | CO# XXXXX-X | 5A | DESHIELDS, D
PEUGEOT, P. | CO# 12817-C | 3 |  | FREIDLAND, M. | 3 | CO# 13437-C | 3 | FREIDLAND, M.
ROUSE, Y | CO# XXXXX-X | 4 |  | HENDERSON, K. | 4 | CO# 5087-B | 4 | HENDERSON, K.
NOBERT, B. | CO# 9661-C | 4A |  | KOKLAS, D. | 4A | CO# 13506-C | 4A | KOKLAS, D.
FREIDLAND, M. | CO# 13437-C | 2 |  | NOBERT, B. | 2 | CO# 9661-C | 2 | NOBERT, B.
SANDERS, C. | CO# 13500-C | 1 |  | PEUGEOT, P. | 1 | CO# 12817-C | 1 | PEUGEOT, P.
HENDERSON, K. | CO# 5087-B | 1D |  | ROUSE, Y | 1D | CO# XXXXX-X | 1D | ROUSE, Y
1 | #N/A | 3D |  | SANDERS, C. | 3D | CO# 13500-C | 3D | SANDERS, C.
KOKLAS, D. | CO# 13506-C | 5 |  | VERBOSH, R. | 5 | CO# 12667-C | 5 | VERBOSH, R.
|  | 4 | 1 | BERNARDI, J | 4 | CO# XXXX-X
|  | 3 | 2 | FREIDLAND, M. | 3 | CO# 13437-C
|  | 5A | 3 | FUTURE, 5A | 5A | CO# XXXX-X
|  | 1 | 4 | HENDERSON, K. | 1 | CO# 5087-B
|  | 2 | 5 | KOKLAS, D. | 2 | CO# 13506-C
|  | 5 | 6 | NOBERT, B. | 5 | CO# 9661-C
|  | 4A | 7 | PEUGEOT, P. | 4A | CO# 12817-C
|  | 1D | 8 | SANDERS, C. | 1D | CO# 13500-C
|  | 3D | 9 | VERBOSH, R. | 3D | CO# 12667-C

## COVER PAGE
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
|  | JUNE |  | 2005
| OPERATOR | TITLE | CERTIFICATE # | TOTAL COST |  |  | 77580.5731
1 ST SHIFT |  |  |  | PEAK TO FLOW RATIO |  |  | 1.2366
2230-0630 | BAROFSKY, J. | OP. II | CO# 5096-C
| PEUGEOT, P. | OP. I | CO# 12817-C |  | TOTAL SUSPENDED SOLIDS
| ROUSE, Y | OP. I DEWAT | CO# XXXXX-X |  |  |  | LBS/DAY
|  |  |  | RAW INFLUENT |  |  | 31748.4236
2 ND SHIFT |  |  |  | FINAL EFFLUENT |  |  | 4182.1945
0630-1430 | McGEARY, J. | CHIEF | CO# 4545-A |  | TOTAL CBOD
| JVACANT | OP. II RELIEF | CO# XXXX-X |  |  |  | LBS/DAY
| HULL, S. | OP. II DEWAT | CO# 5613-C | RAW INFLUENT |  |  | 22761.4605
| NOBERT, B. | OP. I RELIEF | CO# 9661-C | FINAL EFFLUENT |  |  | 956.7657
CHEMICALS
3 RD SHIFT | BAYLER, J. | CHIEF | CO# 4474-A |  |  | COST | POUNDS
1430-2230 | THOMAS, P. | OP. II | CO# 12833 C | HYDROGEN PEROXIDE |  | 2969.7015 | 20271
| FREIDLAND, M. | OP. I | CO# 13437-C | CHLORINE |  | 12171.7 | 41260
| SANDERS, C. | OP. I DEWAT | CO# 13500-C | POLYMER |  | 9330.2916 | 15295.56
SLUDGE REMOVED
4 TH SHIFT | [6 empty] | TONS
WEEKEND | BENTLEY, J. | OP. II | CO# 9366-C | DRY TONS |  |  | 508.7959
2230-1030 | HENDERSON, K. | OP. I | CO# 5087-B |  | ENERGY
| KOKLAS, D. | OPI | CO# 13506-C |  |  | COST | KILOWATTS
5 TH SHIFT |  |  |  | FPL CONSUMPTION |  | 53108.88 | 965616
WEEKEND | CURMODE, S. | OP. II | CO# 9379-A
1030-2230 | 1 | OP. I | #N/A | POPULATION EQUIVALENCE |  |  | 133890.9443
This Monthly Operation Report prepared by: |  |  | BAYLER, J. | CO# 4474-A
State DEP Plant Classification: Class "A" Level "II"
I certify that I am familiar with the information contained in this report and that to the best of my knowledge and
belief, such information is true, complete and accurate.
Facilitiy Manager's Signature: ____________________________________ CO# __________________
Division Manager's Signature: ____________________________________ CO# __________________
Please direct all inquiries reguarding this report to the City Official Mailing Address:
Director of Public Services |  |  | Phone (954) 776-5151
City of Fort Lauderdale
P.O. Drawer 14250 |  |  | Copies mailed: Date ________________ To: DEP _____
Fort Lauderdale, Florida | [5 empty] | DNRP _____
33302
PAGE 1

## PRINT PAGES
UNDERGROUND INJECTION CONTROL SECTION
[29 empty] | MONTHLY OPERATING REPORT DATA SUMMARY | [13 empty] | DEP From # 17-801.900 (1) | [11 empty] | DEP From # 17-801.900 (1) | [19 empty] | DAILY SAMPLE RESULTS - PART B
[25 empty] | FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT DATE: |  | JUNE | 2005 | [8 empty] | Form Title:Domestic Wastewater Treatment | [11 empty] | Form Title:Domestic Wastewater Treatment
[25 empty] | I.D. NUMBER: 5006M02066 |  |  |  |  | CHIEF OPERATOR: |  |  | McGEARY, J. | CO# 4545-A | [8 empty] | Plant Monthly Operating Report | [11 empty] | Plant Monthly Operating Report | [15 empty] | Permit Number: |  | FLA041378 |  |  |  |  | Three-month Average Daily Flow: | [5 empty] | 37.8641
[25 empty] | TELEPHONE NUMBER: (954) 523-1002 | [17 empty] | Effective Date: July 1, 1991 | [11 empty] | Effective Date: July 1, 1991 | [15 empty] | Monitoring Period |  | From: | 2005-06-01 | To: | 2005-07-01 |  | (TMADF):/Permitted Capacity)x100: | [5 empty] | 67.98%
[19 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [9 empty] | INJECTION WELL DATA | [13 empty] | DEP Application No. __________________ | [11 empty] | DEP Application No. __________________ | [11 empty] | Department of Natural Resource Protection
[5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [13 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [6 empty] | IW-1 | IW-2 |  | IW-3 |  | IW-4 | IW-5 | [35 empty] | Laboratory/Licensing/Enforcement |  |  |  | Flow | Flow | Flow | Flow | Flow | Flow | CBOD5 | CBOD5 | TSS | TSS | pH | pH | TDS | NH-3 | TKN | pH | cond. | temp. | TP
[5 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [13 empty] | MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING | [5 empty] | PERMIT/CERTIFICATION NUMBER: | 0054569-142-UO | 0054569-142-UO |  | 0054569-142-UO |  | 0054569-142-UO | 0054569-142-UO | [19 empty] | DOMESTIC WASTEWATER TREATMENT PLANT | [11 empty] | BROWARD COUNTY DEPARTMENT OF NATURAL RESOURCE PROTECTION | [5 empty] | 218 S. W. 1st Avenue |  |  | (MGD) | (MGD) | (MGD) | (MGD) | (MGD) | (mg/l) | (mg/l) | (mg/l) | (mg/l) | (Min) | (Max) | mg/L | mg/L | mg/L | units | umho/ | F | mg/L
[5 empty] | MONTHLY OPERATIONAL REPORT | [13 empty] | MONITORING WELL ONE |  |  |  | 1/07/04 thru 1/06/09 |  | PERMIT EXPIRATION DATE: | 2009-01-06 | 2009-01-06 |  | 2009-01-06 |  | 2009-01-06 | 2009-01-06 | [19 empty] | MONTHLY OPERATING REPORT | [11 empty] | WASTEWATER TREATMENT PLANT | [5 empty] | Fort Lauderdale, FL 33301 | [17 empty] | cm
[5 empty] | PROCESS DATA | [11 empty] | MW-1 | I.D. #: 5066A11311 |  |  | PERMIT # 0054569-142-UO |  |  |  | CASING DEPTH | 2799' | 2798' |  | 2800' |  | 2804' | 2818' | [8 empty] | DOMESTIC WASTEWATER TREATMENT PLANT |  |  |  |  | (34) | [8 empty] | MONTH: | JUNE |  | YEAR: | 2005 |  |  |  |  | MONTHLY SLUDGE REPORTS | [5 empty] | Tel. No. (954) 765-4804 | Code | 50050 | 50050 | 50050 | 50050 | 50050 | 50050 | 80082 | 80082 | 00530 | 00530 | 00400 | 00400
| RUN DATE | [14 empty] | RUN DATE | [8 empty] | TOTAL DEPTH | 3513' | 3518' |  | 3977' |  | 3305' | 3462' | [8 empty] | MONTHLY OPERATING REPORT |  |  |  |  | DAY OF | FLOW | CHLORINE | CHLORINE | CBOD5 | TSS | CBOD5 | TSS | PH |  |  | EFFLUENT NUTRIENTS (MG/L) |  |  | I. | [10 empty] | Mon. Site | INF-001 | EFF-003 | EFF-004 | EFF-005 | EFF-006 | EFF-007 | INF-002 | EFF-001 | INF-002 | EFF-002 | EFF-002 | EFF-002
| 2026-07-30 | [14 empty] | 2026-07-30 |  | UPPER MONITOR ZONE |  |  |  |  | LOWER MONITOR ZONE |  | AVERAGE DAILY FLOW: | 9.49 | 9.6223 |  | 9.1297 |  | 9.3813 | 8.768 | MGD | [7 empty] | Part II - General Information |  |  |  |  | THE |  | RESIDUAL | RESIDUAL | INFLUENT | INFLUENT | EFFLUENT | EFFLUENT | EFFLUENT | TKN | NH3-N | NITRATE | TOTAL | FECAL | Plant Name: | GEORGE T. LOHMEYER WASTEWATER TREATMENT FACILITY | [6 empty] | MONTH: | JUNE |  | 1 | 42.712 | 10.99 | 11.21 | 10.64 | 9.47 | 0.29 | 79.5 | 3.94 | 200 | 11 | 6.6 | 6.6 | 1591 | 8 | 20 | 6.6 | 3110 | 84 | 0.56
[17 empty] | MIN | MAX | AVG |  |  | MIN | MAX | AVG | **MAX DAILY FLOW PER MO (mg): | 13.5 | 13.36 |  | 12.64 |  | 13.11 | 12.24 | MG | [12 empty] | MONTH | (MGD) | AFTER | AFTER DE- | [8 empty] | P | COLIFORM | II. | [7 empty] | YEAR: | 2005 |  | 2 | 46.568 | 5.18 | 12.27 | 11.31 | 9.48 | 8.43 | 61 | 2.64 | 90 | 15 | 6.5 | 6.5 | 1326 | 8.5 | 18 | 6.6 | 2690 | 84 | 0.57
| JUNE | INFLUENT | HOURLY | INFLUENT | INFLUENT | RAS | PERCENT | WAS | RAIN | Sufates | [5 empty] | JUNE | FT HEAD | FT HEAD | FT HEAD |  |  | FT HEAD | FT HEAD | FT HEAD | ** PEAK HR FLOW (MGD) ON MAX DAY: | 14.5881 | 14.8027 |  | 14.0503 |  | 14.4452 | 13.5099 | MGD |  | (1) Month: |  | JUNE |  | Year: | 2005 |  | Parameter | Units | STORET | Value |  |  | CONTACT | CHLORINATION | MG/L | MG/L | MG/L | MG/L | [6 empty] | A) | Sludge Treatment Provided: |  |  |  |  | B) | Sludge Dewater Processes |  |  |  | 3 | 47.958 | 10.54 | 4.7 | 11.26 | 11.43 | 10.34 | 74.36 | 3.69 | 38 | 6 | 6.6 | 6.7 | 1251 | 8.3 | 16 | 6.6 | 2520 | 84 | 0.57
| 2005 | FLOW | MAXIMUM | MAXIMUM | MINIMUM | FLOW | RAS | FLOW | INCHES | [6 empty] | 2005 | ABOVE | ABOVE | ABOVE |  |  | ABOVE | ABOVE | ABOVE | MAX SUSTAINED INJECTION PRESSURE: | 76 | 74.8 |  | 79.2 |  | 79.6 | 76 | PSIG |  | (2) Plant's DEP Identification Number: |  |  |  |  | 5006M02066 |  |  |  | Code |  | 1 | 42.712 | 0.8 |  | 79.5 | 200 | 3.94 | 11 | 6.6 | 20 | 8 | 0.32 | 0.56 | 0 |  |  | Aerobic Digestion | [5 empty] | Thickner |  |  | 4 | 45.725 | 11.63 | 10.55 | 0.64 | 11.49 | 10.75 | 52.28 | 2.35 | 70 | 17 | 6.5 | 6.6 | 1294 | 8 | 17 | 6.5 | 2550 | 84 | 0.86
|  | MGD | MGD | MGD | MGD | MGD |  | MGD | [8 empty] | NGVD | NGVD | NGVD |  |  | NGVD | NGVD | NGVD | MONTHLY AVG. INJECTION PRESSURE: | 54.774 | 54.1407 |  | 55.7207 |  | 56.283 | 55.1283 | PSIG |  | (3) Plant Name: |  |  |  | George T. Lohmeyer Regional Wastewater |  |  | (16) Monthly average daily flow | mgd | 050053 | 46.5754 | 2 | 46.568 | 0.8 |  | 61 | 90 | 2.64 | 15 | 6.6 | 18 | 8.5 | 0.25 | 0.57 | 179 |  |  | Anaerobic Digestion | [5 empty] | DGA___X___Filter Press |  |  | 5 | 48.199 | 12.09 | 10.1 | 9.13 | 4.53 | 11.22 | 22.47 | 2 | 68 | 10 | 6.5 | 6.6 | 1253 | 7.1 | 19 | 6.5 | 2490 | 84 | 1.8
| 1 | 42.712 | 2.323 | 63.12 | 12.239 | 13.621 | 31.89% | 0.679 | 1.45 | 132.5 |  | 1 |  |  |  | 1 | 48.09 | 48.39 | 48.44 |  |  | 40.67 | 43.53 | 41.8 | *** MAX INJECTION PRESSURE PERMITTED: | 99 | 99 |  | 99 |  | 99 | 99 | PSIG |  |  |  |  | Treatment Facility |  |  |  | (17) Permitted capacity | mgd | - | 55.7 | 3 | 47.958 | 1.5 |  | 74.36 | 38 | 3.69 | 6 | 6.6 | 16 | 8.3 | 0.36 | 0.57 | 0 |  |  | Other | [5 empty] | Centrifuge Drying Beds, Bed #______ |  |  | 6 | 48.32 | 12.07 | 12.3 | 11.58 | 10.08 | 1.16 | 38.53 | 2.33 | 78 | 8 | 6.6 | 6.8 | 1148 | 8.8 | 9 | 6.7 | 2380 | 84 | 0.43
| 2 | 46.568 | 2.34 | 61.903 | 24.735 | 13.202 | 28.35% | 0.633 | 0.84 | 131 |  | 2 |  |  |  | 2 | 48.09 | 48.44 | 48.24 |  |  | 40.69 | 44.33 | 42.37 | ***NOTE: (INJECTION PRESSURE NOT TO EXCEED 66% TESTED PRESSURE | [9 empty] | (4) Plant Address: |  |  | 1765 S.E. 18th Street at |  |  |  | (18) Three-month average daily flow | mgd | - | 37.8641 | 4 | 45.725 | 1.3 |  | 52.28 | 70 | 2.35 | 17 | 6.5 | 17 | 8 | 0.44 | 0.86 | 0 | [8 empty] | Heat Treatment____No Treatment |  |  | 7 | 44.575 | 2.65 | 12.37 | 11.37 | 9.37 | 8.35 | 44 | 2 | 84 | 13 | 6.6 | 6.8 | 1210 | 10 | 11 | 6.6 | 2450 | 83.8 | 0.41
| 3 | 47.958 | 2.345 | 62.223 | 29.349 | 13.58 | 28.32% | 0.198 | 0.03 | 130.5 |  | 3 |  |  |  | 3 | 48.18 | 48.54 | 48.38 |  |  | 41.99 | 45.18 | 43.46 | TESTED CASING PRESSURE DURING MIT | 150 | 150 |  | 150 |  | 150 | 150 | PSIG |  |  |  |  | Eisenhower Boulevard |  |  |  | (19) Percent of permitted capacity | % | - | 67.98% | 5 | 48.199 | 1.1 |  | 22.47 | 68 | 2 | 10 | 6.5 | 19 | 7.1 | 0.044 | 1.8 | 0 | [7 empty] | x | Other: | Press Dewatered |  | 8 | 42.458 | 9.08 | 2.71 | 10.98 | 11.11 | 8.53 | 53.8 | 2.3 | 78 | 3 | 6.6 | 6.6 | 1304 | 9.4 | 10 | 6.6 | 2500 | 84 | 0.47
| 4 | 45.725 | 2.15 | 59.692 | 23.299 | 13.206 | 28.88% | 0 | 0.5 | 137.8 |  | 4 |  |  |  | 4 | 48.19 | 48.56 | 48.39 |  |  | 41.53 | 44.13 | 42.97 | [10 empty] | (5) City: |  | Fort Lauderdale |  |  |  |  | (20) CBOD5 Effluent | mg/L | 080082 | 2.4631 | 6 | 48.32 | 1.2 |  | 38.53 | 78 | 2.33 | 8 | 6.7 | 9 | 8.8 | 0.14 | 0.43 | 0 | [9 empty] | To Landfill |  | 9 | 41.712 | 10.13 | 8.75 | 1.46 | 10.97 | 10.28 | 71.8 | 2.21 | 42 | 9 | 6.5 | 6.7 | 1231 | 9.8 | 12 | 6.6 | 2490 | 84 | 0.71
| 5 | 48.199 | 2.473 | 64.883 | 22.396 | 12.227 | 25.37% | 0.698 | 0.209 | 135.5 |  | 5 |  |  |  | 5 | 48.25 | 48.59 | 48.44 |  |  | 41.46 | 45.19 | 42.88 |  |  | MONITORING WELL DATA | [7 empty] | (6) County: |  | Broward |  |  |  |  | (21) CBOD5 Effluent | lbs/day | - | 956.7657 | 7 | 44.575 | 1 |  | 44 | 84 | 2 | 13 | 6.6 | 11 | 10 | 0.13 | 0.41 | 18 | III. | Final Sludge Disposal: | [9 empty] | 10 | 42.112 | 11.18 | 9.32 | 8.49 | 2.48 | 10.51 | 86.4 | 2 | 60 | 14 | 6.5 | 6.6 | 1084 | 7.7 | 12 | 6.6 | 2250 | 84 | 0.98
| 6 | 48.32 | 2.281 | 63.505 | 28.74 | 12.636 | 26.15% | 0.481 | 0 | 131.3 |  | 6 |  |  |  | 6 | 40.7 | 48.52 | 43.36 |  |  | 38.15 | 44.77 | 41.65 |  | MW-1 | MW-2 |  | MW-3 |  | RMW-1 |  |  |  | (7) Phone Number: |  |  | (954) 523-1002 |  |  |  | (22) TSS Effluent | mg/L | 900201 | 10.7667 | 8 | 42.458 | 1 |  | 53.8 | 78 | 2.3 | 3 | 6.6 | 10 | 9.4 | 0.24 | 0.47 | TNTC | A) | Liquid Sludge Disposal: | [9 empty] | 11 | 51.15 | 12.62 | 12.85 | 11.87 | 9.87 | 3.08 | 48.8 | 1.99 | 118 | 22 | 6.5 | 6.7 | 979 | 9.2 | 9.2 | 6.6 | 1988 | 84 | 0.77
| 7 | 44.575 | 2.116 | 58.346 | 25.023 | 13.747 | 30.84% | 0.216 | 0.03 | 133.5 |  | 7 |  |  |  | 7 | 41.07 | 49.01 | 46.4 |  |  | 37.1 | 40.83 | 39.22 | PERMIT NUMBER | 0054569-142-UO | 0054569-142-UO |  | 0054569-142-UO |  | 0054569-142-UO |  |  |  | (8) Permit Number: |  |  | FLA041378 |  |  |  | (23) TSS Effluent | lbs/day | - | 4182.1945 | 9 | 41.712 | 1 |  | 71.8 | 42 | 2.21 | 9 | 6.6 | 12 | 9.8 | 0.21 | 0.71 | TNTC |  | WEEK OF | JUNE | GALLONS | % SOLIDS |  |  | HAULERS |  |  | DISPOSAL SITE | 12 | 49.335 | 0.96 | 13.36 | 12.13 | 12.28 | 10.04 | 72.28 | 2.22 | 80 | 9 | 6.5 | 6.6 | 938 | 5 | 8.4 | 6.6 | 1869 | 84 | 0.6
| 8 | 42.458 | 1.987 | 54.405 | 20.665 | 14.153 | 33.33% | 0.451 | 0.28 | 144 |  | 8 |  |  |  | 8 | 48.52 | 48.83 | 48.68 |  |  | 40.22 | 44.3 | 42.16 | UPPER MONITORING INTERVAL | 1288'-1320' | 1300'-1344' |  | 1300'-1349' |  | 1300'-1339' |  | Ft. bls. |  | (9) Plant Type: |  |  | Oxygen Activated Sludge |  |  |  | (24) Minimum pH |  | - | 6.5 | 10 | 42.112 | 1.1 |  | 86.4 | 60 | 2 | 14 | 6.6 | 12 | 7.7 | 0.3 | 0.98 | 0 | [11 empty] | 13 | 45.518 | 10.87 | 0.74 | 11.43 | 11.58 | 10.83 | 81.6 | 2.23 | 108 | 10 | 6.5 | 6.6 | 1076 | 8.6 | 11 | 6.6 | 2020 | 84 | 0.49
| 9 | 41.712 | 1.95 | 55.302 | 23.613 | 14.263 | 34.19% | 0.765 | 0.04 | 129 |  | 9 |  |  |  | 9 | 48.58 | 48.85 | 48.68 |  |  | 41.94 | 44.11 | 42.77 | MONTHLY MAX DAILY PRESSURE | 49.46 | 32.68 |  | 34.04 |  | 44.64 |  | FT. HEAD |  | (10) Test Site Identification Number: |  |  |  |  | 5006X10744 |  | (25) Maximum pH |  | - | 7 | 11 | 51.15 | 1.3 |  | 48.8 | 118 | 1.99 | 22 | 6.6 | 9.2 | 9.2 | 0.24 | 0.77 | 0 |  | FIRST THRU SEVENTH | [9 empty] | 14 | 42.822 | 9.41 | 9.03 | 2.6 | 11.19 | 10.53 | 83.6 | 2.64 | 84 | 10 | 6.6 | 6.7 | 1076 | 8.8 | 11 | 6.6 | 2110 | 84 | 0.52
| 10 | 42.112 | 2.011 | 55.494 | 20.089 | 14.23 | 33.79% | 0.159 | 0.89 | 112.5 |  | 10 |  |  |  | 10 | 48.68 | 48.92 | 48.77 |  |  | 42.05 | 43.47 | 42.81 | MONTHLY MIN DAILY PRESSURE | 40.7 | 24.9 |  | 17.82 |  | 44.54 |  | FT. HEAD |  | (11) Fecal Coliform Method | [6 empty] | (26) Total N | mg/L | 000600 | 11.2007 | 12 | 49.335 | 1.2 |  | 72.28 | 80 | 2.22 | 9 | 6.6 | 8.4 | 5 | 0.24 | 0.6 | 0 | [11 empty] | 15 | 40.675 | 10.63 | 8.72 | 7.96 | 2.55 | 10.07 | 92.7 | 2 | 100 | 11 | 6.6 | 6.7 | 1222 | 8.9 | 12 | 6.6 | 2110 | 84 | 0.65
| 11 | 51.15 | 2.544 | 68.054 | 26.273 | 13.054 | 25.52% | 0 | 0.82 | 103.3 |  | 11 |  |  |  | 11 | 48.75 | 48.96 | 48.91 |  |  | 42.37 | 45.37 | 43.52 | TDS (MONTHLY AVERAGE) | 7624.25 | 7386.75 |  | 7612.5 |  | 5589 |  | mg/l |  |  | XX | Membrane Filter |  |  |  |  | (27) TKN | mg/L | 000625 | 10.9467 | 13 | 45.518 | 1 |  | 81.6 | 108 | 2.23 | 10 | 6.6 | 11 | 8.6 | 0.25 | 0.49 | 0 |  | EIGHT THRU FORTEENTH | [9 empty] | 16 | 40.132 | 10.36 | 10.56 | 8.27 | 8.26 | 2.19 | 89.9 | 2.19 | 108 | 12 | 6.6 | 6.7 | 1084 | 7.3 | 13 | 6.6 | 2150 | 84 | 0.6
| 12 | 49.335 | 2.294 | 62.544 | 33.513 | 12.712 | 25.77% | 0.225 | 0 | 105.5 |  | 12 |  |  |  | 12 | 48.77 | 48.96 | 48.92 |  |  | 42.8 | 46.05 | 44.03 | CHLORIDE (MONTHLY AVERAGE) | 3800 | 3650 |  | 3700 |  | 2800 |  | mg/l |  |  |  | Most Probable Number |  |  |  |  | (28) Ammonia (NH3 - N) | mg/L | 000610 | 7.9733 | 14 | 42.822 | 0.9 |  | 83.6 | 84 | 2.64 | 10 | 6.6 | 11 | 8.8 | 0.23 | 0.52 | TNTC |  | FIFTHTEENTH THRU | [9 empty] | 17 | 42.276 | 0.16 | 12.97 | 11.74 | 11.93 | 11.06 | 85.8 | 2.91 | 94 | 8 | 6.6 | 6.7 | 1171 | 8.5 | 13 | 6.6 | 2170 | 84 | 0.76
| 13 | 45.518 | 2.142 | 59.083 | 25.087 | 13.955 | 30.66% | 0.638 | 0 | 108.5 |  | 13 |  |  |  | 13 | 43.02 | 48.98 | 44.81 |  |  | 39 | 43.94 | 42.3 | AMMONIA-N (MONTHLY AVERAGE) | 0.9125 | 0.8875 |  | 0.885 |  | 0.68 |  | mg/l |  | (12) Type of Effluent Disposal or Reclaimed Water Reuse | [6 empty] | (29) Nitrate | mg/L | 071850 | 0.25407 | 15 | 40.675 | 1 |  | 92.7 | 100 | 2 | 11 | 6.6 | 12 | 8.9 | 0.02 | 0.65 | 0 |  | TWENTY SECOND | [9 empty] | 18 | 45.26 | 9.89 | 2.6 | 11.27 | 11.41 | 10.14 | 87.3 | 2.71 | 76 | 12 | 6.6 | 6.6 | 1105 | 6 | 9.9 | 6.6 | 2160 | 85 | 0.79
| 14 | 42.822 | 2.07 | 56.936 | 26.497 | 14.073 | 32.86% | 0.491 | 0.19 | 120 |  | 14 |  |  |  | 14 | 43.47 | 49.16 | 47.39 |  |  | 38.41 | 42.94 | 40.79 | TKN (MONTHLY AVERAGE) | 0.96 | 0.9875 |  | 1.04 |  | 0.8 |  | mg/l |  |  |  | Deep Well Injection |  |  |  |  | (30) Total Phosphorus | mg/L | 000665 | 0.785 | 16 | 40.132 | 1.1 |  | 89.9 | 108 | 2.19 | 12 | 6.6 | 13 | 7.3 | 0.23 | 0.6 | 0 |  | TWENTY THIRD THRU | [9 empty] | 19 | 45.708 | 11.85 | 10.11 | 0.61 | 11.63 | 10.87 | 83.1 | 2.43 | 74 | 12 | 6.5 | 6.6 | 1311 | 6 | 10 | 6.6 | 2410 | 85 | 0.61
| 15 | 40.675 | 1.885 | 56.071 | 17.717 | 13.268 | 32.62% | 0.482 | 0 | 113 |  | 15 |  |  |  | 15 | 48.78 | 49 | 48.93 |  |  | 41.12 | 44.62 | 42.93 | pH (MONTHLY AVERAGE) | 7.945 | 8.03 |  | 8.155 |  | 8.2 |  | Std units |  | (13) Limited Wet Wheather Discharge Activated | [6 empty] | (31) Minimum Chlorine Residual | mg/L | - | 0.8 | 17 | 42.276 | 0.8 |  | 85.8 | 94 | 2.91 | 8 | 6.6 | 13 | 8.5 | 0.31 | 0.76 | TNTC |  | THIRTY FIRST | [9 empty] | 20 | 45.815 | 12.03 | 10.02 | 9.08 | 2.68 | 11.23 | 44.4 | 2 | 114 | 18 | 6.5 | 6.7 | 1375 | 9.6 | 10 | 6.6 | 2580 | 84 | 0.43
| 16 | 40.132 | 1.952 | 57.609 | 20.121 | 13.525 | 33.7% | 0.544 | 0.66 | 122.8 |  | 16 |  |  |  | 16 | 48.82 | 49.09 | 48.95 |  |  | 41.05 | 46.59 | 43.15 | CONDUCTIVITY (MONTHLY AVERAGE) | 12215 | 11930 |  | 12070 |  | 9370 |  | umho/cm |  |  |  | YES |  | XX | Not Applicable |  | (32) Maximum Chlorine Residual | mg/L | - | 1.5 | 18 | 45.26 | 1.2 |  | 87.3 | 76 | 2.71 | 12 | 6.6 | 9.9 | 6 | 0.24 | 0.79 | 0 | [11 empty] | 21 | 47.854 | 12.08 | 12.31 | 9.36 | 9.11 | 4.17 | 69.5 | 2.8 | 98 | 21 | 6.6 | 6.6 | 1211 | 8.7 | 10 | 6.6 | 2320 | 84.1 | 0.59
| 17 | 42.276 | 2.137 | 57.801 | 18.807 | 13.743 | 32.51% | 0.277 | 0.9 | 128.3 |  | 17 |  |  |  | 17 | ER | 49.15 | 48.86 |  |  | ER | 45.69 | 43.31 | FECAL COLIFORM (MONTHLY AVERAGE) | 0 | 0 |  | 0 |  | 0 |  | # col/100ml |  |  |  | NO |  |  |  |  | (33) Other Effluent Parameters |  |  |  | 19 | 45.708 | 1.2 |  | 83.1 | 74 | 2.43 | 12 | 6.6 | 10 | 6 | 0.25 | 0.61 | 0 | B) | Solid Sludge Hauled from Plant: | [9 empty] | 22 | 45.069 | 3.02 | 12.47 | 11.51 | 9.53 | 8.46 | 44.6 | 2 | 88 | 12 | 6.6 | 6.6 | 996 | 9.5 | 9.9 | 6.6 | 2050 | 84 | 0.89
| 18 | 45.26 | 2.157 | 60.237 | 24.382 | 13.018 | 28.76% | 0 | 0.32 | 122 |  | 18 |  |  |  | 18 | 48.85 | 49.18 | 49 |  |  | 42.79 | 46.19 | 43.81 | TEMPERATURE (MONTHLY AVERAGE) | 76 | 74.5 |  | 73 |  | 70 |  | deg. F | [12 empty] | 20 | 45.815 | 0.9 |  | 44.4 | 114 | 2 | 18 | 6.6 | 10 | 9.6 | 0.31 | 0.43 | 0 |  | WEEK OF | JUNE | TONS |  | % SOLIDS |  | HAULERS |  |  | DISPOSAL SITE | 23 | 46.868 | 10.63 | 3.04 | 11.47 | 11.57 | 10.85 | 41.2 | 2 | 70 | 5 | 6.6 | 6.8 | 990 | 10 | 0 | 6.7 | 2040 | 84 | 1.9
| 19 | 45.708 | 2.189 | 58.186 | 26.85 | 13.088 | 28.63% | 0.211 | 0.28 | 131.8 |  | 19 |  |  |  | 19 | 48.83 | 49.16 | 49 |  |  | 41.87 | 46.89 | 43.79 | TOTAL PHOSPHOROUS (MONTHLY AVG.) | 0.01 | 0.01125 |  | 0.01075 |  | 0.01 |  | mg/l |  | (14) Cumulative Days of Wet Wheather Discharge | [10 empty] | 21 | 47.854 | 0.9 |  | 69.5 | 98 | 2.8 | 21 | 6.6 | 10 | 8.7 | 0.34 | 0.59 | 0 | [10 empty] | Central Sanitary Landfill | 24 | 57.594 | 12.28 | 12.43 | 9.6 | 11.84 | 11.12 | 67 | 2.85 | 118 | 12 | 6.6 | 6.8 | 888 | 7.9 | 7.9 | 6.7 | 1682 | 84 | 0.96
| 20 | 45.815 | 2.172 | 59.66 | 25.6 | 13.239 | 28.9% | 0.582 | 0.98 | 117 |  | 20 |  |  |  | 20 | 44.13 | 49.06 | 46.08 |  |  | 39.02 | 43.32 | 41.44 | SULFATE (MONTHLY AVERAGE) | 963.3333 | 987.6667 |  | 928.6667 |  | 808 |  | mg/l |  |  |  | N/A | [8 empty] | 22 | 45.069 | 0.9 |  | 44.6 | 88 | 2 | 12 | 6.6 | 9.9 | 9.5 | 0.3 | 0.89 | 26 |  | FIRST THRU SEVENTH |  | 462 |  | 17.796 |  | SYNAGRO |  |  | Pompano Beach, FL | 25 | 52.491 | 11.94 | 12.13 | 11.22 | 5.04 | 11.05 | 34.4 | 2 | 16 | 4 | 6.6 | 6.8 | 877 | 5.4 | 8.2 | 6.6 | 1803 | 84 | 0.7
| 21 | 47.854 | 2.304 | 61.486 | 31.785 | 12.669 | 26.47% | 0.604 | 0.82 | 111.3 |  | 21 |  |  |  | 21 | 44.43 | 49.29 | 47.51 |  |  | 38.41 | 42.52 | 40.4 | C.O.D. (MONTHLY AVERAGE) | #DIV/0! | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | mg/l |  | (15) Plant Staffing: | [10 empty] | 23 | 46.868 | 1.4 |  | 41.2 | 70 | 2 | 5 | 6.7 | 0 | 10 | 0.21 | 1.9 | 0 | [10 empty] | Central Sanitary Landfill | 26 | 48.201 | 11.92 | 12.14 | 11.37 | 9.9 | 1.59 | 34 | 2 | 68 | 8 | 6.6 | 7 | 963 | 6.7 | 8.4 | 6.7 | 1912 | 84 | 0.52
| 22 | 45.069 | 2.187 | 59.019 | 23.177 | 12.563 | 27.88% | 0.604 | 0.43 | 107 |  | 22 |  |  |  | 22 | 48.77 | 49.18 | 48.97 |  |  | 40.76 | 43.37 | 42.01 | IRON (MONTHLY AVERAGE) | #DIV/0! | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | mg/l | [12 empty] | 24 | 57.594 | 1 |  | 67 | 118 | 2.85 | 12 | 6.7 | 7.9 | 7.9 | 0.36 | 0.96 | 9 |  | EIGHT THRU FORTEENTH |  | 550 |  | 17.97 |  | SYNAGRO |  |  | Pompano Beach, FL | 27 | 48.385 | 0.67 | 13.35 | 12.16 | 12.36 | 10.24 | LS | LS | 78 | 11 | 6.6 | 6.7 | 960 | 6.3 | 8.6 | 6.7 | 1936 | 84 | 0.71
| 23 | 46.868 | 2.985 | 76.289 | 25.023 | 12.546 | 26.77% | 0.598 | 1.22 | 107.3 |  | 23 |  |  |  | 23 | 48.87 | 49.33 | 49.09 |  |  | 41.33 | 45.98 | 43.55 | SULFIDE (MONTHLY AVERAGE) | #DIV/0! | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | mg/l |  |  | Day Shift Operator: |  |  | Class | 0 | Cert. No. | 0 |  |  |  | 25 | 52.491 | 1.1 |  | 34.4 | 16 | 2 | 4 | 6.6 | 8.2 | 5.4 | 0.058 | 0.7 | 0 |  | FIFTHTEENTH THRU | [8 empty] | Central Sanitary Landfill | 28 | 50.065 | 12.28 | 0.81 | 12.64 | 12.74 | 11.93 | 11 | 2 | 70 | 8 | 6.6 | 6.7 | 926 | 6.6 | 8 | 6.7 | 1866 | 84 | 1.2
| 24 | 57.594 | 2.632 | 68.919 | 44.088 | 12.785 | 22.2% | 0.237 | 0.02 | 97.3 |  | 24 |  |  |  | 24 | 49.09 | 49.46 | 49.21 |  |  | 42.32 | 46.11 | 44.03 | LOWER MONITORING INTERVAL | 1449'-1557' | 1970'-2025' |  | 1970'-2027' |  | 1500'-1600' |  | Ft. bls | [12 empty] | 26 | 48.201 | 1.3 |  | 34 | 68 | 2 | 8 | 6.7 | 8.4 | 6.7 | 0.32 | 0.52 | 9 |  | TWENTY SECOND |  | 609 |  | 17.97 |  | SYNAGRO |  |  | Pompano Beach, FL | 29 | 52.667 | 13.5 | 12.5 | 0.74 | 13.11 | 12.24 | 34 | 2 | 42 | 10 | 6.6 | 6.7 | 759 | 7.7 | 7.8 | 6.7 | 1672 | 84 | 1.2
| 25 | 52.491 | 2.431 | 63.922 | 35.821 | 12.645 | 24.09% | 0 | 0 | 99.5 |  | 25 |  |  |  | 25 | 49.13 | 49.46 | 49.29 |  |  | 42.98 | 46.65 | 44.48 | MONTHLY MAX DAILY PRESSURE | 46.89 | 43.48 |  | 46.21 |  | 22.68 |  | FT. HEAD |  |  | Evening Shift Operator: |  |  | Class | 0 | Cert. No. | 0 |  |  |  | 27 | 48.385 | 1 |  | LS | 78 | LS | 11 | 6.7 | 8.6 | 6.3 | 0.32 | 0.71 | 0 |  | TWENTY THIRD THRU | [8 empty] | Central Sanitary Landfill | 30 | 49.039 | 12.06 | 12.25 | 10 | 2.45 | 11.49 | 10 | 5 | 40 | 2 | 6.6 | 6.8 | 778 | 6.9 | 8.1 | 6.7 | 1726 | 84 | 1.3
| 26 | 48.201 | 2.194 | 61.743 | 30.951 | 12.913 | 26.79% | 0.154 | 0 | 109 |  | 26 |  |  |  | 26 | 49.07 | 49.41 | 49.19 |  |  | 43.38 | 45.97 | 44.27 | MONTHLY MIN DAILY PRESSURE | 37.1 | 35.04 |  | 35.49 |  | 22.53 |  | FT. HEAD | [12 empty] | 28 | 50.065 | 1 |  | 11 | 70 | 2 | 8 | 6.7 | 8 | 6.6 | 0.29 | 1.2 | 0 |  | THIRTY FIRST |  | 594 |  | 18.7667 |  | SYNAGRO |  |  | Pompano Beach, FL | 31
| 27 | 48.385 | 2.282 | 60.076 | 28.676 | 13.745 | 28.41% | 0.458 | 1.43 | 108.8 |  | 27 |  |  |  | 27 | 41.69 | 49.33 | 44.27 |  |  | 39.2 | 45.23 | 42.23 | TDS (MONTHLY AVERAGE) | 9550.25 | 31967.75 |  | 28928.5 |  | 25230 |  | mg/l |  |  | Night Shift Operator: |  |  | Class | 0 | Cert. No. | 0 |  |  |  | 29 | 52.667 | 0.8 |  | 34 | 42 | 2 | 10 | 6.7 | 7.8 | 7.7 | 0.36 | 1.2 | 0 | C) | Monthly quantities of solid sludge stockpiled at plant.Solid Sludge Hauled from Plant: | [9 empty] | TOT | 1397.263 | 284.7 | 288.67 | 273.89 | 281.44 | 263.04 | 1699.32 | 71.43 | 2452 | 323 | 197 | 200.6 | 33377 | 239.2 | 328.4 | 198.6 | 66004 | 2521.9 | 23.55
| 28 | 50.065 | 2.304 | 62.832 | 28.292 | 12.982 | 25.93% | 0.53 | 0.77 | 108 |  | 28 |  |  |  | 28 | 42.13 | 49.37 | 47 |  |  | 38.68 | 42.92 | 40.76 | CHLORIDE (MONTHLY AVERAGE) | 5050 | 17550 |  | 15750 |  | 14800 |  | mg/l | [12 empty] | 30 | 49.039 | 1 |  | 10 | 40 | 5 | 2 | 6.7 | 8.1 | 6.9 | 0.31 | 1.3 | 9 |  | 1) | Additions |  |  | Cubic Yards | [5 empty] | AVG | 46.5754 | 9.49 | 9.6223 | 9.1297 | 9.3813 | 8.768 | 58.5972 | 2.4631 | 81.7333 | 10.7667 | 6.5667 | 6.6867 | 1112.5667 | 7.9733 | 10.9467 | 6.62 | 2200.1333 | 84.0633 | 0.785
| 29 | 52.667 | 2.394 | 65.139 | 37.551 | 12.869 | 24.43% | 0.581 | 0.05 | 102.8 |  | 29 |  |  |  | 29 | 49.05 | 49.36 | 49.19 |  |  | 40.46 | 44.75 | 42.75 | AMMONIA-N (MONTHLY AVERAGE) | 9.2 | 1.4 |  | 2.4 |  | 0.38 |  | mg/l |  |  | Lead Operator:_________________________________ | [28 empty] | Tons | [5 empty] | MAX | 57.594 | 13.5 | 13.36 | 12.64 | 13.11 | 12.24 | 92.7 | 5 | 200 | 22 | 6.6 | 7 | 1591 | 10 | 20 | 6.7 | 3110 | 85 | 1.9
| 30 | 49.039 | 2.459 | 66.229 | 27.875 | 13.634 | 27.8% | 0.414 | 0.58 | 104 |  | 30 |  |  |  | 30 | 49.1 | 49.45 | 49.29 |  |  | 41.83 | 45.77 | 43.62 | TKN (MONTHLY AVERAGE) | 10.05 | 1.75 |  | 2.75 |  | 0.73 |  | mg/l | [5 empty] | Signature |  | Cert. No. |  |  |  |  | Lead Operator : This is to certify that I am familar with the information contained on this report and that to the best of | [14 empty] | 2) | Removals |  |  | Cubic Yards | [5 empty] | MIN | 40.132 | 0.16 | 0.74 | 0.61 | 2.45 | 0.29 | 10 | 1.99 | 16 | 2 | 6.5 | 6.5 | 759 | 5 | 0 | 6.5 | 1672 | 83.8 | 0.41
[25 empty] | pH (MONTHLY AVERAGE) | 7.4125 | 7.595 |  | 7.5175 |  | 7.54 |  | Std units | [12 empty] | my knowledge and belief, this information is true, complete and accuate. | [16 empty] | X |  | Tons | [6 empty] | item #1 | 14.5881 | 14.8027 | 14.0503 | 14.4452 | 13.5099 | MAX HOURLY FLOW (MG) = |  |  |  | 2.985 | ON THE | 23 | DAY OF THIS MONTH
| TOTAL | 1397.263 | 67.69 | 1840.708 | 788.234 | 397.891 |  | 11.91 | 13.739 | 3544.8 | [5 empty] | TOTAL | 1363.1 | 1470.99 | 1441.64 |  |  | 1183.58 | 1340.71 | 1279.26 | CONDUCTIVITY (MONTHLY AVERAGE) | 15672.5 | 47050 |  | 43150 |  | 40000 |  | umho/cm | [33 empty] | Signature |  |  |  |  | item #2 | 54.774 | 54.1407 | 55.7207 | 56.283 | 55.1283
| AVERAGE | 46.5754 | 2.2563 | 61.3569 | 26.2745 | 13.263 | 28.48% | 0.45808 | 0.45797 | 118.16 | [5 empty] | AVERAGE | 47.0034 | 49.033 | 48.0547 |  |  | 40.8131 | 44.6903 | 42.642 | FECAL COLIFORM (MONTHLY AVERAGE) | 0 | 0 |  | 0 |  | 0 |  | # col/100ml | [12 empty] | Signed: ____________________________ Date: ___________________ | [20 empty] | Title |  |  |  |  | item #3 | 36.14 | 36.72 | 37.65 | 38.22 | 36.64
[16 empty] | MAXIMUM | 49.13 | 49.46 | 49.29 |  |  | 43.38 | 46.89 | 44.48 | TEMPERATURE (MONTHLY AVERAGE) | 76.5 | 73 |  | 72.25 |  | 66 |  | deg. F | [33 empty] | Date |  |  |  | item #1 | =monthly maximum of the daily flows (MG), with peakhour flow (MGD) on the day of the month with maximum flow = | [14 empty] | 2.985 | MG/hour multiplied by
[16 empty] | MINIMUM | 40.7 | 48.39 | 43.36 |  |  | 37.1 | 40.83 | 39.22 | TOTAL PHOSPHOROUS (MONTHLY AVG.) | 0.01 | 0.01 |  | 0.02975 |  | 0.01 |  | mg/l | [12 empty] | Name: Michael A. Just | [14 empty] | * Sludge Reports should be submitted along with the monthly operating reports to Broward County Department | [10 empty] | the % of average % of TOTAL RAW FLOW to each Injection well.
[25 empty] | SULFATE (MONTHLY AVERAGE) | 869.3333 | 3200 |  | 3153.3333 |  | 2140 |  | mg/l | [27 empty] | of Natural Resource Protection, 218 S. W. 1st Avenue, Fort Lauderdale, Florida 33301 | [9 empty] | item #2 | =monthly average injection well pressure at injection well (psig)
[25 empty] | C.O.D. (MONTHLY AVERAGE) | #DIV/0! | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | mg/l | [12 empty] | Company Name: City of Fort Lauderdale Telephone No. (954) 523-1002 | [24 empty] | item #3 | =monthly wellhead pressure with no flow (shut-in pressure,psig)
[25 empty] | IRON (MONTHLY AVERAGE) | #DIV/0! | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | mg/l | [37 empty] | PLANT STAFFING
[5 empty] | PAGE 2 | [19 empty] | SULFIDE (MONTHLY AVERAGE) | #DIV/0! | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | mg/l | [37 empty] | Day Shift Operator |  |  | Class: | 0 | Certificate No. | 0 | Name: |  | McGEARY, J.
[71 empty] | Evening Shift Operator |  |  | Class: | 0 | Certificate No. | 0 | Name: |  | BAYLER, J.
[20 empty] | PAGE 20 | [50 empty] | Night Shift Operator |  |  | Class: | 0 | Certificate No. | 0 | Name: |  | 0
[71 empty] | Lead Operator |  |  | Class: | "A" | Certificate No. | 2769 | Name: |  | JUST, M.
[71 empty] | Type of Effluent Disposal or Reclaimed Water Reuse: |  |  |  |  | DEEPWELL INJECTION
[71 empty] | Permited Wet Weather Discharge Activated: |  |  |  | YES: |  | NO: |  |  | Not Applicable |  | X
[28 empty] | Page 28 | [42 empty] | If Yes, cumulative days of wet weather:
Attach additional sheets if necessary to list all certified operators. See page 1 "COVER PAGE" of supplental attachements.
DEP form 62-620.910(10), effective November 29, 1994
[19 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [47 empty] | Department of Natural Resource Protection
[5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [13 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [47 empty] | Division of Pollution Prevention and Remediation Programs
[5 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [13 empty] | MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING | [50 empty] | 218 S. W. 1st Avenue
[5 empty] | MONTHLY OPERATIONAL REPORT | [13 empty] | MONITORING WELL TWO |  |  |  | 1/07/04 thru 1/06/09 | [39 empty] | SLUDGE HAULERS MONTHLY REPORT | [6 empty] | Fort Lauderdale, FL 33301
[5 empty] | INFLUENT DATA | [11 empty] | MW-2 | I.D. #: 5066A11308 & 09 |  |  | PERMIT # 0054569-142-UO | [41 empty] | BROWARD COUNTY CODE SECTION 27-356 (d)(4)(1) | [5 empty] | Tel. No. (954) 523-1002
| RUN DATE | [14 empty] | RUN DATE | [52 empty] | *FAX (954) 519-1245
| 2026-07-30 | [14 empty] | 2026-07-30 |  | UPPER MONITOR ZONE |  |  |  |  | LOWER MONITOR ZONE
[17 empty] | MIN | MAX | AVG |  |  | MIN | MAX | AVG | [35 empty] | Plant Name: | GEORGE T. LOHMEYER WASTEWATER TREATMENT FACILITY
| JUNE | RAW | RAW TSS | RAW SS | RAW | RAW | RAW | RAW | RAW | RAW | [5 empty] | JUNE | FT HEAD | FT HEAD | FT HEAD |  |  | FT HEAD | FT HEAD | FT HEAD | [35 empty] | Address: | 1765 S.E. 18th Street at Eisenhower Boulevard | [6 empty] | MONTH: | JUNE
| 2005 | CBOD | TOTAL | FIXED | COD | pH | CL_ | ALK. | H2S | TEMP.(F) | [5 empty] | 2005 | ABOVE | ABOVE | ABOVE |  |  | ABOVE | ABOVE | ABOVE | [35 empty] | Phone: | (954) 523-1002 * FAX (954) 468-1577 | [6 empty] | YEAR: | 2005
[17 empty] | NGVD | NGVD | NGVD |  |  | NGVD | NGVD | NGVD
| 1 | 79.5 | 200 | 22 | 129 | 7 | 720 | 202 | 6 | 81.7 | [5 empty] | 1 | 28.7 | 29.86 | 29.22 |  |  | 42.56 | 42.76 | 42.58 | [35 empty] | a) | WEEK OF | JUNE |  | Type of Sludge |  |  | Disopsal Site |  |  | Cubic Yards
| 2 | 61 | 90 | 14 | 113 | 7 | 660 | 194 | 3 | 82 | [5 empty] | 2 | 28.65 | 30.15 | 29.37 |  |  | 42.62 | 42.84 | 42.81
| 3 | 74.36 | 38 | 15 | 93 | 7.1 | 620 | 202 | 3 | 81 | [5 empty] | 3 | 29.22 | 30.78 | 29.88 |  |  | 42.77 | 42.96 | 42.89 | [36 empty] | FIRST THRU SEVENTH |  |  | GRIT |  |  | Central Landfill |  |  | 20
| 4 | 52.28 | 70 | 16 | 132 | 7 | 630 | 190 | 5 | 80 | [5 empty] | 4 | 29.16 | 30.26 | 29.77 |  |  | 42.78 | 42.98 | 42.91
| 5 | 22.47 | 68 | 4 | 102 | NR | 580 | 192 | NR | NR | [5 empty] | 5 | 29.26 | 30.53 | 29.74 |  |  | 42.86 | 43.01 | 42.96 | [36 empty] | EIGHT THRU FORTEENTH |  |  | GRIT |  |  | Central Landfill |  |  | 0
| 6 | 38.53 | 78 | 2 | 93 | 7 | 620 | 192 | 4 | 80 | [5 empty] | 6 | 25.15 | 30.05 | 27.06 |  |  | 37.09 | 43.01 | 38.95 | [36 empty] | FIFTHTEENTH THRU
| 7 | 44 | 84 | 4 | 98 | 7.1 | 620 | 202 | 4 | 81 | [5 empty] | 7 | 24.9 | 30.49 | 28.52 |  |  | 37.06 | 42.71 | 40.89 | [36 empty] | TWENTY SECOND |  |  | GRIT |  |  | Central Landfill |  |  | 10
| 8 | 53.8 | 78 | 16 | 107 | 7 | 680 | 210 | 4 | 80 | [5 empty] | 8 | 29.55 | 30.76 | 30.2 |  |  | 42.7 | 42.94 | 42.85 | [36 empty] | TWENTY THIRD THRU
| 9 | 71.8 | 42 | 0 | 100 | 7 | 600 | 192 | 4 | 81 | [5 empty] | 9 | 29.99 | 30.77 | 30.34 |  |  | 42.88 | 43.04 | 42.97 | [36 empty] | THIRTY FIRST |  |  | GRIT |  |  | Central Landfill |  |  | 20
| 10 | 86.4 | 60 | 0 | 110 | 7 | 530 | 189 | 3 | 81 | [5 empty] | 10 | 29.86 | 30.51 | 30.23 |  |  | 43.02 | 43.17 | 43.01
| 11 | 48.8 | 118 | 24 | 99 | 7.1 | 420 | 190 | 3 | 81 | [5 empty] | 11 | 30.1 | 31.2 | 30.54 |  |  | 43.1 | 43.2 | 43.08 | [35 empty] | b) | WEEK OF | JUNE |  | Type of Sludge |  |  | Disopsal Site |  |  | Cubic Yards
| 12 | 72.28 | 80 | 8 | 95 | 7.2 | 440 | 212 | 4 | 81 | [5 empty] | 12 | 30.45 | 31.5 | 30.85 |  |  | 43.13 | 43.22 | 43.12
| 13 | 81.6 | 108 | 12 | 102 | 7.1 | 480 | 218 | 3 | 81 | [5 empty] | 13 | 25.59 | 30.66 | 27.65 |  |  | 37.85 | 43.26 | 39.41 | [36 empty] | FIRST THRU SEVENTH |  |  | RAGS |  |  | Central Landfill |  |  | 10
| 14 | 83.6 | 84 | 16 | 116 | 7 | 500 | 218 | 3 | 81 | [5 empty] | 14 | 25.41 | 31.18 | 29.17 |  |  | 37.83 | 42.89 | 41.37
| 15 | 92.7 | 100 | 16 | 115 | 7 | 580 | 222 | 2 | 81 | [5 empty] | 15 | 30.29 | 31.65 | 30.87 |  |  | 42.89 | 43.08 | 42.99 | [36 empty] | EIGHT THRU FORTEENTH |  |  | RAGS |  |  | Central Landfill |  |  | 10
| 16 | 89.9 | 108 | 18 | 162 | 7.1 | 530 | 210 | 2 | 82 | [5 empty] | 16 | 30.04 | 32.11 | 30.9 |  |  | 43.03 | 43.24 | 43.03 | [36 empty] | FIFTHTEENTH THRU
| 17 | 85.8 | 94 | 8 | 173 | 7.1 | 500 | 192 | 2 | 81 | [5 empty] | 17 | ER | 32.06 | 30.96 |  |  | ER | 43.31 | 43.08 | [36 empty] | TWENTY SECOND |  |  | RAGS |  |  | Central Landfill |  |  | 10
| 18 | 87.3 | 76 | 14 | 167 | 7.1 | 510 | 206 | 3 | 81 | [5 empty] | 18 | 30.74 | 32.04 | 31.19 |  |  | 43.18 | 43.37 | 43.35 | [36 empty] | TWENTY THIRD THRU
| 19 | 83.1 | 74 | 10 | 311 | 7.1 | 610 | 208 | 2 | 81 | [5 empty] | 19 | 30.47 | 31.99 | 31.12 |  |  | 43.22 | 43.37 | 43.37 | [36 empty] | THIRTY FIRST |  |  | RAGS |  |  | Central Landfill |  |  | 0
| 20 | 44.4 | 114 | 32 | 106 | 7.1 | 610 | 206 | 3 | 81 | [5 empty] | 20 | 25.22 | 30.86 | 27.68 |  |  | 35.69 | 43.34 | 38.74 | [36 empty] | BCSR = Broward County Septage Receiving
| 21 | 69.5 | 98 | 28 | 97 | 7.1 | 580 | 208 | 2 | 81 | [5 empty] | 21 | 25 | 30.88 | 28.93 |  |  | 35.63 | 42.84 | 40.51 | [35 empty] | c) | WEEK OF | JUNE |  | Type of Sludge |  |  | Disopsal Site |  |  | Gallons
| 22 | 44.6 | 88 | 6 | 98 | 7.1 | 460 | 202 | 2 | 81 | [5 empty] | 22 | 30.12 | 31.22 | 30.6 |  |  | 42.82 | 43.09 | 42.94
| 23 | 41.2 | 70 | 12 | 103 | 7.2 | 510 | 202 | 3 | 81 | [5 empty] | 23 | 30.37 | 31.69 | 31.01 |  |  | 43.05 | 43.29 | 43.11 | [36 empty] | FIRST THRU SEVENTH |  |  | VAC/Plastic & Rags |  |  | BCSR |  |  | 0
| 24 | 67 | 118 | 22 | 111 | 7.2 | 400 | 206 | 3 | 80 | [5 empty] | 24 | 30.66 | 32.07 | 31.38 |  |  | 43.26 | 43.46 | 43.36
| 25 | 34.4 | 16 | 14 | 96 | 7.1 | 430 | 198 | 2 | 81 | [5 empty] | 25 | 30.96 | 32.59 | 31.76 |  |  | 43.36 | 43.47 | 43.47 | [36 empty] | EIGHT THRU FORTEENTH |  |  | VAC/Plastic & Rags |  |  | BCSR |  |  | 0
| 26 | 34 | 68 | 8 | 129 | 7.1 | 430 | 7.28 | 8 | 82 | [5 empty] | 26 | 31.23 | 32.4 | 31.76 |  |  | 43.33 | 43.48 | 43.46 | [36 empty] | FIFTHTEENTH THRU
| 27 | LS | 78 | 2 | 102 | 7.1 | 450 | 194 | 3 | 81 | [5 empty] | 27 | 25.8 | 31.56 | 28.27 |  |  | 35.06 | 43.47 | 37.73 | [36 empty] | TWENTY SECOND |  |  | VAC/Plastic & Rags |  |  | BSCR |  |  | 4500
| 28 | 11 | 70 | 0 | 94 | 7 | 410 | 184 | 2 | 81 | [5 empty] | 28 | 25.92 | 31.99 | 29.68 |  |  | 35.04 | 42.99 | 40.48 | [36 empty] | TWENTY THIRD THRU
| 29 | 34 | 42 | 30 | 106 | 7 | 370 | 202 | 2 | 80 | [5 empty] | 29 | 30.66 | 32.17 | 31.44 |  |  | 42.99 | 43.22 | 43.02 | [36 empty] | THIRTY FIRST |  |  | VAC/Plastic & Rags |  |  | BSCR |  |  | 0
| 30 | 10 | 40 | 0 | 97 | 7 | 360 | 190 | 3 | 82 | [5 empty] | 30 | 31.14 | 32.68 | 31.65 |  |  | 43.14 | 43.35 | 43.35 | [35 empty] | TOTALS
[61 empty] | a) | 50 | cu.yds |  | GRIT |  | Signature
| TOTAL | 1699.32 | 2452 | 373 | 3556 | 205 | 15840 | 5840.28 | 93 | 2348.7 | [5 empty] | TOTAL | 834.61 | 938.66 | 901.74 |  |  | 1193.94 | 1294.36 | 1265.79 | [36 empty] | b) | 30 | cu.yds |  | RAGS |  | Title
| AVERAGE | 58.5972 | 81.7333 | 14.3462 | 118.5333 | 7.069 | 528 | 194.676 | 3.2069 | 80.9897 | [5 empty] | AVERAGE | 28.7797 | 31.2887 | 30.058 |  |  | 41.1703 | 43.1453 | 42.193 | [36 empty] | c) | 4500 | gal. |  | VAC/Plastic & Rags |  | Date
[16 empty] | MAXIMUM | 31.23 | 32.68 | 31.76 |  |  | 43.36 | 43.48 | 43.47
[16 empty] | MINIMUM | 24.9 | 29.86 | 27.06 |  |  | 35.04 | 42.71 | 37.73 | [36 empty] | * Sludge Reports should be submitted along with the monthly operating reports to Broward County Department
of Natural Resource Protection, 218 S. W. 1st Avenue, Fort Lauderdale, Florida 33301
PAGE 3
PAGE 21
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
[5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [13 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
[5 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [13 empty] | MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
[5 empty] | MONTHLY OPERATIONAL REPORT | [13 empty] | MONITORING WELL THREE |  |  |  | 1/07/04 thru 1/06/09
[5 empty] | EFFLUENT DATA PART 1 | [11 empty] | MW-3 | I.D. #: 5066A11310 |  |  | PERMIT # 0054569-142-UO
RUN DATE
[16 empty] | 2026-07-30 |  | UPPER MONITOR ZONE |  |  |  |  | LOWER MONITOR ZONE
| RUN DATE | [15 empty] | MIN | MAX | AVG |  |  | MIN | MAX | AVG
| 2026-07-30 | [14 empty] | JUNE | FT HEAD | FT HEAD | FT HEAD |  |  | FT HEAD | FT HEAD | FT HEAD
[14 empty] | BOD | TSS | 2005 | ABOVE | ABOVE | ABOVE |  |  | ABOVE | ABOVE | ABOVE
| JUNE | EFFLUENT | EFFL. TSS | EFFL. SS | EFFLUENT | EFFL. | EFFL. | EFFL. | EFFL. | EFFL. | TDS |  |  | MONTHLY AVG OVER 30 | MONTHLY AVG OVER 30 |  | NGVD | NGVD | NGVD |  |  | NGVD | NGVD | NGVD
| 2005 | CBOD | TOTAL | FIXED | COD | CL_ | ALK. | TURB. | COND. | TEMP.(F) |  |  |  | 0 | 0 | 1 | 32.92 | 33.29 | 33.09 |  |  | 45.23 | 45.44 | 45.39
[14 empty] | WEKKLY OVER 45 | WEKKLY OVER 45 | 2 | 33.09 | 33.43 | 33.31 |  |  | 45.33 | 45.53 | 45.47
| 1 | 3.94 | 11 | 0 | 22.1 | 800 | 190 | 7.9 | 3110 | 84 | 1591 | 1 |  | 0 | 0 | 3 | 33.3 | 33.61 | 33.42 |  |  | 45.47 | 45.65 | 45.52
| 2 | 2.64 | 15 | 2 | 38.9 | 680 | 186 | 6.4 | 2690 | 84 | 1326 | 1 |  | SINGLE DAY OVER 60 | SINGLE DAY OVER 60 | 4 | 33.35 | 33.67 | 33.46 |  |  | 45.51 | 45.7 | 45.52
| 3 | 3.69 | 6 | 2 | 40.8 | 620 | 184 | 6.23 | 2520 | 84 | 1251 | 1 |  | 0 | 0 | 5 | 33.45 | 33.72 | 33.52 |  |  | 45.6 | 45.73 | 45.58
| 4 | 2.35 | 17 | 6 | 37.8 | 630 | 186 | 8.32 | 2550 | 84 | 1294 | 1 |  | 0 | 0 | 6 | 17.9 | 33.65 | 22.81 |  |  | 36.44 | 45.73 | 39.37
| 5 | 2 | 10 | 0 | 36.5 | 610 | 184 | 6.75 | 2490 | 84 | 1253 | 1 |  |  |  | 7 | 17.82 | 32.95 | 28.18 |  |  | 36.44 | 45.37 | 42.57
| 6 | 2.33 | 8 | 0 | 36.5 | 600 | 178 | 4.85 | 2380 | 84 | 1148 | 1 |  |  |  | 8 | 32.87 | 33.23 | 32.97 |  |  | 45.37 | 45.62 | 45.47
| 7 | 2 | 13 | 0 | 37.5 | 610 | 188 | 5.16 | 2450 | 83.8 | 1210 | 1 | 2.7071 | 2.7071 | 11.4286 | 9 | 33.09 | 33.32 | 33.17 |  |  | 45.59 | 45.73 | 45.58
| 8 | 2.3 | 3 | 0 | 25.3 | 630 | 198 | 3.32 | 2500 | 84 | 1304 | 1 |  | 2.4729 | 10.2857 | 10 | 33.21 | 33.45 | 33.31 |  |  | 45.73 | 45.86 | 45.81
| 9 | 2.21 | 9 | 0 | 39.9 | 630 | 186 | 5.08 | 2490 | 84 | 1231 | 1 |  | 2.4114 | 9.4286 | 11 | 33.3 | 33.56 | 33.45 |  |  | 45.83 | 45.91 | 45.91
| 10 | 2 | 14 | 0 | 41.5 | 540 | 184 | 5.34 | 2250 | 84 | 1084 | 1 |  | 2.17 | 10.5714 | 12 | 33.4 | 33.58 | 33.49 |  |  | 45.86 | 45.95 | 45.95
| 11 | 1.99 | 22 | 7 | 39.3 | 490 | 178 | 5.6 | 1988 | 84 | 979 | 1 |  | 2.1186 | 11.2857 | 13 | 17.99 | 33.61 | 22.08 |  |  | 38.01 | 45.99 | 40.11
| 12 | 2.22 | 9 | 1 | 37.6 | 420 | 182 | 3.75 | 1869 | 84 | 938 | 1 |  | 2.15 | 11.1429 | 14 | 17.92 | 33.09 | 28.42 |  |  | 38.02 | 45.56 | 43.22
| 13 | 2.23 | 10 | 2 | 39.1 | 490 | 194 | 4.94 | 2020 | 84 | 1076 | 1 |  | 2.1357 | 11.4286 | 15 | 33.08 | 33.34 | 33.17 |  |  | 45.56 | 45.79 | 45.65
| 14 | 2.64 | 10 | 5 | 39.2 | 500 | 196 | 8.63 | 2110 | 84 | 1076 | 1 | 2.2271 | 2.2271 | 11 | 16 | 33.23 | 33.51 | 33.39 |  |  | 45.73 | 45.95 | 45.88
| 15 | 2 | 11 | 4 | 43.2 | 510 | 192 | 3.5 | 2110 | 84 | 1222 | 1 |  | 2.1843 | 12.1429 | 17 | ER | 33.63 | 33.43 |  |  | ER | 46.04 | 45.82
| 16 | 2.19 | 12 | 2 | 44.5 | 520 | 196 | 4.54 | 2150 | 84 | 1084 | 1 |  | 2.1814 | 12.5714 | 18 | 33.4 | 33.7 | 33.53 |  |  | 45.89 | 46.13 | 46
| 17 | 2.91 | 8 | 0 | 41.7 | 520 | 200 | 4.8 | 2170 | 84 | 1171 | 1 |  | 2.3114 | 11.7143 | 19 | 33.44 | 33.7 | 33.54 |  |  | 45.98 | 46.11 | 46.02
| 18 | 2.71 | 12 | 2 | 44.6 | 490 | 198 | 4.63 | 2160 | 85 | 1105 | 1 |  | 2.4143 | 10.2857 | 20 | 17.98 | 33.6 | 23.78 |  |  | 35.51 | 46.08 | 39.45
| 19 | 2.43 | 12 | 2 | 54.6 | 600 | 194 | 4.78 | 2410 | 85 | 1311 | 1 |  | 2.4443 | 10.7143 | 21 | 17.93 | 33.25 | 28.16 |  |  | 35.49 | 45.52 | 42.27
| 20 | 2 | 18 | 7 | 39.7 | 630 | 192 | 4.16 | 2580 | 84 | 1375 | 1 |  | 2.4114 | 11.8571 | 22 | 33.16 | 33.55 | 33.31 |  |  | 45.52 | 45.79 | 45.64
| 21 | 2.8 | 21 | 9 | 42.7 | 560 | 194 | 6.5 | 2320 | 84.1 | 1211 | 1 | 2.4343 | 2.4343 | 13.4286 | 23 | 33.4 | 33.81 | 33.53 |  |  | 45.76 | 46 | 45.87
| 22 | 2 | 12 | 0 | 40.7 | 510 | 188 | 4.58 | 2050 | 84 | 996 | 1 |  | 2.4343 | 13.5714 | 24 | 33.66 | 34.04 | 33.79 |  |  | 45.99 | 46.17 | 46
| 23 | 2 | 5 | 1 | 48.4 | 480 | 186 | 3.31 | 2040 | 84 | 990 | 1 |  | 2.4071 | 12.5714 | 25 | 33.79 | 34.04 | 33.95 |  |  | 46.1 | 46.2 | 46.08
| 24 | 2.85 | 12 | 2 | 22.2 | 390 | 188 | 6.95 | 1682 | 84 | 888 | 1 |  | 2.3986 | 13.1429 | 26 | 33.72 | 34 | 33.88 |  |  | 46.09 | 46.21 | 46.09
| 25 | 2 | 4 | 11 | 38.5 | 400 | 189 | 5.48 | 1803 | 84 | 877 | 1 |  | 2.2971 | 12 | 27 | 18.08 | 33.94 | 22.95 |  |  | 36.83 | 46.2 | 39.82
| 26 | 2 | 8 | 0 | 38.6 | 440 | 178 | 4.98 | 1912 | 84 | 963 | 1 |  | 2.2357 | 11.4286 | 28 | 18.03 | 33.41 | 28.47 |  |  | 36.87 | 45.7 | 42.79
| 27 | LS | 11 | 0 | 40.3 | 450 | 216 | 4.86 | 1936 | 84 | 960 | 0 |  | 2.275 | 10.4286 | 29 | 33.4 | 33.74 | 33.53 |  |  | 45.7 | 45.94 | 45.87
| 28 | 2 | 8 | 0 | 40.8 | 430 | 180 | 5.47 | 1866 | 84 | 926 | 1 |  | 2.1417 | 8.5714 | 30 | 33.59 | 33.91 | 33.79 |  |  | 45.86 | 46.09 | 45.98
| 29 | 2 | 10 | 9 | 40.9 | 370 | 190 | 6.05 | 1672 | 84 | 759 | 1 |  | 2.1417 | 8.2857
| 30 | 5 | 2 | 0 | 39.3 | 380 | 186 | 6.31 | 1726 | 84 | 778 | 1 |  | 2.6417 | 7.8571 | TOTAL | 843.5 | 1007.33 | 940.88 |  |  | 1253.31 | 1375.69 | 1336.7
[12 empty] | 0 | 2.4813 | 2.6 | 7.1667 | AVERAGE | 29.0862 | 33.5777 | 31.3627 |  |  | 43.2176 | 45.8563 | 44.5567
| TOTAL | 71.43 | 323 | 74 | 1172.7 | 15930 | 5681 | 163.17 | 66004 | 2521.9 | 33377 |  |  |  |  | MAXIMUM | 33.79 | 34.04 | 33.95 |  |  | 46.1 | 46.21 | 46.09
| AVERAGE | 2.4631 | 10.7667 | 4.3529 | 39.09 | 531 | 189.3667 | 5.439 | 2200.1333 | 84.0633 | 1112.5667 |  |  | 2.3339 | 10.9724 | MINIMUM | 17.82 | 32.95 | 22.08 |  |  | 35.49 | 45.37 | 39.37
| MAXIMUM | 5 | 22
[5 empty] | PAGE 4 | [14 empty] | PAGE 22
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
[5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [13 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
[5 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [13 empty] | MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
[5 empty] | MONTHLY OPERATIONAL REPORT | [13 empty] | REGIONAL MONITORING WELL ONE
[5 empty] | EFFLUENT DATA PART 2 | [13 empty] | RMW-1 |  |  |  | 1/07/04 thru 1/06/09
[16 empty] | RUN DATE |  |  |  |  | PERMIT # 0054569-142-UO
[16 empty] | 2026-07-30 |  | UPPER MONITOR ZONE |  |  |  |  | LOWER MONITOR ZONE
RUN DATE | [16 empty] | MIN | MAX | AVG |  |  | MIN | MAX | AVG
2026-07-30 | [15 empty] | JUNE | FT HEAD | FT HEAD | FT HEAD |  |  | FT HEAD | FT HEAD | FT HEAD
[16 empty] | 2005 | ABOVE | ABOVE | ABOVE |  |  | ABOVE | ABOVE | ABOVE
| JUNE | EFF. BACT. | EFF. BACT. | FREE | TOTAL | EFFL. | EFF PH | EFF PH | EFF. SAP | AVG. | Sufates | [5 empty] | NGVD | NGVD | NGVD |  |  | NGVD | NGVD | NGVD
| 2005 | TOTAL | FECAL | CL2 | CL2 | pH | MIN | MAX | TEMP.(C) | BLK. | [5 empty] | 1 | 44.54 | 44.64 | 44.59 |  |  | 22.53 | 22.68 | 22.63
2
| 1 | 170 | 0 | 0 | 0.8 | 6.6 | 6.6 | 6.6 | 2 | 41 | 134.5 |  |  |  |  | 3
| 2 | TNTC | 179 | 0 | 0.8 | 6.6 | 6.5 | 6.5 | 3 | 33 | 123.5 |  |  |  |  | 4
| 3 | 300 | 0 | 0 | 1.5 | 6.6 | 6.6 | 6.7 | 5 | 38 | 124.3 |  |  |  |  | 5
| 4 | 0 | 0 | 0 | 1.3 | 6.5 | 6.5 | 6.6 | 5 | 55 | 120 |  |  |  |  | 6
| 5 | 18 | 0 | 0 | 1.1 | 6.5 | 6.5 | 6.6 | 2 | 44 | 110.8 |  |  |  |  | 7
| 6 | 410 | 0 | 0 | 1.2 | 6.7 | 6.6 | 6.8 | 3 | 33 | 121 |  |  |  |  | 8
| 7 | 4200 | 18 | 0 | 1 | 6.6 | 6.6 | 6.8 | 3 | 40 | 108.5 |  |  |  |  | 9
| 8 | TNTC | TNTC | 0 | 1 | 6.6 | 6.6 | 6.6 | 3 | 33 | 106.8 |  |  |  |  | 10
| 9 | TNTC | TNTC | 0 | 1 | 6.6 | 6.5 | 6.7 | 3 | 30 | 122 |  |  |  |  | 11
| 10 | 64 | 0 | 0 | 1.1 | 6.6 | 6.5 | 6.6 | 1.2 | 35 | 126 |  |  |  |  | 12
| 11 | 41 | 0 | 0 | 1.3 | 6.6 | 6.5 | 6.7 | 3.3 | 49 | 110.5 |  |  |  |  | 13
| 12 | 9 | 0 | 0 | 1.2 | 6.6 | 6.5 | 6.6 | 3 | 16 | 95.5 |  |  |  |  | 14
| 13 | 9 | 0 | 0 | 1 | 6.6 | 6.5 | 6.6 | 3 | 32 | 109.8 |  |  |  |  | 15
| 14 | TNTC | TNTC | 0 | 0.9 | 6.6 | 6.6 | 6.7 | 3 | 26 | 108.8 |  |  |  |  | 16
| 15 | 0 | 0 | 0 | 1 | 6.6 | 6.6 | 6.7 | 3 | 24 | 97.8 |  |  |  |  | 17
| 16 | 9 | 0 | 0 | 1.1 | 6.6 | 6.6 | 6.7 | 2 | 22 | 106 |  |  |  |  | 18
| 17 | TNTC | TNTC | 0 | 0.8 | 6.6 | 6.6 | 6.7 | 0.5 | 23 | 111.5 |  |  |  |  | 19
| 18 | 0 | 0 | 0 | 1.2 | 6.6 | 6.6 | 6.6 | 1.6 | 34 | 112.3 |  |  |  |  | 20
| 19 | 16 | 0 | 0 | 1.2 | 6.6 | 6.5 | 6.6 | 3 | 28 | 120 |  |  |  |  | 21
| 20 | 18 | 0 | 0 | 0.9 | 6.6 | 6.5 | 6.7 | 3 | 25 | 113.5 |  |  |  |  | 22
| 21 | 0 | 0 | 0 | 0.9 | 6.6 | 6.6 | 6.6 | 3 | 20 | 107.8 |  |  |  |  | 23
| 22 | TNTC | 26 | 0 | 0.9 | 6.6 | 6.6 | 6.6 | 2 | 17 | 99 |  |  |  |  | 24
| 23 | 0 | 0 | 0 | 1.4 | 6.7 | 6.6 | 6.8 | 0 | 0 | 96.8 |  |  |  |  | 25
| 24 | 117 | 9 | 0 | 1 | 6.7 | 6.6 | 6.8 | 0 | 19 | 92.3 |  |  |  |  | 26
| 25 | 455 | 0 | 0 | 1.1 | 6.6 | 6.6 | 6.8 | 2.5 | 23 | 89.8 |  |  |  |  | 27
| 26 | 0 | 9 | 0.1 | 1.3 | 6.7 | 6.6 | 7 | 0 | 20 | 81.8 |  |  |  |  | 28
| 27 | 9 | 0 | 0 | 1 | 6.7 | 6.6 | 6.7 | 3 | 21 | 96.3 |  |  |  |  | 29
| 28 | 9 | 0 | 0 | 1 | 6.7 | 6.6 | 6.7 | 3 | 14 | 100.3 |  |  |  |  | 30
| 29 | 18 | 0 | 0 | 0.8 | 6.7 | 6.6 | 6.7 | 3 | 12 | 85.5
| 30 | 63 | 9 | 0 | 1 | 6.7 | 6.6 | 6.8 | 2 | 14 | 85.5 |  |  |  |  | TOTAL | 44.54 | 44.64 | 44.59 |  |  | 22.53 | 22.68 | 22.63
[16 empty] | AVERAGE | 44.54 | 44.64 | 44.59 |  |  | 22.53 | 22.68 | 22.63
| TOTAL | 5935 | 250 | 0.1 | 31.8 | 198.6 | 197 | 200.6 | 74.1 | 821 | 3218.2 |  |  |  |  | MAXIMUM | 44.54 | 44.64 | 44.59 |  |  | 22.53 | 22.68 | 22.63
| AVERAGE | 247.2917 | 9.6154 | 0.0033333 | 1.06 | 6.62 | 6.5667 | 6.6867 | 2.3903 | 27.3667 | 107.2733 |  |  |  |  | MINIMUM | 44.54 | 44.64 | 44.59 |  |  | 22.53 | 22.68 | 22.63
[7 empty] | 6.5 | 7
[7 empty] | MIN | MAX
PAGE 5
PAGE 23
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
NUTRIENTS
RUN DATE
| 2026-07-30 |  | INFLUENT | [5 empty] | EFFLUENT
| JUNE | INFLUENT | INFLUENT | INFLUENT | INFLUENT |  | EFFL. | EFFL. | EFFL. | EFFL.
| 2005 | NH-3 | N03-N | TKN | TOT P |  | NH-3 | N03-N | TKN | TOT P
| 1 | 11 | 0.02 | 43 | 2.3 |  | 8 | 0.32 | 20 | 0.56
| 2 | 11 | 0.057 | 47 | 2.4 |  | 8.5 | 0.25 | 18 | 0.57
| 3 | 11 | 0.06 | 45 | 2.1 |  | 8.3 | 0.36 | 16 | 0.57
| 4 | 12 | 0.02 | 32 | 2.2 |  | 8 | 0.44 | 17 | 0.86
| 5 | 11 | 0.055 | 32 | 2.2 |  | 7.1 | 0.044 | 19 | 1.8
| 6 | 10 | 0.063 | 17 | 2 |  | 8.8 | 0.14 | 9 | 0.43
| 7 | 12 | 0.071 | 15 | 2.2 |  | 10 | 0.13 | 11 | 0.41
| 8 | 13 | 0.072 | 20 | 2.5 |  | 9.4 | 0.24 | 10 | 0.47
| 9 | 12 | 0.074 | 19 | 2.3 |  | 9.8 | 0.21 | 12 | 0.71
| 10 | 12 | 0.071 | 17 | 2.3 |  | 7.7 | 0.3 | 12 | 0.98
| 11 | 7.8 | 0.02 | 12 | 2.1 |  | 9.2 | 0.24 | 9.2 | 0.77
| 12 | 6.5 | 0.07 | 14 | 2.1 |  | 5 | 0.24 | 8.4 | 0.6
| 13 | 11 | 0.11 | 16 | 2.4 |  | 8.6 | 0.25 | 11 | 0.49
| 14 | 11 | 0.11 | 19 | 2.3 |  | 8.8 | 0.23 | 11 | 0.52
| 15 | 12 | 0.091 | 21 | 2.6 |  | 8.9 | 0.02 | 12 | 0.65
| 16 | 13 | 0.02 | 20 | 2.5 |  | 7.3 | 0.23 | 13 | 0.6
| 17 | 12 | 0.02 | 19 | 2.4 |  | 8.5 | 0.31 | 13 | 0.76
| 18 | 12 | 0.02 | 17 | 1.9 |  | 6 | 0.24 | 9.9 | 0.79
| 19 | 13 | 0.02 | 21 | 4.3 |  | 6 | 0.25 | 10 | 0.61
| 20 | 13 | 0.14 | 16 | 2.3 |  | 9.6 | 0.31 | 10 | 0.43
| 21 | 11 | 0.15 | 15 | 2 |  | 8.7 | 0.34 | 10 | 0.59
| 22 | 12 | 0.11 | 17 | 2.4 |  | 9.5 | 0.3 | 9.9 | 0.89
| 23 | 12 | 0.14 | 16 | 2.2 |  | 10 | 0.21 | 0 | 1.9
| 24 | 8.8 | 0.02 | 14 | 1.8 |  | 7.9 | 0.36 | 7.9 | 0.96
| 25 | 9.4 | 0.02 | 12 | 1.5 |  | 5.4 | 0.058 | 8.2 | 0.7
| 26 | 9.4 | 0.02 | 16 | 2.1 |  | 6.7 | 0.32 | 8.4 | 0.52
| 27 | 10 | 0.12 | 12 | 1.8 |  | 6.3 | 0.32 | 8.6 | 0.71
| 28 | 9.2 | 0.15 | 12 | 1.8 |  | 6.6 | 0.29 | 8 | 1.2
| 29 | 9.2 | 0.12 | 12 | 1.7 |  | 7.7 | 0.36 | 7.8 | 1.2
| 30 | 11 | 0.11 | 13 | 1.9 |  | 6.9 | 0.31 | 8.1 | 1.3
| TOTAL | 328.3 | 2.144 | 601 | 66.6 | TOT. | 239.2 | 7.622 | 328.4 | 23.55
| AVERAGE | 10.9433 | 0.071467 | 20.0333 | 2.22 | AVG. | 7.9733 | 0.25407 | 10.9467 | 0.785
PAGE 6
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
REACTOR ONE PROCESS
RUN DATE
| 2026-07-30 |  | TRAIN "A" | [5 empty] | TRAIN "B"
| JUNE | MLSS | MLVSS | SS | SVI |  | MLSS | MLVSS | SS | SVI
| 2005 | "A" | "A" | "A" | "A" |  | "B" | "B" | "B" | "B"
| 1 | O/S | O/S | O/S |  |  | 2300 | 1960 | 24 | 104.3478
| 2 | O/S | O/S | O/S |  |  | 2540 | 2090 | 21 | 82.6772
| 3 | O/S | O/S | O/S |  |  | 2710 | 2250 | 23 | 84.8708
| 4 | O/S | O/S | O/S |  |  | 2580 | 2090 | 29 | 112.4031
| 5 | O/S | O/S | O/S |  |  | 1870 | 1570 | 25 | 133.6898
| 6 | O/S | O/S | O/S |  |  | 2740 | 2270 | 24 | 87.5912
| 7 | O/S | O/S | O/S |  |  | 2730 | 2250 | 24 | 87.9121
| 8 | O/S | O/S | O/S |  |  | 2900 | 2380 | 25 | 86.2069
| 9 | O/S | O/S | O/S |  |  | 2930 | 2450 | 23 | 78.4983
| 10 | O/S | O/S | O/S |  |  | 3280 | 2770 | 25 | 76.2195
| 11 | O/S | O/S | O/S |  |  | 2450 | 2020 | 25 | 102.0408
| 12 | O/S | O/S | O/S |  |  | 2340 | 1960 | 22 | 94.0171
| 13 | O/S | O/S | O/S |  |  | 2690 | 2250 | 22 | 81.7844
| 14 | O/S | O/S | O/S |  |  | 2480 | 2020 | 21 | 84.6774
| 15 | O/S | O/S | O/S |  |  | 2550 | 2100 | 20 | 78.4314
| 16 | O/S | O/S | O/S |  |  | 2880 | 2360 | 20 | 69.4444
| 17 | O/S | O/S | O/S |  |  | 4270 | 3280 | 21 | 49.1803
| 18 | O/S | O/S | O/S |  |  | 2630 | 2140 | 26 | 98.8593
| 19 | O/S | O/S | O/S |  |  | 2280 | 1890 | 25 | 109.6491
| 20 | O/S | O/S | O/S |  |  | 2180 | 1710 | 20 | 91.7431
| 21 | O/S | O/S | O/S |  |  | 1990 | 1560 | 18 | 90.4523
| 22 | O/S | O/S | O/S |  |  | 2110 | 1700 | 18 | 85.3081
| 23 | O/S | O/S | O/S |  |  | 1490 | 1170 | 16 | 107.3826
| 24 | O/S | O/S | O/S |  |  | 1910 | 1520 | 15 | 78.534
| 25 | O/S | O/S | O/S |  |  | 2540 | 2080 | 19 | 74.8031
| 26 | O/S | O/S | O/S |  |  | 2220 | 1870 | 18 | 81.0811
| 27 | O/S | O/S | O/S |  |  | 1750 | 1440 | 20 | 114.2857
| 28 | O/S | O/S | O/S |  |  | 1370 | 1180 | 15 | 109.4891
| 29 | O/S | O/S | O/S |  |  | 1210 | 900 | 12 | 99.1736
| 30 | O/S | O/S | O/S |  |  | 1260 | 1160 | 11 | 87.3016
|  | O/S | O/S | O/S
| TOTAL | 0 | 0 | 0 |  |  | 71180 | 58390 | 627
| AVERAGE | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 2372.6667 | 1946.3333 | 20.9 | 88.0865
PAGE 7
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
REACTOR TWO PROCESS
RUN DATE
| 2026-07-30 |  | TRAIN "C" | [5 empty] | TRAIN "D"
| JUNE | MLSS | MLVSS | SS | SVI |  | MLSS | MLVSS | SS | SVI
| 2005 | "C" | "C" | "C" | "C" |  | "D" | "D" | "D" | "D"
| 1 | O/S | O/S | O/S |  |  | 2100 | 1810 | 24 | 114.2857
| 2 | O/S | O/S | O/S |  |  | 2120 | 1770 | 22 | 103.7736
| 3 | O/S | O/S | O/S |  |  | 2420 | 1970 | 23 | 95.0413
| 4 | O/S | O/S | O/S |  |  | 2010 | 1640 | 28 | 139.3035
| 5 | O/S | O/S | O/S |  |  | 1890 | 1590 | 25 | 132.2751
| 6 | O/S | O/S | O/S |  |  | 2350 | 1910 | 24 | 102.1277
| 7 | O/S | O/S | O/S |  |  | 2460 | 2030 | 25 | 101.626
| 8 | O/S | O/S | O/S |  |  | 2790 | 2260 | 25 | 89.6057
| 9 | O/S | O/S | O/S |  |  | 3390 | 2790 | 24 | 70.7965
| 10 | O/S | O/S | O/S |  |  | 2900 | 2510 | 26 | 89.6552
| 11 | O/S | O/S | O/S |  |  | 2380 | 1960 | 25 | 105.042
| 12 | O/S | O/S | O/S |  |  | 2260 | 1860 | 22 | 97.3451
| 13 | O/S | O/S | O/S |  |  | 2140 | 1790 | 23 | 107.4766
| 14 | O/S | O/S | O/S |  |  | 2580 | 2090 | 22 | 85.2713
| 15 | O/S | O/S | O/S |  |  | 2480 | 2040 | 21 | 84.6774
| 16 | O/S | O/S | O/S |  |  | 2290 | 1870 | 20 | 87.3362
| 17 | O/S | O/S | O/S |  |  | 3360 | 2690 | 21 | 62.5
| 18 | O/S | O/S | O/S |  |  | 2480 | 2040 | 26 | 104.8387
| 19 | O/S | O/S | O/S |  |  | 2100 | 1760 | 25 | 119.0476
| 20 | O/S | O/S | O/S |  |  | 2380 | 1890 | 20 | 84.0336
| 21 | O/S | O/S | O/S |  |  | 1970 | 1540 | 18 | 91.3706
| 22 | O/S | O/S | O/S |  |  | 1810 | 1510 | 18 | 99.4475
| 23 | O/S | O/S | O/S |  |  | 1480 | 1170 | 16 | 108.1081
| 24 | O/S | O/S | O/S |  |  | 2250 | 1710 | 15 | 66.6667
| 25 | O/S | O/S | O/S |  |  | 3240 | 2640 | 19 | 58.642
| 26 | O/S | O/S | O/S |  |  | 1900 | 1590 | 18 | 94.7368
| 27 | O/S | O/S | O/S |  |  | 1840 | 1530 | 20 | 108.6957
| 28 | O/S | O/S | O/S |  |  | 1260 | 1110 | 15 | 119.0476
| 29 | O/S | O/S | O/S |  |  | 1170 | 860 | 12 | 102.5641
| 30 | O/S | O/S | O/S |  |  | 1380 | 1280 | 10 | 72.4638
|  | O/S | O/S | O/S
| TOTAL | 0 | 0 | 0 |  |  | 67180 | 55210 | 632
| AVERAGE | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 2239.3333 | 1840.3333 | 21.0667 | 94.0756
PAGE 8
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
RAS SUMMARY
RUN DATE
2026-07-30
| JUNE | R-1 | R-2 | TOTAL | F/M | TOTAL | SLUDGE | % TOT | % FIX | % VOL.
| 2005 | TOT. RAS | TOT. RAS | MLVSS | RATIO | MLSS | AGE | RAS | RAS | RAS
|  | MGD | MGD
| 1 | 6.187 | 7.434 | 3770 | 1.0596 | 4400 | 0.43782 | 0.62 | 29.76 | 70.24
| 2 | 6.278 | 6.925 | 3860 | 0.86579 | 4660 | 0.94509 | 0.93 | 28.85 | 71.15
| 3 | 6.305 | 7.276 | 4220 | 0.99419 | 5130 | 2.3927 | 0.94 | 27.66 | 72.34
| 4 | 6.441 | 6.765 | 3730 | 0.75398 | 4590 | 1.2189 | 0.99 | 28.28 | 71.72
| 5 | 6.189 | 6.037 | 3160 | 0.40321 | 3760 | 0.97512 | 0.89 | 26.97 | 73.03
| 6 | 6.148 | 6.488 | 4180 | 0.524 | 5090 | 1.1479 | 0.91 | 27.47 | 72.53
| 7 | 6.344 | 7.403 | 4280 | 0.53911 | 5190 | 1.1782 | 0.97 | 26.4 | 73.6
| 8 | 6.388 | 7.765 | 4640 | 0.57917 | 5690 | 1.4604 | 0.7 | 31.43 | 68.57
| 9 | 6.417 | 7.846 | 5240 | 0.67241 | 6320 | 3.0664 | 0.75 | 29.25 | 70.75
| 10 | 6.37 | 7.86 | 5280 | 0.81071 | 6180 | 2.079 | 1.07 | 24.3 | 75.7
| 11 | 6.358 | 6.696 | 3980 | 0.73784 | 4830 | 0.6802 | 1.12 | 23.74 | 76.26
| 12 | 6.231 | 6.48 | 3820 | 1.0982 | 4600 | 0.99068 | 0.91 | 24.3 | 75.7
| 13 | 6.548 | 7.408 | 4040 | 1.0816 | 4830 | 0.83514 | 1.1 | 25.22 | 74.78
| 14 | 6.46 | 7.613 | 4110 | 1.0247 | 5060 | 1.1957 | 0.9 | 27.88 | 72.12
| 15 | 6.234 | 7.034 | 4140 | 1.0715 | 5030 | 1.0511 | 0.98 | 21.33 | 78.67
| 16 | 6.183 | 7.342 | 4230 | 1.0034 | 5170 | 1.0139 | 0.94 | 27.66 | 72.34
| 17 | 6.33 | 7.413 | 5970 | 0.71481 | 7630 | 1.632 | 1.26 | 23.02 | 76.98
| 18 | 6.281 | 6.736 | 4180 | 1.1121 | 5110 | 1.2627 | 1.13 | 26.55 | 73.45
| 19 | 6.132 | 6.907 | 3650 | 1.2243 | 4380 | 1.1007 | 1.05 | 23.81 | 76.19
| 20 | 6.235 | 7.004 | 3600 | 0.66477 | 4560 | 0.74212 | 0.91 | 27.03 | 72.97
| 21 | 6.397 | 6.272 | 3100 | 1.2622 | 3960 | 0.71774 | 0.71 | 32.04 | 67.96
| 22 | 6.496 | 6.067 | 3210 | 0.7367 | 3920 | 0.84013 | 0.67 | 31.34 | 68.66
| 23 | 6.447 | 6.099 | 2340 | 0.97082 | 2970 | 0.76949 | 0.85 | 29.41 | 70.59
| 24 | 6.459 | 6.326 | 3230 | 1.4055 | 4160 | 0.5203 | 0.79 | 24.76 | 75.24
| 25 | 6.343 | 6.302 | 4720 | 0.45007 | 5780 | 5.8498 | 0.96 | 25 | 75
| 26 | 6.294 | 6.618 | 3460 | 0.55724 | 4120 | 1.0684 | 0.79 | 25.3 | 74.7
| 27 | 6.121 | 7.624 | 2970 |  | 3590 | 0.80855 | 0.68 | 19.12 | 80.88
| 28 | 6.237 | 6.745 | 2290 | 0.28293 | 2630 | 0.63789 | 0.61 | 29.51 | 70.49
| 29 | 6.369 | 6.499 | 1760 | 1.197 | 2380 | 0.91455 | 0.65 | 29.23 | 70.77
| 30 | 6.259 | 7.375 | 2440 | 0.23645 | 2640 | 1.144 | 0.47 | 29.03 | 70.97
| TOTAL | 189.481 | 208.359 | 113600 |  | 138360 |  | 26.25 | 805.65 | 2194.35
| AVERAGE | 6.316 | 6.9453 | 3786.6667 | 0.84793 | 4612 | 1.0298 | 0.875 | 26.855 | 73.145
PAGE 9
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
DEWATERING DATA
RUN DATE
| 2026-07-30 |  | FEED SLUDGE |  |  |  |  | FILTRATE RETURN
| JUNE | % TOT. | % FIX. | % VOL. | pH |  | % TOT. | % FIX. | % VOL. | pH
| 2005 | FEED | FEED | FEED |  |  | FILT. | FILT. | FILT.
| 1 | 1.41 | 21.99 | 78.01 | 6.43 |  | 0.3 | 50 | 50 | 7.03
| 2 | 1.42 | 23.24 | 76.76 | 6.42 |  | 0.31 | 51.61 | 48.39 | 7.11
3
4
| 5 | 1.54 | 22.73 | 77.27 | 6.38 |  | 0.19 | 63.16 | 36.84 | 6.91
| 6 | 1.1 | 26.36 | 73.64 | 6.54 |  | 0.26 | 53.85 | 46.15 | 6.88
| 7 | 1.3 | 25.38 | 74.62 | 6.43 |  | 0.22 | 59.09 | 40.91 | 6.94
| 8 | 1.11 | 26.13 | 73.87 | 6.74 |  | 0.26 | 57.69 | 42.31 | 7.14
| 9 | 1.3 | 25.38 | 74.62 | 6.5 |  | 0.23 | 60.87 | 39.13 | 6.89
10
11
| 12 | 1.17 | 23.08 | 76.92 | 6.23 |  | 0.22 | 54.55 | 45.45 | 6.61
| 13 | 1.15 | 23.48 | 76.52 | 6.38 |  | 0.25 | 52 | 48 | 6.64
| 14 | 1.52 | 22.37 | 77.63 | 6.2 |  | 0.25 | 52 | 48 | 6.74
| 15 | 1.19 | 14.29 | 85.71 | 6.41 |  | 0.34 | 41.18 | 58.82 | 6.69
| 16 | 1.57 | 22.29 | 77.71 | 6.22 |  | 0.31 | 48.39 | 51.61 | 6.8
17
18
| 19 | 1.71 | 21.05 | 78.95 | 6.22 |  | 0.23 | 56.52 | 43.48 | 6.73
| 20 | 1.1 | 26.36 | 73.64 | 6.62 |  | 0.23 | 60.87 | 39.13 | 6.87
| 21 | 0.83 | 34.94 | 65.06 | 6.48 |  | 0.2 | 70 | 30 | 6.82
| 22 | 0.56 | 33.93 | 66.07 | 6.42 |  | 0.16 | 68.75 | 31.25 | 6.75
| 23 | 0.55 | 32.73 | 67.27 | 6.49 |  | 0.17 | 64.71 | 35.29 | 6.75
24
25
| 26 | 1 | 25 | 75 | 6.04 |  | 0.13 | 61.54 | 38.46 | 6.67
| 27 | 1.11 | 25.23 | 74.77 | 6.28 |  | 0.12 | 83.33 | 16.67 | 6.8
| 28 | 1.21 | 23.97 | 76.03 | 6.11 |  | 0.14 | 71.43 | 28.57 | 6.8
| 29 | 0.46 | 32.61 | 67.39 | 6.36 |  | 0.13 | 92.31 | 7.69 | 6.71
| 30 | 0.13 | 69.23 | 30.77 | 6.64 |  | 0.39 | 30.77 | 69.23 | 6.47
| TOTAL | 24.44 | 601.77 | 1598.23 | 140.54 |  | 5.04 | 1304.62 | 895.38 | 149.75
| AVERAGE | 1.1109 | 27.3532 | 72.6468 | 6.3882 |  | 0.22909 | 59.3009 | 40.6991 | 6.8068
PAGE 10
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
SLUDGE VOLUME REMOVED
RUN DATE
2026-07-30
|  | JUNE | TRAILERS | TONS | DRY TONS | % LIME | % TOT. | % FIX. | % VOL.
|  | 2005 | REMOVED | SLUDGE | REMOVED | CAKE | CAKE | CAKE | CAKE
|  | 1 | 4 | 88 | 39.9232 |  | 17.18 | 13.68 | 86.32
|  | 2 | 6 | 132 | 37.4825 |  | 18.1 | 14.48 | 85.52
|  | 3 | 4 | 88
|  | 4 | 0 | 0
|  | 5 | 0 | 0 | 44.8242 |  | 17.21 | 15.75 | 84.25
|  | 6 | 2 | 44 | 22.0635 |  | 18.06 | 17.05 | 82.95
|  | 7 | 5 | 110 | 11.7094 |  | 18.43 | 16.39 | 83.61
|  | 8 | 4 | 88 | 20.8754 |  | 17.88 | 16.5 | 83.5
|  | 9 | 6 | 132 | 41.4706 |  | 18.21 | 18.51 | 81.49
|  | 10 | 5 | 110
|  | 11 | 0 | 0
|  | 12 | 0 | 0 | 10.9775 |  | 17.44 | 21.56 | 78.44
|  | 13 | 4 | 88 | 30.5953 |  | 18.29 | 22.64 | 77.36
|  | 14 | 6 | 132 | 31.1215 |  | 18.03 | 23.24 | 76.76
|  | 15 | 3 | 66 | 23.9183 |  | 18.7 | 21.28 | 78.72
|  | 16 | 3 | 66 | 35.6151 |  | 16.26 | 17.59 | 82.41
|  | 17 | 5 | 110
|  | 18 | 0 | 0
|  | 19 | 0 | 0 | 15.0458 |  | 21.17 | 21.68 | 78.32
|  | 20 | 5 | 125 | 26.6963 |  | 18.04 | 23.28 | 76.72
|  | 21 | 5 | 110 | 20.905 |  | 18.9 | 18.73 | 81.27
|  | 22 | 6 | 132 | 14.1046 |  | 19.05 | 18.74 | 81.26
|  | 23 | 5 | 110 | 13.7151 |  | 19.03 | 19.76 | 80.24
|  | 24 | 5 | 110
|  | 25 | 0 | 0
|  | 26 | 0 | 0 | 6.4218 |  | 18.26 | 19.5 | 80.5
|  | 27 | 5 | 110 | 21.1994 |  | 18.31 | 18.22 | 81.78
|  | 28 | 5 | 110 | 26.7422 |  | 18.91 | 19.83 | 80.17
|  | 29 | 4 | 88 | 11.1447 |  | 19.35 | 20.41 | 79.59
|  | 30 | 3 | 66 | 2.2443 |  | 18.74 | 20.6 | 79.4
|  | TOTAL | 100 | 2215 | 508.7959 | 0 | 403.55 | 419.42 | 1780.58
|  | AVERAGE | 3.3333 | 73.8333 | 23.1271 | #DIV/0! | 18.3432 | 19.0645 | 80.9355
PAGE 11
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
CHEMICAL USEAGE
RUN DATE
2026-07-30
| JUNE | H2O2 | CL2 | POLYMER | POLYMER | LIME | GOX | O2 % | LOX | FPL
| 2005 | POUNDS | POUNDS | GALLONS | POUNDS | DELV. | TONS | PURITY | TONS | KW
| 1 | 1357 | 1400 | 38 | 316.92 | 0 | 34.2 | 99% | 97.7 | 33078
| 2 | 150 | 1640 | 85 | 708.9 | 0 | 27.8 | 100% | 99.8 | 33090
| 3 | 319 | 1360 | 16 | 133.44 | 0 | 24.5 | 100% | 98.7 | 32310
| 4 | 190 | 1420 | 17 | 141.78 | 0 | 24.8 | 100% | 96.9 | 32126
| 5 | 200 | 1520 | 68 | 567.12 | 0 | 30.5 | 99% | 96.5 | 32310
| 6 | 0 | 1400 | 87 | 725.58 | 0 | 29.9 | 99% | 96.4 | 31976
| 7 | 0 | 1240 | 39 | 325.26 | 0 | 31.7 | 99% | 97.1 | 32742
| 8 | 0 | 680 | 51 | 425.34 | 0 | 31.4 | 99% | 97.7 | 32737
| 9 | 978 | 1540 | 168 | 1401.12 | 0 | 30.3 | 96% | 96.4 | 29159
| 10 | 1787 | 1580 | 45 | 375.3 | 0 | 29.6 | 100% | 94.8 | 29965
| 11 | 1497 | 1520 | 0 | 0 | 0 | 32 | 98% | 94.6 | 32686
| 12 | 1946 | 1520 | 32 | 266.88 | 0 | 33.3 | 95% | 93.4 | 32224
| 13 | 1677 | 1360 | 143 | 1192.62 | 0 | 32.2 | 99% | 93.6 | 32249
| 14 | 1866 | 840 | 105 | 875.7 | 0 | 30.1 | 100% | 93.2 | 32567
| 15 | 1677 | 1280 | 17 | 141.78 | 0 | 22.7 | 100% | 93.2 | 32565
| 16 | 1148 | 1440 | 103 | 859.02 | 0 | 22.3 | 100% | 93.5 | 32393
| 17 | 1327 | 1260 | 51 | 425.34 | 0 | 22.7 | 100% | 94.3 | 31995
| 18 | 639 | 1380 | 0 | 0 | 0 | 24.3 | 99% | 94.6 | 32099
| 19 | 170 | 1500 | 68 | 567.12 | 0 | 29.2 | 99% | 94.9 | 32430
| 20 | 1397 | 1360 | 43 | 358.62 | 0 | 27.6 | 100% | 95.4 | 32551
| 21 | 279 | 1480 | 83 | 692.22 | 0 | 22.8 | 100% | 95.4 | 32337
| 22 | 529 | 1320 | 109 | 909.06 | 0 | 22 | 100% | 95.9 | 32352
| 23 | 568 | 1600 | 113 | 942.42 | 0 | 24.2 | 100% | 96.1 | 32004
| 24 | 180 | 1400 | 0 | 0 | 0 | 18.5 | 100% | 96.3 | 32336
| 25 | 0 | 1460 | 0 | 0 | 0 | 19.3 | 100% | 97.7 | 32182
| 26 | 0 | 900 | 0 | 0 | 0 | 24.5 | 100% | 98.5 | 32376
| 27 | 390 | 1560 | 84 | 700.56 | 0 | 20.5 | 100% | 98.6 | 32348
| 28 | 0 | 1420 | 107 | 892.38 | 0 | 27.6 | 100% | 100 | 32418
| 29 | 0 | 1400 | 66 | 550.44 | 0 | 23.2 | 100% | 101.4 | 32000
| 30 | 0 | 1480 | 96 | 800.64 | 0 | 19.8 | 100% | 101.5 | 32011
| TOTAL | 20271 | 41260 | 1834 | 15295.56 | 0 | 793.5 |  | 2894.1 | 965616
| AVERAGE | 675.7 | 1375.3333 | 61.1333 | 509.852 | 0 | 26.45 | 99.37% | 96.47 | 32187.2
PAGE 12
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL ONE
|  | RUN DATE |  |  | PERMIT NUMBER 0054569-142-UO
|  | 2026-07-30 |  |  | 1/07/04 thru 1/06/09 |  |  | I.D. #:5006A11308
|  | JUNE | % INFL. | MAX | MIN | WELL 1 | MAX | MIN | AVG
|  | 2005 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 25.73% | 14.73 | 5.87 | 10.99 | 70.8 | 42.37 | 56.45
|  | 2 | 11.12% | 12.5 | 0 | 5.18 | 60.6 | 36.13 | 45.8
|  | 3 | 21.98% | 15.22 | 0 | 10.54 | 71 | 36.41 | 56.61
|  | 4 | 25.43% | 14.26 | 4.87 | 11.63 | 67.34 | 45.68 | 58.23
|  | 5 | 25.08% | 15.29 | 7.98 | 12.09 | 72.7 | 47.4 | 59.74
|  | 6 | 24.98% | 14.29 | 7.6 | 12.07 | 68.18 | 46.73 | 59.84
|  | 7 | 5.945% | 12.64 | 0 | 2.65 | 61.19 | 36.06 | 41.36
|  | 8 | 21.39% | 14.44 | 0.01 | 9.08 | 67.91 | 35.62 | 53.13
|  | 9 | 24.29% | 13.99 | 0.01 | 10.13 | 65.13 | 35.6 | 54.21
|  | 10 | 26.55% | 13.46 | 7.94 | 11.18 | 64.71 | 47.39 | 56.75
|  | 11 | 24.67% | 15.16 | 8.67 | 12.62 | 72 | 50.33 | 62.37
|  | 12 | 1.946% | 13.12 | 0.01 | 0.96 | 64.43 | 36.21 | 38.92
|  | 13 | 23.88% | 14.52 | 0.01 | 10.87 | 68.28 | 36.54 | 57.43
|  | 14 | 21.97% | 14.49 | 0 | 9.41 | 69.61 | 35.85 | 53.64
|  | 15 | 26.13% | 13.98 | 6.32 | 10.63 | 66.86 | 44.01 | 55.28
|  | 16 | 25.81% | 12.61 | 6.6 | 10.36 | 62.06 | 44.74 | 54.56
|  | 17 | 0.3785% | 9.63 | 0 | 0.16 | 55.76 | 0 | 37.5
|  | 18 | 21.85% | 14.7 | 0 | 9.89 | 69.44 | 36.15 | 55.76
|  | 19 | 25.93% | 13.91 | 8.08 | 11.85 | 65.72 | 48.34 | 58.9
|  | 20 | 26.26% | 14.44 | 7.89 | 12.03 | 68.77 | 46.7 | 59.3
|  | 21 | 25.24% | 14.82 | 8.72 | 12.08 | 71 | 48.89 | 60
|  | 22 | 6.701% | 12.99 | 0 | 3.02 | 63.23 | 36.61 | 42.46
|  | 23 | 22.68% | 15.92 | 0 | 10.63 | 76 | 35.9 | 57.36
|  | 24 | 21.32% | 14.81 | 9.47 | 12.28 | 70.8 | 53.13 | 61.45
|  | 25 | 22.75% | 14.66 | 8.3 | 11.94 | 70.2 | 48.17 | 60.05
|  | 26 | 24.73% | 14.38 | 7.51 | 11.92 | 68.47 | 47.44 | 59.82
|  | 27 | 1.385% | 10.85 | 0 | 0.67 | 56.12 | 36.25 | 38.35
|  | 28 | 24.53% | 15.23 | 0 | 12.28 | 70.5 | 36.78 | 62.26
|  | 29 | 25.63% | 14.94 | 10.53 | 13.5 | 70 | 54.91 | 64.78
|  | 30 | 24.59% | 15.96 | 0.01 | 12.06 | 73.5 | 36.88 | 60.91
|  | TOTAL | 610.9% | 421.94 | 116.4 | 284.7 | 2022.31 | 1223.22 | 1643.22
|  | AVERAGE | 20.36% | 14.0647 | 3.88 | 9.49 | 67.4103 | 40.774 | 54.774
|  | MAXIMUM | 26.55% | 15.96 | 10.53 | 13.5 | 76 | 54.91 | 64.78
|  | MINIMUM | 0.3785% | 9.63 | 0 | 0.16 | 55.76 | 0 | 37.5
PAGE 13
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL TWO
|  | RUN DATE |  |  | PERMIT NUMBER 0054569-142-UO
|  | 2026-07-30 |  |  | 1/07/04 thru 1/06/09 |  |  | I.D. #:5006A11309
|  | JUNE | % INFL. | MAX | MIN | WELL 2 | MAX | MIN | AVG
|  | 2005 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 26.25% | 15 | 5.89 | 11.21 | 69.64 | 41.75 | 55.6
|  | 2 | 26.35% | 15.21 | 8.29 | 12.27 | 68.19 | 46.79 | 58.5
|  | 3 | 9.8% | 14.29 | 0.05 | 4.7 | 63.97 | 36.65 | 45.14
|  | 4 | 23.07% | 14.72 | 0.05 | 10.55 | 66.17 | 36.93 | 55.02
|  | 5 | 20.95% | 15.57 | 0.05 | 10.1 | 71.4 | 36.57 | 55.25
|  | 6 | 25.46% | 14.55 | 7.61 | 12.3 | 66.95 | 46.1 | 59.02
|  | 7 | 27.75% | 14.38 | 9.47 | 12.37 | 64.62 | 50.12 | 58.06
|  | 8 | 6.383% | 13.69 | 0.05 | 2.71 | 61.54 | 37.06 | 41.5
|  | 9 | 20.98% | 13.04 | 0.05 | 8.75 | 60.61 | 35.88 | 50.83
|  | 10 | 22.13% | 13.69 | 0.05 | 9.32 | 63.56 | 36.71 | 52.6
|  | 11 | 25.12% | 15.36 | 8.93 | 12.85 | 70.8 | 49.63 | 61.38
|  | 12 | 27.08% | 15.45 | 8.39 | 13.36 | 69.31 | 48.5 | 62.06
|  | 13 | 1.626% | 12.12 | 0.05 | 0.74 | 58.76 | 37.2 | 39.01
|  | 14 | 21.09% | 14.87 | 0.05 | 9.03 | 69.19 | 36.46 | 51.96
|  | 15 | 21.44% | 12.63 | 0.05 | 8.72 | 60.13 | 36.97 | 50.87
|  | 16 | 26.31% | 12.82 | 6.71 | 10.56 | 60.76 | 44.06 | 53.58
|  | 17 | 30.68% | 15.43 | 0 | 12.97 | 69.32 | 0 | 60.51
|  | 18 | 5.745% | 13.27 | 0.05 | 2.6 | 61.36 | 36.88 | 42.07
|  | 19 | 22.12% | 14.26 | 0.05 | 10.11 | 64.7 | 37.27 | 54.48
|  | 20 | 21.87% | 14.8 | 0.05 | 10.02 | 67.76 | 36.84 | 54.66
|  | 21 | 25.72% | 15.11 | 8.83 | 12.31 | 69.88 | 48.26 | 59
|  | 22 | 27.67% | 15.59 | 8.24 | 12.47 | 70.9 | 47.96 | 58.96
|  | 23 | 6.486% | 16.06 | 0.05 | 3.04 | 74.8 | 36.5 | 43.52
|  | 24 | 21.58% | 15.09 | 8.76 | 12.43 | 69.6 | 52.21 | 60.33
|  | 25 | 23.11% | 14.88 | 8.43 | 12.13 | 69.07 | 47.41 | 59.04
|  | 26 | 25.19% | 14.54 | 7.53 | 12.14 | 67.42 | 46.68 | 58.88
|  | 27 | 27.59% | 15.47 | 9.23 | 13.35 | 69.14 | 49.27 | 61.78
|  | 28 | 1.618% | 12.22 | 0.05 | 0.81 | 58.05 | 37.31 | 39.4
|  | 29 | 23.73% | 15.11 | 0.05 | 12.5 | 68.38 | 37.86 | 61.33
|  | 30 | 24.98% | 16.01 | 0.05 | 12.25 | 71.2 | 38.43 | 59.88
|  | TOTAL | 619.9% | 435.23 | 107.11 | 288.67 | 1997.18 | 1210.26 | 1624.22
|  | AVERAGE | 20.66% | 14.5077 | 3.5703 | 9.6223 | 66.5727 | 40.342 | 54.1407
|  | MAXIMUM | 30.68% | 16.06 | 9.47 | 13.36 | 74.8 | 52.21 | 62.06
|  | MINIMUM | 1.618% | 12.12 | 0 | 0.74 | 58.05 | 0 | 39.01
PAGE 14
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL THREE
|  | RUN DATE |  |  | PERMIT NUMBER 0054569-142-UO
|  | 2026-07-30 |  |  | 1/07/04 thru 1/06/09 |  |  | I.D. #:5006A11310
|  | JUNE | % INFL. | MAX | MIN | WELL 3 | MAX | MIN | AVG
|  | 2005 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 24.91% | 13.94 | 5.98 | 10.64 | 71 | 42.58 | 56.73
|  | 2 | 24.29% | 13.56 | 8.04 | 11.31 | 69.46 | 47.74 | 59.65
|  | 3 | 23.48% | 14.06 | 7.09 | 11.26 | 71.1 | 46.39 | 59.63
|  | 4 | 1.4% | 11.82 | ER | 0.64 | 61.53 | 37.56 | 39.69
|  | 5 | 18.94% | 14.65 | ER | 9.13 | 73 | 37.13 | 55.8
|  | 6 | 23.97% | 13.57 | 4.72 | 11.58 | 68.25 | 44.78 | 60.13
|  | 7 | 25.51% | 12.94 | 9.1 | 11.37 | 65.78 | 51.14 | 59.19
|  | 8 | 25.86% | 13.31 | 8.74 | 10.98 | 67.69 | 50.41 | 57.79
|  | 9 | 3.5% | 13.95 | ER | 1.46 | 69.72 | 37.45 | 41.08
|  | 10 | 20.16% | 12.95 | ER | 8.49 | 64.93 | 37.14 | 53.09
|  | 11 | 23.21% | 14.22 | ER | 11.87 | 72.3 | 37.7 | 62.22
|  | 12 | 24.59% | 14.02 | 7.97 | 12.13 | 70.6 | 49.45 | 63.19
|  | 13 | 25.11% | 13.48 | 8.74 | 11.43 | 68.37 | 50.79 | 60.09
|  | 14 | 6.072% | 13.31 | ER | 2.6 | 67.28 | 37.79 | 43.7
|  | 15 | 19.57% | 12.03 | ER | 7.96 | 61.4 | 37.54 | 51.37
|  | 16 | 20.61% | 12.06 | ER | 8.27 | 61.97 | 37.05 | 51.73
|  | 17 | 27.77% | 13.9 | 0 | 11.74 | 70.6 | 0 | 61.53
|  | 18 | 24.9% | 13.69 | 7.74 | 11.27 | 69.66 | 48.66 | 59.7
|  | 19 | 1.335% | 10.78 | ER | 0.61 | 57.67 | 38.07 | 39.97
|  | 20 | 19.82% | 13.93 | ER | 9.08 | 69.29 | 37.54 | 55.25
|  | 21 | 19.56% | 14.06 | ER | 9.36 | 71.3 | 37.38 | 55.88
|  | 22 | 25.54% | 14.09 | 8.1 | 11.51 | 72.2 | 48.94 | 60.07
|  | 23 | 24.47% | 14.86 | 7.73 | 11.47 | 76.4 | 47.68 | 60.4
|  | 24 | 16.67% | 13.66 | ER | 9.6 | 70.2 | 39.85 | 57.15
|  | 25 | 21.38% | 14.02 | ER | 11.22 | 70.5 | 39.86 | 59.7
|  | 26 | 23.59% | 13.62 | ER | 11.37 | 68.76 | 38.06 | 59.72
|  | 27 | 25.13% | 13.94 | 8.61 | 12.16 | 70.4 | 50.24 | 62.96
|  | 28 | 25.25% | 14.12 | 9.66 | 12.64 | 70.7 | 53.06 | 64.87
|  | 29 | 1.405% | 12.58 | ER | 0.74 | 64.18 | 38.9 | 41.21
|  | 30 | 20.39% | 15.97 | ER | 10 | 79.2 | 37.87 | 58.13
|  | TOTAL | 588.4% | 407.09 | 102.22 | 273.89 | 2065.44 | 1238.75 | 1671.62
|  | AVERAGE | 19.61% | 13.5697 | 7.3014 | 9.1297 | 68.848 | 41.2917 | 55.7207
|  | MAXIMUM | 27.77% | 15.97 | 9.66 | 12.64 | 79.2 | 53.06 | 64.87
|  | MINIMUM | 1.335% | 10.78 | 0 | 0.61 | 57.67 | 0 | 39.69
PAGE 15
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL FOUR
|  | RUN DATE |  |  | PERMIT NUMBER 0054569-142-UO
|  | 2026-07-30 |  |  | 1/07/04 thru 1/06/09
|  | JUNE | % INFL. | MAX | MIN | WELL 4 | MAX | MIN | AVG
|  | 2005 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 22.17% | 14.6 | 0.04 | 9.47 | 71.3 | 36.32 | 54.85
|  | 2 | 20.36% | 13.88 | 0.04 | 9.48 | 69.93 | 36.75 | 56.39
|  | 3 | 23.83% | 14.29 | 7.23 | 11.43 | 71.6 | 47.05 | 60.27
|  | 4 | 25.13% | 13.98 | 8.6 | 11.49 | 68.14 | 49.59 | 59.29
|  | 5 | 9.399% | 12.82 | 0.03 | 4.53 | 62.87 | 37.57 | 46.6
|  | 6 | 20.86% | 14 | 0.04 | 10.08 | 68.73 | 36.89 | 57.21
|  | 7 | 21.02% | 13.09 | 0.04 | 9.37 | 66.34 | 36.8 | 55.74
|  | 8 | 26.17% | 13.49 | 8.84 | 11.11 | 68.24 | 51.03 | 58.38
|  | 9 | 26.3% | 14.03 | 7.31 | 10.97 | 70.2 | 46.84 | 57.18
|  | 10 | 5.889% | 12.51 | 0.04 | 2.48 | 62.28 | 37.7 | 42.58
|  | 11 | 19.3% | 14.84 | 0.04 | 9.87 | 72.7 | 37.2 | 58.27
|  | 12 | 24.89% | 14.56 | 4.98 | 12.28 | 71.1 | 46.28 | 63.58
|  | 13 | 25.44% | 13.75 | 8.94 | 11.58 | 68.77 | 51.38 | 60.68
|  | 14 | 26.13% | 14.12 | 6.24 | 11.19 | 64.71 | 46.74 | 58.52
|  | 15 | 6.269% | 13.57 | 0.04 | 2.55 | 67.52 | 37.87 | 42.86
|  | 16 | 20.58% | 12.66 | 0.04 | 8.26 | 62.37 | 37.16 | 51.66
|  | 17 | 28.22% | 14.06 | 0 | 11.93 | 71.2 | 0 | 62.26
|  | 18 | 25.21% | 13.8 | 7.82 | 11.41 | 70.2 | 49.32 | 60.37
|  | 19 | 25.44% | 13.54 | 8.25 | 11.63 | 66.65 | 49.22 | 59.78
|  | 20 | 5.85% | 13.72 | 0.04 | 2.68 | 66.62 | 38.07 | 43.26
|  | 21 | 19.04% | 14.47 | 0.03 | 9.11 | 71.8 | 37.19 | 55.45
|  | 22 | 21.15% | 14.31 | 0.04 | 9.53 | 72.7 | 37.15 | 56.72
|  | 23 | 24.69% | 15.06 | 7.78 | 11.57 | 76.9 | 48.36 | 61
|  | 24 | 20.56% | 14.34 | 9.3 | 11.84 | 71.6 | 53.9 | 62.19
|  | 25 | 9.602% | 12.67 | 0.05 | 5.04 | 64.58 | 38.98 | 47.88
|  | 26 | 20.54% | 14.04 | 0.05 | 9.9 | 69.25 | 37.35 | 56.83
|  | 27 | 25.55% | 14.23 | 6.14 | 12.36 | 70.8 | 45.57 | 63.37
|  | 28 | 25.45% | 14.15 | 9.7 | 12.74 | 71.2 | 53.7 | 65.44
|  | 29 | 24.89% | 14.49 | 10.46 | 13.11 | 70.9 | 55.74 | 65.7
|  | 30 | 4.996% | 15.95 | 0.04 | 2.45 | 79.6 | 38.03 | 44.18
|  | TOTAL | 604.9% | 419.02 | 112.19 | 281.44 | 2080.8 | 1255.75 | 1688.49
|  | AVERAGE | 20.16% | 13.9673 | 3.7397 | 9.3813 | 69.36 | 41.8583 | 56.283
|  | MAXIMUM | 28.22% | 15.95 | 10.46 | 13.11 | 79.6 | 55.74 | 65.7
|  | MINIMUM | 4.996% | 12.51 | 0 | 2.45 | 62.28 | 0 | 42.58
PAGE 16
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL FIVE
|  | RUN DATE |  |  | PERMIT NUMBER 0054569-142-UO
|  | 2026-07-30 |  |  | 1/07/04 thru 1/06/09 |  |  | I.D. #:5006A11311
|  | JUNE | % INFL. | MAX | MIN | WELL 5 | MAX | MIN | AVG
|  | 2005 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 0.679% | 8.51 | ER | 0.29 | 57.32 | 34.75 | 37.23
|  | 2 | 18.1% | 12.94 | ER | 8.43 | 69.01 | 34.95 | 54.64
|  | 3 | 21.56% | 13.42 | ER | 10.34 | 70.7 | 37.26 | 58.39
|  | 4 | 23.51% | 13.02 | 8.09 | 10.75 | 67.06 | 48.56 | 58.25
|  | 5 | 23.28% | 14.17 | 7.91 | 11.22 | 72.4 | 47.39 | 59.67
|  | 6 | 2.401% | 11.1 | ER | 1.16 | 59 | 35.88 | 39.48
|  | 7 | 18.73% | 12.3 | ER | 8.35 | 65.29 | 35.42 | 53.9
|  | 8 | 20.09% | 12.68 | ER | 8.53 | 67.25 | 36.6 | 53.88
|  | 9 | 24.65% | 13.19 | 6.91 | 10.28 | 69.34 | 45.82 | 56.12
|  | 10 | 24.96% | 12.52 | 7.81 | 10.51 | 64.38 | 47.6 | 56.6
|  | 11 | 6.022% | 12.01 | ER | 3.08 | 65.07 | 36.13 | 43.82
|  | 12 | 20.35% | 13.19 | ER | 10.04 | 70 | 37.1 | 59.55
|  | 13 | 23.79% | 12.78 | 5.26 | 10.83 | 67.91 | 46.87 | 59.57
|  | 14 | 24.59% | 13.18 | 6.67 | 10.53 | 69.13 | 48.39 | 57.57
|  | 15 | 24.76% | 12.63 | 6.29 | 10.07 | 66.5 | 43.9 | 54.98
|  | 16 | 5.457% | 11.75 | ER | 2.19 | 60.44 | 36.81 | 40.81
|  | 17 | 26.16% | 13.17 | 0 | 11.06 | 70.2 | 0 | 60.99
|  | 18 | 22.4% | 12.95 | ER | 10.14 | 69.19 | 37.59 | 58.19
|  | 19 | 23.78% | 12.65 | 7.75 | 10.87 | 65.52 | 48.23 | 58.75
|  | 20 | 24.51% | 13.47 | 7.56 | 11.23 | 68.7 | 46.58 | 59.2
|  | 21 | 8.714% | 13.01 | ER | 4.17 | 65.75 | 36.85 | 45.53
|  | 22 | 18.77% | 13.44 | ER | 8.46 | 71.7 | 35.49 | 54.8
|  | 23 | 23.15% | 14.11 | 6.23 | 10.85 | 76 | 47.35 | 59.91
|  | 24 | 19.31% | 13.37 | 8.79 | 11.12 | 70.5 | 52.96 | 61.18
|  | 25 | 21.05% | 13.48 | 7.83 | 11.05 | 69.89 | 48.11 | 59.81
|  | 26 | 3.299% | 12.51 | ER | 1.59 | 63.68 | 36.34 | 40.65
|  | 27 | 21.16% | 13.18 | ER | 10.24 | 69.97 | 36.87 | 60
|  | 28 | 23.83% | 13.28 | 6.58 | 11.93 | 70.2 | 49.62 | 64.35
|  | 29 | 23.24% | 13.48 | 9.8 | 12.24 | 69.87 | 54.74 | 64.61
|  | 30 | 23.43% | 14.33 | 0.18 | 11.49 | 73.7 | 37.76 | 61.42
|  | TOTAL | 565.7% | 385.82 | 103.66 | 263.04 | 2035.67 | 1221.92 | 1653.85
|  | AVERAGE | 18.86% | 12.8607 | 6.4787 | 8.768 | 67.8557 | 40.7307 | 55.1283
|  | MAXIMUM | 26.16% | 14.33 | 9.8 | 12.24 | 76 | 54.74 | 64.61
|  | MINIMUM | 0.679% | 8.51 | 0 | 0.29 | 57.32 | 0 | 37.23
PAGE 17
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
INJECTION WELL SUMMARY
RUN DATE
2026-07-30
| JUNE | INFLUENT | EFFLUENT | EFFLUENT | IW-1 | IW-2 | IW-3 | IW-4 | IW-5 | TOTAL
| 2005 | FLOW | FLOW | SS | LBS SS | LBS SS | LBS SS | LBS SS | LBS SS | LBS SS
|  | MGD | MGD
| 1 | 42.712 | 42.258 | 11 | 1008.2226 | 1028.4054 | 976.1136 | 868.7778 | 26.6046 | 3039.3462
| 2 | 46.568 | 46.344 | 15 | 648.018 | 1534.977 | 1414.881 | 1185.948 | 1054.593 | 4652.469
| 3 | 47.958 | 48.351 | 6 | 527.4216 | 235.188 | 563.4504 | 571.9572 | 517.4136 | 1843.4736
| 4 | 45.725 | 45.119 | 17 | 1648.9014 | 1495.779 | 90.7392 | 1629.0522 | 1524.135 | 4759.5546
| 5 | 48.199 | 46.856 | 10 | 1008.306 | 842.34 | 761.442 | 377.802 | 935.748 | 3547.836
| 6 | 48.32 | 47.233 | 8 | 805.3104 | 820.656 | 772.6176 | 672.5376 | 77.3952 | 2475.9792
| 7 | 44.575 | 44.157 | 13 | 287.313 | 1341.1554 | 1232.7354 | 1015.8954 | 905.307 | 3766.5108
| 8 | 42.458 | 42.319 | 3 | 227.1816 | 67.8042 | 274.7196 | 277.9722 | 213.4206 | 783.126
| 9 | 41.712 | 41.63 | 9 | 760.3578 | 656.775 | 109.5876 | 823.4082 | 771.6168 | 2298.3372
| 10 | 42.112 | 41.833 | 14 | 1305.3768 | 1088.2032 | 991.2924 | 289.5648 | 1227.1476 | 4612.02
| 11 | 51.15 | 49.977 | 22 | 2315.5176 | 2357.718 | 2177.9076 | 1810.9476 | 565.1184 | 7416.2616
| 12 | 49.335 | 48.848 | 9 | 72.0576 | 1002.8016 | 910.4778 | 921.7368 | 753.6024 | 2738.9394
| 13 | 45.518 | 45.477 | 10 | 906.558 | 61.716 | 953.262 | 965.772 | 903.222 | 2824.758
| 14 | 42.822 | 42.77 | 10 | 784.794 | 753.102 | 216.84 | 933.246 | 878.202 | 2632.938
| 15 | 40.675 | 39.974 | 11 | 975.1962 | 799.9728 | 730.2504 | 233.937 | 923.8218 | 3429.2412
| 16 | 40.132 | 39.552 | 12 | 1036.8288 | 1056.8448 | 827.6616 | 826.6608 | 219.1752 | 3140.5104
| 17 | 42.276 | 42.865 | 8 | 10.6752 | 865.3584 | 783.2928 | 795.9696 | 737.9232 | 2397.2496
| 18 | 45.26 | 45.212 | 12 | 989.7912 | 260.208 | 1127.9016 | 1141.9128 | 1014.8112 | 3392.712
| 19 | 45.708 | 45.151 | 12 | 1185.948 | 1011.8088 | 61.0488 | 1163.9304 | 1087.8696 | 3346.6752
| 20 | 45.815 | 44.925 | 18 | 1805.9436 | 1504.2024 | 1363.0896 | 402.3216 | 1685.8476 | 6359.0832
| 21 | 47.854 | 46.964 | 21 | 2115.6912 | 2155.9734 | 1639.3104 | 1595.5254 | 730.3338 | 6641.3088
| 22 | 45.069 | 44.967 | 12 | 302.2416 | 1247.9976 | 1151.9208 | 953.7624 | 846.6768 | 3548.8368
| 23 | 46.868 | 46.928 | 5 | 443.271 | 126.768 | 478.299 | 482.469 | 452.445 | 1500.783
| 24 | 57.594 | 57.462 | 12 | 1228.9824 | 1243.9944 | 960.768 | 1184.9472 | 1112.8896 | 4546.6344
| 25 | 52.491 | 51.617 | 4 | 398.3184 | 404.6568 | 374.2992 | 168.1344 | 368.628 | 1545.9024
| 26 | 48.201 | 46.987 | 8 | 795.3024 | 809.9808 | 758.6064 | 660.528 | 106.0848 | 2469.9744
| 27 | 48.385 | 48.647 | 11 | 61.4658 | 1224.729 | 1115.5584 | 1133.9064 | 939.4176 | 3341.1708
| 28 | 50.065 | 50.085 | 8 | 819.3216 | 54.0432 | 843.3408 | 850.0128 | 795.9696 | 2512.6752
| 29 | 52.667 | 52.267 | 10 | 1125.9 | 1042.5 | 61.716 | 1093.374 | 1020.816 | 3250.932
| 30 | 49.039 | 48.179 | 2 | 201.1608 | 204.33 | 166.8 | 40.866 | 191.6532 | 763.944
| TOTAL | 1397.263 | 1384.954 | 323 | 25801.3746 | 27299.9892 | 23889.93 | 25072.8756 | 22587.8892 | 99579.183
| AVERAGE | 46.5754 | 46.1651 | 10.7667 | 860.0458 | 909.9996 | 796.331 | 835.7625 | 752.9296 | 3319.3061
PAGE 18
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
| RUN DATE |  |  |  | SOLIDS REMOVAL INVENTORY DATA SHEET
2026-07-30
| JUNE | TONS | CAKE |  |  |  | JUNE | RAGS | GRIT | OTHER
| 2005 | SLUDGE | TSS |  |  |  | 2005 |  |  | (vac)
| 1st - 7th | [5 empty] | 1st - 7th
| 1 | 88 | 17.18 |  |  |  | 1
| 2 | 132 | 18.1 |  |  |  | 2
| 3 | 88 |  |  |  |  | 3 | 10 | 10
| 4 | 0 |  |  |  |  | 4
| 5 | 0 | 17.21 |  |  |  | 5
| 6 | 44 | 18.06 |  |  |  | 6
| 7 | 110 | 18.43 |  |  |  | 7 |  | 10
| TOTAL = | 462 | 17.796 | = AVG. |  |  | TOTAL = | 10 | 20 | 0
| 8th - 14th | [5 empty] | 8th - 14th
| 8 | 88 | 17.88 |  |  |  | 8
| 9 | 132 | 18.21 |  |  |  | 9
| 10 | 110 |  |  |  |  | 10
| 11 | 0 |  |  |  |  | 11
| 12 | 0 | 17.44 |  |  |  | 12
| 13 | 88 | 18.29 |  |  |  | 13
| 14 | 132 | 18.03 |  |  |  | 14 | 10
| TOTAL = | 550 | 17.97 | = AVG. |  |  | TOTAL = | 10 | 0 | 0
| 15th - 22nd | [5 empty] | 15th-22nd
| 15 | 66 | 18.7 |  |  |  | 15
| 16 | 66 | 16.26 |  |  |  | 16 |  |  | 4500
| 17 | 110 |  |  |  |  | 17 | 10
| 18 | 0 |  |  |  |  | 18
| 19 | 0 | 21.17 |  |  |  | 19
| 20 | 125 | 18.04 |  |  |  | 20
| 21 | 110 | 18.9 |  |  |  | 21
| 22 | 132 | 19.05 |  |  |  | 22 |  | 10
| TOTAL = | 609 | 18.6867 | = AVG. |  |  | TOTAL = | 10 | 10 | 4500
| 23rd - 31st | [5 empty] | 23rd-31st
| 23 | 110 | 19.03 |  |  |  | 23
| 24 | 110 |  |  |  |  | 24
| 25 | 0 |  |  |  |  | 25
| 26 | 0 | 18.26 |  |  |  | 26
| 27 | 110 | 18.31 |  |  |  | 27
| 28 | 110 | 18.91 |  |  |  | 28 |  | 10
| 29 | 88 | 19.35 |  |  |  | 29
| 30 | 66 | 18.74 |  |  |  | 30 |  | 10
| TOTAL = | 594 | 18.7667 | = AVG. |  |  | TOTAL = | 0 | 20 | 0
RAGS & GRIT go to Central LandFill
Other(VAC) go to BCSR
PAGE 19

## INJECTION PAGES
|  |  |  | UNDERGROUND INJECTION CONTROL | [10 empty] | UNDERGROUND INJECTION CONTROL | [10 empty] | UNDERGROUND INJECTION CONTROL
[15 empty] | MONTHLY OPERATING REPORT | [10 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES |  |  |  |  | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES |  |  |  |  | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [10 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [10 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-1 | [7 empty] | Wet Well Description: |  |  | Effuent Wet Well for IW-1, IW-2, IW3, IW-4 and IW-5 | [7 empty] | Monitoring Well Decription: |  |  | UPPER ZONE OF MONITORING WELL MW-1
Permit #: |  | 0054569-142-UO |  |  |  |  | Date of Issuance: |  | 2004-01-07 |  | Facility ID #: |  | 5006M02066 |  |  |  | Permit Number: |  |  | FLA041378 |  | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | 0054569-142-UO
[22 empty] | Monitoring Well ID #: |  |  | 5006A11311
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2009-01-06 | [7 empty] | Issue Date: |  |  | 1999-10-18 |  | As Identified in Permit: |  | Monitor Well MW-1 Upper Monitor Zone |  |  |  | Issue Date: |  |  | 2004-01-07
[22 empty] | Monitoring Well Interval: |  |  | 1288' to 1320'
Injection Well ID #: |  | 5006A11308 | [8 empty] | Wet Well ID #: |  | Well Facility U-001 |  |  |  | Expiration Date: |  |  | 2004-10-17 |  | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.7 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24 | Associated Injection Well(s):
Injection Interval: |  |  | 2799' to 3513' | [18 empty] | 500A11311 |  |  | INJECTION WELL IW-5
[11 empty] | Injection Well ID #: |  |  | Injection Well Description
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s): | [10 empty] | 5006A11308 |  |  | INJECTION WELL IW-1
[11 empty] | 5006A11309 |  |  | INJECTION WELL IW-2 | [7 empty] | REPORT MONTH / YEAR: |  | 2005-06-01 | DATE OF SAP / RECORDING: |  |  | 2005-06-07 | 2005-06-14 | 2005-06-21 | 2005-06-28
Monitoring Zone ID #: | [5 empty] | Description |  |  |  |  | 5006A11310 |  |  | INJECTION WELL IW-3
[11 empty] | N/A |  |  | INJECTION WELL IW-4 | [7 empty] | OPERATOR'S NAME: |  |  | McGEARY, J.
UO-06-279401 |  | UPPER ZONE OF MONITORING WELL MW-2 | [8 empty] | 5006A11311 |  |  | INJECTION WELL IW-5
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4545-A
UO-06-279401 |  | LOWER ZONE OF MONITORING WELL MW-2
[11 empty] | THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [10 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [10 empty] | REPORT MONTH / YEAR: |  | 2005-06-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous |  |  | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2005-06-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous |  |  | OPERATOR'S NAME: |  |  | McGEARY, J.
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
OPERATOR'S NAME: |  |  | McGEARY, J. | [7 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4545-A | [7 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4545-A | [7 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: |  |  |  | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 49.46 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 40.7 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: |  |  |  | PARAMETER |  |  |  | Sampling Frequency |  |  |  | VALUE |  | UNITS | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 48.0547 | PSIG
[11 empty] | Nitrogen, Total as N |  |  |  |  | Daily/Monthly Average |  |  | 11.2007 |  | mg/L as N | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[11 empty] | Nitrogen, Nitrate, Total as N |  |  |  |  | Daily/Monthly Average |  |  | 0.25407 |  | mg/L as N | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7624.25 | mg/l
Total monthly flow | [7 empty] | 284.7 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 3800 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [7 empty] | Nitrogen, Total Kjeildahl as N |  |  |  |  | Daily/Monthly Average |  |  | 10.9467 |  | mg/L as N | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.9125 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 15.96 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.96 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 76 |  | PSIG | pH |  |  |  |  | Daily/Monthly Average |  |  | 6.62 |  | s.u. | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7.945 | Std units
Monthly average of the daily flow rates | [7 empty] | 9.49 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 12215 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 14.5881 |  | MG | Phosphorus, Total as P |  |  |  |  | Daily/Monthly Average |  |  | 0.785 |  | mg/L as P | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 2.985 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 76 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [10 empty] | Total Dissolved Solids (TDS) |  |  |  |  | Daily/Monthly Average |  |  | 1112.5667 |  | mg/L | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.01 | mg/l
Monthly average pressure | [7 empty] | 54.774 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 963.3333 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 36.14 |  | PSIG | Residue, Total filterable (TSS dried at 180 C) |  |  |  |  | Daily/Monthly Average |  |  | 10.7667 |  | mg/L | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[11 empty] | Specific Conductance (Temperature Compensated) |  |  |  |  | Daily/Monthly Average |  |  | 2200.1333 |  | umhos/cm | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just | [6 empty] | Temperature, Water |  |  |  |  | Daily/Monthly Average |  |  | 84.0633 |  | deg C
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [9 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just |  |  | Date: |  |  |  |  | (Signature):
[12 empty] | (Signature): | [10 empty] | Date:
|  |  |  | UNDERGROUND INJECTION CONTROL | [21 empty] | UNDERGROUND INJECTION CONTROL
|  |  |  | MONTHLY OPERATING REPORT | [21 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES | [15 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [21 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-2 | [18 empty] | Monitoring Well Decription: |  |  | LOWER ZONE OF MONITORING WELL MW-1
Permit #: |  | 0054569-142-UO |  |  |  |  | Date of Issuance: |  | 2004-01-07 | [12 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | 0054569-142-UO
[22 empty] | Monitoring Well ID #: |  |  | 5006A11311
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2009-01-06 | [12 empty] | As Identified in Permit: |  | Monitor Well MW-1 Lower Monitor Zone |  |  |  | Issue Date: |  |  | 2004-01-07
[22 empty] | Monitoring Well Interval: |  |  | 1449' to 1557'
Injection Well ID #: |  | 5006A11309 | [19 empty] | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.7 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24
Injection Interval: |  |  | 2798' to 3518' | [18 empty] | 500A11311 |  |  | INJECTION WELL IW-5
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s):
[22 empty] | REPORT MONTH / YEAR: |  | 2005-06-01 | DATE OF SAP / RECORDING: |  |  | 2005-06-07 | 2005-06-14 | 2005-06-21 | 2005-06-28
Monitoring Zone ID #: | [5 empty] | Description
[22 empty] | OPERATOR'S NAME: |  |  | McGEARY, J.
UO-06-279401 |  | UPPER ZONE OF MONITORING WELL MW-2
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4545-A
UO-06-279401 |  | LOWER ZONE OF MONITORING WELL MW-2
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [21 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2005-06-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
OPERATOR'S NAME: |  |  | McGEARY, J. | [18 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4545-A | [18 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 46.89 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 37.1 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: | [14 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 42.642 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 9550.25 | mg/l
Total monthly flow | [7 empty] | 288.67 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 5050 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [18 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 9.2 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 16.06 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 10.05 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 74.8 |  | PSIG | [11 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7.4125 | Std units
Monthly average of the daily flow rates | [7 empty] | 9.6223 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 15672.5 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 14.8027 |  | MG | [11 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 2.985 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 76.5 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [21 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.01 | mg/l
Monthly average pressure | [7 empty] | 54.1407 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 869.3333 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 36.72 |  | PSIG | [11 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [21 empty] | (Signature):
Date:
|  |  |  | UNDERGROUND INJECTION CONTROL | [21 empty] | UNDERGROUND INJECTION CONTROL
|  |  |  | MONTHLY OPERATING REPORT | [21 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES | [15 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [21 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-3 | [18 empty] | Monitoring Well Decription: |  |  | UPPER ZONE OF MONITORING WELL MW-2
Permit #: |  | 0054569-142-UO |  |  |  |  | Date of Issuance: |  | 2004-01-07 | [12 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | 0054569-142-UO
[22 empty] | Monitoring Well ID #: |  |  | 5006A11308 & 309
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2009-01-06 | [12 empty] | As Identified in Permit: |  | Monitor Well MW-2 Upper Monitor Zone |  |  |  | Issue Date: |  |  | 2004-01-07
[22 empty] | Monitoring Well Interval: |  |  | 1300' to 1344'
Injection Well ID #: |  | 5006A11310 | [19 empty] | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.7 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24
Injection Interval: |  |  | 2800' to 3977' | [18 empty] | 5006A11308 |  |  | INJECTION WELL IW-1
[22 empty] | 5006A11309 |  |  | INJECTION WELL IW-2
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s):
[22 empty] | REPORT MONTH / YEAR: |  | 2005-06-01 | DATE OF SAP / RECORDING: |  |  | 2005-06-07 | 2005-06-14 | 2005-06-21 | 2005-06-28
Monitoring Zone ID #: | [5 empty] | Description
[22 empty] | OPERATOR'S NAME: |  |  | McGEARY, J.
UO-06-279510 |  | UPPER ZONE OF MONITORING WELL MW-3
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4545-A
UO-06-279510 |  | LOWER ZONE OF MONITORING WELL MW-3
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [21 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2005-06-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
OPERATOR'S NAME: |  |  | McGEARY, J. | [18 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4545-A | [18 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 32.68 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 24.9 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: | [14 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 30.058 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7386.75 | mg/l
Total monthly flow | [7 empty] | 273.89 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 3650 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [18 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.8875 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 15.97 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.9875 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 79.2 |  | PSIG | [11 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 8.03 | Std units
Monthly average of the daily flow rates | [7 empty] | 9.1297 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 11930 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 14.0503 |  | MG | [11 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 2.985 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 74.5 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [21 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.01125 | mg/l
Monthly average pressure | [7 empty] | 55.7207 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 987.6667 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 37.65 |  | PSIG | [11 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [21 empty] | (Signature):
Date:
|  |  |  | UNDERGROUND INJECTION CONTROL | [21 empty] | UNDERGROUND INJECTION CONTROL
|  |  |  | MONTHLY OPERATING REPORT | [21 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES | [15 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [21 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-4 | [18 empty] | Monitoring Well Decription: |  |  | LOWER ZONE OF MONITORING WELL MW-2
Permit #: |  | 0054569-142-UO |  |  |  |  | Date of Issuance: |  | 2004-01-07 | [12 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | 0054569-142-UO
[22 empty] | Monitoring Well ID #: |  |  | 5006A11308 & 309
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2009-01-06 | [12 empty] | As Identified in Permit: |  | Monitor Well MW-2 Lower Monitor Zone |  |  |  | Issue Date: |  |  | 2004-01-07
[22 empty] | Monitoring Well Interval: |  |  | 1970' to 2025'
Injection Well ID #: |  | N/A | [19 empty] | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.7 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24
Injection Interval: |  |  | 2804' to 3977' | [18 empty] | 5006A11308 |  |  | INJECTION WELL IW-1
[22 empty] | 5006A11309 |  |  | INJECTION WELL IW-2
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s):
[22 empty] | REPORT MONTH / YEAR: |  | 2005-06-01 | DATE OF SAP / RECORDING: |  |  | 2005-06-07 | 2005-06-14 | 2005-06-21 | 2005-06-28
Monitoring Zone ID #: | [5 empty] | Description
[22 empty] | OPERATOR'S NAME: |  |  | McGEARY, J.
UO-06-279510 |  | UPPER ZONE OF MONITORING WELL MW-3
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4545-A
UO-06-279510 |  | LOWER ZONE OF MONITORING WELL MW-3
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [21 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2005-06-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
OPERATOR'S NAME: |  |  | McGEARY, J. | [18 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4545-A | [18 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 43.48 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 35.04 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: | [14 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 42.193 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 31967.75 | mg/l
Total monthly flow | [7 empty] | 281.44 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 17550 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [18 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.4 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 15.95 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.75 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 79.6 |  | PSIG | [11 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7.595 | Std units
Monthly average of the daily flow rates | [7 empty] | 9.3813 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 47050 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 14.4452 |  | MG | [11 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 2.985 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 73 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [21 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.01 | mg/l
Monthly average pressure | [7 empty] | 56.283 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 3200 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 38.22 |  | PSIG | [11 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [21 empty] | (Signature):
Date:
|  |  |  | UNDERGROUND INJECTION CONTROL | [21 empty] | UNDERGROUND INJECTION CONTROL
|  |  |  | MONTHLY OPERATING REPORT | [21 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES | [15 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [21 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-5 | [18 empty] | Monitoring Well Decription: |  |  | UPPER ZONE OF MONITORING WELL MW-3
Permit #: |  | 0054569-142-UO |  |  |  |  | Date of Issuance: |  | 2004-01-07 | [12 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | 0054569-142-UO
[22 empty] | Monitoring Well ID #: |  |  | 5006A11310
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2009-01-06 | [12 empty] | As Identified in Permit: |  | Monitor Well MW-3 Upper Monitor Zone |  |  |  | Issue Date: |  |  | 2004-01-07
[22 empty] | Monitoring Well Interval: |  |  | 1300' to 1349'
Injection Well ID #: |  | 5006A11311 | [19 empty] | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.7 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24
Injection Interval: |  |  | 2818' to 3462' | [18 empty] | 5006A11310 |  |  | INJECTION WELL IW-3
[22 empty] | N/A |  |  | INJECTION WELL IW-4
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s):
[22 empty] | REPORT MONTH / YEAR: |  | 2005-06-01 | DATE OF SAP / RECORDING: |  |  | 2005-06-07 | 2005-06-14 | 2005-06-21 | 2005-06-28
Monitoring Zone ID #: | [5 empty] | Description
[22 empty] | OPERATOR'S NAME: |  |  | McGEARY, J.
UO-06-279512 |  | UPPER ZONE OF MONITORING WELL MW-1
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4545-A
UO-06-279512 |  | LOWER ZONE OF MONITORING WELL MW-1
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [21 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2005-06-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
OPERATOR'S NAME: |  |  | McGEARY, J. | [18 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4545-A | [18 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 34.04 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 17.82 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: | [14 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 31.3627 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7612.5 | mg/l
Total monthly flow | [7 empty] | 263.04 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 3700 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [18 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.885 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 14.33 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.04 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 76 |  | PSIG | [11 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 8.155 | Std units
Monthly average of the daily flow rates | [7 empty] | 8.768 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 12070 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 13.5099 |  | MG | [11 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 2.985 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 73 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [21 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.01075 | mg/l
Monthly average pressure | [7 empty] | 55.1283 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 928.6667 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 36.64 |  | PSIG | [11 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [21 empty] | (Signature):
Date:
UNDERGROUND INJECTION CONTROL
MONTHLY OPERATING REPORT
[22 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
[22 empty] | Monitoring Well Decription: |  |  | LOWER ZONE OF MONITORING WELL MW-3
[22 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | 0054569-142-UO
[22 empty] | Monitoring Well ID #: |  |  | 5006A11310
[22 empty] | As Identified in Permit: |  | Monitor Well MW-3 Lower Monitor Zone |  |  |  | Issue Date: |  |  | 2004-01-07
[22 empty] | Monitoring Well Interval: |  |  | 1970 to 2027'
Associated Injection Well(s):
[22 empty] | Injection Well ID #: |  |  | Injection Well Description
[22 empty] | 5006A11310 |  |  | INJECTION WELL IW-3
[22 empty] | N/A |  |  | INJECTION WELL IW-4
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
[22 empty] | REPORT MONTH / YEAR: |  | 2005-06-01 | DATE OF SAP / RECORDING: |  |  | 2005-06-07 | 2005-06-14 | 2005-06-21 | 2005-06-28
[22 empty] | OPERATOR'S NAME: |  |  | McGEARY, J.
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4545-A
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
[22 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
[22 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
[22 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 46.21 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 35.49 | PSIG
[22 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 44.5567 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
[22 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 28928.5 | mg/l
[22 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 15750 | mg/l
[22 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 2.4 | mg/l
[22 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 2.75 | mg/l
[22 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7.5175 | Std units
[22 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 43150 | umho/cm
[22 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
[22 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 72.25 | deg. F
[22 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.02975 | mg/l
[22 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 3153.3333 | mg/l
[22 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
Date:

## DEP PART-A FORMS
30 | [5 empty] | Department of Environmental Protection Discharge Monitoring Report - Part A
When Completed mail this report to: Department of Environmental Protection, Southeast District, 400 North Congress Avenue, Suite 200 West Palm Beach, FL, 33401
| PERMITEE NAME: | City of Fort Lauderdale |  |  |  |  | PERMIT NUMBER: |  | FLA041378 |  | REPORT: | Monthly
| MAILING ADDRESS: | 949 NW 38th Street |  |  |  |  | LIMIT: |  | Final |  | GROUP: | Domestic
|  | Fort Lauderdale, FL 33309 |  |  |  |  | CLASS SIZE: |  | N/A |  | GMS TEST SITE
[7 empty] | MONITORING GROUP NUMBER: |  | U-001 |  | NO:
| FACILITY: | City of Fort Lauderdale G. T. Lohmeyer WWTF |  |  |  |  | MONITORING GROUP DESC: |  | Effluent Disposal including Influent
| LOCATION: | 1765 SE 18th Street |  |  |  |  | NO DISCHARGE FROM SITE:
Fort Lauderdale, FL 33316
| COUNTY: | Broward |  |  |  |  | MONITORING PERIOD: | From: | 2005-06-01 |  | To: | 2005-06-30
| Parameter |  | Quantity of Loading |  | Units |  | Quality or Concentration |  | Units | No. Ex. | Frequency of Analysis | Sample Type
| Flow | Sample Measurement | 8.768 | 13.5099 | [5 empty] | 0
| PARM Code 50050 1 Mon.Site No. EFF-007 | Permit Requirement | Report (Mo. Avg.) | Report (Peak Hour) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
| Flow | Sample Measurement | 9.3813 | 14.4452 | [5 empty] | 0
| PARM Code 50050 P Mon.Site No. EFF-006 | Permit Requirement | Report (Mo. Avg.) | Report (Peak Hour) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
| Flow | Sample Measurement | 9.1297 | 14.0503 | [5 empty] | 0
| PARM Code 50050 Q Mon.Site No. EFF-005 | Permit Requirement | Report (Mo. Avg.) | Report (Peak Hour) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
| Flow | Sample Measurement | 9.6223 | 14.8027 | [5 empty] | 0
| PARM Code 50050 R Mon.Site No. EFF-004 | Permit Requirement | Report (Mo. Avg.) | Report (Peak Hour) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
| Flow | Sample Measurement | 9.49 | 14.5881 | [5 empty] | 0
| PARM Code 50050 S Mon.Site No. EFF-003 | Permit Requirement | Report (Mo. Avg.) | Report (Peak Hour) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
| BOD, Carbonaceous 5 day, 20C | Sample Measurement |  |  |  | 4.7 |  |  |  | 0
| PARM Code 80082 Y Mon.Site No. EFF-002 | Permit Requirement |  |  |  | 20.0 (An.Avg.) |  |  | mg/l |  | Daily | 24-hour FPC
I certify under penalty of law that I have personally examined and am familiar with the informantion submitted herein; and based on my inquiry of those individuals immeadiately responsible for obtaining the information, I believe the submitted
information is true, accurate and complete. I am aware that there are significant penalties for submitting false information including the possiblity of fine and imprisonment.
| NAME/TITLE OF PRINCIPAL EXECUTIVE OFFICER OR AUTHORIZED AGENT |  |  |  | SIGNATURE OF PRINCIPAL EXECUTIVE OFFICER OR AUTHORIZED AGENT |  |  |  |  | TELEPHONE |  | DATE (YY/MM/DD)
954-523-1002 ext 2021
REGIONAL WASTEWATER FACILITIES MANAGER
COMMENTS AND EXPLANATION OF ANY VIOLATIONS (Reference all attachments here):
Version 3/30/05
Discharge Monitoring Report - Part A (Continued)
[13 empty] | FACILITY: | City of Fort Lauderdale G. T. Lohmeyer WWTF | [5 empty] | MONITORING GROUP NUMBER: U-001 |  |  | PERMIT NUMBER: |  | FLA041378
[20 empty] | MONITORING PERIOD: |  | From: | 2005-06-01 | To: | 2005-06-30
[13 empty] | Parameter |  |  | Quantity of Loading |  | Units |  | Quality or Concentration |  | Units | No. Ex. | Frequency of Analysis | Sample Type
[13 empty] | BOD, Carbonaceous 5 day, 20C |  | Sample Measurement |  |  |  | 2.4631 | 2.3339 | 5 |  | 0
[13 empty] | PARM Code 80082 1 Mon.Site No. EFF-002 |  | Permit Requirement |  |  |  | 30.0 (Mo.Avg.) | 45.0 (Week.Avg.) | 60.0 (Max.) | mg/l |  | Daily | 24-hour FPC
[13 empty] | Solids, Total Suspended |  | Sample Measurement |  |  |  | 17 |  |  |  | 0
[13 empty] | PARM Code 00530 Y Mon.Site No. EFF-002 |  | Permit Requirement |  |  |  | 20.0 (An.Avg.) |  |  | mg/l |  | Daily | 24-hour FPC
[13 empty] | Solids, Total Suspended |  | Sample Measurement |  |  |  | 10.7667 | 10.9724 | 22 |  | 0
[13 empty] | PARM Code 00530 1 Mon.Site No. EFF-002 |  | Permit Requirement |  |  |  | 30.0 (Mo.Avg.) | 45.0 (Week.Avg.) | 60.0 (Max.) | mg/l |  | Daily | 24-hour FPC
[13 empty] | pH |  | Sample Measurement |  |  |  | 6.5 |  |  |  | 0
[13 empty] | PARM Code 00400 1 Mon.Site No. EFF-002 |  | Permit Requirement |  |  |  | 6.0 (Min.) |  |  | s.u. |  | Continuous | Meter
[13 empty] | Flow |  | Sample Measurement | 36.532 | [6 empty] | N/A
[13 empty] | PARM Code 50050 G Mon.Site No. INF-001 |  | Permit Requirement | Report (An.Avg.) |  | mgd | [5 empty] | Continuous | Flow meters and totalizers
[13 empty] | Flow |  | Sample Measurement | 46.5754 | 37.8641 | [5 empty] | 0
[13 empty] | PARM Code 50050 T Mon.Site No. INF-001 |  | Permit Requirement | Report (Mo.Avg.) | 55.7 (3-Mo.Avg.) | mgd | [5 empty] | Continuous | Flow meters and totalizers
[13 empty] | BOD, Carbonaceous 5 day, 20C |  | Sample Measurement |  |  |  | 58.5972 |  |  |  | N/A
[13 empty] | PARM Code 80082 G Mon.Site No. INF-002 |  | Permit Requirement |  |  |  | Report (Mo.Avg.) |  |  | mg/l |  | Daily | 24-hour FPC
[13 empty] | Solids, Total Suspended |  | Sample Measurement |  |  |  | 81.7333 |  |  |  | N/A
[13 empty] | PARM Code 00530 G Mon.Site No. INF-002 |  | Permit Requirement |  |  |  | Report (Mo.Avg.) |  |  | mg/l |  | Daily | 24-hour FPC
[13 empty] | Percent Capacity, (TMADF/Permitted Capacity) x 100 |  | Sample Measurement |  |  |  | 67.98% |  |  |  | 0
[13 empty] | PARM Code 00530 G Mon.Site No. INF-002 |  | Permit Requirement |  |  |  | Report (Mo.Total) |  |  | mg/l |  | PERCENT | Calculated
Version 03/30/05
Formulas:
Monthly = ([FLA041378]-1)+A2

## DEP PART-B FORMS
DAILY SAMPLE RESULTS - B
| Permit Number |  | FLA041378 |  |  | Facility: | City of Fort Lauderdale G. T. Lohmeyer WWTF
| Monitoring Period: |  | From: | 2005-06-01 |  | To: | 2005-06-30
|  | CBOD5 (mg/L | pH (Max) | pH (Min) | TSS (mg/L | Flow (mgd) | Flow (mgd) | Flow (mgd) | Flow (mgd) | Flow (mgd)
Code |  | 80082 | 00400 | 00400 | 00530 | 50050 | 50050 | 50050 | 50050 | 50050
Mon. Site |  | EFF-002 | EFF-002 | EFF-002 | EFF-002 | EFF-003 | EFF-004 | EFF-005 | EFF-006 | EFF-007
1 |  | 3.94 | 6.6 | 6.6 | 11 | 10.99 | 11.21 | 10.64 | 9.47 | 0.29
2 |  | 2.64 | 6.5 | 6.5 | 15 | 5.18 | 12.27 | 11.31 | 9.48 | 8.43
3 |  | 3.69 | 6.7 | 6.6 | 6 | 10.54 | 4.7 | 11.26 | 11.43 | 10.34
4 |  | 2.35 | 6.6 | 6.5 | 17 | 11.63 | 10.55 | 0.64 | 11.49 | 10.75
5 |  | 2 | 6.6 | 6.5 | 10 | 12.09 | 10.1 | 9.13 | 4.53 | 11.22
6 |  | 2.33 | 6.8 | 6.6 | 8 | 12.07 | 12.3 | 11.58 | 10.08 | 1.16
7 |  | 2 | 6.8 | 6.6 | 13 | 2.65 | 12.37 | 11.37 | 9.37 | 8.35
8 |  | 2.3 | 6.6 | 6.6 | 3 | 9.08 | 2.71 | 10.98 | 11.11 | 8.53
9 |  | 2.21 | 6.7 | 6.5 | 9 | 10.13 | 8.75 | 1.46 | 10.97 | 10.28
10 |  | 2 | 6.6 | 6.5 | 14 | 11.18 | 9.32 | 8.49 | 2.48 | 10.51
11 |  | 1.99 | 6.7 | 6.5 | 22 | 12.62 | 12.85 | 11.87 | 9.87 | 3.08
12 |  | 2.22 | 6.6 | 6.5 | 9 | 0.96 | 13.36 | 12.13 | 12.28 | 10.04
13 |  | 2.23 | 6.6 | 6.5 | 10 | 10.87 | 0.74 | 11.43 | 11.58 | 10.83
14 |  | 2.64 | 6.7 | 6.6 | 10 | 9.41 | 9.03 | 2.6 | 11.19 | 10.53
15 |  | 2 | 6.7 | 6.6 | 11 | 10.63 | 8.72 | 7.96 | 2.55 | 10.07
16 |  | 2.19 | 6.7 | 6.6 | 12 | 10.36 | 10.56 | 8.27 | 8.26 | 2.19
17 |  | 2.91 | 6.7 | 6.6 | 8 | 0.16 | 12.97 | 11.74 | 11.93 | 11.06
18 |  | 2.71 | 6.6 | 6.6 | 12 | 9.89 | 2.6 | 11.27 | 11.41 | 10.14
19 |  | 2.43 | 6.6 | 6.5 | 12 | 11.85 | 10.11 | 0.61 | 11.63 | 10.87
20 |  | 2 | 6.7 | 6.5 | 18 | 12.03 | 10.02 | 9.08 | 2.68 | 11.23
21 |  | 2.8 | 6.6 | 6.6 | 21 | 12.08 | 12.31 | 9.36 | 9.11 | 4.17
22 |  | 2 | 6.6 | 6.6 | 12 | 3.02 | 12.47 | 11.51 | 9.53 | 8.46
23 |  | 2 | 6.8 | 6.6 | 5 | 10.63 | 3.04 | 11.47 | 11.57 | 10.85
24 |  | 2.85 | 6.8 | 6.6 | 12 | 12.28 | 12.43 | 9.6 | 11.84 | 11.12
25 |  | 2 | 6.8 | 6.6 | 4 | 11.94 | 12.13 | 11.22 | 5.04 | 11.05
26 |  | 2 | 7 | 6.6 | 8 | 11.92 | 12.14 | 11.37 | 9.9 | 1.59
27 |  | LS | 6.7 | 6.6 | 11 | 0.67 | 13.35 | 12.16 | 12.36 | 10.24
28 |  | 2 | 6.7 | 6.6 | 8 | 12.28 | 0.81 | 12.64 | 12.74 | 11.93
29 |  | 2 | 6.7 | 6.6 | 10 | 13.5 | 12.5 | 0.74 | 13.11 | 12.24
30 |  | 5 | 6.8 | 6.6 | 2 | 12.06 | 12.25 | 10 | 2.45 | 11.49
31
Total |  | 71.43 | 200.6 | 197 | 323 | 284.7 | 288.67 | 273.89 | 281.44 | 263.04
Mo. Avg. |  | 2.4631 | 6.6867 | 6.5667 | 10.7667 | 9.49 | 9.6223 | 9.1297 | 9.3813 | 8.768
PLANT STAFFING
Day Shift Operator |  |  | Class: | "A" | Certificate No. | 4545 | Name: |  | McGEARY, J.
Evening Shift Operator |  |  | Class: | "A" | Certificate No. | 4474 | Name: |  | BAYLER, J.
Night Shift Operator |  |  | Class: |  | Certificate No. |  | Name:
Lead Operator |  |  | Class: |  | Certificate No. |  | Name:
DAILY SAMPLE RESULTS - B
| Permit Number |  | FLA041378 |  |  | Facility: | City of Fort Lauderdale G. T. Lohmeyer WWTF
| Monitoring Period: |  | From: | 2005-06-01 |  | To: | 2005-06-30
|  | Flow (mgd) | CBOD5 (mg/L | TSS (mg/L
Code |  | 50050 | 80082 | 00530
Mon. Site |  | INF-001 | INF-002 | INF-002
1 |  | 42.712 | 79.5 | 200
2 |  | 46.568 | 61 | 90
3 |  | 47.958 | 74.36 | 38
4 |  | 45.725 | 52.28 | 70
5 |  | 48.199 | 22.47 | 68
6 |  | 48.32 | 38.53 | 78
7 |  | 44.575 | 44 | 84
8 |  | 42.458 | 53.8 | 78
9 |  | 41.712 | 71.8 | 42
10 |  | 42.112 | 86.4 | 60
11 |  | 51.15 | 48.8 | 118
12 |  | 49.335 | 72.28 | 80
13 |  | 45.518 | 81.6 | 108
14 |  | 42.822 | 83.6 | 84
15 |  | 40.675 | 92.7 | 100
16 |  | 40.132 | 89.9 | 108
17 |  | 42.276 | 85.8 | 94
18 |  | 45.26 | 87.3 | 76
19 |  | 45.708 | 83.1 | 74
20 |  | 45.815 | 44.4 | 114
21 |  | 47.854 | 69.5 | 98
22 |  | 45.069 | 44.6 | 88
23 |  | 46.868 | 41.2 | 70
24 |  | 57.594 | 67 | 118
25 |  | 52.491 | 34.4 | 16
26 |  | 48.201 | 34 | 68
27 |  | 48.385 | LS | 78
28 |  | 50.065 | 11 | 70
29 |  | 52.667 | 34 | 42
30 |  | 49.039 | 10 | 40
31
Total |  | 1397.263 | 1699.32 | 2452
Mo. Avg. |  | 46.5754 | 58.5972 | 81.7333

## JULIAN CONVERT
2005-06-01 | 38504 | 1999-01-01 | 2343
FROM DATE ON "DATA INPUT" PAGE | [5 empty] | 2005-06-01
2005
MONTHYY.PAR RANGE TO COMPILE (JULIAN DAY VALUES) FOR SPLIT PROGRAM ARE | [7 empty] | 152 | THROUGH | 2374
|  | 6 | JUNE
[5 empty] | 2005-06-01 | 2005-06-01 | 6
2005-06-01 |  |  |  |  | 1 | JANUARY |  | 1995 | 1995-01-01
[5 empty] | 2 | FEBRUARY |  | 1996 | 1996-01-01
[5 empty] | 3 | MARCH |  | 1997 | 1997-01-01
JUNE |  | 0 |  | 0 | 4 | APRIL |  | 1998 | 1998-01-01
|  | 1 |  | 2 | 5 | MAY |  | 1999 | 1999-01-01
|  | 0 |  |  | 6 | JUNE |  | 2000 | 2000-01-01
|  | 0 |  |  | 7 | JULY |  | 2001 | 2001-01-01
|  | 0 |  | 0 | 8 | AUGUST |  | 2002 | 2002-01-01
|  |  |  | 2 | 9 | SEPTEMBER |  | 2003 | 2003-01-01
[5 empty] | 10 | OCTOBER |  | 2004 | 2004-01-01
[5 empty] | 11 | NOVEMBER |  | 2005 | 2005-01-01
2005 |  |  |  |  | 12 | DECEMBER |  | 2006 | 2006-01-01
38504 | [6 empty] | JUNE | 2007 | 2007-01-01
38353 | [7 empty] | 2008 | 2008-01-01
151 | 1 |  | 1 | 152 | Wednesday
| 2 |  | 2 | 153 | Thursday
| 3 |  | 3 | 154 | Friday
| 4 |  | 4 | 155 | Saturday
| 5 |  | 5 | 156 | Sunday
| 6 |  | 6 | 157 | Monday
| 7 |  | 7 | 158 | Tuesday
| 8 |  | 8 | 159 | Wednesday
| 9 |  | 9 | 160 | Thursday
| 10 |  | 10 | 161 | Friday
| 11 |  | 11 | 162 | Saturday
| 12 |  | 12 | 163 | Sunday
| 13 |  | 13 | 164 | Monday
| 14 |  | 14 | 165 | Tuesday
| 15 |  | 15 | 166 | Wednesday
| 16 |  | 16 | 167 | Thursday
| 17 |  | 17 | 168 | Friday
| 18 |  | 18 | 169 | Saturday
| 19 |  | 19 | 170 | Sunday
| 20 |  | 20 | 171 | Monday
| 21 |  | 21 | 172 | Tuesday
| 22 |  | 22 | 173 | Wednesday
| 23 |  | 23 | 174 | Thursday
| 24 |  | 24 | 175 | Friday
| 25 |  | 25 | 176 | Saturday
| 26 |  | 26 | 177 | Sunday
| 27 |  | 27 | 178 | Monday
| 28 |  | 28 | 179 | Tuesday
| 29 |  | 29 | 180 | Wednesday
| 30 |  | 30 | 181 | Thursday
30