## DATA INPUT
ENTER THE AVERAGE MONTHLY INFLUENT FLOW
INTO THE CORROSPONDING BOXES BELOW:
FEBRUARY | 39.43 | JANUARY | 31.827
ENTER THE PRESENT MONTH AND YEAR IN BOX BELOW (A5) | [5 empty] | MARCH
2004-03-01 | [5 empty] | 2004
IW-1 | IW-2 | IW-3 | IW-4 | IW-5
35.5 | 36 | 36.1 | 35.6 | 34.5 | 2004-03-02
|  | ENTER INJECTION WELL SHUT-IN PRESSURE ABOVE |  |  | ENTER DATE OF SHUT-IN READINGS
ENTER SLUDGE DISPOSAL SITE FOR EACH WEEK BELOW
| WEEK 1 | WEEK 2 | WEEK 3 | WEEK 4
1 st | Nutri-Cylcle\CSLOL Inc. | Nutri-Cylcle\CSLOL Inc. | Nutri-Cylcle\CSLOL Inc. | Nutri-Cylcle\CSLOL Inc.
2 nd | Okeechobee, FL | Okeechobee, FL | Okeechobee, FL | Okeechobee, FL
RAW DATA REPORT ENTRY CATEGORIES
GTL PLANT DAILY PROCESS SUMMARY
[6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TOTAL RAW INFLUENT FLOW (MGD) | [5 empty] | 34.923 | 33.842 | 32.544 | 32.86 | 32.363 | 31.963 | 31.38 | 31.59 | 31.592 | 31.801 | 31.601 | 31.848 | 31.858 | 32.025 | 32.993 | 32.778 | 32.612 | 32.716 | 32.551 | 32.624 | 32.208 | 31.884 | 32.466 | 32.546 | 32.876 | 33.314 | 32.973 | 31.898 | 32.025 | 32.02 | 31.508
TOTAL EFFLUENT FLOW (MGD) | [5 empty] | 33.838 | 32.431 | 31.379 | 31.864 | 31.647 | 30.711 | 29.895 | 30.65 | 30.542 | 30.659 | 30.611 | 31.085 | 30.61 | 30.546 | 32.012 | 32.342 | 32.394 | 32.194 | 32.845 | 31.957 | 31.516 | 31.592 | 31.379 | 31.405 | 31.835 | 32.356 | 31.698 | 30.252 | 30.923 | 30.911 | 30.499
MAXIMUM HOURLY RAW INFLUENT FLOW (MGD) | [5 empty] | 1.719 | 1.694 | 1.651 | 1.671 | 1.667 | 1.688 | 1.613 | 1.588 | 1.575 | 1.577 | 1.538 | 1.556 | 1.61 | 1.616 | 1.692 | 1.677 | 1.679 | 1.666 | 1.71 | 1.768 | 1.698 | 1.649 | 1.707 | 1.589 | 1.612 | 1.645 | 1.735 | 1.579 | 1.573 | 1.579 | 1.556
MAXIMUM INSTANANEOUS PEAK RAW INFUENT FLOW (MGD) | [5 empty] | 51.232 | 52.866 | 51.008 | 49.311 | 52.61 | 51.585 | 49.311 | 50.175 | 47.42 | 47.388 | 47.228 | 46.523 | 50.463 | 47.485 | 49.407 | 49.952 | 48.83 | 50.816 | 49.311 | 50.079 | 49.599 | 50.079 | 50.239 | 48.894 | 49.728 | 48.927 | 48.702 | 49.087 | 47.549 | 48.446 | 46.299
MINIMUM INSTANANEOUS PEAK RAW INFUENT FLOW (MGD) | [5 empty] | 15.604 | 12.784 | 5.222 | 12.592 | 11.374 | 12.528 | 11.534 | 11.887 | 11.695 | 6.888 | 12.752 | 12.592 | 14.226 | 12.976 | 14.386 | 14.578 | 12.367 | 13.809 | 12.207 | 14.45 | 13.809 | 8.49 | 12.432 | 13.361 | 15.027 | 14.162 | 14.771 | 14.707 | 13.008 | 13.809 | 13.04
TOTAL RETURN ACTIVATED SLUDGE FLOW (MGD) | [5 empty] | 11.02 | 10.957 | 10.993 | 11.275 | 11.391 | 10.804 | 11.14 | 9.522 | 9.118 | 8.175 | 8.528 | 10.86 | 10.314 | 10.032 | 11.811 | 13.609 | 11.757 | 11.909 | 11.987 | 10.954 | 10.941 | 10.956 | 9.9 | 10.35 | 10.758 | 10.441 | 10.34 | 11.27 | 10.411 | 10.061 | 12.175
TOTAL WASTE FLOW TO DEWATERING PROCESS (MG) | [5 empty] | 0.666 | 0.631 | 0.685 | 0.666 | 0.362 | 0 | 0.222 | 0.611 | 0.68 | 0.736 | 0.724 | 0.178 | 0 | 0.217 | 0.683 | 0.629 | 0.714 | 0.666 | 0.323 | 0 | 0.207 | 0.801 | 0.807 | 0.769 | 0.817 | 0.352 | 0 | 0.213 | 0.496 | 0.71 | 0.755
TOTAL DAILY RAINFALL | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.69 | 0.06 | 0 | 0.01 | 0 | 0
RAW INFLUENT pH | [5 empty] | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7.1 | 7 | 7.1 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7.2 | 7 | 7 | 7
RAW INFLUENT HYDROGEN SULFIDE (PPM) | [5 empty] | 6 | 6 | 6 | 6 | 5 | 6 | 6 | 6 | 7 | 6 | 6 | 6 | 7 | 7 | 6 | 6 | 6 | 6 | 7 | 6 | 7 | 7 | 6 | 7 | 7 | 6 | 5 | 7 | 6 | 6 | 5
RAW INFLUENT TEMPERATURE (F ) | [5 empty] | 77 | 77 | 77 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 79 | 79 | 78 | 78 | 78 | 79 | 79 | 78 | 78 | 77 | 78 | 79 | 79 | 77 | 77 | 78
TOTAL DAILY KILOWATTS (FPL POWER CONSUMPTION) | [5 empty] | 28512 | 29234 | 28431 | 21195 | 29895 | 29984 | 29682 | 29630 | 29081 | 29097 | 28981 | 28973 | 28937 | 29080 | 29037 | 27578 | 27645 | 27836 | 28425 | 28411 | 28547 | 28535 | 28723 | 28760 | 28671 | 28600 | 28558 | 28262 | 28391 | 29184 | 31170
GTL PLANT DAILY PROCESS SUMMARY
(CONTINUED)
[6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
FINAL EFFLUENT FREE CHLORINE RESIDUAL (PPM) | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FINAL EFFLUENT TOTAL CHLORINE RESIDUAL (PPM) | [5 empty] | 0.7 | 0.7 | 0.5 | 0.6 | 0.7 | 0.6 | 0.8 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0 | 0.6 | 0.5 | 0.5 | 0.7 | 0.4 | 0.4 | 0.6 | 0.6 | 0.4 | 0.9 | 0.4 | 0.5 | 0.5 | 0 | 0.6 | 0.3 | 0.4 | 0.5
FINAL EFFLUENT pH (daily average) | [5 empty] | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.4 | 6.5 | 6.4 | 6.4 | 6.5 | 6.5 | 6.5 | 6.4 | 6.5 | 6.4 | 6.5 | 6.5 | 6.6 | 6.5 | 6.4 | 6.5 | 6.4 | 6.4 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.4 | 6.5 | 6.5
FINAL EFFLUENT pH (daily minimum) | [5 empty] | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.3 | 6.2 | 6.2 | 6.3 | 6.4 | 6.2 | 6.4 | 6.1 | 6.3 | 6.4 | 6.5 | 6.4 | 6.3 | 6.4 | 6.1 | 6.3 | 6.3 | 6.4 | 6.4 | 6.4 | 6.5 | 6.5 | 6.4 | 6.4
FINAL EFFLUENT pH (daily maximum) | [5 empty] | 6.6 | 6.5 | 6.5 | 6.5 | 6.6 | 6.5 | 6.5 | 6.5 | 6.5 | 6.6 | 6.6 | 6.5 | 6.4 | 6.5 | 6.5 | 6.6 | 6.5 | 6.6 | 6.5 | 6.5 | 6.9 | 6.5 | 6.6 | 6.6 | 6.5 | 6.6 | 6.5 | 6.5 | 6.4 | 6.6 | 6.6
FINAL EFFLUENT TEMPARTURE (F ) | [5 empty] | 79 | 79 | 80 | 80 | 80 | 81 | 81 | 81 | 80 | 80 | 80 | 80 | 80 | 80 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 80 | 80 | 80 | 81 | 81 | 81 | 81 | 81 | 81
AVERAGE CLARIFIER BLANKET DEPTH (INCHES) | [5 empty] | 52 | 56 | 53 | 40 | 38 | 48 | 45 | 39 | 41 | 28 | 26 | 30 | 40 | 48 | 42 | 41 | 31 | 27 | 27 | 29 | 45 | 29 | 31 | 23 | 17 | 19 | 21 | 32 | 24 | 22 | 23
FINAL EFFLUENT SAMPLE TEMPARTURE (C ) | [5 empty] | 2 | 2 | 2 | 3 | 10 | 8 | 5 | 5 | 2 | 2 | 2 | 5 | 0 | 0 | 4 | 0 | 4 | 4 | 5 | 5 | 5 | 4 | 2 | 1 | 0 | 5 | 5 | 5 | 2 | 0 | 1
TOTAL RETURN ACTIVATED SLUDGE FLOW TO REACTOR ONE (MGD) | [5 empty] | 4.952 | 4.951 | 5.498 | 5.381 | 5.733 | 5.361 | 5.654 | 4.897 | 3.567 | 2.835 | 2.615 | 4.28 | 4.893 | 5.119 | 5.728 | 7.5 | 6.342 | 5.926 | 5.608 | 5.023 | 5.465 | 4.741 | 4.118 | 4.324 | 4.315 | 4.425 | 4.552 | 5.1 | 4.862 | 4.594 | 5.707
TOTAL RETURN ACTIVATED SLUDGE FLOW TO REACTOR TWO (MGD) | [5 empty] | 6.068 | 6.005 | 5.495 | 5.894 | 5.659 | 5.444 | 5.486 | 4.624 | 5.551 | 5.34 | 5.913 | 6.58 | 5.421 | 4.914 | 6.082 | 6.109 | 5.416 | 5.982 | 6.379 | 5.931 | 5.475 | 6.215 | 5.782 | 6.026 | 6.443 | 6.017 | 5.788 | 6.17 | 5.549 | 5.467 | 6.468
GTL PLANT DAILY PROCESS SUMMARY
CONTINUED
[6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TOTAL DAILY TRUCKING LOAD OF DEWATERED SLUDGE REMOVED | [5 empty] | 7 | 7 | 7 | 7 | 6 | 0 | 1 | 6 | 7 | 6 | 7 | 5 | 0 | 0 | 6 | 7 | 6 | 6 | 6 | 1 | 0 | 6 | 7 | 6 | 7 | 4 | 1 | 0 | 3 | 5 | 5
TOTAL DAILY HYDROGEN PEROXIDE CONSUMED (LBS) | [5 empty] | 1537 | 1357 | 1397 | 1337 | 1058 | 1836 | 1916 | 1976 | 1836 | 2016 | 1576 | 1737 | 1656 | 1829 | 1556 | 1956 | 1777 | 1897 | 1687 | 1717 | 1827 | 1846 | 1486 | 1637 | 1796 | 1287 | 1786 | 1487 | 1576 | 1268 | 1378
TOTAL DAILY CHLORINE CONSUMED (LBS) | [5 empty] | 1080 | 1120 | 1440 | 1180 | 1240 | 1260 | 1200 | 1240 | 1460 | 1200 | 1200 | 1160 | 1400 | 1260 | 1040 | 1300 | 1280 | 1040 | 1160 | 1160 | 1080 | 1180 | 1320 | 1240 | 1160 | 1220 | 1280 | 1280 | 1080 | 1200 | 1200
TOTAL DAILY POLYMER CONSUMED (GALS) | [5 empty] | 93 | 107 | 120 | 57 | 26 | 38 | 77 | 45 | 72 | 96 | 64 | 13 | 25 | 40 | 83 | 99 | 59 | 68 | 43 | 9 | 14 | 126 | 71 | 87 | 49 | 0 | 29 | 37 | 40 | 69 | 81
TOTAL TONS OF LIME DELIVERED DAILY | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTAL DAILY GASIOUS OXYGEN PRODUCED (TONS) | [5 empty] | 27.9 | 23.9 | 30.3 | 30.3 | 28.3 | 27.5 | 35.6 | 27.2 | 32 | 20.6 | 24.5 | 28.8 | 33.6 | 28.8 | 38 | 28.5 | 22.7 | 19.6 | 21.7 | 23.5 | 22.6 | 23 | 19.8 | 17.4 | 18 | 18.5 | 20.5 | 28.7 | 25.1 | 18.4 | 18.5
AVERAGE PERCENT OXYGEN PRODUCT PURITY | [5 empty] | 100 | 99 | 99 | 99 | 99 | 98 | 97 | 98 | 98 | 99 | 99 | 96 | 99 | 97 | 98 | 93 | 100 | 99 | 99 | 100 | 100 | 100 | 100 | 100 | 100 | 99 | 100 | 100 | 100 | 100 | 100
TOTAL DAILY LIQUID OXYGEN IN STORAGE (TONS) | [5 empty] | 193 | 194 | 192 | 184 | 184 | 184 | 184 | 185 | 184 | 184 | 184 | 184 | 183 | 184 | 185 | 185 | 184 | 183 | 183.9 | 184 | 184 | 198 | 192 | 192 | 196 | 193 | 196 | 194 | 195 | 198 | 200
MONITORING WELL PRESSURE DATA
MONITORING WELL ONE UPPER/LOWER LEVEL
| MW-1 |  | UPPER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MINIMUM | [5 empty] | 47.24 | 47.46 | 48.05 | 48.11 | 48.1 | 48.14 | 48.14 | 46.54 | 46.87 | 48.31 | 48.2 | 48.25 | 48.2 | 48.21 | 46.4 | 46.89 | 48.29 | 48.23 | 48.19 | 48.19 | 48.28 | 47.03 | 47.21 | 48.12 | 48.14 | 48.18 | 48.21 | 48.22 | 46.8 | 47.23 | 48.25
MAXIMUM | [5 empty] | 48.53 | 48.28 | 48.33 | 48.38 | 48.41 | 48.43 | 48.48 | 48.46 | 48.74 | 48.68 | 48.51 | 48.51 | 48.53 | 48.49 | 48.53 | 48.77 | 48.67 | 48.53 | 48.5 | 48.52 | 48.64 | 48.55 | 48.55 | 48.38 | 48.38 | 48.38 | 48.37 | 48.4 | 48.43 | 48.41 | 48.52
AVERAGE | [5 empty] | 47.87 | 47.92 | 48.19 | 48.25 | 48.28 | 48.29 | 48.26 | 47.35 | 48.01 | 48.5 | 48.36 | 48.43 | 48.35 | 48.36 | 47.41 | 48.07 | 48.52 | 48.42 | 48.35 | 48.35 | 48.45 | 47.61 | 47.97 | 48.23 | 48.25 | 48.27 | 48.31 | 48.34 | 47.45 | 47.94 | 48.41
| MW-1 |  | LOWER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MINIMUM | [5 empty] | 38.03 | 38.04 | 41.27 | 41.38 | 41.4 | 41.45 | 41.46 | 37.58 | 37.54 | 41.45 | 41.42 | 41.49 | 41.5 | 41.51 | 37.25 | 37.27 | 41.5 | 41.49 | 41.48 | 41.49 | 41.56 | 37.31 | 37.29 | 41.35 | 41.28 | 41.37 | 41.43 | 41.58 | 37.41 | 37.39 | 41.41
MAXIMUM | [5 empty] | 41.7 | 41.41 | 41.55 | 41.6 | 41.61 | 41.61 | 41.78 | 41.74 | 41.61 | 41.7 | 41.64 | 41.67 | 41.7 | 41.74 | 41.72 | 41.78 | 41.95 | 41.72 | 41.68 | 41.68 | 41.84 | 41.76 | 41.46 | 41.53 | 41.59 | 41.7 | 41.72 | 41.85 | 41.75 | 41.79 | 42.01
AVERAGE | [5 empty] | 39.65 | 40.03 | 41.46 | 41.49 | 41.49 | 41.49 | 41.53 | 39.24 | 40.18 | 41.56 | 41.5 | 41.53 | 41.57 | 41.56 | 38.98 | 40.19 | 41.66 | 41.56 | 41.54 | 41.53 | 41.69 | 39.05 | 40.08 | 41.46 | 41.48 | 41.51 | 41.55 | 41.65 | 39.07 | 39.98 | 41.67
MONITORING WELL TWO UPPER/LOWER LEVEL
| MW-2 |  | UPPER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MINIMUM | [5 empty] | 26.97 | 26.97 | 30.22 | 30.46 | 30.58 | 30.72 | 30.64 | 27.47 | 26.89 | 29.67 | 29.46 | 30.22 | 30.5 | 30.48 | 26.9 | 26.92 | 30.26 | 30.26 | 30.25 | 30.24 | 30.48 | 27.33 | 27.2 | 30.06 | 29.91 | 30.09 | 30.25 | 30.46 | 27.41 | 26.97 | 29.77
MAXIMUM | [5 empty] | 30.77 | 30.94 | 31.34 | 31.62 | 31.8 | 31.82 | 32.09 | 30.98 | 31.22 | 31.28 | 31.18 | 31.43 | 31.46 | 31.41 | 31.04 | 31.37 | 31.78 | 31.21 | 31.16 | 31.14 | 31.55 | 30.7 | 30.69 | 30.76 | 30.94 | 31.26 | 31.38 | 31.56 | 30.78 | 30.88 | 31.75
AVERAGE | [5 empty] | 29.03 | 29.17 | 30.68 | 30.9 | 31.1 | 31.16 | 31.19 | 29.47 | 29.51 | 30.32 | 30.36 | 30.68 | 30.82 | 30.86 | 28.78 | 29.57 | 30.69 | 30.66 | 30.68 | 30.71 | 30.99 | 29.28 | 29.39 | 30.39 | 30.41 | 30.62 | 30.74 | 30.89 | 29.09 | 29.19 | 30.65
| MW-2 |  | LOWER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MINIMUM | [5 empty] | 38.48 | 36.85 | 41.97 | 42.14 | 42.2 | 42.28 | 42.31 | 38.72 | 38.62 | 42.25 | 42.24 | 42.33 | 42.36 | 42.39 | 37.58 | 37.59 | 42.22 | 42.28 | 42.28 | 42.32 | 42.42 | 37.6 | 36.92 | 42.13 | 42.23 | 42.32 | 42.37 | 42.44 | 40.28 | 40.25 | 42.27
MAXIMUM | [5 empty] | 42.54 | 42.04 | 42.22 | 42.33 | 42.4 | 42.45 | 42.51 | 42.5 | 42.32 | 42.35 | 42.4 | 42.45 | 42.5 | 42.53 | 42.61 | 42.34 | 42.46 | 42.42 | 42.45 | 42.51 | 42.64 | 42.62 | 42.15 | 42.27 | 42.35 | 42.4 | 42.45 | 42.52 | 42.57 | 42.29 | 42.56
AVERAGE | [5 empty] | 40.26 | 40.53 | 42.03 | 42.3 | 42.36 | 42.41 | 42.45 | 40.29 | 40.99 | 42.35 | 42.37 | 42.43 | 42.49 | 42.5 | 39.4 | 40.73 | 42.39 | 42.4 | 42.41 | 42.43 | 42.49 | 39.28 | 40.54 | 42.15 | 42.3 | 42.4 | 42.46 | 42.5 | 41.22 | 41.47 | 42.44
MONITORING WELL THREE UPPER/LOWER LEVEL
| MW-3 |  | UPPER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MINIMUM | [5 empty] | 23.25 | 23.19 | 31.27 | 31.51 | 31.59 | 31.67 | 31.71 | 24.79 | 24.55 | 31.8 | 31.75 | 31.84 | 31.86 | 31.9 | 19.56 | 19.56 | 31.27 | 31.36 | 31.35 | 31.41 | 31.52 | 20.6 | 20.44 | 31.15 | 31.3 | 31.36 | 31.42 | 31.47 | 19.2 | 19.15 | 31.07
MAXIMUM | [5 empty] | 31.68 | 31.37 | 31.65 | 31.79 | 31.88 | 31.93 | 32 | 31.95 | 31.95 | 31.98 | 31.99 | 32.05 | 32.09 | 32.11 | 32.15 | 31.42 | 31.61 | 31.58 | 31.62 | 31.69 | 31.83 | 31.79 | 31.26 | 31.42 | 31.49 | 31.52 | 31.57 | 31.62 | 31.65 | 31.07 | 31.48
AVERAGE | [5 empty] | 26.93 | 27.94 | 31.49 | 31.7 | 31.78 | 31.81 | 31.82 | 27.59 | 29.34 | 31.92 | 31.9 | 31.98 | 32 | 32 | 23.94 | 27.52 | 31.47 | 31.48 | 31.48 | 31.49 | 31.72 | 24.41 | 27.58 | 31.27 | 31.4 | 31.47 | 31.49 | 31.52 | 23.68 | 26.4 | 31.34
| MW-3 |  | LOWER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MINIMUM | [5 empty] | 40.57 | 40.57 | 45.03 | 45.22 | 45.29 | 45.39 | 45.43 | 40.93 | 40.88 | 45.33 | 45.33 | 45.43 | 45.46 | 45.51 | 38.51 | 38.53 | 45.28 | 45.35 | 45.36 | 45.41 | 45.52 | 39.41 | 39.36 | 45.17 | 45.3 | 45.4 | 45.46 | 45.53 | 41.36 | 41.39 | 45.2
MAXIMUM | [5 empty] | 45.67 | 45.11 | 45.3 | 45.43 | 45.49 | 45.55 | 45.6 | 45.6 | 45.38 | 45.41 | 45.46 | 45.54 | 45.6 | 45.65 | 45.7 | 45.39 | 45.53 | 45.5 | 45.52 | 45.59 | 45.72 | 45.71 | 45.17 | 45.31 | 45.41 | 45.48 | 45.55 | 45.65 | 45.68 | 45.22 | 45.53
AVERAGE | [5 empty] | 42.79 | 43.17 | 45.22 | 45.38 | 45.46 | 45.48 | 45.49 | 42.78 | 43.81 | 45.44 | 45.42 | 45.5 | 45.52 | 45.53 | 41.02 | 43.19 | 45.45 | 45.46 | 45.48 | 45.49 | 45.57 | 41.61 | 43.16 | 45.19 | 45.39 | 45.48 | 45.5 | 45.52 | 43 | 43.64 | 45.39
MONITORING WELL RMW-1 UPPER/LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
[5 empty] | JULIAN DATE | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91
| RMW-1 |  | UPPER LEVEL
MINIMUM | [5 empty] | 42.59 | 42.48 | 44.09 | 44.22 | 44.28 | 44.3 | 44.33 | 44.4 | 44.46 | 44.43 | 44.41 | 44.44 | 44.44 | 44.46 | 44.5 | 44.58 | 44.58 | 44.48 | 44.45 | 44.44 | 44.52 | 44.57 | 44.46 | 44.43 | 44.45 | 44.5 | 44.51 | 44.55 | 44.57 | 44.57 | 44.63
MAXIMUM | [5 empty] | 44.52 | 44.11 | 44.25 | 44.36 | 44.39 | 44.44 | 44.47 | 44.53 | 44.62 | 44.6 | 44.48 | 44.5 | 44.54 | 44.52 | 44.6 | 44.75 | 44.75 | 44.63 | 44.57 | 44.57 | 44.69 | 44.7 | 44.62 | 44.53 | 44.53 | 44.58 | 44.59 | 44.61 | 44.65 | 44.67 | 44.75
AVERAGE | [5 empty] | 43.48 | 43.44 | 44.19 | 44.3 | 44.34 | 44.37 | 44.41 | 44.47 | 44.53 | 44.52 | 44.44 | 44.47 | 44.48 | 44.48 | 44.55 | 44.67 | 44.67 | 44.56 | 44.51 | 44.51 | 44.61 | 44.64 | 44.54 | 44.49 | 44.5 | 44.54 | 44.56 | 44.58 | 44.6 | 44.61 | 44.68
| RMW-1 |  | LOWER LEVEL
MINIMUM | [5 empty] | 21.05 | 21 | 21.74 | 21.92 | 21.99 | 22.06 | 22.07 | 22.16 | 22.25 | 22.19 | 22.15 | 22.16 | 22.14 | 22.16 | 22.19 | 22.27 | 22.3 | 22.21 | 22.18 | 22.17 | 22.26 | 22.32 | 22.2 | 22.14 | 22.14 | 22.17 | 22.17 | 22.17 | 22.21 | 22.24 | 22.29
MAXIMUM | [5 empty] | 23.12 | 21.78 | 21.96 | 22.07 | 22.12 | 22.16 | 22.22 | 22.29 | 22.38 | 22.4 | 22.25 | 22.27 | 22.3 | 22.26 | 22.32 | 22.49 | 22.46 | 22.32 | 22.25 | 22.29 | 22.4 | 22.42 | 22.37 | 22.25 | 22.25 | 22.27 | 22.3 | 22.3 | 22.32 | 22.35 | 22.44
AVERAGE | [5 empty] | 22.29 | 21.48 | 21.88 | 22.01 | 22.06 | 22.11 | 22.14 | 22.22 | 22.31 | 22.3 | 22.19 | 22.21 | 22.21 | 22.21 | 22.28 | 22.4 | 22.39 | 22.27 | 22.22 | 22.22 | 22.33 | 22.36 | 22.26 | 22.18 | 22.19 | 22.21 | 22.22 | 22.24 | 22.26 | 22.29 | 22.36
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
| INJECTION WELL ONE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 12.03 | 12.28 | 13.28 | 12.22 | 11.7 | 13.37 | 11.6 | 11.09 | 10.91 | 10.19 | 10.15 | 10.17 | 13.37 | 13.8 | 11.88 | 10.88 | 10.85 | 10.45 | 18.13 | 11.47 | 12.11 | 9.69 | 15.06 | 10.19 | 13.2 | 12.75 | 12.88 | 10.14 | 10.16 | 10.95 | 10.16
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 0 | 5.26 | 4.71 | 3.96 | 3.97 | 5.31 | 5.44 | 4.73 | 3.79 | 3.73 | 4.09 | 3.7 | 5.36 | 5.69 | 4.31 | 4.12 | 0 | 4.48 | 0 | 4.83 | 0 | 0 | 4.49 | 5.22 | 5.26 | 4.53 | 0 | 4.31 | 0 | 4.53 | 5.44
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 7.55 | 9.05 | 8.54 | 8.33 | 8.29 | 8.82 | 8.53 | 8.05 | 8.03 | 8.08 | 8.06 | 8.17 | 8.66 | 9.11 | 7.99 | 7.75 | 6.92 | 8.02 | 7.11 | 8.07 | 6.48 | 6.74 | 9.27 | 8.56 | 8.69 | 8.5 | 6.85 | 7.97 | 7.02 | 8.13 | 8.42
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 56.87 | 58.84 | 61.62 | 57.45 | 56.56 | 61.64 | 56.3 | 55.64 | 53.73 | 50.93 | 50.78 | 50.81 | 62.81 | 62.42 | 56.88 | 53.4 | 53.91 | 53.96 | 80.5 | 56.27 | 57.93 | 49.6 | 69.19 | 50.72 | 61.84 | 59.89 | 60.41 | 51.15 | 51.13 | 54.08 | 50.96
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 34.59 | 40.13 | 39 | 37.72 | 37.68 | 39.93 | 39.78 | 38.86 | 37.41 | 37.14 | 37.81 | 37.11 | 40.38 | 40.56 | 38.62 | 38.35 | 34.56 | 38.37 | 34.21 | 38.94 | 34.29 | 34.23 | 38.12 | 39.54 | 39.79 | 38.65 | 34.36 | 38.31 | 34.44 | 38.51 | 40.18
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 46.99 | 48.3 | 47.2 | 47.05 | 46.94 | 48.26 | 47.4 | 46.41 | 46.23 | 46.03 | 45.88 | 46.18 | 47.63 | 48.57 | 46.01 | 45.39 | 44.68 | 45.92 | 45.54 | 45.98 | 43.9 | 44.15 | 49.35 | 46.88 | 47.44 | 47.13 | 45.14 | 45.96 | 45.14 | 46.48 | 46.76
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
| INJECTION WELL TWO |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 12.23 | 12.52 | 13.58 | 12.39 | 11.94 | 13.55 | 11.72 | 11.23 | 11.03 | 10.28 | 10.34 | 10.31 | 13.59 | 14.1 | 12.19 | 11.01 | 11.01 | 10.66 | 15.92 | 11.67 | 12.4 | 9.73 | 10.16 | 10.32 | 13.51 | 12.96 | 13.09 | 10.26 | 10.27 | 11.04 | 10.22
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 5.5 | 0.02 | 4.53 | 3.49 | 3.61 | 5.31 | 0.02 | 4.41 | 3.12 | 3.06 | 3.62 | 3.02 | 5.14 | 5.57 | 4.02 | 3 | 4.75 | 4.08 | 0.02 | 4.55 | 4.74 | 4.83 | 0.03 | 5.1 | 5.21 | 4.26 | 5.62 | 3.91 | 4.7 | 4.23 | 0.02
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 9.48 | 7.51 | 8.67 | 8.4 | 8.34 | 8.92 | 6.03 | 8.1 | 8.07 | 8.08 | 8.08 | 8.21 | 8.74 | 9.28 | 8.06 | 7.78 | 8.15 | 8.08 | 8.12 | 8.13 | 7.97 | 7.91 | 3.49 | 8.7 | 8.81 | 8.59 | 8.96 | 7.98 | 8.62 | 8.17 | 6.92
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 55.9 | 57.68 | 60.41 | 56.35 | 55.46 | 60.56 | 55.27 | 54.68 | 52.71 | 49.96 | 49.88 | 49.91 | 61.67 | 35.86 | 56.05 | 52.54 | 53.08 | 53.01 | 68.87 | 55.31 | 56.89 | 48.75 | 49.42 | 49.72 | 60.6 | 58.72 | 59.27 | 50.12 | 50.14 | 53 | 49.94
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 39.43 | 34.89 | 38.24 | 36.98 | 36.96 | 39.15 | 34.96 | 38.09 | 36.66 | 36.38 | 37.04 | 36.36 | 39.58 | 39.77 | 37.9 | 37.08 | 38.77 | 37.72 | 36.07 | 38.2 | 38.4 | 38.54 | 34.62 | 38.74 | 39 | 37.85 | 39.81 | 37.55 | 38.7 | 37.74 | 34.85
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 48.45 | 45.38 | 46.28 | 46.13 | 46.06 | 47.34 | 43.53 | 45.5 | 45.33 | 45.11 | 44.99 | 45.32 | 46.74 | 47.74 | 45.29 | 44.72 | 45.37 | 45.17 | 45.64 | 45.14 | 44.71 | 44.57 | 39.82 | 45.95 | 46.49 | 46.18 | 46.96 | 45.06 | 46.11 | 45.55 | 44.13
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
| INJECTION WELL THREE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 10.82 | 11.11 | 11.95 | 10.91 | 10.52 | 11.98 | 10.36 | 9.91 | 9.72 | 9.04 | 9.07 | 9.09 | 12.1 | 10.7 | 10.64 | 9.42 | 9.5 | 9.1 | 16.66 | 10.08 | 10.77 | 8.51 | 13.12 | 9.1 | 11.11 | 11.39 | 11.47 | 9.01 | 9.02 | 9.73 | 9.02
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 4.84 | 2.38 | ER | 3.18 | 3.28 | 4.69 | 4.63 | 3.91 | 2.91 | 2.94 | 3.23 | 2.8 | 4.48 | ER | 3.58 | 3.48 | 4.07 | 3.47 | ER | 3.94 | 4 | 4.22 | 3.56 | ER | ER | 3.8 | 4.93 | 3.53 | 4.16 | 3.75 | 4.7
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 8.33 | 8.03 | 6.34 | 7.4 | 7.36 | 7.89 | 7.58 | 7.14 | 7.11 | 7.15 | 7.11 | 7.21 | 7.73 | 6.71 | 7.01 | 6.69 | 6.98 | 6.96 | 7.04 | 7.1 | 6.91 | 6.84 | 8.1 | 6.29 | 7.53 | 7.56 | 7.84 | 7.04 | 7.52 | 7.18 | 7.47
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 57.14 | 59.13 | 61.94 | 57.74 | 56.84 | 61.99 | 56.6 | 55.94 | 53.99 | 51.16 | 51.11 | 51.18 | 63.25 | 57.1 | 57.34 | 53.72 | 54.31 | 54.25 | 83.1 | 56.59 | 58.22 | 49.85 | 69.3 | 50.97 | 58.41 | 60.2 | 60.71 | 51.39 | 51.32 | 54.34 | 51.16
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 40.38 | 39.74 | 35.13 | 37.83 | 37.81 | 40.08 | 39.91 | 38.96 | 37.5 | 37.24 | 37.91 | 37.22 | 40.51 | 35.19 | 38.75 | 38.74 | 39.64 | 38.57 | 36.12 | 39.06 | 39.24 | 39.43 | 38.21 | 34.94 | 35.96 | 38.74 | 40.75 | 38.41 | 39.57 | 38.6 | 40.27
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 49.62 | 48.44 | 45.6 | 47.23 | 47.16 | 48.46 | 47.58 | 46.58 | 46.43 | 46.21 | 46.09 | 46.41 | 47.88 | 46.05 | 46.32 | 45.72 | 46.39 | 46.22 | 46.9 | 46.19 | 45.72 | 45.58 | 49.47 | 45.29 | 47.13 | 47.3 | 48.08 | 46.12 | 47.2 | 46.65 | 46.94
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
FUTURE
| INJECTION WELL FOUR |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 0.14 | 0.14 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.14 | 0.15 | 0.15 | 0.14 | 13.17 | 13.69 | 13.73 | 13.23 | 14.31 | 14.44 | 15.35 | 12.23 | 18.47 | 0.14 | 0.14 | 0.14 | 0.14 | 0.15 | 0.13 | 0.15 | 0.14
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.11 | 0.11 | 0.12 | 0.12 | 0.12 | 0.12 | 5.85 | 6.69 | 0.12 | 0.13 | 0.12 | 6.4 | 6.67 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.12 | 0.12 | 0.13 | 0.13 | 0.13 | 5.79 | 10.07 | 10.39 | 9.17 | 9.4 | 8.73 | 10.19 | 10.11 | 7.77 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 36.98 | 37.1 | 37.4 | 37.17 | 37.11 | 37.11 | 37.25 | 37.29 | 37.12 | 36.83 | 36.69 | 36.71 | 37 | 50.93 | 53.05 | 53.61 | 54.17 | 54.23 | 55.59 | 56.53 | 57.95 | 50.1 | 68.42 | 36.75 | 37.02 | 37.45 | 37.65 | 36.89 | 36.84 | 37.03 | 36.9
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 35.48 | 35.37 | 35 | 35.17 | 35.21 | 34.98 | 35.41 | 35.37 | 35.15 | 35.08 | 35.01 | 34.9 | 34.97 | 34.52 | 35.31 | 39.33 | 40.16 | 35.42 | 35.9 | 35.31 | 39.79 | 40.02 | 36 | 35.01 | 34.8 | 35.15 | 35.46 | 35.31 | 35.57 | 35.4 | 35.55
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 36.31 | 36.15 | 36.05 | 36.21 | 36.23 | 36.05 | 36.3 | 36.33 | 36.3 | 36.17 | 36.04 | 36.1 | 35.97 | 35.87 | 41.96 | 45.96 | 46.67 | 45.4 | 45.51 | 44.91 | 45.98 | 45.95 | 45.52 | 36.14 | 36.07 | 36.2 | 36.35 | 36.23 | 36.33 | 36.3 | 36.32
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
| INJECTION WELL FIVE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 10.67 | 10.9 | 11.78 | 10.83 | 10.48 | 10.4 | 10.31 | 9.85 | 9.66 | 9.04 | 9.04 | 9.05 | 10.02 | 10.63 | 10.65 | ER | ER | ER | 16.13 | ER | ER | ER | 8.92 | 9.07 | 11.11 | 11.38 | 11.44 | 9.08 | 9.09 | 9.73 | 9.04
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 5.13 | ER | 4.38 | 3.64 | 0.98 | ER | 4.87 | 4.26 | 3.28 | 3.3 | 3.66 | 3.19 | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | 4.74 | ER | 4.16 | 5.17 | 3.9 | 4.53 | 4.1 | 4.91
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 8.35 | 7.8 | 7.75 | 7.58 | 7.53 | 5.02 | 7.66 | 7.26 | 7.24 | 7.27 | 7.25 | 7.35 | 5.42 | 5.35 | 3.23 | ER | ER | ER | 0.76 | ER | ER | ER | 2.78 | 7.75 | 6.7 | 7.69 | 7.94 | 7.22 | 7.65 | 7.35 | 7.59
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 56.7 | 58.67 | 61.46 | 57.3 | 56.4 | 56.02 | 56.08 | 55.39 | 53.43 | 50.77 | 50.72 | 50.71 | 54.41 | 56.67 | 56.85 | 36.15 | 36.14 | 35.86 | 82.3 | 36.31 | 36.37 | 35.67 | 50.3 | 50.62 | 58.66 | 59.74 | 60.25 | 50.89 | 50.92 | 53.91 | 50.8
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 40.16 | 34.55 | 38.87 | 37.6 | 36.08 | 33.54 | 39.66 | 38.77 | 37.4 | 37.19 | 37.82 | 37.06 | 33.65 | 33.36 | 34.96 | 34.39 | 34.45 | 33.06 | 34.05 | 33.29 | 34.33 | 34.25 | 34.05 | 39.46 | 33.51 | 38.58 | 40.52 | 38.24 | 39.4 | 38.5 | 40.12
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 49.23 | 47.52 | 47.01 | 46.87 | 46.78 | 42.9 | 47.2 | 46.21 | 46.13 | 45.92 | 45.77 | 46.11 | 43.26 | 43.17 | 40.15 | 35.3 | 35.25 | 34.87 | 37.38 | 35.02 | 35.16 | 35.09 | 39.48 | 46.73 | 45.51 | 46.99 | 47.74 | 45.79 | 46.91 | 46.32 | 46.59
GTL DAILY LABORATORY ANALYSIS REPORT DATA
| RAW INFLUENT DATA |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
RAW TOTAL SUSPENDED SOLIDS | [5 empty] | 90 | 100 | 136 | 136 | 212 | 156 | 298 | 80 | 134 | 168 | 76 | 116 | 122 | 110 | 116 | 160 | 114 | 120 | 120 | 128 | 186 | 114 | 134 | 136 | 140 | 120 | 2588 | 120 | 106 | 100 | 94
RAW FIXED SUSPENDED SOLIDS | [5 empty] | 14 | 18 | 20 | 22 | 34 | 20 | 66 | 12 | 24 | 32 | 30 | 16 | 22 | 20 | 20 | 28 | 22 | 22 | 20 | 22 | 38 | 20 | 14 | 26 | 28 | 22 | 976 | 22 | 16 | 16 | 14
RAW ALKILINITY | [5 empty] | 216 | 206 | 206 | 206 | 208 | 210 | 204 | 220 | 216 | 220 | 228 | 222 | 220 | 214 | 214 | 216 | 218 | 218 | 220 | 220 | 216 | 216 | 214 | 218 | 218 | 220 | 250 | 220 | 208 | 202 | 212
RAW CHLORIDES | [5 empty] | 590 | 610 | 620 | 620 | 570 | 600 | 510 | 600 | 630 | 770 | 730 | 670 | 630 | 750 | 670 | 770 | 830 | 770 | 700 | 790 | 770 | 810 | 800 | 600 | 750 | 680 | 840 | 810 | 770 | 730 | 810
RAW COD | [7 empty] | 396 | 365 | 352 | 290 | 349 |  |  | 360 | 386 | 349 | 378 | 452 |  |  | 360 | 306 | 374 | 323 | 362 |  |  | 400 | 332 | 404 | 682 | 368 |  |  | 337
RAW CBOD | [5 empty] | 55 | 60 | 79 | 60 | 48 | 100.5 | 157.2 | 99 | 114 | 109 | 63 | 87 | 145 | 108.9 | 105 | 104 | 112 | 97 | 118 | 152 | 130 | 119 | 86 | 120 | 121 | 119 | 204 | 116 | 99 | 94 | 94
| EFFLUENT DATA |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
EFFLUENT TOTAL DISSOLVED SOLIDS | [5 empty] | 1263 | 1249 | 1266 | 1267 | 1267 | 1149 | 1234 | 1206 | 1210 | 1256 | 1272 | 1290 | 1274 | 1429 | 1421 | 1320 | 1323 | 1298 | 1360 | 1424 | 1412 | 1532 | 1654 | 1370 | 1502 | 1451 | 1434 | 1521 | 1460 | 1471 | 1502
EFFLUENT TOTAL SUSPENDED SOLIDS | [5 empty] | 8 | 12 | 11 | 6 | 15 | 13 | 11 | 11 | 12 | 15 | 24 | 10 | 11 | 12 | 9 | 9 | 13 | 9 | 11 | 10 | 13 | 17 | 11 | 15 | 20 | 14 | 11 | 17 | 12 | 12 | 10
EFFLUENT FIXED SUSPENDED SOLIDS | [5 empty] | 1 | 2 | 2 | 0 | 2 | 1 | 1 | 2 | 2 | 2 | 9 | 2 | 2 | 2 | 1 | 1 | 2 | 1 | 2 | 2 | 3 | 4 | 2 | 3 | 5 | 3 | 2 | 5 | 3 | 2 | 2
EFFLUENT ALKILINITY | [5 empty] | 190 | 192 | 192 | 190 | 196 | 196 | 190 | 194 | 190 | 190 | 188 | 190 | 190 | 192 | 198 | 196 | 194 | 196 | 194 | 196 | 196 | 196 | 196 | 198 | 200 | 198 | 196 | 174 | 186 | 192 | 194
EFFLUENT TURBIDITY | [5 empty] | 5.92 | 7.26 | 6.2 | 5.19 | 5.22 | 5.47 | 5.57 | 7.34 | 6.51 | 7.18 | 6.75 | 6.83 | 6.74 | 6.73 | 5.94 | 5.19 | 5.72 | 5.91 | 5.67 | 5.86 | 7.37 | 9.03 | 7.3 | 8.14 | 9.02 | 8.63 | 7.76 | 7.43 | 7.4 | 8.03 | 6.41
EFFLUENT CHLORIDES | [5 empty] | 570 | 620 | 610 | 610 | 660 | 600 | 610 | 580 | 650 | 570 | 640 | 660 | 660 | 760 | 810 | 710 | 720 | 730 | 750 | 760 | 760 | 820 | 850 | 800 | 830 | 770 | 750 | 520 | 730 | 770 | 820
EFFLUENT CONDUCTIVITY | [5 empty] | 2390 | 2370 | 2330 | 2390 | 2370 | 2360 | 2250 | 2330 | 2670 | 2680 | 2620 | 2630 | 2650 | 2830 | 2840 | 2910 | 2880 | 2890 | 2890 | 2900 | 2990 | 3080 | 3230 | 3140 | 3140 | 3210 | 3160 | 2810 | 2890 | 3000 | 3110
EFFLUENT TOTAL BACTERIA COUNT | [5 empty] | 143 | 0 | 200 | 8000 | 643 | 45 | 1750 | 54 | 230 | 2100 | 530 | 339 | 29500 | 540 | 3100 | 1667 | 3000 | 833 | 5667 | 6667 | 19000 | 107 | 600 | 7000 | 9500 | 19500 | TNTC | TNTC | 1333 | 188 | 5400
EFFLUENT FECAL BACTERIA COUNT | [5 empty] | 0 | 0 | 9 | 89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 36 | 3 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 750 | 0 | 0 | 0 | 0
EFFLUENT COD | [7 empty] | 52.3 | 46.6 | 46.7 | 40.9 | 54.8 |  |  | 40.3 | 58.4 | 52.8 | 50.3 | 53.6 |  |  | 49.8 | 44.8 | 52.4 | 47.8 | 59.4 |  |  | 55.9 | 73.8 | 76.8 | 76.9 | 67.2 |  |  | 63.4
EFFLUENT CBOD | [5 empty] | 1.6 | 2 | 1.5 | 2.2 | 1.2 | 3.24 | 3.62 | 2.8 | 2.8 | 3 | 3.1 | 4.6 | 4.3 | 3.8 | 4 | 3.6 | 3.5 | 4 | 3.7 | 5 | 5.3 | 4.7 | 5.4 | 4.4 | 5.2 | 6.3 | 8 | 7 | 5 | 6 | 5
LABORATORY NUTRIENT DATA
RAW INFLUENT | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
RAW AMMONIA (PPM) | [7 empty] | 19.06 | 18.7 | 18.39 | 17.76 | 17.63 |  |  | 19.36 | 19.18 | 19.49 | 18.05 | 19.18 |  |  | 18.79 | 18.18 | 19.09 | 18.83 | 18.99 |  |  | 19.44 | 18.42 | 18.27 | 17.48 | 17.43 |  |  | LS
RAW NITRATES (PPM) | [7 empty] | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 |  |  | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 |  |  | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 |  |  | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 |  |  | LS
RAW TOTAL KNEDJAHL NITRIGEN | [7 empty] | 23 | 22 | 17 | 19 | 18 |  |  | 22 | 20 | 20 | 21 | 22 |  |  | 21 | 22 | 22 | 22 | 31 |  |  | 22 | 27 | 25 | 20 | 24 |  |  | LS
RAW TOTAL PHOSPHORUS | [7 empty] | 3.5 | 2.9 | 2.9 | 3.1 | 3.1 |  |  | 3.1 | 3.2 | 3.1 | 2.8 | 3.3 |  |  | 3 | 2.9 | 3.2 | 3.4 | 3 |  |  | 3.3 | 3 | 3 | 2.7 | 3 |  |  | LS
EFFLUENT | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
EFFLUENT AMMONIA (PPM) | [7 empty] | 14.06 | 14.45 | 14.82 | 12.67 | 14.63 |  |  | 15.53 | 15.41 | 15.32 | 14.59 | 14.25 |  |  | 14.35 | 14.94 | 14.8 | 13.69 | 12.98 |  |  | 14.79 | 14.69 | 14.37 | 13.05 | 12.15 |  |  | LS
EFFLUENT NITRATES (PPM) | [7 empty] | 0.326 | 0.344 | 0.243 | 0.195 | 0.216 |  |  | 0.24 | 0.279 | 0.234 | 0.294 | 0.504 |  |  | 0.559 | 0.588 | 0.228 | 0.227 | 0.628 |  |  | 0.272 | 0.261 | 0.199 | 0.215 | 0.566 |  |  | LS
EFFLUENT TOTAL KNEDJAHL NITRIGEN | [7 empty] | 14 | 13 | 17 | 12 | 16 |  |  | 15 | 14 | 13 | 15 | 15 |  |  | 16 | 13 | 15 | 16 | 15 |  |  | 17 | 16 | 18 | 15 | 14 |  |  | LS
EFFLUENT TOTAL PHOSPHORUS | [7 empty] | 0.78 | 0.73 | 0.66 | 0.91 | 0.82 |  |  | 0.95 | 1.8 | 1.2 | 1.1 | 1.1 |  |  | 1 | 1.6 | 1 | 1 | 0.98 |  |  | 1.9 | 2.2 | 1.5 | 1.4 | 1.2 |  |  | LS
LABORATORY REACTOR PROCESSES DATA
| REACTOR ONE TRAIN A |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MIXED-LIQUIR SUSPENDED SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
AVERAGE SETTLABLE SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
MIXED LIQUIR VOLITLE SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
| REACTOR ONE TRAIN B |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MIXED-LIQUIR SUSPENDED SOLIDS | [5 empty] | 3760 | 4340 | 3920 | 4060 | 2030 | 1960 | 3790 | 3450 | 3490 | 1900 | 1900 | 1730 | 2310 | 3040 | 3640 | 3340 | 3150 | 3460 | 2510 | 2490 | 3130 | 2580 | 1900 | 2000 | 1440 | 1200 | 1720 | 2810 | 2770 | 1850 | 2240
AVERAGE SETTLABLE SOLIDS | [5 empty] | 33 | 37 | 35 | 32 | 32 | 28 | 34 | 26 | 30 | 24 | 18 | 20 | 27 | 27 | 26 | 30 | 25 | 33 | 25 | 26 | 25 | 22 | 14 | 14 | 13 | 15 | 18 | 19 | 21 | 19 | 19
MIXED LIQUIR VOLITLE SOLIDS | [5 empty] | 3160 | 3650 | 3180 | 3410 | 1600 | 1560 | 2980 | 2900 | 2930 | 1600 | 1500 | 1490 | 1940 | 2550 | 3060 | 2810 | 2650 | 2910 | 2090 | 2090 | 2630 | 2170 | 1600 | 1680 | 1210 | 1090 | 1440 | 2450 | 2330 | 1550 | 1880
LABORATORY REACTOR PROCESSES DATA
CONTINUED
| REACTOR TWO TRAIN C |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MIXED-LIQUIR SUSPENDED SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
AVERAGE SETTLABLE SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
MIXED LIQUIR VOLITLE SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
| REACTOR TWO TRAIN D |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MIXED-LIQUIR SUSPENDED SOLIDS | [5 empty] | 3280 | 3400 | 2610 | 3020 | 2660 | 2510 | 2880 | 2930 | 3030 | 2100 | 2260 | 1980 | 2680 | 3090 | 3350 | 2700 | 2770 | 2670 | 2340 | 2760 | 3050 | 2330 | 2140 | 2260 | 1480 | 1780 | 1780 | 3190 | 2930 | 1800 | 1980
AVERAGE SETTLABLE SOLIDS | [5 empty] | 32 | 34 | 32 | 31 | 28 | 30 | 30 | 26 | 27 | 23 | 17 | 26 | 33 | 28 | 29 | 30 | 23 | 31 | 24 | 30 | 23 | 22 | 14 | 15 | 17 | 16 | 18 | 20 | 24 | 20 | 17
MIXED LIQUIR VOLITLE SOLIDS | [5 empty] | 2760 | 2860 | 2220 | 2540 | 2200 | 2070 | 2350 | 2460 | 2550 | 1760 | 1810 | 1680 | 2250 | 2600 | 2810 | 2270 | 2330 | 2240 | 1950 | 2320 | 2560 | 1960 | 1800 | 1900 | 1240 | 1620 | 1490 | 2740 | 2460 | 1510 | 1660
LABORATORY RETURN ACTIVATED SLUDGE AND WASTE SLUDGE DATA
| RETURN ACTIVATED SLUDGE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
PERCENT RETURN SLUDGE TOTAL SUSPENDED SOLIDS | [5 empty] | 1.07 | 1.15 | 0.97 | 0.96 | 1.01 | 0.97 | 1 | 0.92 | 0.99 | 0.96 | 0.78 | 1.08 | 1.05 | 0.82 | 1.05 | 0.96 | 0.82 | 0.9 | 1.31 | 0.95 | 0.8 | 0.84 | 0.79 | 0.7 | 0.71 | 1.06 | 1.13 | 1.05 | 0.88 | 0.62 | 0.69
PERCENT RETURN SLUDGE FIXED SUSPENDED SOLIDS | [5 empty] | 21.5 | 22.4 | 20.7 | 20.8 | 20.8 | 24.8 | 21.9 | 20.6 | 20.3 | 17.6 | 33.1 | 20.4 | 21.7 | 22.4 | 20.7 | 20.7 | 21.1 | 20.5 | 21.4 | 21 | 20.8 | 22.4 | 0.23 | 22.7 | 23.8 | 23.6 | 22.8 | 22.7 | 22.7 | 22 | 25.2
|  | WASTE SLUDGE |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
PERCENT WASTE FEED TOTAL SUSPENDED SOLDS | [5 empty] | 1.38 | 1.24 | 1.15 | 1.29 |  |  | 1.19 | 1.35 | 1.34 | 1.29 | 1.08 |  |  | 1.03 | 1.44 | 1.1 |  | 1.1 |  |  | 1.7 | 1.18 | 1.11 | 1.18 | 0.96 |  |  | 1.31 | 1.23 | 1.33 | 0.89
PERCENT WASTE FEED FIXED SUSPENDED SOLIDS | [5 empty] | 21.7 | 22.6 | 20 | 20.9 |  |  | 22.7 | 22.2 | 20.9 | 22.5 | 27.8 |  |  | 26.2 | 20.1 | 20.9 |  | 20 |  |  | 21.2 | 24.6 | 0.29 | 21.2 | 27.1 |  |  | 22.1 | 22.8 | 21.1 | 27
WASTE FEED SLUDGE pH | [5 empty] | 6.7 | 6.69 | 6.69 | 6.71 |  |  | 6.59 | 6.72 | 6.7 | 6.71 | 6.48 |  |  | 6.74 | 6.36 | 6.4 |  | 6.47 |  |  | 6.61 | 6.44 | 6.51 | 6.59 | 6.58 |  |  | 6.34 | 6.57 | 6.48 | 6.44
DEWATERING FILTRATE TOTAL SUSPENDED SOLIDS | [5 empty] | 0.19 | 0.21 | 0.21 | 0.23 |  |  | 0.16 | 0.2 | 0.2 | 0.21 | 0.21 |  |  | 0.19 | 0.23 | 0.24 |  | 0.24 |  |  | 0.21 | 0.23 | 0.25 | 0.25 | 0.29 |  |  | 0.23 | 0.24 | 0.26 | 0.23
DEWATERING FILTRATE FIXED SUSPENDED SOLIDS | [5 empty] | 68.4 | 57.1 | 57.1 | 65.2 |  |  | 75 | 65 | 60 | 66.7 | 71.4 |  |  | 68.4 | 56.5 | 58.3 |  | 62.5 |  |  | 57.1 | 73.9 | 0.17 | 60 | 58.6 |  |  | 56.5 | 58.3 | 53.8 | 65.2
DEWATERING FILTRATE pH | [5 empty] | 7.18 | 7.14 | 7.13 | 7.18 |  |  | 6.96 | 7.17 | 7.18 | 7.18 | 6.91 |  |  | 7.16 | 6.78 | 6.82 |  | 6.89 |  |  | 7.01 | 6.85 | 6.9 | 6.91 | 6.89 |  |  | 6.92 | 7.09 | 6.91 | 6.98
| DEWATERED CAKE SLUDGE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
PERCENT TOTAL SOLIDS PRESS CAKE | [5 empty] | 17.35 | 17.75 | 18.34 | 18.16 |  |  | 16.61 | 17.56 | 18.01 | 19.03 | 19.25 |  |  | 17.71 | 17.83 | 17.82 |  | 18.3 |  |  | 17.46 | 17.83 | 19.07 | 18.61 | 20.72 |  |  | 18.62 | 17.94 | 17.85 | 18.89
PERCENT FIXED SOLIDS PRESS CAKE | [5 empty] | 13.4 | 14.1 | 13.8 | 15.9 |  |  | 13.8 | 13.4 | 13.6 | 16.5 | 14.7 |  |  | 12.7 | 13.5 | 14.9 |  | 15.7 |  |  | 14.3 | 13.3 | 2.75 | 14 | 14.5 |  |  | 14.2 | 14.7 | 13.8 | 18.4
PERCENT TOTAL SOLIDS LIME CAKE
OTHER SLUDGE REMOVAL
[6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
GRIT (CU.YDS.) | [5 empty] | 4: 10; 11: 10; 19: 10; 26: 10
RAGS (CU.YDS.) | [5 empty] | 5: 10; 12: 10; 19: 10; 26: 10
VACUUM DEBRIS (EST. GAL) | [5 empty] | 9: 4500
MONITORING WELLS LABORATORY DATA
| MONITOR WELL ONE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
UPPER LEVEL
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
MONITORING WELLS LABORATORY DATA
| MONITOR WELL TWO |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
UPPER LEVEL
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
MONITORING WELLS LABORATORY DATA
| MONITOR WELL THREE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
FUTURE
UPPER LEVEL
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
MONITORING WELLS LABORATORY DATA
| REGIONAL MONITOR WELL ONE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
UPPER LEVEL
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
MARCH |  | 1 |  | 3
|  | 0 |  | 0
1
0
|  | 1 |  | 0
3
[5 empty] | 1st WEEK | 1: 2nd WEEK; 2: 3rd WEEK; 3: 4th WEEK
| 1 |  | 1 |  | 1 | 1: 8; 2: 15; 3: 23
| 2 |  | 2 |  | 2 | 1: 9; 2: 16; 3: 24
| 3 |  | 3 |  | 3 | 1: 10; 2: 17; 3: 25
| 4 |  | 4 |  | 4 | 1: 11; 2: 18; 3: 26
| 5 |  | 5 |  | 5 | 1: 12; 2: 19; 3: 27
| 6 |  | 6 |  | 6 | 1: 13; 2: 20; 3: 28
| 7 |  | 7 |  | 7 | 1: 14; 2: 21; 3: 29
| 8 |  | 8 |  |  | 2: 22; 3: 30
| 9 |  | 9 |  |  | 3: 31
| 10 |  | 10
| 11 |  | 11
| 12 |  | 12
| 13 |  | 13
| 14 |  | 14
| 15 |  | 15
| 16 |  | 16
| 17 |  | 17
| 18 |  | 18
| 19 |  | 19
| 20 |  | 20
| 21 |  | 21
| 22 |  | 22
| 23 |  | 23
| 24 |  | 24
| 25 |  | 25
| 26 |  | 26
| 27 |  | 27
| 28 |  | 28
29
30
31
| APRIL | MARCH | FEBRUARY
| AUGUST | JULY | JUNE
| DECEMBER | NOVEMBER | OCTOBER
| FEBRUARY | JANUARY | DECEMBER
| JANUARY | DECEMBER | NOVEMBER
| JUNE | MAY | APRIL
| JULY | JUNE | MAY | FEBRUARY
| MARCH | FEBRUARY | JANUARY | JANUARY
| MAY | APRIL | MARCH
| NOVEMBER | OCTOBER | SEPTEMBER
| OCTOBER | SEPTEMBER | AUGUST
| SEPTEMBER | AUGUST | JULY
| HYDROGEN PEROXIDE |  | 0.1395
| CHLORINE |  | 0.1475
| POLYMER |  | 0.61
| FPL |  | 0.055
[6 empty] | 1st WEEK |  |  | 2nd WEEK |  |  | 3rd WEEK |  |  | 4th WEEK
[7 empty] | G | H | I | J
[5 empty] | MW1 UP | 1: 311
312
313
314
315
316
317
318

## MONITOR DATA
UNDERGROUND INJECTION CONTROL SECTION
MONTHLY OPERATING REPORT DATA SUMMARY
FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT MONTH/YEAR |  |  |  | MARCH |  | 2004
I.D. NUMBER: 5006M02066 | [5 empty] | LEAD OPERATOR: |  |  |  |  | MIKE JUST
TELEPHONE NUMBER: (954) 523-1002
MONITORING WELL 1 DATA | [6 empty] | I.D. # 5006A11311
MW-1
PERMIT/CERTIFICATION NUMBER | [6 empty] | 0054569-142-UO
PERMIT EXPIRATION DATE |  | 2009-01-06
UPPER MONITORING INTERVAL | [6 empty] | 1,288' - 1,320' |  |  |  |  | Ft. bls.
Sample Date |  | 2004-03-02 |  | 2004-03-09 |  | 2004-03-16 |  | 2004-03-23 |  | 2004-03-30
Submittal Date |  | 2004-03-03 |  | 2004-03-10 |  | 2004-03-17 |  | 2004-03-24 |  | 2004-03-31
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [9 empty] | 48.77 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [9 empty] | 46.4 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 72 |  | 72 |  | 75 |  | 73 |  | 76 |  | degrees (F) |  | 73.6
TDS |  | 7113 |  | 7150 |  | 7170 |  | 7227 |  | 7170 |  | mg/l |  | 7166
CHLORIDE |  | 4000 |  | 3800 |  | 3800 |  | 3750 |  | 3850 |  | mg/l |  | 3840
AMMONIA-N |  | 0.842 |  | 0.872 |  | 0.848 |  | 0.844 |  | 0.832 |  | mg/l |  | 0.8476
TKN |  | 1.1 |  | 0.95 |  | 0.94 |  | 1.1 |  | 0.9 |  | mg/l |  | 0.998
pH |  | 7.98 |  | 8.11 |  | 8.16 |  | 8.06 |  | 7.99 |  | Std units |  | 8.06
CONDUCTIVITY |  | 11070 |  | 12010 |  | 12020 |  | 12070 |  | 12070 |  | umho/cm |  | 11848
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.01 | < | 0.01 | < | 0.01 | < | 0.01 | < | 0.01 |  | mg/l |  | 0.01
SULFATE |  | 950 |  | 783 |  | 853 |  | 773 |  | 885 |  | mg/l |  | 848.8
C.O.D. 'S | [11 empty] | mg/l |  | #DIV/0!
IRON | [11 empty] | mg/l |  | #DIV/0!
SULFIDE | [11 empty] | mg/l |  | #DIV/0!
LOWER MONITORING INTERVAL | [6 empty] | 1,449' - 1,557' |  |  |  |  | Ft. bls
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [9 empty] | 42.01 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [9 empty] | 37.25 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 73 |  | 72 |  | 74 |  | 72 |  | 74 |  | degrees (F) |  | 73
TDS |  | 10428 |  | 9152 |  | 9010 |  | 9243 |  | 9234 |  | mg/l |  | 9413.4
CHLORIDE |  | 5600 |  | 5000 |  | 5000 |  | 5000 |  | 5000 |  | mg/l |  | 5120
AMMONIA-N |  | 9.14 |  | 9.75 |  | 9.71 |  | 9.55 |  | 9.65 |  | mg/l |  | 9.56
TKN |  | 8.2 |  | 10 |  | 9.2 |  | 9.3 |  | 12 |  | mg/l |  | 9.74
pH |  | 7.39 |  | 7.44 |  | 7.43 |  | 7.52 |  | 7.46 |  | Std units |  | 7.448
CONDUCTIVITY |  | 16180 |  | 15580 |  | 15570 |  | 15600 |  | 15640 |  | umho/cm |  | 15714
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.01 | < | 0.01 | < | 0.01 | < | 0.01 | < | 0.01 |  | mg/l |  | 0.01
SULFATE |  | 900 |  | 753 |  | 745 |  | 760 |  | 760 |  | mg/l |  | 783.6
C.O.D. 'S | [11 empty] | mg/l |  | #DIV/0!
IRON | [11 empty] | mg/l |  | #DIV/0!
SULFIDE | [11 empty] | mg/l |  | #DIV/0!
PAGE 24
UNDERGROUND INJECTION CONTROL SECTION
MONTHLY OPERATING REPORT DATA SUMMARY
FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT MONTH/YEAR |  |  |  | MARCH |  | 2004
I.D. NUMBER: 5006M02066 | [5 empty] | LEAD OPERATOR: |  |  |  |  | MIKE JUST
TELEPHONE NUMBER: (954) 523-1002
MONITORING WELL 2 DATA | [6 empty] | I.D. # 5006A11308 & 309
MW-2
PERMIT/CERTIFICATION NUMBER | [6 empty] | 0054569-142-UO
PERMIT EXPIRATION DATE |  | 2009-01-06
UPPER MONITORING INTERVAL | [6 empty] | 1,300' - 1,344' |  |  |  |  | Ft. bls.
Sample Date |  | 2004-03-02 |  | 2004-03-09 |  | 2004-03-16 |  | 2004-03-23 |  | 2004-03-30
Submittal Date |  | 2004-03-03 |  | 2004-03-10 |  | 2004-03-17 |  | 2004-03-24 |  | 2004-03-31
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [9 empty] | 32.09 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [9 empty] | 26.89 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 73 |  | 72 |  | 72 |  | 72 |  | 74 |  | degrees (F) |  | 72.6
TDS |  | 7064 |  | 7153 |  | 7162 |  | 7053 |  | 7134 |  | mg/l |  | 7113.2
CHLORIDE |  | 3800 |  | 3650 |  | 3650 |  | 3700 |  | 3700 |  | mg/l |  | 3700
AMMONIA-N |  | 0.875 |  | 0.86 |  | 0.841 |  | 0.869 |  | 0.786 |  | mg/l |  | 0.8462
TKN |  | 1.1 |  | 0.77 |  | 1.1 |  | 1 |  | 1.1 |  | mg/l |  | 1.014
pH |  | 7.93 |  | 8.15 |  | 8.14 |  | 8.15 |  | 8.22 |  | Std units |  | 8.118
CONDUCTIVITY |  | 10810 |  | 11740 |  | 11730 |  | 11800 |  | 11910 |  | umho/cm |  | 11598
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.01 | < | 0.01 | < | 0.01 | < | 0.01 | < | 0.01 |  | mg/l |  | 0.01
SULFATE |  | 950 |  | 750 |  | 793 |  | 768 |  | 885 |  | mg/l |  | 829.2
C.O.D. 'S | [11 empty] | mg/l |  | #DIV/0!
IRON | [11 empty] | mg/l |  | #DIV/0!
SULFIDE | [11 empty] | mg/l |  | #DIV/0!
LOWER MONITORING INTERVAL | [6 empty] | 1,970' - 2,025' |  |  |  |  | Ft. bls
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [9 empty] | 42.64 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [9 empty] | 36.85 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 71 |  | 70 |  | 71 |  | 70 |  | 72 |  | degrees (F) |  | 70.8
TDS |  | 30360 |  | 30840 |  | 30850 |  | 31100 |  | 31470 |  | mg/l |  | 30924
CHLORIDE |  | 17800 |  | 17600 |  | 17800 |  | 17600 |  | 17400 |  | mg/l |  | 17640
AMMONIA-N |  | 1.36 |  | 1.36 |  | 1.35 |  | 1.37 |  | 1.35 |  | mg/l |  | 1.358
TKN |  | 2.1 |  | 2.1 |  | 2.1 |  | 1.9 |  | 3.2 |  | mg/l |  | 2.28
pH |  | 7.47 |  | 7.49 |  | 7.51 |  | 7.5 |  | 7.49 |  | Std units |  | 7.492
CONDUCTIVITY |  | 42800 |  | 46800 |  | 46700 |  | 46800 |  | 46900 |  | umho/cm |  | 46000
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.01 | < | 0.01 | < | 0.01 | < | 0.01 | < | 0.01 |  | mg/l |  | 0.01
SULFATE |  | 2700 |  | 2390 |  | 2710 |  | 2550 |  | 2420 |  | mg/l |  | 2554
C.O.D. 'S | [11 empty] | mg/l |  | #DIV/0!
IRON | [11 empty] | mg/l |  | #DIV/0!
SULFIDE | [11 empty] | mg/l |  | #DIV/0!
PAGE 25
UNDERGROUND INJECTION CONTROL SECTION
MONTHLY OPERATING REPORT DATA SUMMARY
FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT MONTH/YEAR |  |  |  | MARCH |  | 2004
I.D. NUMBER: 5006M02066 | [5 empty] | LEAD OPERATOR: |  |  |  |  | MIKE JUST
TELEPHONE NUMBER: (954) 523-1002
MONITORING WELL 2 DATA | [6 empty] | I.D. # 5006A11310
MW-3
PERMIT/CERTIFICATION NUMBER | [6 empty] | 0054569-142-UO
PERMIT EXPIRATION DATE |  | 2009-01-06
UPPER MONITORING INTERVAL | [6 empty] | 1,300' - 1,349' |  |  |  |  | Ft. bls.
Sample Date |  | 2004-03-02 |  | 2004-03-09 |  | 2004-03-16 |  | 2004-03-23 |  | 2004-03-30
Submittal Date |  | 2004-03-03 |  | 2004-03-10 |  | 2004-03-17 |  | 2004-03-24 |  | 2004-03-31
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [9 empty] | 32.15 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [9 empty] | 19.15 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 71 |  | 70 |  | 70 |  | 70 |  | 71 |  | degrees (F) |  | 70.4
TDS |  | 7140 |  | 7140 |  | 7130 |  | 7150 |  | 6900 |  | mg/l |  | 7092
CHLORIDE |  | 4050 |  | 3700 |  | 3700 |  | 3700 |  | 3650 |  | mg/l |  | 3760
AMMONIA-N |  | 0.872 |  | 0.858 |  | 0.88 |  | 0.868 |  | 0.826 |  | mg/l |  | 0.8608
TKN |  | 1.1 |  | 0.86 |  | 1.2 |  | 1 |  | 0.97 |  | mg/l |  | 1.026
pH |  | 8.15 |  | 8.19 |  | 8.26 |  | 8.25 |  | 7.7 |  | Std units |  | 8.11
CONDUCTIVITY |  | 10960 |  | 11890 |  | 11950 |  | 11940 |  | 11710 |  | umho/cm |  | 11690
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.01 | < | 0.01 | < | 0.01 | < | 0.01 | < | 0.01 |  | mg/l |  | 0.01
SULFATE |  | 850 |  | 838 |  | 845 |  | 823 |  | 793 |  | mg/l |  | 829.8
C.O.D. 'S | [11 empty] | mg/l |  | #DIV/0!
IRON | [11 empty] | mg/l |  | #DIV/0!
SULFIDE | [11 empty] | mg/l |  | #DIV/0!
LOWER MONITORING INTERVAL | [6 empty] | 1,970' - 2,027' |  |  |  |  | Ft. bls
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [9 empty] | 45.72 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [9 empty] | 38.51 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 70 |  | 69 |  | 69 |  | 69 |  | 70 |  | degrees (F) |  | 69.4
TDS |  | 27812 |  | 28150 |  | 28130 |  | 28560 |  | 28190 |  | mg/l |  | 28168.4
CHLORIDE |  | 16400 |  | 15800 |  | 16400 |  | 16200 |  | 16200 |  | mg/l |  | 16200
AMMONIA-N |  | 2.46 |  | 2.5 |  | 2.34 |  | 2.39 |  | 2.36 |  | mg/l |  | 2.41
TKN |  | 3.5 |  | 3.2 |  | 3.3 |  | 2.8 |  | 1.9 |  | mg/l |  | 2.94
pH |  | 7.43 |  | 7.52 |  | 7.52 |  | 7.49 |  | 7.46 |  | Std units |  | 7.484
CONDUCTIVITY |  | 39200 |  | 43100 |  | 43000 |  | 43200 |  | 43200 |  | umho/cm |  | 42340
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS |  | 0.013 | < | 0.01 | < | 0.01 | < | 0.01 | < | 0.01 |  | mg/l |  | 0.0106
SULFATE |  | 2600 |  | 2080 |  | 2440 |  | 2400 |  | 2700 |  | mg/l |  | 2444
C.O.D. 'S | [11 empty] | mg/l |  | #DIV/0!
IRON | [11 empty] | mg/l |  | #DIV/0!
SULFIDE | [11 empty] | mg/l |  | #DIV/0!
PAGE 26
UNDERGROUND INJECTION CONTROL SECTION
MONTHLY OPERATING REPORT DATA SUMMARY
FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT MONTH/YEAR |  |  |  | MARCH |  | 2004
I.D. NUMBER: 5006M02066 | [5 empty] | LEAD OPERATOR: |  |  |  |  | MIKE JUST
TELEPHONE NUMBER: (954) 523-1002
REGIONAL MONITORING WELL DATA
RMW-1
PERMIT NUMBER | [6 empty] | 0054569-142-UO
PERMIT EXPIRATION DATE |  | 2009-01-06
UPPER MONITORING INTERVAL | [6 empty] | 1300' - 1339' |  |  |  |  | Ft. bls.
Sample Date |  | 2004-03-02
Submittal Date |  | 2004-03-03
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [9 empty] | 44.75 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [9 empty] | 42.48 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 75 | [9 empty] | degrees (F) |  | 75
TDS |  | 5408 | [9 empty] | mg/l |  | 5408
CHLORIDE |  | 3150 | [9 empty] | mg/l |  | 3150
AMMONIA-N |  | 0.599 | [9 empty] | mg/l |  | 0.599
TKN |  | 0.94 | [9 empty] | mg/l |  | 0.94
pH |  | 8.33 | [9 empty] | Std units |  | 8.33
CONDUCTIVITY |  | 8500 | [9 empty] | umho/cm |  | 8500
FECAL COLIFORM |  | 0 | [9 empty] | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.01 | [9 empty] | mg/l |  | 0.01
SULFATE |  | 650 | [9 empty] | mg/l |  | 650
C.O.D. 'S | [11 empty] | mg/l |  | #DIV/0!
IRON | [11 empty] | mg/l |  | #DIV/0!
SULFIDE | [11 empty] | mg/l |  | #DIV/0!
LOWER MONITORING INTERVAL | [6 empty] | 1500' - 1600' |  |  |  |  | Ft. bls
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [9 empty] | 23.12 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [9 empty] | 21 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 74 | [9 empty] | degrees (F) |  | 74
TDS |  | 26080 | [9 empty] | mg/l |  | 26080
CHLORIDE |  | 17200 | [9 empty] | mg/l |  | 17200
AMMONIA-N |  | 0.238 | [9 empty] | mg/l |  | 0.238
TKN |  | 0.77 | [9 empty] | mg/l |  | 0.77
pH |  | 7.51 | [9 empty] | Std units |  | 7.51
CONDUCTIVITY |  | 38000 | [9 empty] | umho/cm |  | 38000
FECAL COLIFORM |  | 0 | [9 empty] | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.01 | [9 empty] | mg/l |  | 0.01
SULFATE |  | 1550 | [9 empty] | mg/l |  | 1550
C.O.D. 'S | [11 empty] | mg/l |  | #DIV/0!
IRON | [11 empty] | mg/l |  | #DIV/0!
SULFIDE | [11 empty] | mg/l |  | #DIV/0!
PAGE 27
Formulas:
LEAD OPERATOR: = [LEAD OPERATOR:, row above]+1

## WELL PRN DATA
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 1 |  |  | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91
61 | 12.03 | 0 | 7.55 | 56.87 | 34.59 | 46.99
62 | 12.28 | 5.26 | 9.05 | 58.84 | 40.13 | 48.3 |  |  | FLOW
63 | 13.28 | 4.71 | 8.54 | 61.62 | 39 | 47.2 | I |  | MAX | 12.03 | 12.28 | 13.28 | 12.22 | 11.7 | 13.37 | 11.6 | 11.09 | 10.91 | 10.19 | 10.15 | 10.17 | 13.37 | 13.8 | 11.88 | 10.88 | 10.85 | 10.45 | 18.13 | 11.47 | 12.11 | 9.69 | 15.06 | 10.19 | 13.2 | 12.75 | 12.88 | 10.14 | 10.16 | 10.95 | 10.16
64 | 12.22 | 3.96 | 8.33 | 57.45 | 37.72 | 47.05 | N |  | MIN | 0 | 5.26 | 4.71 | 3.96 | 3.97 | 5.31 | 5.44 | 4.73 | 3.79 | 3.73 | 4.09 | 3.7 | 5.36 | 5.69 | 4.31 | 4.12 | 0 | 4.48 | 0 | 4.83 | 0 | 0 | 4.49 | 5.22 | 5.26 | 4.53 | 0 | 4.31 | 0 | 4.53 | 5.44
65 | 11.7 | 3.97 | 8.29 | 56.56 | 37.68 | 46.94 | J |  | TOT | 7.55 | 9.05 | 8.54 | 8.33 | 8.29 | 8.82 | 8.53 | 8.05 | 8.03 | 8.08 | 8.06 | 8.17 | 8.66 | 9.11 | 7.99 | 7.75 | 6.92 | 8.02 | 7.11 | 8.07 | 6.48 | 6.74 | 9.27 | 8.56 | 8.69 | 8.5 | 6.85 | 7.97 | 7.02 | 8.13 | 8.42
66 | 13.37 | 5.31 | 8.82 | 61.64 | 39.93 | 48.26 | E | INJECTION WELL ONE
67 | 11.6 | 5.44 | 8.53 | 56.3 | 39.78 | 47.4 | C |  | PSI
68 | 11.09 | 4.73 | 8.05 | 55.64 | 38.86 | 46.41 | T |  | MAX | 56.87 | 58.84 | 61.62 | 57.45 | 56.56 | 61.64 | 56.3 | 55.64 | 53.73 | 50.93 | 50.78 | 50.81 | 62.81 | 62.42 | 56.88 | 53.4 | 53.91 | 53.96 | 80.5 | 56.27 | 57.93 | 49.6 | 69.19 | 50.72 | 61.84 | 59.89 | 60.41 | 51.15 | 51.13 | 54.08 | 50.96
69 | 10.91 | 3.79 | 8.03 | 53.73 | 37.41 | 46.23 | O |  | MIN | 34.59 | 40.13 | 39 | 37.72 | 37.68 | 39.93 | 39.78 | 38.86 | 37.41 | 37.14 | 37.81 | 37.11 | 40.38 | 40.56 | 38.62 | 38.35 | 34.56 | 38.37 | 34.21 | 38.94 | 34.29 | 34.23 | 38.12 | 39.54 | 39.79 | 38.65 | 34.36 | 38.31 | 34.44 | 38.51 | 40.18
70 | 10.19 | 3.73 | 8.08 | 50.93 | 37.14 | 46.03 | N |  | AVG | 46.99 | 48.3 | 47.2 | 47.05 | 46.94 | 48.26 | 47.4 | 46.41 | 46.23 | 46.03 | 45.88 | 46.18 | 47.63 | 48.57 | 46.01 | 45.39 | 44.68 | 45.92 | 45.54 | 45.98 | 43.9 | 44.15 | 49.35 | 46.88 | 47.44 | 47.13 | 45.14 | 45.96 | 45.14 | 46.48 | 46.76
71 | 10.15 | 4.09 | 8.06 | 50.78 | 37.81 | 45.88
72 | 10.17 | 3.7 | 8.17 | 50.81 | 37.11 | 46.18 | W
73 | 13.37 | 5.36 | 8.66 | 62.81 | 40.38 | 47.63 | E
74 | 13.8 | 5.69 | 9.11 | 62.42 | 40.56 | 48.57 | L
75 | 11.88 | 4.31 | 7.99 | 56.88 | 38.62 | 46.01 | L
76 | 10.88 | 4.12 | 7.75 | 53.4 | 38.35 | 45.39 | O
77 | 10.85 | 0 | 6.92 | 53.91 | 34.56 | 44.68 | N
78 | 10.45 | 4.48 | 8.02 | 53.96 | 38.37 | 45.92 | E
79 | 18.13 | 0 | 7.11 | 80.5 | 34.21 | 45.54
80 | 11.47 | 4.83 | 8.07 | 56.27 | 38.94 | 45.98 | D
81 | 12.11 | 0 | 6.48 | 57.93 | 34.29 | 43.9 | A
82 | 9.69 | 0 | 6.74 | 49.6 | 34.23 | 44.15 | T
83 | 15.06 | 4.49 | 9.27 | 69.19 | 38.12 | 49.35 | A
84 | 10.19 | 5.22 | 8.56 | 50.72 | 39.54 | 46.88
85 | 13.2 | 5.26 | 8.69 | 61.84 | 39.79 | 47.44
86 | 12.75 | 4.53 | 8.5 | 59.89 | 38.65 | 47.13
87 | 12.88 | 0 | 6.85 | 60.41 | 34.36 | 45.14
88 | 10.14 | 4.31 | 7.97 | 51.15 | 38.31 | 45.96
89 | 10.16 | 0 | 7.02 | 51.13 | 34.44 | 45.14
90 | 10.95 | 4.53 | 8.13 | 54.08 | 38.51 | 46.48
91 | 10.16 | 5.44 | 8.42 | 50.96 | 40.18 | 46.76
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 2 |  |  | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91
61 | 12.23 | 5.5 | 9.48 | 55.9 | 39.43 | 48.45
62 | 12.52 | 0.02 | 7.51 | 57.68 | 34.89 | 45.38 |  |  | FLOW
63 | 13.58 | 4.53 | 8.67 | 60.41 | 38.24 | 46.28 | I |  | MAX | 12.23 | 12.52 | 13.58 | 12.39 | 11.94 | 13.55 | 11.72 | 11.23 | 11.03 | 10.28 | 10.34 | 10.31 | 13.59 | 14.1 | 12.19 | 11.01 | 11.01 | 10.66 | 15.92 | 11.67 | 12.4 | 9.73 | 10.16 | 10.32 | 13.51 | 12.96 | 13.09 | 10.26 | 10.27 | 11.04 | 10.22
64 | 12.39 | 3.49 | 8.4 | 56.35 | 36.98 | 46.13 | N |  | MIN | 5.5 | 0.02 | 4.53 | 3.49 | 3.61 | 5.31 | 0.02 | 4.41 | 3.12 | 3.06 | 3.62 | 3.02 | 5.14 | 5.57 | 4.02 | 3 | 4.75 | 4.08 | 0.02 | 4.55 | 4.74 | 4.83 | 0.03 | 5.1 | 5.21 | 4.26 | 5.62 | 3.91 | 4.7 | 4.23 | 0.02
65 | 11.94 | 3.61 | 8.34 | 55.46 | 36.96 | 46.06 | J |  | TOT | 9.48 | 7.51 | 8.67 | 8.4 | 8.34 | 8.92 | 6.03 | 8.1 | 8.07 | 8.08 | 8.08 | 8.21 | 8.74 | 9.28 | 8.06 | 7.78 | 8.15 | 8.08 | 8.12 | 8.13 | 7.97 | 7.91 | 3.49 | 8.7 | 8.81 | 8.59 | 8.96 | 7.98 | 8.62 | 8.17 | 6.92
66 | 13.55 | 5.31 | 8.92 | 60.56 | 39.15 | 47.34 | E | INJECTION WELL TWO
67 | 11.72 | 0.02 | 6.03 | 55.27 | 34.96 | 43.53 | C |  | PSI
68 | 11.23 | 4.41 | 8.1 | 54.68 | 38.09 | 45.5 | T |  | MAX | 55.9 | 57.68 | 60.41 | 56.35 | 55.46 | 60.56 | 55.27 | 54.68 | 52.71 | 49.96 | 49.88 | 49.91 | 61.67 | 35.86 | 56.05 | 52.54 | 53.08 | 53.01 | 68.87 | 55.31 | 56.89 | 48.75 | 49.42 | 49.72 | 60.6 | 58.72 | 59.27 | 50.12 | 50.14 | 53 | 49.94
69 | 11.03 | 3.12 | 8.07 | 52.71 | 36.66 | 45.33 | I |  | MIN | 39.43 | 34.89 | 38.24 | 36.98 | 36.96 | 39.15 | 34.96 | 38.09 | 36.66 | 36.38 | 37.04 | 36.36 | 39.58 | 39.77 | 37.9 | 37.08 | 38.77 | 37.72 | 36.07 | 38.2 | 38.4 | 38.54 | 34.62 | 38.74 | 39 | 37.85 | 39.81 | 37.55 | 38.7 | 37.74 | 34.85
70 | 10.28 | 3.06 | 8.08 | 49.96 | 36.38 | 45.11 | O |  | AVG | 48.45 | 45.38 | 46.28 | 46.13 | 46.06 | 47.34 | 43.53 | 45.5 | 45.33 | 45.11 | 44.99 | 45.32 | 46.74 | 47.74 | 45.29 | 44.72 | 45.37 | 45.17 | 45.64 | 45.14 | 44.71 | 44.57 | 39.82 | 45.95 | 46.49 | 46.18 | 46.96 | 45.06 | 46.11 | 45.55 | 44.13
71 | 10.34 | 3.62 | 8.08 | 49.88 | 37.04 | 44.99 | N
72 | 10.31 | 3.02 | 8.21 | 49.91 | 36.36 | 45.32
73 | 13.59 | 5.14 | 8.74 | 61.67 | 39.58 | 46.74 | W
74 | 14.1 | 5.57 | 9.28 | 61.31 | 39.77 | 47.74 | E
75 | 12.19 | 4.02 | 8.06 | 56.05 | 37.9 | 45.29 | L
76 | 11.01 | 3 | 7.78 | 52.54 | 37.08 | 44.72 | L
77 | 11.01 | 4.75 | 8.15 | 53.08 | 38.77 | 45.37
78 | 10.66 | 4.08 | 8.08 | 53.01 | 37.72 | 45.17 | T
79 | 15.92 | 0.02 | 8.12 | 68.87 | 36.07 | 45.64 | W
80 | 11.67 | 4.55 | 8.13 | 55.31 | 38.2 | 45.14 | O
81 | 12.4 | 4.74 | 7.97 | 56.89 | 38.4 | 44.71
82 | 9.73 | 4.83 | 7.91 | 48.75 | 38.54 | 44.57 | D
83 | 10.16 | 0.03 | 3.49 | 49.42 | 34.62 | 39.82 | A
84 | 10.32 | 5.1 | 8.7 | 49.72 | 38.74 | 45.95 | T
85 | 13.51 | 5.21 | 8.81 | 60.6 | 39 | 46.49 | A
86 | 12.96 | 4.26 | 8.59 | 58.72 | 37.85 | 46.18
87 | 13.09 | 5.62 | 8.96 | 59.27 | 39.81 | 46.96
88 | 10.26 | 3.91 | 7.98 | 50.12 | 37.55 | 45.06
89 | 10.27 | 4.7 | 8.62 | 50.14 | 38.7 | 46.11
90 | 11.04 | 4.23 | 8.17 | 53 | 37.74 | 45.55
91 | 10.22 | 0.02 | 6.92 | 49.94 | 34.85 | 44.13
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 3 |  |  | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91
61 | 10.82 | 4.84 | 8.33 | 57.14 | 40.38 | 49.62
62 | 11.11 | 2.38 | 8.03 | 59.13 | 39.74 | 48.44 |  |  | FLOW
63 | 11.95 | ER | 6.34 | 61.94 | 35.13 | 45.6 | I |  | MAX | 10.82 | 11.11 | 11.95 | 10.91 | 10.52 | 11.98 | 10.36 | 9.91 | 9.72 | 9.04 | 9.07 | 9.09 | 12.1 | 10.7 | 10.64 | 9.42 | 9.5 | 9.1 | 16.66 | 10.08 | 10.77 | 8.51 | 13.12 | 9.1 | 11.11 | 11.39 | 11.47 | 9.01 | 9.02 | 9.73 | 9.02
64 | 10.91 | 3.18 | 7.4 | 57.74 | 37.83 | 47.23 | N |  | MIN | 4.84 | 2.38 | ER | 3.18 | 3.28 | 4.69 | 4.63 | 3.91 | 2.91 | 2.94 | 3.23 | 2.8 | 4.48 | ER | 3.58 | 3.48 | 4.07 | 3.47 | ER | 3.94 | 4 | 4.22 | 3.56 | ER | ER | 3.8 | 4.93 | 3.53 | 4.16 | 3.75 | 4.7
65 | 10.52 | 3.28 | 7.36 | 56.84 | 37.81 | 47.16 | J |  | TOT | 8.33 | 8.03 | 6.34 | 7.4 | 7.36 | 7.89 | 7.58 | 7.14 | 7.11 | 7.15 | 7.11 | 7.21 | 7.73 | 6.71 | 7.01 | 6.69 | 6.98 | 6.96 | 7.04 | 7.1 | 6.91 | 6.84 | 8.1 | 6.29 | 7.53 | 7.56 | 7.84 | 7.04 | 7.52 | 7.18 | 7.47
66 | 11.98 | 4.69 | 7.89 | 61.99 | 40.08 | 48.46 | E | INJECTION WELL THREE
67 | 10.36 | 4.63 | 7.58 | 56.6 | 39.91 | 47.58 | C |  | PSI
68 | 9.91 | 3.91 | 7.14 | 55.94 | 38.96 | 46.58 | T |  | MAX | 57.14 | 59.13 | 61.94 | 57.74 | 56.84 | 61.99 | 56.6 | 55.94 | 53.99 | 51.16 | 51.11 | 51.18 | 63.25 | 57.1 | 57.34 | 53.72 | 54.31 | 54.25 | 83.1 | 56.59 | 58.22 | 49.85 | 69.3 | 50.97 | 58.41 | 60.2 | 60.71 | 51.39 | 51.32 | 54.34 | 51.16
69 | 9.72 | 2.91 | 7.11 | 53.99 | 37.5 | 46.43 | I |  | MIN | 40.38 | 39.74 | 35.13 | 37.83 | 37.81 | 40.08 | 39.91 | 38.96 | 37.5 | 37.24 | 37.91 | 37.22 | 40.51 | 35.19 | 38.75 | 38.74 | 39.64 | 38.57 | 36.12 | 39.06 | 39.24 | 39.43 | 38.21 | 34.94 | 35.96 | 38.74 | 40.75 | 38.41 | 39.57 | 38.6 | 40.27
70 | 9.04 | 2.94 | 7.15 | 51.16 | 37.24 | 46.21 | O |  | AVG | 49.62 | 48.44 | 45.6 | 47.23 | 47.16 | 48.46 | 47.58 | 46.58 | 46.43 | 46.21 | 46.09 | 46.41 | 47.88 | 46.05 | 46.32 | 45.72 | 46.39 | 46.22 | 46.9 | 46.19 | 45.72 | 45.58 | 49.47 | 45.29 | 47.13 | 47.3 | 48.08 | 46.12 | 47.2 | 46.65 | 46.94
71 | 9.07 | 3.23 | 7.11 | 51.11 | 37.91 | 46.09 | N
72 | 9.09 | 2.8 | 7.21 | 51.18 | 37.22 | 46.41
73 | 12.1 | 4.48 | 7.73 | 63.25 | 40.51 | 47.88 | W
74 | 10.7 | ER | 6.71 | 57.1 | 35.19 | 46.05 | E
75 | 10.64 | 3.58 | 7.01 | 57.34 | 38.75 | 46.32 | L
76 | 9.42 | 3.48 | 6.69 | 53.72 | 38.74 | 45.72 | L
77 | 9.5 | 4.07 | 6.98 | 54.31 | 39.64 | 46.39
78 | 9.1 | 3.47 | 6.96 | 54.25 | 38.57 | 46.22 | T
79 | 16.66 | ER | 7.04 | 83.1 | 36.12 | 46.9 | H
80 | 10.08 | 3.94 | 7.1 | 56.59 | 39.06 | 46.19 | R
81 | 10.77 | 4 | 6.91 | 58.22 | 39.24 | 45.72 | E
82 | 8.51 | 4.22 | 6.84 | 49.85 | 39.43 | 45.58 | E
83 | 13.12 | 3.56 | 8.1 | 69.3 | 38.21 | 49.47
84 | 9.1 | ER | 6.29 | 50.97 | 34.94 | 45.29 | D
85 | 11.11 | ER | 7.53 | 58.41 | 35.96 | 47.13 | A
86 | 11.39 | 3.8 | 7.56 | 60.2 | 38.74 | 47.3 | T
87 | 11.47 | 4.93 | 7.84 | 60.71 | 40.75 | 48.08 | A
88 | 9.01 | 3.53 | 7.04 | 51.39 | 38.41 | 46.12
89 | 9.02 | 4.16 | 7.52 | 51.32 | 39.57 | 47.2
90 | 9.73 | 3.75 | 7.18 | 54.34 | 38.6 | 46.65
91 | 9.02 | 4.7 | 7.47 | 51.16 | 40.27 | 46.94
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 4 |  |  | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91
61 | 0.14 | 0.12 | 0.13 | 36.98 | 35.48 | 36.31
62 | 0.14 | 0.12 | 0.13 | 37.1 | 35.37 | 36.15 |  |  | FLOW
63 | 0.15 | 0.12 | 0.13 | 37.4 | 35 | 36.05 | I |  | MAX | 0.14 | 0.14 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.14 | 0.15 | 0.15 | 0.14 | 13.17 | 13.69 | 13.73 | 13.23 | 14.31 | 14.44 | 15.35 | 12.23 | 18.47 | 0.14 | 0.14 | 0.14 | 0.14 | 0.15 | 0.13 | 0.15 | 0.14
64 | 0.15 | 0.12 | 0.13 | 37.17 | 35.17 | 36.21 | N |  | MIN | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.11 | 0.11 | 0.12 | 0.12 | 0.12 | 0.12 | 5.85 | 6.69 | 0.12 | 0.13 | 0.12 | 6.4 | 6.67 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
65 | 0.15 | 0.12 | 0.13 | 37.11 | 35.21 | 36.23 | J |  | TOT | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.12 | 0.12 | 0.13 | 0.13 | 0.13 | 5.79 | 10.07 | 10.39 | 9.17 | 9.4 | 8.73 | 10.19 | 10.11 | 7.77 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13
66 | 0.15 | 0.12 | 0.13 | 37.11 | 34.98 | 36.05 | E | INJECTION WELL FOUR
67 | 0.15 | 0.12 | 0.13 | 37.25 | 35.41 | 36.3 | C |  | PSI
68 | 0.15 | 0.12 | 0.13 | 37.29 | 35.37 | 36.33 | T |  | MAX | 36.98 | 37.1 | 37.4 | 37.17 | 37.11 | 37.11 | 37.25 | 37.29 | 37.12 | 36.83 | 36.69 | 36.71 | 37 | 50.93 | 53.05 | 53.61 | 54.17 | 54.23 | 55.59 | 56.53 | 57.95 | 50.1 | 68.42 | 36.75 | 37.02 | 37.45 | 37.65 | 36.89 | 36.84 | 37.03 | 36.9
69 | 0.15 | 0.12 | 0.13 | 37.12 | 35.15 | 36.3 | I |  | MIN | 35.48 | 35.37 | 35 | 35.17 | 35.21 | 34.98 | 35.41 | 35.37 | 35.15 | 35.08 | 35.01 | 34.9 | 34.97 | 34.52 | 35.31 | 39.33 | 40.16 | 35.42 | 35.9 | 35.31 | 39.79 | 40.02 | 36 | 35.01 | 34.8 | 35.15 | 35.46 | 35.31 | 35.57 | 35.4 | 35.55
70 | 0.15 | 0.11 | 0.12 | 36.83 | 35.08 | 36.17 | O |  | AVG | 36.31 | 36.15 | 36.05 | 36.21 | 36.23 | 36.05 | 36.3 | 36.33 | 36.3 | 36.17 | 36.04 | 36.1 | 35.97 | 35.87 | 41.96 | 45.96 | 46.67 | 45.4 | 45.51 | 44.91 | 45.98 | 45.95 | 45.52 | 36.14 | 36.07 | 36.2 | 36.35 | 36.23 | 36.33 | 36.3 | 36.32
71 | 0.14 | 0.11 | 0.12 | 36.69 | 35.01 | 36.04 | N
72 | 0.15 | 0.12 | 0.13 | 36.71 | 34.9 | 36.1
73 | 0.15 | 0.12 | 0.13 | 37 | 34.97 | 35.97 | W
74 | 0.14 | 0.12 | 0.13 | 37.19 | 34.52 | 35.87 | E
75 | 13.17 | 0.12 | 5.79 | 53.05 | 35.31 | 41.96 | L
76 | 13.69 | 5.85 | 10.07 | 53.61 | 39.33 | 45.96 | L
77 | 13.73 | 6.69 | 10.39 | 54.17 | 40.16 | 46.67
78 | 13.23 | 0.12 | 9.17 | 54.23 | 35.42 | 45.4 | F
79 | 14.31 | 0.13 | 9.4 | 55.59 | 35.9 | 45.51 | O
80 | 14.44 | 0.12 | 8.73 | 56.53 | 35.31 | 44.91 | U
81 | 15.35 | 6.4 | 10.19 | 57.95 | 39.79 | 45.98 | R
82 | 12.23 | 6.67 | 10.11 | 50.1 | 40.02 | 45.95
83 | 18.47 | 0.12 | 7.77 | 68.42 | 36 | 45.52 | D
84 | 0.14 | 0.12 | 0.13 | 36.75 | 35.01 | 36.14 | A
85 | 0.14 | 0.12 | 0.13 | 37.02 | 34.8 | 36.07 | T
86 | 0.14 | 0.12 | 0.13 | 37.45 | 35.15 | 36.2 | A
87 | 0.14 | 0.12 | 0.13 | 37.65 | 35.46 | 36.35
88 | 0.15 | 0.12 | 0.13 | 36.89 | 35.31 | 36.23
89 | 0.13 | 0.12 | 0.13 | 36.84 | 35.57 | 36.33
90 | 0.15 | 0.12 | 0.13 | 37.03 | 35.4 | 36.3
91 | 0.14 | 0.12 | 0.13 | 36.9 | 35.55 | 36.32
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 5 |  |  | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91
61 | 10.67 | 5.13 | 8.35 | 56.7 | 40.16 | 49.23
62 | 10.9 | ER | 7.8 | 58.67 | 34.55 | 47.52 |  |  | FLOW
63 | 11.78 | 4.38 | 7.75 | 61.46 | 38.87 | 47.01 | I |  | MAX | 10.67 | 10.9 | 11.78 | 10.83 | 10.48 | 10.4 | 10.31 | 9.85 | 9.66 | 9.04 | 9.04 | 9.05 | 10.02 | 10.63 | 10.65 | ER | ER | ER | 16.13 | ER | ER | ER | 8.92 | 9.07 | 11.11 | 11.38 | 11.44 | 9.08 | 9.09 | 9.73 | 9.04
64 | 10.83 | 3.64 | 7.58 | 57.3 | 37.6 | 46.87 | N |  | MIN | 5.13 | ER | 4.38 | 3.64 | 0.98 | ER | 4.87 | 4.26 | 3.28 | 3.3 | 3.66 | 3.19 | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | 4.74 | ER | 4.16 | 5.17 | 3.9 | 4.53 | 4.1 | 4.91
65 | 10.48 | 0.98 | 7.53 | 56.4 | 36.08 | 46.78 | J |  | TOT | 8.35 | 7.8 | 7.75 | 7.58 | 7.53 | 5.02 | 7.66 | 7.26 | 7.24 | 7.27 | 7.25 | 7.35 | 5.42 | 5.35 | 3.23 | ER | ER | ER | 0.76 | ER | ER | ER | 2.78 | 7.75 | 6.7 | 7.69 | 7.94 | 7.22 | 7.65 | 7.35 | 7.59
66 | 10.4 | ER | 5.02 | 56.02 | 33.54 | 42.9 | E | INJECTION WELL FIVE
67 | 10.31 | 4.87 | 7.66 | 56.08 | 39.66 | 47.2 | C |  | PSI
68 | 9.85 | 4.26 | 7.26 | 55.39 | 38.77 | 46.21 | T |  | MAX | 56.7 | 58.67 | 61.46 | 57.3 | 56.4 | 56.02 | 56.08 | 55.39 | 53.43 | 50.77 | 50.72 | 50.71 | 54.41 | 56.67 | 56.85 | 36.15 | 36.14 | 35.86 | 82.3 | 36.31 | 36.37 | 35.67 | 50.3 | 50.62 | 58.66 | 59.74 | 60.25 | 50.89 | 50.92 | 53.91 | 50.8
69 | 9.66 | 3.28 | 7.24 | 53.43 | 37.4 | 46.13 | I |  | MIN | 40.16 | 34.55 | 38.87 | 37.6 | 36.08 | 33.54 | 39.66 | 38.77 | 37.4 | 37.19 | 37.82 | 37.06 | 33.65 | 33.36 | 34.96 | 34.39 | 34.45 | 33.06 | 34.05 | 33.29 | 34.33 | 34.25 | 34.05 | 39.46 | 33.51 | 38.58 | 40.52 | 38.24 | 39.4 | 38.5 | 40.12
70 | 9.04 | 3.3 | 7.27 | 50.77 | 37.19 | 45.92 | O |  | AVG | 49.23 | 47.52 | 47.01 | 46.87 | 46.78 | 42.9 | 47.2 | 46.21 | 46.13 | 45.92 | 45.77 | 46.11 | 43.26 | 43.17 | 40.15 | 35.3 | 35.25 | 34.87 | 37.38 | 35.02 | 35.16 | 35.09 | 39.48 | 46.73 | 45.51 | 46.99 | 47.74 | 45.79 | 46.91 | 46.32 | 46.59
71 | 9.04 | 3.66 | 7.25 | 50.72 | 37.82 | 45.77 | N
72 | 9.05 | 3.19 | 7.35 | 50.71 | 37.06 | 46.11
73 | 10.02 | ER | 5.42 | 54.41 | 33.65 | 43.26 | W
74 | 10.63 | ER | 5.35 | 56.67 | 33.36 | 43.17 | E
75 | 10.65 | ER | 3.23 | 56.85 | 34.96 | 40.15 | L
76 | ER | ER | ER | 36.15 | 34.39 | 35.3 | L
77 | ER | ER | ER | 36.14 | 34.45 | 35.25
78 | ER | ER | ER | 35.86 | 33.06 | 34.87 | F
79 | 16.13 | ER | 0.76 | 82.3 | 34.05 | 37.38 | I
80 | ER | ER | ER | 36.31 | 33.29 | 35.02 | V
81 | ER | ER | ER | 36.37 | 34.33 | 35.16 | E
82 | ER | ER | ER | 35.67 | 34.25 | 35.09
83 | 8.92 | ER | 2.78 | 50.3 | 34.05 | 39.48 | D
84 | 9.07 | 4.74 | 7.75 | 50.62 | 39.46 | 46.73 | A
85 | 11.11 | ER | 6.7 | 58.66 | 33.51 | 45.51 | T
86 | 11.38 | 4.16 | 7.69 | 59.74 | 38.58 | 46.99 | A
87 | 11.44 | 5.17 | 7.94 | 60.25 | 40.52 | 47.74
88 | 9.08 | 3.9 | 7.22 | 50.89 | 38.24 | 45.79
89 | 9.09 | 4.53 | 7.65 | 50.92 | 39.4 | 46.91
90 | 9.73 | 4.1 | 7.35 | 53.91 | 38.5 | 46.32
91 | 9.04 | 4.91 | 7.59 | 50.8 | 40.12 | 46.59

## RMW PRN DATA
julian | u-avg | u-min | u-max | l-avg | l-min | l-max
61 | 22.29 | 21.05 | 23.12 | 43.48 | 42.59 | 44.52 | R |  |  | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91
62 | 21.48 | 21 | 21.78 | 43.44 | 42.48 | 44.11 | E
63 | 21.88 | 21.74 | 21.96 | 44.19 | 44.09 | 44.25 | G |  | LOW
64 | 22.01 | 21.92 | 22.07 | 44.3 | 44.22 | 44.36 | I |  | MIN | 21.05 | 21 | 21.74 | 21.92 | 21.99 | 22.06 | 22.07 | 22.16 | 22.25 | 22.19 | 22.15 | 22.16 | 22.14 | 22.16 | 22.19 | 22.27 | 22.3 | 22.21 | 22.18 | 22.17 | 22.26 | 22.32 | 22.2 | 22.14 | 22.14 | 22.17 | 22.17 | 22.17 | 22.21 | 22.24 | 22.29
65 | 22.06 | 21.99 | 22.12 | 44.34 | 44.28 | 44.39 | O |  | MAX | 23.12 | 21.78 | 21.96 | 22.07 | 22.12 | 22.16 | 22.22 | 22.29 | 22.38 | 22.4 | 22.25 | 22.27 | 22.3 | 22.26 | 22.32 | 22.49 | 22.46 | 22.32 | 22.25 | 22.29 | 22.4 | 22.42 | 22.37 | 22.25 | 22.25 | 22.27 | 22.3 | 22.3 | 22.32 | 22.35 | 22.44
66 | 22.11 | 22.06 | 22.16 | 44.37 | 44.3 | 44.44 | N |  | AVG | 22.29 | 21.48 | 21.88 | 22.01 | 22.06 | 22.11 | 22.14 | 22.22 | 22.31 | 22.3 | 22.19 | 22.21 | 22.21 | 22.21 | 22.28 | 22.4 | 22.39 | 22.27 | 22.22 | 22.22 | 22.33 | 22.36 | 22.26 | 22.18 | 22.19 | 22.21 | 22.22 | 22.24 | 22.26 | 22.29 | 22.36
67 | 22.14 | 22.07 | 22.22 | 44.41 | 44.33 | 44.47 | A | RMW
68 | 22.22 | 22.16 | 22.29 | 44.47 | 44.4 | 44.53 | L |  | UP
69 | 22.31 | 22.25 | 22.38 | 44.53 | 44.46 | 44.62 |  |  | MIN | 42.59 | 42.48 | 44.09 | 44.22 | 44.28 | 44.3 | 44.33 | 44.4 | 44.46 | 44.43 | 44.41 | 44.44 | 44.44 | 44.46 | 44.5 | 44.58 | 44.58 | 44.48 | 44.45 | 44.44 | 44.52 | 44.57 | 44.46 | 44.43 | 44.45 | 44.5 | 44.51 | 44.55 | 44.57 | 44.57 | 44.63
70 | 22.3 | 22.19 | 22.4 | 44.52 | 44.43 | 44.6 | M |  | MAX | 44.52 | 44.11 | 44.25 | 44.36 | 44.39 | 44.44 | 44.47 | 44.53 | 44.62 | 44.6 | 44.48 | 44.5 | 44.54 | 44.52 | 44.6 | 44.75 | 44.75 | 44.63 | 44.57 | 44.57 | 44.69 | 44.7 | 44.62 | 44.53 | 44.53 | 44.58 | 44.59 | 44.61 | 44.65 | 44.67 | 44.75
71 | 22.19 | 22.15 | 22.25 | 44.44 | 44.41 | 44.48 | O |  | AVG | 43.48 | 43.44 | 44.19 | 44.3 | 44.34 | 44.37 | 44.41 | 44.47 | 44.53 | 44.52 | 44.44 | 44.47 | 44.48 | 44.48 | 44.55 | 44.67 | 44.67 | 44.56 | 44.51 | 44.51 | 44.61 | 44.64 | 44.54 | 44.49 | 44.5 | 44.54 | 44.56 | 44.58 | 44.6 | 44.61 | 44.68
72 | 22.21 | 22.16 | 22.27 | 44.47 | 44.44 | 44.5 | N
73 | 22.21 | 22.14 | 22.3 | 44.48 | 44.44 | 44.54 | I
74 | 22.21 | 22.16 | 22.26 | 44.48 | 44.46 | 44.52 | T
75 | 22.28 | 22.19 | 22.32 | 44.55 | 44.5 | 44.6 | O
76 | 22.4 | 22.27 | 22.49 | 44.67 | 44.58 | 44.75 | R
77 | 22.39 | 22.3 | 22.46 | 44.67 | 44.58 | 44.75
78 | 22.27 | 22.21 | 22.32 | 44.56 | 44.48 | 44.63 | W
79 | 22.22 | 22.18 | 22.25 | 44.51 | 44.45 | 44.57 | E
80 | 22.22 | 22.17 | 22.29 | 44.51 | 44.44 | 44.57 | L
81 | 22.33 | 22.26 | 22.4 | 44.61 | 44.52 | 44.69 | L
82 | 22.36 | 22.32 | 22.42 | 44.64 | 44.57 | 44.7
83 | 22.26 | 22.2 | 22.37 | 44.54 | 44.46 | 44.62
84 | 22.18 | 22.14 | 22.25 | 44.49 | 44.43 | 44.53 | R
85 | 22.19 | 22.14 | 22.25 | 44.5 | 44.45 | 44.53 | M
86 | 22.21 | 22.17 | 22.27 | 44.54 | 44.5 | 44.58 | W
87 | 22.22 | 22.17 | 22.3 | 44.56 | 44.51 | 44.59
88 | 22.24 | 22.17 | 22.3 | 44.58 | 44.55 | 44.61 | O
89 | 22.26 | 22.21 | 22.32 | 44.6 | 44.57 | 44.65 | N
90 | 22.29 | 22.24 | 22.35 | 44.61 | 44.57 | 44.67 | E
91 | 22.36 | 22.29 | 22.44 | 44.68 | 44.63 | 44.75
61 | 39.65 | 38.03 | 41.7 | 47.87 | 47.24 | 48.53 | M |  |  | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91
62 | 40.03 | 38.04 | 41.41 | 47.92 | 47.46 | 48.28 | O
63 | 41.46 | 41.27 | 41.55 | 48.19 | 48.05 | 48.33 | N |  | LOW
64 | 41.49 | 41.38 | 41.6 | 48.25 | 48.11 | 48.38 | I |  | MIN | 38.03 | 38.04 | 41.27 | 41.38 | 41.4 | 41.45 | 41.46 | 37.58 | 37.54 | 41.45 | 41.42 | 41.49 | 41.5 | 41.51 | 37.25 | 37.27 | 41.5 | 41.49 | 41.48 | 41.49 | 41.56 | 37.31 | 37.29 | 41.35 | 41.28 | 41.37 | 41.43 | 41.58 | 37.41 | 37.39 | 41.41
65 | 41.49 | 41.4 | 41.61 | 48.28 | 48.1 | 48.41 | T |  | MAX | 41.7 | 41.41 | 41.55 | 41.6 | 41.61 | 41.61 | 41.78 | 41.74 | 41.61 | 41.7 | 41.64 | 41.67 | 41.7 | 41.74 | 41.72 | 41.78 | 41.95 | 41.72 | 41.68 | 41.68 | 41.84 | 41.76 | 41.46 | 41.53 | 41.59 | 41.7 | 41.72 | 41.85 | 41.75 | 41.79 | 42.01
66 | 41.49 | 41.45 | 41.61 | 48.29 | 48.14 | 48.43 | O |  | AVG | 39.65 | 40.03 | 41.46 | 41.49 | 41.49 | 41.49 | 41.53 | 39.24 | 40.18 | 41.56 | 41.5 | 41.53 | 41.57 | 41.56 | 38.98 | 40.19 | 41.66 | 41.56 | 41.54 | 41.53 | 41.69 | 39.05 | 40.08 | 41.46 | 41.48 | 41.51 | 41.55 | 41.65 | 39.07 | 39.98 | 41.67
67 | 41.53 | 41.46 | 41.78 | 48.26 | 48.14 | 48.48 | R | MW-1
68 | 39.24 | 37.58 | 41.74 | 47.35 | 46.54 | 48.46 |  |  | UP
69 | 40.18 | 37.54 | 41.61 | 48.01 | 46.87 | 48.74 | W |  | MIN | 47.24 | 47.46 | 48.05 | 48.11 | 48.1 | 48.14 | 48.14 | 46.54 | 46.87 | 48.31 | 48.2 | 48.25 | 48.2 | 48.21 | 46.4 | 46.89 | 48.29 | 48.23 | 48.19 | 48.19 | 48.28 | 47.03 | 47.21 | 48.12 | 48.14 | 48.18 | 48.21 | 48.22 | 46.8 | 47.23 | 48.25
70 | 41.56 | 41.45 | 41.7 | 48.5 | 48.31 | 48.68 | E |  | MAX | 48.53 | 48.28 | 48.33 | 48.38 | 48.41 | 48.43 | 48.48 | 48.46 | 48.74 | 48.68 | 48.51 | 48.51 | 48.53 | 48.49 | 48.53 | 48.77 | 48.67 | 48.53 | 48.5 | 48.52 | 48.64 | 48.55 | 48.55 | 48.38 | 48.38 | 48.38 | 48.37 | 48.4 | 48.43 | 48.41 | 48.52
71 | 41.5 | 41.42 | 41.64 | 48.36 | 48.2 | 48.51 | L |  | AVG | 47.87 | 47.92 | 48.19 | 48.25 | 48.28 | 48.29 | 48.26 | 47.35 | 48.01 | 48.5 | 48.36 | 48.43 | 48.35 | 48.36 | 47.41 | 48.07 | 48.52 | 48.42 | 48.35 | 48.35 | 48.45 | 47.61 | 47.97 | 48.23 | 48.25 | 48.27 | 48.31 | 48.34 | 47.45 | 47.94 | 48.41
72 | 41.53 | 41.49 | 41.67 | 48.43 | 48.25 | 48.51 | L
73 | 41.57 | 41.5 | 41.7 | 48.35 | 48.2 | 48.53
74 | 41.56 | 41.51 | 41.74 | 48.36 | 48.21 | 48.49 | O
75 | 38.98 | 37.25 | 41.72 | 47.41 | 46.4 | 48.53 | N
76 | 40.19 | 37.27 | 41.78 | 48.07 | 46.89 | 48.77 | E
77 | 41.66 | 41.5 | 41.95 | 48.52 | 48.29 | 48.67
78 | 41.56 | 41.49 | 41.72 | 48.42 | 48.23 | 48.53 | I
79 | 41.54 | 41.48 | 41.68 | 48.35 | 48.19 | 48.5 | N
80 | 41.53 | 41.49 | 41.68 | 48.35 | 48.19 | 48.52 | J
81 | 41.69 | 41.56 | 41.84 | 48.45 | 48.28 | 48.64 | E
82 | 39.05 | 37.31 | 41.76 | 47.61 | 47.03 | 48.55 | C
83 | 40.08 | 37.29 | 41.46 | 47.97 | 47.21 | 48.55 | T
84 | 41.46 | 41.35 | 41.53 | 48.23 | 48.12 | 48.38 | I
85 | 41.48 | 41.28 | 41.59 | 48.25 | 48.14 | 48.38 | O
86 | 41.51 | 41.37 | 41.7 | 48.27 | 48.18 | 48.38 | N
87 | 41.55 | 41.43 | 41.72 | 48.31 | 48.21 | 48.37
88 | 41.65 | 41.58 | 41.85 | 48.34 | 48.22 | 48.4 | W
89 | 39.07 | 37.41 | 41.75 | 47.45 | 46.8 | 48.43 | E
90 | 39.98 | 37.39 | 41.79 | 47.94 | 47.23 | 48.41 | L
91 | 41.67 | 41.41 | 42.01 | 48.41 | 48.25 | 48.52 | L
61 | 40.26 | 38.48 | 42.54 | 29.03 | 26.97 | 30.77 | M |  |  | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91
62 | 40.53 | 36.85 | 42.04 | 29.17 | 26.97 | 30.94 | O
63 | 42.03 | 41.97 | 42.22 | 30.68 | 30.22 | 31.34 | N |  | LOW
64 | 42.3 | 42.14 | 42.33 | 30.9 | 30.46 | 31.62 | I |  | MIN | 38.48 | 36.85 | 41.97 | 42.14 | 42.2 | 42.28 | 42.31 | 38.72 | 38.62 | 42.25 | 42.24 | 42.33 | 42.36 | 42.39 | 37.58 | 37.59 | 42.22 | 42.28 | 42.28 | 42.32 | 42.42 | 37.6 | 36.92 | 42.13 | 42.23 | 42.32 | 42.37 | 42.44 | 40.28 | 40.25 | 42.27
65 | 42.36 | 42.2 | 42.4 | 31.1 | 30.58 | 31.8 | T |  | MAX | 42.54 | 42.04 | 42.22 | 42.33 | 42.4 | 42.45 | 42.51 | 42.5 | 42.32 | 42.35 | 42.4 | 42.45 | 42.5 | 42.53 | 42.61 | 42.34 | 42.46 | 42.42 | 42.45 | 42.51 | 42.64 | 42.62 | 42.15 | 42.27 | 42.35 | 42.4 | 42.45 | 42.52 | 42.57 | 42.29 | 42.56
66 | 42.41 | 42.28 | 42.45 | 31.16 | 30.72 | 31.82 | O |  | AVG | 40.26 | 40.53 | 42.03 | 42.3 | 42.36 | 42.41 | 42.45 | 40.29 | 40.99 | 42.35 | 42.37 | 42.43 | 42.49 | 42.5 | 39.4 | 40.73 | 42.39 | 42.4 | 42.41 | 42.43 | 42.49 | 39.28 | 40.54 | 42.15 | 42.3 | 42.4 | 42.46 | 42.5 | 41.22 | 41.47 | 42.44
67 | 42.45 | 42.31 | 42.51 | 31.19 | 30.64 | 32.09 | R | MW-2
68 | 40.29 | 38.72 | 42.5 | 29.47 | 27.47 | 30.98 |  |  | UP
69 | 40.99 | 38.62 | 42.32 | 29.51 | 26.89 | 31.22 | W |  | MIN | 26.97 | 26.97 | 30.22 | 30.46 | 30.58 | 30.72 | 30.64 | 27.47 | 26.89 | 29.67 | 29.46 | 30.22 | 30.5 | 30.48 | 26.9 | 26.92 | 30.26 | 30.26 | 30.25 | 30.24 | 30.48 | 27.33 | 27.2 | 30.06 | 29.91 | 30.09 | 30.25 | 30.46 | 27.41 | 26.97 | 29.77
70 | 42.35 | 42.25 | 42.35 | 30.32 | 29.67 | 31.28 | E |  | MAX | 30.77 | 30.94 | 31.34 | 31.62 | 31.8 | 31.82 | 32.09 | 30.98 | 31.22 | 31.28 | 31.18 | 31.43 | 31.46 | 31.41 | 31.04 | 31.37 | 31.78 | 31.21 | 31.16 | 31.14 | 31.55 | 30.7 | 30.69 | 30.76 | 30.94 | 31.26 | 31.38 | 31.56 | 30.78 | 30.88 | 31.75
71 | 42.37 | 42.24 | 42.4 | 30.36 | 29.46 | 31.18 | L |  | AVG | 29.03 | 29.17 | 30.68 | 30.9 | 31.1 | 31.16 | 31.19 | 29.47 | 29.51 | 30.32 | 30.36 | 30.68 | 30.82 | 30.86 | 28.78 | 29.57 | 30.69 | 30.66 | 30.68 | 30.71 | 30.99 | 29.28 | 29.39 | 30.39 | 30.41 | 30.62 | 30.74 | 30.89 | 29.09 | 29.19 | 30.65
72 | 42.43 | 42.33 | 42.45 | 30.68 | 30.22 | 31.43 | L
73 | 42.49 | 42.36 | 42.5 | 30.82 | 30.5 | 31.46
74 | 42.5 | 42.39 | 42.53 | 30.86 | 30.48 | 31.41 | T
75 | 39.4 | 37.58 | 42.61 | 28.78 | 26.9 | 31.04 | W
76 | 40.73 | 37.59 | 42.34 | 29.57 | 26.92 | 31.37 | O
77 | 42.39 | 42.22 | 42.46 | 30.69 | 30.26 | 31.78
78 | 42.4 | 42.28 | 42.42 | 30.66 | 30.26 | 31.21 | I
79 | 42.41 | 42.28 | 42.45 | 30.68 | 30.25 | 31.16 | N
80 | 42.43 | 42.32 | 42.51 | 30.71 | 30.24 | 31.14 | J
81 | 42.49 | 42.42 | 42.64 | 30.99 | 30.48 | 31.55 | E
82 | 39.28 | 37.6 | 42.62 | 29.28 | 27.33 | 30.7 | C
83 | 40.54 | 36.92 | 42.15 | 29.39 | 27.2 | 30.69 | T
84 | 42.15 | 42.13 | 42.27 | 30.39 | 30.06 | 30.76 | I
85 | 42.3 | 42.23 | 42.35 | 30.41 | 29.91 | 30.94 | O
86 | 42.4 | 42.32 | 42.4 | 30.62 | 30.09 | 31.26 | N
87 | 42.46 | 42.37 | 42.45 | 30.74 | 30.25 | 31.38
88 | 42.5 | 42.44 | 42.52 | 30.89 | 30.46 | 31.56 | W
89 | 41.22 | 40.28 | 42.57 | 29.09 | 27.41 | 30.78 | E
90 | 41.47 | 40.25 | 42.29 | 29.19 | 26.97 | 30.88 | L
91 | 42.44 | 42.27 | 42.56 | 30.65 | 29.77 | 31.75 | L
61 | 42.79 | 40.57 | 45.67 | 26.93 | 23.25 | 31.68 | M |  |  | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91
62 | 43.17 | 40.57 | 45.11 | 27.94 | 23.19 | 31.37 | O
63 | 45.22 | 45.03 | 45.3 | 31.49 | 31.27 | 31.65 | N |  | LOW
64 | 45.38 | 45.22 | 45.43 | 31.7 | 31.51 | 31.79 | I |  | MIN | 40.57 | 40.57 | 45.03 | 45.22 | 45.29 | 45.39 | 45.43 | 40.93 | 40.88 | 45.33 | 45.33 | 45.43 | 45.46 | 45.51 | 38.51 | 38.53 | 45.28 | 45.35 | 45.36 | 45.41 | 45.52 | 39.41 | 39.36 | 45.17 | 45.3 | 45.4 | 45.46 | 45.53 | 41.36 | 41.39 | 45.2
65 | 45.46 | 45.29 | 45.49 | 31.78 | 31.59 | 31.88 | T |  | MAX | 45.67 | 45.11 | 45.3 | 45.43 | 45.49 | 45.55 | 45.6 | 45.6 | 45.38 | 45.41 | 45.46 | 45.54 | 45.6 | 45.65 | 45.7 | 45.39 | 45.53 | 45.5 | 45.52 | 45.59 | 45.72 | 45.71 | 45.17 | 45.31 | 45.41 | 45.48 | 45.55 | 45.65 | 45.68 | 45.22 | 45.53
66 | 45.48 | 45.39 | 45.55 | 31.81 | 31.67 | 31.93 | O |  | AVG | 42.79 | 43.17 | 45.22 | 45.38 | 45.46 | 45.48 | 45.49 | 42.78 | 43.81 | 45.44 | 45.42 | 45.5 | 45.52 | 45.53 | 41.02 | 43.19 | 45.45 | 45.46 | 45.48 | 45.49 | 45.57 | 41.61 | 43.16 | 45.19 | 45.39 | 45.48 | 45.5 | 45.52 | 43 | 43.64 | 45.39
67 | 45.49 | 45.43 | 45.6 | 31.82 | 31.71 | 32 | R | MW-3
68 | 42.78 | 40.93 | 45.6 | 27.59 | 24.79 | 31.95 |  |  | UP
69 | 43.81 | 40.88 | 45.38 | 29.34 | 24.55 | 31.95 | W |  | MIN | 23.25 | 23.19 | 31.27 | 31.51 | 31.59 | 31.67 | 31.71 | 24.79 | 24.55 | 31.8 | 31.75 | 31.84 | 31.86 | 31.9 | 19.56 | 19.56 | 31.27 | 31.36 | 31.35 | 31.41 | 31.52 | 20.6 | 20.44 | 31.15 | 31.3 | 31.36 | 31.42 | 31.47 | 19.2 | 19.15 | 31.07
70 | 45.44 | 45.33 | 45.41 | 31.92 | 31.8 | 31.98 | E |  | MAX | 31.68 | 31.37 | 31.65 | 31.79 | 31.88 | 31.93 | 32 | 31.95 | 31.95 | 31.98 | 31.99 | 32.05 | 32.09 | 32.11 | 32.15 | 31.42 | 31.61 | 31.58 | 31.62 | 31.69 | 31.83 | 31.79 | 31.26 | 31.42 | 31.49 | 31.52 | 31.57 | 31.62 | 31.65 | 31.07 | 31.48
71 | 45.42 | 45.33 | 45.46 | 31.9 | 31.75 | 31.99 | L |  | AVG | 26.93 | 27.94 | 31.49 | 31.7 | 31.78 | 31.81 | 31.82 | 27.59 | 29.34 | 31.92 | 31.9 | 31.98 | 32 | 32 | 23.94 | 27.52 | 31.47 | 31.48 | 31.48 | 31.49 | 31.72 | 24.41 | 27.58 | 31.27 | 31.4 | 31.47 | 31.49 | 31.52 | 23.68 | 26.4 | 31.34
72 | 45.5 | 45.43 | 45.54 | 31.98 | 31.84 | 32.05 | L
73 | 45.52 | 45.46 | 45.6 | 32 | 31.86 | 32.09
74 | 45.53 | 45.51 | 45.65 | 32 | 31.9 | 32.11 | T
75 | 41.02 | 38.51 | 45.7 | 23.94 | 19.56 | 32.15 | H
76 | 43.19 | 38.53 | 45.39 | 27.52 | 19.56 | 31.42 | R
77 | 45.45 | 45.28 | 45.53 | 31.47 | 31.27 | 31.61 | E
78 | 45.46 | 45.35 | 45.5 | 31.48 | 31.36 | 31.58 | E
79 | 45.48 | 45.36 | 45.52 | 31.48 | 31.35 | 31.62
80 | 45.49 | 45.41 | 45.59 | 31.49 | 31.41 | 31.69 | I
81 | 45.57 | 45.52 | 45.72 | 31.72 | 31.52 | 31.83 | N
82 | 41.61 | 39.41 | 45.71 | 24.41 | 20.6 | 31.79 | J
83 | 43.16 | 39.36 | 45.17 | 27.58 | 20.44 | 31.26 | E
84 | 45.19 | 45.17 | 45.31 | 31.27 | 31.15 | 31.42 | C
85 | 45.39 | 45.3 | 45.41 | 31.4 | 31.3 | 31.49 | T
86 | 45.48 | 45.4 | 45.48 | 31.47 | 31.36 | 31.52 | I
87 | 45.5 | 45.46 | 45.55 | 31.49 | 31.42 | 31.57 | O
88 | 45.52 | 45.53 | 45.65 | 31.52 | 31.47 | 31.62 | N
89 | 43 | 41.36 | 45.68 | 23.68 | 19.2 | 31.65
90 | 43.64 | 41.39 | 45.22 | 26.4 | 19.15 | 31.07 | W
91 | 45.39 | 45.2 | 45.53 | 31.34 | 31.07 | 31.48 | E
L
L

## SHIFT DATA
PERSONNEL LIST
|  | SHIFT CODE |  | OPERATOR NAME |  | CERTIFICATION NUMBER |  | SOCIAL SECURITY NUMBER
CHIEF OPERATORS
HOSTNICK, N. | CO# 3207-A | 3 |  | BAYLER, J. | 3 | CO# 4474-A | "A" |  | "A" | 4474 | 3207 | 2D | J. BAROFSKY | 5096-C
McGEARY, J. | CO# 4545-A | 1 |  | HOSTNICK, N. | 1 | CO# 3207-A | "A" |  | "A" | 3207 | 4545 | 5 | S. HULL | 5613-C
BAYLER, J. | CO# 4474-A | 2 |  | McGEARY, J. | 2 | CO# 4545-A | "A" |  | "A" | 4545 | 4474 | 4 | VACANT | X
POMEROY, D. | CO# 421-B | 5 |  | POMEROY, D. | 5 | CO# 421-B | "B" |  | "B" | 421 | 421 | 3 | J. TINKER | 3291-C
[12 empty] | 1 | G. SLAYTON | 2606-B
[12 empty] | 2 | H. WALKER | 4700-A
OPERATOR II' S
THOMAS, P. | CO# 12833 C | 2D |  | BAROFSKY, J. | 2D | CO# 5096-C | [5 empty] | 5 | J. BENTLEY | X
HULL, S. | CO# 5613-C | 4 |  | BENTLEY, J. | 4 | CO# 9366-C | [5 empty] | 1D | S. CURMODE | X
JONES, K. | CO# 2466-B | 5 |  | CURMODE, S. | 5 | CO# 9379-A | [5 empty] | 4 | K. HENDERSON | 5087-B
BENTLEY, J. | CO# 9366-C | 2 |  | HULL, S. | 2 | CO# 5613-C | [5 empty] | 3D | K. JONES | 2466-C
CURMODE, S. | CO# 9379-A | 3 |  | JONES, K. | 3 | CO# 2466-B | [5 empty] | 3 | G. KLEYNHANS | 7367-C
BAROFSKY, J. | CO# 5096-C | 1 |  | THOMAS, P. | 1 | CO# 12833 C | [5 empty] | 2 | A. MORROW | 9164-C
[12 empty] | 1 | J. RAINFORTH | 2718-C
OPERATOR I' S
HENDERSON, K. | CO# 5087-B | 3D |  | FREIDLAND, M. | 3D | CO# 13437-C
SANDERS, C. | CO# 13500-C | 1 |  | HENDERSON, K. | 1 | CO# 5087-B
PEUGEOT, P. | CO# 12817-C | 3 |  | KOKLAS, D. | 3 | CO# 13506-C
KOKLAS, D. | CO# 13506-C | 5 |  | NOBERT, B. | 5 | CO# 9661-C
FREIDLAND, M. | CO# 13437-C | 2 |  | PEUGEOT, P. | 2 | CO# 12817-C
VERBOSH, R. | CO# 12667-C | 1D |  | SANDERS, C. | 1D | CO# 13500-C
NOBERT, B. | CO# 9661-C | 4 |  | VERBOSH, R. | 4 | CO# 12667-C
|  | 4 | 1 | BERNARDI, J | 4 | CO# XXXX-X
|  | 3 | 2 | FREIDLAND, M. | 3 | CO# 13437-C
|  | 5A | 3 | FUTURE, 5A | 5A | CO# XXXX-X
|  | 1 | 4 | HENDERSON, K. | 1 | CO# 5087-B
|  | 2 | 5 | KOKLAS, D. | 2 | CO# 13506-C
|  | 5 | 6 | NOBERT, B. | 5 | CO# 9661-C
|  | 4A | 7 | PEUGEOT, P. | 4A | CO# 12817-C
|  | 1D | 8 | SANDERS, C. | 1D | CO# 13500-C
|  | 3D | 9 | VERBOSH, R. | 3D | CO# 12667-C

## COVER PAGE
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
|  | MARCH |  | 2004
| OPERATOR | TITLE | CERTIFICATE # | TOTAL COST |  |  | 70806.2848
1 ST SHIFT | HOSTNICK, N. | CHIEF | CO# 3207-A | PEAK TO FLOW RATIO |  |  | 1.0781
2230-0630 | THOMAS, P. | OP. II | CO# 12833 C
| HENDERSON, K. | OP. I | CO# 5087-B |  | TOTAL SUSPENDED SOLIDS
| SANDERS, C. | OP. I DEWAT | CO# 13500-C |  |  |  | LBS/DAY
|  |  |  | RAW INFLUENT |  |  | 56907.3388
2 ND SHIFT |  |  |  | FINAL EFFLUENT |  |  | 3346.4653
0630-1430 | McGEARY, J. | CHIEF | CO# 4545-A |  | TOTAL CBOD
| HULL, S. | OP. II RELIEF | CO# 5613-C |  |  |  | LBS/DAY
| BAROFSKY, J. | OP. II DEWAT | CO# 5096-C | RAW INFLUENT |  |  | 28546.0458
| PEUGEOT, P. | OP. I RELIEF | CO# 12817-C | FINAL EFFLUENT |  |  | 1096.8388
CHEMICALS
3 RD SHIFT | BAYLER, J. | CHIEF | CO# 4474-A |  |  | COST | POUNDS
1430-2230 | JONES, K. | OP. II | CO# 2466-B | HYDROGEN PEROXIDE |  | 7118.406 | 51028
| KOKLAS, D. | OP. I | CO# 13506-C | CHLORINE |  | 5554.85 | 37660
| FREIDLAND, M. | OP. I DEWAT | CO# 13437-C | POLYMER |  | 9345.5538 | 15320.58
SLUDGE REMOVED
4 TH SHIFT | [6 empty] | TONS
WEEKEND | BENTLEY, J. | OP. II | CO# 9366-C | DRY TONS |  |  | 671.4317
2230-1030 | VERBOSH, R. | OP. I | CO# 12667-C |  | ENERGY
| DOLES, L. | OP. I | N/A |  |  | COST | KILOWATTS
5 TH SHIFT | POMEROY, D. | CHIEF | CO# 421-B | FPL CONSUMPTION |  | 48787.475 | 887045
WEEKEND | CURMODE, S. | OP. II | CO# 9379-A
1030-2230 | NOBERT, B. | OP. I | CO# 9661-C | POPULATION EQUIVALENCE |  |  | 167917.9163
This Monthly Operation Report prepared by: |  |  | BAYLER, J. | CO# 4474-A
State DEP Plant Classification: Class "A" Level "II"
I certify that I am familiar with the information contained in this report and that to the best of my knowledge and
belief, such information is true, complete and accurate.
Facilitiy Manager's Signature: ____________________________________ CO# __________________
Division Manager's Signature: ____________________________________ CO# __________________
Please direct all inquiries reguarding this report to the City Official Mailing Address:
Director of Public Services |  |  | Phone (954) 776-5151
City of Fort Lauderdale
P.O. Drawer 14250 |  |  | Copies mailed: Date ________________ To: DEP _____
Fort Lauderdale, Florida | [5 empty] | DNRP _____
33302
PAGE 1

## PRINT PAGES
UNDERGROUND INJECTION CONTROL SECTION
[28 empty] | MONTHLY OPERATING REPORT DATA SUMMARY | [13 empty] | DEP From # 17-801.900 (1) | [11 empty] | DEP From # 17-801.900 (1) | [19 empty] | DAILY SAMPLE RESULTS - PART B
[25 empty] | FACILITY: GEORGE T. LOHMEYER WWTP |  |  |  |  | REPORT DATE: |  | MARCH | 2004 | [8 empty] | Form Title:Domestic Wastewater Treatment | [11 empty] | Form Title:Domestic Wastewater Treatment
[25 empty] | I.D. NUMBER: 5006M02066 |  |  |  | CHIEF OPERATOR: |  |  | BAYLER, J. | CO# 4474-A | [8 empty] | Plant Monthly Operating Report | [11 empty] | Plant Monthly Operating Report | [15 empty] | Permit Number: |  | FLA041378 |  |  |  |  | Three-month Average Daily Flow: | [5 empty] | 34.55
[25 empty] | TELEPHONE NUMBER: (954) 523-1002 | [16 empty] | Effective Date: July 1, 1991 | [11 empty] | Effective Date: July 1, 1991 | [15 empty] | Monitoring Period |  | From: | 2004-03-01 | To: | 2004-03-31 |  | (TMADF):/Permitted Capacity)x100: | [5 empty] | 80.35%
[19 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [8 empty] | INJECTION WELL DATA | [13 empty] | DEP Application No. __________________ | [11 empty] | DEP Application No. __________________ | [11 empty] | Department of Natural Resource Protection
[5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [13 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [6 empty] | IW-1 | IW-2 | IW-3 |  | IW-4 | IW-5 | [35 empty] | Laboratory/Licensing/Enforcement |  |  |  | Flow | Flow | Flow | Flow | Flow | Flow | CBOD5 | CBOD5 | TSS | TSS | pH | pH | TDS | NH-3 | TKN | pH | cond. | temp. | TP
[5 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [13 empty] | MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING | [5 empty] | PERMIT/CERTIFICATION NUMBER: | 0054569-142-UO | 0054569-142-UO | 0054569-142-UO |  | 0054569-142-UO | 0054569-142-UO | [19 empty] | DOMESTIC WASTEWATER TREATMENT PLANT | [11 empty] | BROWARD COUNTY DEPARTMENT OF NATURAL RESOURCE PROTECTION | [5 empty] | 218 S. W. 1st Avenue |  |  | (MGD) | (MGD) | (MGD) | (MGD) | (MGD) | (mg/l) | (mg/l) | (mg/l) | (mg/l) | (Min) | (Max) | mg/L | mg/L | mg/L | units | umho/ | F | mg/L
[5 empty] | MONTHLY OPERATIONAL REPORT | [13 empty] | MONITORING WELL ONE |  |  |  | 1/07/04 thru 1/06/09 |  | PERMIT EXPIRATION DATE: | 2009-01-06 | 2009-01-06 | 2009-01-06 |  | 2009-01-06 | 2009-01-06 | [19 empty] | MONTHLY OPERATING REPORT | [11 empty] | WASTEWATER TREATMENT PLANT | [5 empty] | Fort Lauderdale, FL 33301 | [17 empty] | cm
[5 empty] | PROCESS DATA | [11 empty] | MW-1 | I.D. #: 5066A11311 |  |  | PERMIT # 0054569-142-UO |  |  |  | CASING DEPTH | 2799' | 2798' | 2800' |  | 2804' | 2818' | [8 empty] | DOMESTIC WASTEWATER TREATMENT PLANT |  |  |  |  | (34) | [8 empty] | MONTH: | MARCH |  | YEAR: | 2004 |  |  |  |  | MONTHLY SLUDGE REPORTS | [5 empty] | Tel. No. (954) 765-4804 | Code | 50050 | 50050 | 50050 | 50050 | 50050 | 50050 | 80082 | 80082 | 00530 | 00530 | 00400 | 00400
| RUN DATE | [14 empty] | RUN DATE | [8 empty] | TOTAL DEPTH | 3513' | 3518' | 3977' |  | 3305' | 3462' | [8 empty] | MONTHLY OPERATING REPORT |  |  |  |  | DAY OF | FLOW | CHLORINE | CHLORINE | CBOD5 | TSS | CBOD5 | TSS | PH |  |  | EFFLUENT NUTRIENTS (MG/L) |  |  | I. | [10 empty] | Mon. Site | INF-001 | EFF-002 | EFF-003 | EFF-004 | EFF-005 | EFF-006 | INF-002 | EFF-001 | INF-002 | EFF-001 | EFF-001 | EFF-001
| 2026-07-30 | [14 empty] | 2026-07-30 |  | UPPER MONITOR ZONE |  |  |  |  | LOWER MONITOR ZONE |  | AVERAGE DAILY FLOW: | 8.0568 | 8.0758 | 7.2629 |  | 2.7245 | 6.6196 | MGD | [7 empty] | Part II - General Information |  |  |  |  | THE |  | RESIDUAL | RESIDUAL | INFLUENT | INFLUENT | EFFLUENT | EFFLUENT | EFFLUENT | TKN | NH3-N | NITRATE | TOTAL | FECAL | Plant Name: | GEORGE T. LOHMEYER WASTEWATER TREATMENT FACILITY | [6 empty] | MONTH: | MARCH |  | 1 | 34.923 | 7.55 | 9.48 | 8.33 | 0.13 | 8.35 | 55 | 1.6 | 90 | 8 | 6.5 | 6.5 | 1263 |  |  | 6.5 | 2390 | 79
[17 empty] | MIN | MAX | AVG |  |  | MIN | MAX | AVG | **MAX DAILY FLOW PER MO (mg): | 9.27 | 9.48 | 8.33 |  | 10.39 | 8.35 | MG | [12 empty] | MONTH | (MGD) | AFTER | AFTER DE- | [8 empty] | P | COLIFORM | II. | [7 empty] | YEAR: | 2004 |  | 2 | 33.842 | 9.05 | 7.51 | 8.03 | 0.13 | 7.8 | 60 | 2 | 100 | 12 | 6.4 | 6.4 | 1249 |  |  | 6.5 | 2370 | 79
| MARCH | INFLUENT | HOURLY | INFLUENT | INFLUENT | RAS | PERCENT | WAS | RAIN | RAW | [5 empty] | MARCH | FT HEAD | FT HEAD | FT HEAD |  |  | FT HEAD | FT HEAD | FT HEAD | ** PEAK HR FLOW (MGD) ON MAX DAY: | 10.5597 | 10.5766 | 9.514 |  | 3.557 | 8.6787 | MGD |  | (1) Month: |  | MARCH |  | Year: | 2004 |  | Parameter | Units | STORET | Value |  |  | CONTACT | CHLORINATION | MG/L | MG/L | MG/L | MG/L | [6 empty] | A) | Sludge Treatment Provided: |  |  |  |  | B) | Sludge Dewater Processes |  |  |  | 3 | 32.544 | 8.54 | 8.67 | 6.34 | 0.13 | 7.75 | 79 | 1.5 | 136 | 11 | 6.4 | 6.5 | 1266 | 14.06 | 14 | 6.5 | 2330 | 80 | 0.78
| 2004 | FLOW | MAXIMUM | MAXIMUM | MINIMUM | FLOW | RAS | FLOW | INCHES | SULFATES | [5 empty] | 2004 | ABOVE | ABOVE | ABOVE |  |  | ABOVE | ABOVE | ABOVE | MAX SUSTAINED INJECTION PRESSURE: | 80.5 | 68.87 | 83.1 |  | 68.42 | 82.3 | PSIG |  | (2) Plant's DEP Identification Number: |  |  |  |  | 5006M02066 |  |  |  | Code |  | 1 | 34.923 | 0.7 |  | 55 | 90 | 1.6 | 8 | 6.5 |  |  |  |  | 0 |  |  | Aerobic Digestion | [5 empty] | Thickner |  |  | 4 | 32.86 | 8.33 | 8.4 | 7.4 | 0.13 | 7.58 | 60 | 2.2 | 136 | 6 | 6.4 | 6.5 | 1267 | 14.45 | 13 | 6.5 | 2390 | 80 | 0.73
|  | MGD | MGD | MGD | MGD | MGD |  | MGD | [8 empty] | NGVD | NGVD | NGVD |  |  | NGVD | NGVD | NGVD | MONTHLY AVG. INJECTION PRESSURE: | 46.4813 | 45.5084 | 46.8697 |  | 38.8348 | 43.3665 | PSIG |  | (3) Plant Name: |  |  |  | George T. Lohmeyer Regional Wastewater |  |  | (16) Monthly average daily flow | mgd | 050053 | 32.393 | 2 | 33.842 | 0.7 |  | 60 | 100 | 2 | 12 | 6.5 |  |  |  |  | 0 |  |  | Anaerobic Digestion | [5 empty] | DGA___X___Filter Press |  |  | 5 | 32.363 | 8.29 | 8.34 | 7.36 | 0.13 | 7.53 | 48 | 1.2 | 212 | 15 | 6.4 | 6.6 | 1267 | 14.82 | 17 | 6.5 | 2370 | 80 | 0.66
| 1 | 34.923 | 1.719 | 51.232 | 15.604 | 11.02 | 31.56% | 0.666 | 0 | 142.8 |  | 1 |  |  |  | 1 | 47.24 | 48.53 | 48.28 |  |  | 38.03 | 41.7 | 39.65 | *** MAX INJECTION PRESSURE PERMITTED: | 99 | 99 | 99 |  | 99 | 99 | PSIG |  |  |  |  | Treatment Facility |  |  |  | (17) Permitted capacity | mgd | - | 43 | 3 | 32.544 | 0.5 |  | 79 | 136 | 1.5 | 11 | 6.5 | 14 | 14.06 | 0.326 | 0.78 | 9 |  |  | Other | [5 empty] | Centrifuge Drying Beds, Bed #______ |  |  | 6 | 31.963 | 8.82 | 8.92 | 7.89 | 0.13 | 5.02 | 100.5 | 3.24 | 156 | 13 | 6.4 | 6.5 | 1149 | 12.67 | 12 | 6.4 | 2360 | 81 | 0.91
| 2 | 33.842 | 1.694 | 52.866 | 12.784 | 10.957 | 32.38% | 0.631 | 0 | 134.5 |  | 2 |  |  |  | 2 | 47.46 | 48.28 | 47.87 |  |  | 38.04 | 41.41 | 40.03 | ***NOTE: (INJECTION PRESSURE NOT TO EXCEED 66% TESTED PRESSURE | [8 empty] | (4) Plant Address: |  |  | 1765 S.E. 18th Street at |  |  |  | (18) Three-month average daily flow | mgd | - | 34.55 | 4 | 32.86 | 0.6 |  | 60 | 136 | 2.2 | 6 | 6.5 | 13 | 14.45 | 0.344 | 0.73 | 89 | [8 empty] | Heat Treatment__X__No Treatment |  |  | 7 | 31.38 | 8.53 | 6.03 | 7.58 | 0.13 | 7.66 | 157.2 | 3.62 | 298 | 11 | 6.4 | 6.5 | 1234 | 14.63 | 16 | 6.5 | 2250 | 81 | 0.82
| 3 | 32.544 | 1.651 | 51.008 | 5.222 | 10.993 | 33.78% | 0.685 | 0 | 136.5 |  | 3 |  |  |  | 3 | 48.05 | 48.33 | 48.19 |  |  | 41.27 | 41.55 | 41.46 | TESTED CASING PRESSURE DURING MIT | 150 | 150 | 150 |  | 150 | 150 | PSIG |  |  |  |  | Eisenhower Boulevard |  |  |  | (19) Percent of permitted capacity | % | - | 80.35% | 5 | 32.363 | 0.7 |  | 48 | 212 | 1.2 | 15 | 6.5 | 17 | 14.82 | 0.243 | 0.66 | 0 | [7 empty] | x | Other: |  |  | 8 | 31.59 | 8.05 | 8.1 | 7.14 | 0.13 | 7.26 | 99 | 2.8 | 80 | 11 | 6.3 | 6.5 | 1206 |  |  | 6.4 | 2330 | 81
| 4 | 32.86 | 1.671 | 49.311 | 12.592 | 11.275 | 34.31% | 0.666 | 0 | 129.3 |  | 4 |  |  |  | 4 | 48.11 | 48.38 | 48.25 |  |  | 41.38 | 41.6 | 41.49 | [9 empty] | (5) City: |  | Fort Lauderdale |  |  |  |  | (20) CBOD5 Effluent | mg/L | 080082 | 4.06 | 6 | 31.963 | 0.6 |  | 100.5 | 156 | 3.24 | 13 | 6.4 | 12 | 12.67 | 0.195 | 0.91 | 0 | [9 empty] | CLASS "AA" |  | 9 | 31.592 | 8.03 | 8.07 | 7.11 | 0.13 | 7.24 | 114 | 2.8 | 134 | 12 | 6.2 | 6.5 | 1210 |  |  | 6.4 | 2670 | 80
| 5 | 32.363 | 1.667 | 52.61 | 11.374 | 11.391 | 35.2% | 0.362 | 0 | 123.3 |  | 5 |  |  |  | 5 | 48.1 | 48.41 | 48.28 |  |  | 41.4 | 41.61 | 41.49 |  |  | MONITORING WELL DATA | [6 empty] | (6) County: |  | Broward |  |  |  |  | (21) CBOD5 Effluent | lbs/day | - | 1096.8388 | 7 | 31.38 | 0.8 |  | 157.2 | 298 | 3.62 | 11 | 6.5 | 16 | 14.63 | 0.216 | 0.82 | 0 | III. | Final Sludge Disposal: | [7 empty] | RMF-Azurix (Nutri-Cycle) |  | 10 | 31.801 | 8.08 | 8.08 | 7.15 | 0.12 | 7.27 | 109 | 3 | 168 | 15 | 6.2 | 6.6 | 1256 | 15.53 | 15 | 6.5 | 2680 | 80 | 0.95
| 6 | 31.963 | 1.688 | 51.585 | 12.528 | 10.804 | 33.8% | 0 | 0 | 124.3 |  | 6 |  |  |  | 6 | 48.14 | 48.43 | 48.29 |  |  | 41.45 | 41.61 | 41.49 |  | MW-1 | MW-2 | MW-3 |  | RMW-1 |  |  |  | (7) Phone Number: |  |  | (954) 523-1002 |  |  |  | (22) TSS Effluent | mg/L | 900201 | 12.3871 | 8 | 31.59 | 0.6 |  | 99 | 80 | 2.8 | 11 | 6.4 |  |  |  |  | 0 | A) | Liquid Sludge Disposal: | [9 empty] | 11 | 31.601 | 8.06 | 8.08 | 7.11 | 0.12 | 7.25 | 63 | 3.1 | 76 | 24 | 6.3 | 6.6 | 1272 | 15.41 | 14 | 6.5 | 2620 | 80 | 1.8
| 7 | 31.38 | 1.613 | 49.311 | 11.534 | 11.14 | 35.5% | 0.222 | 0 | 127.3 |  | 7 |  |  |  | 7 | 48.14 | 48.48 | 48.26 |  |  | 41.46 | 41.78 | 41.53 | PERMIT NUMBER | 0054569-142-UO | 0054569-142-UO | 0054569-142-UO |  | 0054569-142-UO |  |  |  | (8) Permit Number: |  |  | FLA041378 |  |  |  | (23) TSS Effluent | lbs/day | - | 3346.4653 | 9 | 31.592 | 0.6 |  | 114 | 134 | 2.8 | 12 | 6.4 |  |  |  |  | 0 |  | WEEK OF | MARCH | GALLONS | % SOLIDS |  |  | HAULERS |  |  | DISPOSAL SITE | 12 | 31.848 | 8.17 | 8.21 | 7.21 | 0.13 | 7.35 | 87 | 4.6 | 116 | 10 | 6.4 | 6.5 | 1290 | 15.32 | 13 | 6.5 | 2630 | 80 | 1.2
| 8 | 31.59 | 1.588 | 50.175 | 11.887 | 9.522 | 30.14% | 0.611 | 0 | 109.8 |  | 8 |  |  |  | 8 | 46.54 | 48.46 | 47.35 |  |  | 37.58 | 41.74 | 39.24 | UPPER MONITORING INTERVAL | 1288'-1320' | 1300'-1344' | 1300'-1349' |  | 1300'-1339' |  | Ft. bls. |  | (9) Plant Type: |  |  | Oxygen Activated Sludge |  |  |  | (24) Minimum pH |  | - | 6.1 | 10 | 31.801 | 0.6 |  | 109 | 168 | 3 | 15 | 6.5 | 15 | 15.53 | 0.24 | 0.95 | 0 | [11 empty] | 13 | 31.858 | 8.66 | 8.74 | 7.73 | 0.13 | 5.42 | 145 | 4.3 | 122 | 11 | 6.2 | 6.4 | 1274 | 14.59 | 15 | 6.4 | 2650 | 80 | 1.1
| 9 | 31.592 | 1.575 | 47.42 | 11.695 | 9.118 | 28.86% | 0.68 | 0 | 142 |  | 9 |  |  |  | 9 | 46.87 | 48.74 | 48.01 |  |  | 37.54 | 41.61 | 40.18 | MONTHLY MAX DAILY PRESSURE | 48.77 | 32.09 | 32.15 |  | 44.75 |  | FT. HEAD |  | (10) Test Site Identification Number: |  |  |  |  | 5006X10744 |  | (25) Maximum pH |  | - | 6.9 | 11 | 31.601 | 0.6 |  | 63 | 76 | 3.1 | 24 | 6.5 | 14 | 15.41 | 0.279 | 1.8 | 0 |  | FIRST THRU SEVENTH | [9 empty] | 14 | 32.025 | 9.11 | 9.28 | 6.71 | 0.13 | 5.35 | 108.9 | 3.8 | 110 | 12 | 6.4 | 6.5 | 1274 | 14.25 | 15 | 6.5 | 2830 | 80 | 1.1
| 10 | 31.801 | 1.577 | 47.388 | 6.888 | 8.175 | 25.71% | 0.736 | 0 | 140.8 |  | 10 |  |  |  | 10 | 48.31 | 48.68 | 48.5 |  |  | 41.45 | 41.7 | 41.56 | MONTHLY MIN DAILY PRESSURE | 46.4 | 26.89 | 19.15 |  | 42.48 |  | FT. HEAD |  | (11) Fecal Coliform Method | [6 empty] | (26) Total N | mg/L | 000600 | 15.2809 | 12 | 31.848 | 0.4 |  | 87 | 116 | 4.6 | 10 | 6.5 | 13 | 15.32 | 0.234 | 1.2 | 0 | [11 empty] | 15 | 32.993 | 7.99 | 8.06 | 7.01 | 5.79 | 3.23 | 105 | 4 | 116 | 9 | 6.1 | 6.5 | 1421 |  |  | 6.4 | 2840 | 81
| 11 | 31.601 | 1.538 | 47.228 | 12.752 | 8.528 | 26.99% | 0.724 | 0 | 137.5 |  | 11 |  |  |  | 11 | 48.2 | 48.51 | 48.36 |  |  | 41.42 | 41.64 | 41.5 | TDS (MONTHLY AVERAGE) | 7166 | 7113.2 | 7092 |  | 5408 |  | mg/l |  |  | XX | Membrane Filter |  |  |  |  | (27) TKN | mg/L | 000625 | 14.95 | 13 | 31.858 | 0 |  | 145 | 122 | 4.3 | 11 | 6.4 | 15 | 14.59 | 0.294 | 1.1 | 0 |  | EIGHT THRU FORTEENTH | [9 empty] | 16 | 32.778 | 7.75 | 7.78 | 6.69 | 10.07 | ER | 104 | 3.6 | 160 | 9 | 6.3 | 6.6 | 1320 |  |  | 6.5 | 2910 | 81
| 12 | 31.848 | 1.556 | 46.523 | 12.592 | 10.86 | 34.1% | 0.178 | 0 | 131 |  | 12 |  |  |  | 12 | 48.25 | 48.51 | 48.43 |  |  | 41.49 | 41.67 | 41.53 | CHLORIDE (MONTHLY AVERAGE) | 3840 | 3700 | 3760 |  | 3150 |  | mg/l |  |  |  | Most Probable Number |  |  |  |  | (28) Ammonia (NH3 - N) | mg/L | 000610 | 14.277 | 14 | 32.025 | 0.6 |  | 108.9 | 110 | 3.8 | 12 | 6.5 | 15 | 14.25 | 0.504 | 1.1 | 0 |  | FIFTHTEENTH THRU | [9 empty] | 17 | 32.612 | 6.92 | 8.15 | 6.98 | 10.39 | ER | 112 | 3.5 | 114 | 13 | 6.4 | 6.5 | 1323 | 14.35 | 16 | 6.5 | 2880 | 81 | 1
| 13 | 31.858 | 1.61 | 50.463 | 14.226 | 10.314 | 32.37% | 0 | 0 | 131 |  | 13 |  |  |  | 13 | 48.2 | 48.53 | 48.35 |  |  | 41.5 | 41.7 | 41.57 | AMMONIA-N (MONTHLY AVERAGE) | 0.8476 | 0.8462 | 0.8608 |  | 0.599 |  | mg/l |  | (12) Type of Effluent Disposal or Reclaimed Water Reuse | [6 empty] | (29) Nitrate | mg/L | 071850 | 0.3309 | 15 | 32.993 | 0.5 |  | 105 | 116 | 4 | 9 | 6.4 |  |  |  |  | 0 |  | TWENTY SECOND | [9 empty] | 18 | 32.716 | 8.02 | 8.08 | 6.96 | 9.17 | ER | 97 | 4 | 120 | 9 | 6.5 | 6.6 | 1298 | 14.94 | 13 | 6.6 | 2890 | 81 | 1.6
| 14 | 32.025 | 1.616 | 47.485 | 12.976 | 10.032 | 31.33% | 0.217 | 0.1 | 134.3 |  | 14 |  |  |  | 14 | 48.21 | 48.49 | 48.36 |  |  | 41.51 | 41.74 | 41.56 | TKN (MONTHLY AVERAGE) | 0.998 | 1.014 | 1.026 |  | 0.94 |  | mg/l |  |  |  | Deep Well Injection |  |  |  |  | (30) Total Phosphorus | mg/L | 000665 | 1.1915 | 16 | 32.778 | 0.5 |  | 104 | 160 | 3.6 | 9 | 6.5 |  |  |  |  | 0 |  | TWENTY THIRD THRU | [9 empty] | 19 | 32.551 | 7.11 | 8.12 | 7.04 | 9.4 | 0.76 | 118 | 3.7 | 120 | 11 | 6.4 | 6.5 | 1360 | 14.8 | 15 | 6.5 | 2890 | 81 | 1
| 15 | 32.993 | 1.692 | 49.407 | 14.386 | 11.811 | 35.8% | 0.683 | 0 | 131.5 |  | 15 |  |  |  | 15 | 46.4 | 48.53 | 47.41 |  |  | 37.25 | 41.72 | 38.98 | pH (MONTHLY AVERAGE) | 8.06 | 8.118 | 8.11 |  | 8.33 |  | Std units |  | (13) Limited Wet Wheather Discharge Activated | [6 empty] | (31) Minimum Chlorine Residual | mg/L | - | 0 | 17 | 32.612 | 0.7 |  | 112 | 114 | 3.5 | 13 | 6.5 | 16 | 14.35 | 0.559 | 1 | 18 |  | THIRTY FIRST | [9 empty] | 20 | 32.624 | 8.07 | 8.13 | 7.1 | 8.73 | ER | 152 | 5 | 128 | 10 | 6.3 | 6.5 | 1424 | 13.69 | 16 | 6.4 | 2900 | 81 | 1
| 16 | 32.778 | 1.677 | 49.952 | 14.578 | 13.609 | 41.52% | 0.629 | 0 | 143.5 |  | 16 |  |  |  | 16 | 46.89 | 48.77 | 48.07 |  |  | 37.27 | 41.78 | 40.19 | CONDUCTIVITY (MONTHLY AVERAGE) | 11848 | 11598 | 11690 |  | 8500 |  | umho/cm |  |  |  | YES |  | XX | Not Applicable |  | (32) Maximum Chlorine Residual | mg/L | - | 0.9 | 18 | 32.716 | 0.4 |  | 97 | 120 | 4 | 9 | 6.6 | 13 | 14.94 | 0.588 | 1.6 | 36 | [11 empty] | 21 | 32.208 | 6.48 | 7.97 | 6.91 | 10.19 | ER | 130 | 5.3 | 186 | 13 | 6.4 | 6.9 | 1412 | 12.98 | 15 | 6.5 | 2990 | 81 | 0.98
| 17 | 32.612 | 1.679 | 48.83 | 12.367 | 11.757 | 36.05% | 0.714 | 0 | 153.8 |  | 17 |  |  |  | 17 | 48.29 | 48.67 | 48.52 |  |  | 41.5 | 41.95 | 41.66 | FECAL COLIFORM (MONTHLY AVERAGE) | 0 | 0 | 0 |  | 0 |  | # col/100ml |  |  |  | NO |  |  |  |  | (33) Other Effluent Parameters |  |  |  | 19 | 32.551 | 0.4 |  | 118 | 120 | 3.7 | 11 | 6.5 | 15 | 14.8 | 0.228 | 1 | 3 | B) | Solid Sludge Hauled from Plant: | [9 empty] | 22 | 31.884 | 6.74 | 7.91 | 6.84 | 10.11 | ER | 119 | 4.7 | 114 | 17 | 6.1 | 6.5 | 1532 |  |  | 6.4 | 3080 | 81
| 18 | 32.716 | 1.666 | 50.816 | 13.809 | 11.909 | 36.4% | 0.666 | 0 | 134.8 |  | 18 |  |  |  | 18 | 48.23 | 48.53 | 48.42 |  |  | 41.49 | 41.72 | 41.56 | TEMPERATURE (MONTHLY AVERAGE) | 73.6 | 72.6 | 70.4 |  | 75 |  | deg. F | [12 empty] | 20 | 32.624 | 0.6 |  | 152 | 128 | 5 | 10 | 6.4 | 16 | 13.69 | 0.227 | 1 | 0 |  | WEEK OF | MARCH | TONS |  | % SOLIDS |  | HAULERS |  |  | DISPOSAL SITE | 23 | 32.466 | 9.27 | 3.49 | 8.1 | 7.77 | 2.78 | 86 | 5.4 | 134 | 11 | 6.3 | 6.6 | 1654 |  |  | 6.4 | 3230 | 80
| 19 | 32.551 | 1.71 | 49.311 | 12.207 | 11.987 | 36.83% | 0.323 | 0 | 139.8 |  | 19 |  |  |  | 19 | 48.19 | 48.5 | 48.35 |  |  | 41.48 | 41.68 | 41.54 | TOTAL PHOSPHOROUS (MONTHLY AVG.) | 0.01 | 0.01 | 0.01 |  | 0.01 |  | mg/l |  | (14) Cumulative Days of Wet Wheather Discharge | [10 empty] | 21 | 32.208 | 0.6 |  | 130 | 186 | 5.3 | 13 | 6.5 | 15 | 12.98 | 0.628 | 0.98 | 0 | [10 empty] | Nutri-Cylcle\CSLOL Inc. | 24 | 32.546 | 8.56 | 8.7 | 6.29 | 0.13 | 7.75 | 120 | 4.4 | 136 | 15 | 6.3 | 6.6 | 1370 | 14.79 | 17 | 6.5 | 3140 | 80 | 1.9
| 20 | 32.624 | 1.768 | 50.079 | 14.45 | 10.954 | 33.58% | 0 | 0 | 131.5 |  | 20 |  |  |  | 20 | 48.19 | 48.52 | 48.35 |  |  | 41.49 | 41.68 | 41.53 | SULFATE (MONTHLY AVERAGE) | 848.8 | 829.2 | 829.8 |  | 650 |  | mg/l |  |  |  | N/A | [8 empty] | 22 | 31.884 | 0.4 |  | 119 | 114 | 4.7 | 17 | 6.4 |  |  |  |  | 9 |  | FIRST THRU SEVENTH |  | 875 |  | 17.642 |  | AZURIX |  |  | Okeechobee, FL | 25 | 32.876 | 8.69 | 8.81 | 7.53 | 0.13 | 6.7 | 121 | 5.2 | 140 | 20 | 6.4 | 6.5 | 1502 | 14.69 | 16 | 6.5 | 3140 | 80 | 2.2
| 21 | 32.208 | 1.698 | 49.599 | 13.809 | 10.941 | 33.97% | 0.207 | 0 | 146.8 |  | 21 |  |  |  | 21 | 48.28 | 48.64 | 48.45 |  |  | 41.56 | 41.84 | 41.69 | C.O.D. (MONTHLY AVERAGE) | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! |  | mg/l |  | (15) Plant Staffing: | [10 empty] | 23 | 32.466 | 0.9 |  | 86 | 134 | 5.4 | 11 | 6.4 |  |  |  |  | 0 | [10 empty] | Nutri-Cylcle\CSLOL Inc. | 26 | 33.314 | 8.5 | 8.59 | 7.56 | 0.13 | 7.69 | 119 | 6.3 | 120 | 14 | 6.4 | 6.6 | 1451 | 14.37 | 18 | 6.5 | 3210 | 81 | 1.5
| 22 | 31.884 | 1.649 | 50.079 | 8.49 | 10.956 | 34.36% | 0.801 | 0 | 145.3 |  | 22 |  |  |  | 22 | 47.03 | 48.55 | 47.61 |  |  | 37.31 | 41.76 | 39.05 | IRON (MONTHLY AVERAGE) | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! |  | mg/l | [12 empty] | 24 | 32.546 | 0.4 |  | 120 | 136 | 4.4 | 15 | 6.5 | 17 | 14.79 | 0.272 | 1.9 | 0 |  | EIGHT THRU FORTEENTH |  | 775 |  | 18.312 |  | AZURIX |  |  | Okeechobee, FL | 27 | 32.973 | 6.85 | 8.96 | 7.84 | 0.13 | 7.94 | 204 | 8 | 2588 | 11 | 6.4 | 6.5 | 1434 | 13.05 | 15 | 6.5 | 3160 | 81 | 1.4
| 23 | 32.466 | 1.707 | 50.239 | 12.432 | 9.9 | 30.49% | 0.807 | 0 | 160.5 |  | 23 |  |  |  | 23 | 47.21 | 48.55 | 47.97 |  |  | 37.29 | 41.46 | 40.08 | SULFIDE (MONTHLY AVERAGE) | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! |  | mg/l |  |  | Day Shift Operator: |  |  | Class | "A" | Cert. No. | 4545 |  |  |  | 25 | 32.876 | 0.5 |  | 121 | 140 | 5.2 | 20 | 6.5 | 16 | 14.69 | 0.261 | 2.2 | 9 |  | FIFTHTEENTH THRU | [8 empty] | Nutri-Cylcle\CSLOL Inc. | 28 | 31.898 | 7.97 | 7.98 | 7.04 | 0.13 | 7.22 | 116 | 7 | 120 | 17 | 6.5 | 6.5 | 1521 | 12.15 | 14 | 6.5 | 2810 | 81 | 1.2
| 24 | 32.546 | 1.589 | 48.894 | 13.361 | 10.35 | 31.8% | 0.769 | 0 | 120.8 |  | 24 |  |  |  | 24 | 48.12 | 48.38 | 48.23 |  |  | 41.35 | 41.53 | 41.46 | LOWER MONITORING INTERVAL | 1449'-1557' | 1970'-2025' | 1970'-2027' |  | 1500'-1600' |  | Ft. bls | [12 empty] | 26 | 33.314 | 0.5 |  | 119 | 120 | 6.3 | 14 | 6.5 | 18 | 14.37 | 0.199 | 1.5 | 0 |  | TWENTY SECOND |  | 950 |  | 18.312 |  | AZURIX |  |  | Okeechobee, FL | 29 | 32.025 | 7.02 | 8.62 | 7.52 | 0.13 | 7.65 | 99 | 5 | 106 | 12 | 6.5 | 6.4 | 1460 |  |  | 6.4 | 2890 | 81
| 25 | 32.876 | 1.612 | 49.728 | 15.027 | 10.758 | 32.72% | 0.817 | 0.2 | 139.8 |  | 25 |  |  |  | 25 | 48.14 | 48.38 | 48.25 |  |  | 41.28 | 41.59 | 41.48 | MONTHLY MAX DAILY PRESSURE | 42.01 | 42.64 | 45.72 |  | 23.12 |  | FT. HEAD |  |  | Evening Shift Operator: |  |  | Class | "A" | Cert. No. | 4474 |  |  |  | 27 | 32.973 | 0 |  | 204 | 2588 | 8 | 11 | 6.5 | 15 | 13.05 | 0.215 | 1.4 | 750 |  | TWENTY THIRD THRU | [8 empty] | Nutri-Cylcle\CSLOL Inc. | 30 | 32.02 | 8.13 | 8.17 | 7.18 | 0.13 | 7.35 | 94 | 6 | 100 | 12 | 6.4 | 6.6 | 1471 |  |  | 6.5 | 3000 | 81
| 26 | 33.314 | 1.645 | 48.927 | 14.162 | 10.441 | 31.34% | 0.352 | 0.69 | 138 |  | 26 |  |  |  | 26 | 48.18 | 48.38 | 48.27 |  |  | 41.37 | 41.7 | 41.51 | MONTHLY MIN DAILY PRESSURE | 37.25 | 36.85 | 38.51 |  | 21 |  | FT. HEAD | [12 empty] | 28 | 31.898 | 0.6 |  | 116 | 120 | 7 | 17 | 6.5 | 14 | 12.15 | 0.566 | 1.2 | 0 |  | THIRTY FIRST |  | 950 |  | 18.8143 |  | AZURIX |  |  | Okeechobee, FL | 31 | 31.508 | 8.42 | 6.92 | 7.47 | 0.13 | 7.59 | 94 | 5 | 94 | 10 | 6.4 | 6.6 | 1502 | LS | LS | 6.5 | 3110 | 81 | LS
| 27 | 32.973 | 1.735 | 48.702 | 14.771 | 10.34 | 31.36% | 0 | 0.06 | 125 |  | 27 |  |  |  | 27 | 48.21 | 48.37 | 48.31 |  |  | 41.43 | 41.72 | 41.55 | TDS (MONTHLY AVERAGE) | 9413.4 | 30924 | 28168.4 |  | 26080 |  | mg/l |  |  | Night Shift Operator: |  |  | Class | "A" | Cert. No. | 3207 |  |  |  | 29 | 32.025 | 0.3 |  | 99 | 106 | 5 | 12 | 6.4 |  |  |  |  | 0 | C) | Monthly quantities of solid sludge stockpiled at plant.Solid Sludge Hauled from Plant: | [9 empty] | TOT | 1004.182 | 249.76 | 250.35 | 225.15 | 84.46 | 165.49 | 3275.6 | 125.86 | 6530 | 384 | 197 | 202.6 | 41932 | 285.54 | 299 | 200.7 | 85940 | 2495 | 23.83
| 28 | 31.898 | 1.579 | 49.087 | 14.707 | 11.27 | 35.33% | 0.213 | 0 | 143.5 |  | 28 |  |  |  | 28 | 48.22 | 48.4 | 48.34 |  |  | 41.58 | 41.85 | 41.65 | CHLORIDE (MONTHLY AVERAGE) | 5120 | 17640 | 16200 |  | 17200 |  | mg/l | [12 empty] | 30 | 32.02 | 0.4 |  | 94 | 100 | 6 | 12 | 6.5 |  |  |  |  | 0 |  | 1) | Additions |  |  | Cubic Yards | [5 empty] | AVG | 32.393 | 8.0568 | 8.0758 | 7.2629 | 2.7245 | 6.6196 | 105.6645 | 4.06 | 210.6452 | 12.3871 | 6.3548 | 6.5355 | 1352.6452 | 14.277 | 14.95 | 6.4742 | 2772.2581 | 80.4839 | 1.1915
| 29 | 32.025 | 1.573 | 47.549 | 13.008 | 10.411 | 32.51% | 0.496 | 0.01 | 143 |  | 29 |  |  |  | 29 | 46.8 | 48.43 | 47.45 |  |  | 37.41 | 41.75 | 39.07 | AMMONIA-N (MONTHLY AVERAGE) | 9.56 | 1.358 | 2.41 |  | 0.238 |  | mg/l |  |  | Lead Operator:_________________________________ | [9 empty] | 31 | 31.508 | 0.5 |  | 94 | 94 | 5 | 10 | 6.5 | LS | LS | LS | LS | 0 | [5 empty] | Tons | [5 empty] | MAX | 34.923 | 9.27 | 9.48 | 8.33 | 10.39 | 8.35 | 204 | 8 | 2588 | 24 | 6.5 | 6.9 | 1654 | 15.53 | 18 | 6.6 | 3230 | 81 | 2.2
| 30 | 32.02 | 1.579 | 48.446 | 13.809 | 10.061 | 31.42% | 0.71 | 0 | 148 |  | 30 |  |  |  | 30 | 47.23 | 48.41 | 47.94 |  |  | 37.39 | 41.79 | 39.98 | TKN (MONTHLY AVERAGE) | 9.74 | 2.28 | 2.94 |  | 0.77 |  | mg/l | [5 empty] | Signature |  | Cert. No. |  |  |  |  | Lead Operator : This is to certify that I am familar with the information contained on this report and that to the best of | [14 empty] | 2) | Removals |  |  | Cubic Yards | [5 empty] | MIN | 31.38 | 6.48 | 3.49 | 6.29 | 0.12 | 0.76 | 48 | 1.2 | 76 | 6 | 6.1 | 6.4 | 1149 | 12.15 | 12 | 6.4 | 2250 | 79 | 0.66
| 31 | 31.508 | 1.556 | 46.299 | 13.04 | 12.175 | 38.64% | 0.755 | 0 | 155.6 |  | 31 |  |  |  | 31 | 48.25 | 48.52 | 48.41 |  |  | 41.41 | 42.01 | 41.67 | pH (MONTHLY AVERAGE) | 7.448 | 7.492 | 7.484 |  | 7.51 |  | Std units | [12 empty] | my knowledge and belief, this information is true, complete and accuate. | [16 empty] | X |  | Tons | [6 empty] | item #1 | 10.5597 | 10.5766 | 9.514 | 3.557 | 8.6787 | MAX HOURLY FLOW (MG) = |  |  |  | 1.768 | ON THE | 20 | DAY OF THIS MONTH
| TOTAL | 1004.182 | 50.877 | 1530.549 | 393.067 | 333.759 |  | 15.32 | 1.06 | 4245.6 | [5 empty] | TOTAL | 1481.68 | 1503.29 | 1493.13 |  |  | 1245.38 | 1292.59 | 1268.93 | CONDUCTIVITY (MONTHLY AVERAGE) | 15714 | 46000 | 42340 |  | 38000 |  | umho/cm | [33 empty] | Signature |  |  |  |  | item #2 | 46.4813 | 45.5084 | 46.8697 | 38.8348 | 43.3665
| AVERAGE | 32.393 | 1.6412 | 49.3725 | 12.6796 | 10.7664 | 33.24% | 0.56741 | 0.034194 | 136.9548 | [5 empty] | AVERAGE | 47.7961 | 48.4932 | 48.1655 |  |  | 40.1735 | 41.6965 | 40.9332 | FECAL COLIFORM (MONTHLY AVERAGE) | 0 | 0 | 0 |  | 0 |  | # col/100ml | [12 empty] | Signed: ____________________________ Date: ___________________ | [20 empty] | Title |  |  |  |  | item #3 | 35.5 | 36 | 36.1 | 35.6 | 34.5
[16 empty] | MAXIMUM | 48.31 | 48.77 | 48.52 |  |  | 41.58 | 42.01 | 41.69 | TEMPERATURE (MONTHLY AVERAGE) | 73 | 70.8 | 69.4 |  | 74 |  | deg. F | [33 empty] | Date |  |  |  | item #1 | =monthly maximum of the daily flows (MG), with peakhour flow (MGD) on the day of the month with maximum flow = | [14 empty] | 1.768 | MG/hour multiplied by
[16 empty] | MINIMUM | 46.4 | 48.28 | 47.35 |  |  | 37.25 | 41.41 | 38.98 | TOTAL PHOSPHOROUS (MONTHLY AVG.) | 0.01 | 0.01 | 0.0106 |  | 0.01 |  | mg/l | [12 empty] | Name: Michael A. Just | [14 empty] | * Sludge Reports should be submitted along with the monthly operating reports to Broward County Department | [10 empty] | the % of average % of TOTAL RAW FLOW to each Injection well.
[25 empty] | SULFATE (MONTHLY AVERAGE) | 783.6 | 2554 | 2444 |  | 1550 |  | mg/l | [27 empty] | of Natural Resource Protection, 218 S. W. 1st Avenue, Fort Lauderdale, Florida 33301 | [9 empty] | item #2 | =monthly average injection well pressure at injection well (psig)
[25 empty] | C.O.D. (MONTHLY AVERAGE) | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! |  | mg/l | [12 empty] | Company Name: City of Fort Lauderdale Telephone No. (954) 523-1002 | [24 empty] | item #3 | =monthly wellhead pressure with no flow (shut-in pressure,psig)
[25 empty] | IRON (MONTHLY AVERAGE) | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! |  | mg/l | [37 empty] | PLANT STAFFING
[5 empty] | PAGE 2 | [19 empty] | SULFIDE (MONTHLY AVERAGE) | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! |  | mg/l | [37 empty] | Day Shift Operator |  |  | Class: | "A" | Certificate No. | 4545 | Name: |  | McGEARY, J.
[70 empty] | Evening Shift Operator |  |  | Class: | "A" | Certificate No. | 4474 | Name: |  | BAYLER, J.
[20 empty] | PAGE 20 | [49 empty] | Night Shift Operator |  |  | Class: | "A" | Certificate No. | 3207 | Name: |  | HOSTNICK, N.
[70 empty] | Lead Operator |  |  | Class: | "A" | Certificate No. | 2769 | Name: |  | JUST, M.
[28 empty] | page 28 | [41 empty] | Type of Effluent Disposal or Reclaimed Water Reuse: |  |  |  |  | DEEPWELL INJECTION
[70 empty] | Permited Wet Weather Discharge Activated: |  |  |  | YES: |  | NO: |  |  | Not Applicable |  | X
If Yes, cumulative days of wet weather:
Attach additional sheets if necessary to list all certified operators. See page 1 "COVER PAGE" of supplental attachements.
DEP form 62-620.910(10), effective November 29, 1994
[19 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [46 empty] | Department of Natural Resource Protection
[5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [13 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [46 empty] | Division of Pollution Prevention and Remediation Programs
[5 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [13 empty] | MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING | [49 empty] | 218 S. W. 1st Avenue
[5 empty] | MONTHLY OPERATIONAL REPORT | [13 empty] | MONITORING WELL TWO |  |  |  | 1/07/04 thru 1/06/09 | [38 empty] | SLUDGE HAULERS MONTHLY REPORT | [6 empty] | Fort Lauderdale, FL 33301
[5 empty] | INFLUENT DATA | [11 empty] | MW-2 | I.D. #: 5066A11308 & 09 |  |  | PERMIT # 0054569-142-UO | [40 empty] | BROWARD COUNTY CODE SECTION 27-356 (d)(4)(1) | [5 empty] | Tel. No. (954) 523-1002
| RUN DATE | [14 empty] | RUN DATE | [51 empty] | *FAX (954) 519-1245
| 2026-07-30 | [14 empty] | 2026-07-30 |  | UPPER MONITOR ZONE |  |  |  |  | LOWER MONITOR ZONE
[17 empty] | MIN | MAX | AVG |  |  | MIN | MAX | AVG | [34 empty] | Plant Name: | GEORGE T. LOHMEYER WASTEWATER TREATMENT FACILITY
| MARCH | RAW | RAW TSS | RAW SS | RAW | RAW | RAW | RAW | RAW | RAW | EFF |  |  |  |  | MARCH | FT HEAD | FT HEAD | FT HEAD |  |  | FT HEAD | FT HEAD | FT HEAD | [34 empty] | Address: | 1765 S.E. 18th Street at Eisenhower Boulevard | [6 empty] | MONTH: | MARCH
| 2004 | CBOD | TOTAL | FIXED | COD | pH | CL_ | ALK. | H2S | TEMP.(F) | SULFATES |  |  |  |  | 2004 | ABOVE | ABOVE | ABOVE |  |  | ABOVE | ABOVE | ABOVE | [34 empty] | Phone: | (954) 523-1002 * FAX (954) 468-1577 | [6 empty] | YEAR: | 2004
[17 empty] | NGVD | NGVD | NGVD |  |  | NGVD | NGVD | NGVD
| 1 | 55 | 90 | 14 |  | 7 | 590 | 216 | 6 | 77 | 92.8 |  |  |  |  | 1 | 26.97 | 30.77 | 29.03 |  |  | 38.48 | 42.54 | 40.26 | [34 empty] | a) | WEEK OF | MARCH |  | Type of Sludge |  |  | Disopsal Site |  |  | Cubic Yards
| 2 | 60 | 100 | 18 |  | 7 | 610 | 206 | 6 | 77 | 111.3 |  |  |  |  | 2 | 26.97 | 30.94 | 29.17 |  |  | 36.85 | 42.04 | 40.53
| 3 | 79 | 136 | 20 | 396 | 7 | 620 | 206 | 6 | 77 | 107.8 |  |  |  |  | 3 | 30.22 | 31.34 | 30.68 |  |  | 41.97 | 42.22 | 42.03 | [35 empty] | FIRST THRU SEVENTH |  |  | GRIT |  |  | Central Landfill |  |  | 10
| 4 | 60 | 136 | 22 | 365 | 7 | 620 | 206 | 6 | 78 | 109.8 |  |  |  |  | 4 | 30.46 | 31.62 | 30.9 |  |  | 42.14 | 42.33 | 42.3
| 5 | 48 | 212 | 34 | 352 | 7 | 570 | 208 | 5 | 78 | 110.3 |  |  |  |  | 5 | 30.58 | 31.8 | 31.1 |  |  | 42.2 | 42.4 | 42.36 | [35 empty] | EIGHT THRU FORTEENTH |  |  | GRIT |  |  | Central Landfill |  |  | 10
| 6 | 100.5 | 156 | 20 | 290 | 7 | 600 | 210 | 6 | 78 | 109.3 |  |  |  |  | 6 | 30.72 | 31.82 | 31.16 |  |  | 42.28 | 42.45 | 42.41 | [35 empty] | FIFTHTEENTH THRU
| 7 | 157.2 | 298 | 66 | 349 | 7 | 510 | 204 | 6 | 78 | 110 |  |  |  |  | 7 | 30.64 | 32.09 | 31.19 |  |  | 42.31 | 42.51 | 42.45 | [35 empty] | TWENTY SECOND |  |  | GRIT |  |  | Central Landfill |  |  | 10
| 8 | 99 | 80 | 12 |  | 7 | 600 | 220 | 6 | 78 | 109.8 |  |  |  |  | 8 | 27.47 | 30.98 | 29.47 |  |  | 38.72 | 42.5 | 40.29 | [35 empty] | TWENTY THIRD THRU
| 9 | 114 | 134 | 24 |  | 7 | 630 | 216 | 7 | 78 | 117.8 |  |  |  |  | 9 | 26.89 | 31.22 | 29.51 |  |  | 38.62 | 42.32 | 40.99 | [35 empty] | THIRTY FIRST |  |  | GRIT |  |  | Central Landfill |  |  | 10
| 10 | 109 | 168 | 32 | 360 | 7 | 770 | 220 | 6 | 78 | 112.8 |  |  |  |  | 10 | 29.67 | 31.28 | 30.32 |  |  | 42.25 | 42.35 | 42.35
| 11 | 63 | 76 | 30 | 386 | 7.1 | 730 | 228 | 6 | 78 | 109.5 |  |  |  |  | 11 | 29.46 | 31.18 | 30.36 |  |  | 42.24 | 42.4 | 42.37 | [34 empty] | b) | WEEK OF | MARCH |  | Type of Sludge |  |  | Disopsal Site |  |  | Cubic Yards
| 12 | 87 | 116 | 16 | 349 | 7 | 670 | 222 | 6 | 78 | 115.3 |  |  |  |  | 12 | 30.22 | 31.43 | 30.68 |  |  | 42.33 | 42.45 | 42.43
| 13 | 145 | 122 | 22 | 378 | 7.1 | 630 | 220 | 7 | 78 | 118.3 |  |  |  |  | 13 | 30.5 | 31.46 | 30.82 |  |  | 42.36 | 42.5 | 42.49 | [35 empty] | FIRST THRU SEVENTH |  |  | RAGS |  |  | Central Landfill |  |  | 10
| 14 | 108.9 | 110 | 20 | 452 | 7 | 750 | 214 | 7 | 78 | 120.8 |  |  |  |  | 14 | 30.48 | 31.41 | 30.86 |  |  | 42.39 | 42.53 | 42.5
| 15 | 105 | 116 | 20 |  | 7 | 670 | 214 | 6 | 78 | 124.3 |  |  |  |  | 15 | 26.9 | 31.04 | 28.78 |  |  | 37.58 | 42.61 | 39.4 | [35 empty] | EIGHT THRU FORTEENTH |  |  | RAGS |  |  | Central Landfill |  |  | 10
| 16 | 104 | 160 | 28 |  | 7 | 770 | 216 | 6 | 79 | 125.3 |  |  |  |  | 16 | 26.92 | 31.37 | 29.57 |  |  | 37.59 | 42.34 | 40.73 | [35 empty] | FIFTHTEENTH THRU
| 17 | 112 | 114 | 22 | 360 | 7 | 830 | 218 | 6 | 79 | 119.3 |  |  |  |  | 17 | 30.26 | 31.78 | 30.69 |  |  | 42.22 | 42.46 | 42.39 | [35 empty] | TWENTY SECOND |  |  | RAGS |  |  | Central Landfill |  |  | 10
| 18 | 97 | 120 | 22 | 306 | 7 | 770 | 218 | 6 | 78 | 122.3 |  |  |  |  | 18 | 30.26 | 31.21 | 30.66 |  |  | 42.28 | 42.42 | 42.4 | [35 empty] | TWENTY THIRD THRU
| 19 | 118 | 120 | 20 | 374 | 7 | 700 | 220 | 7 | 78 | 123.5 |  |  |  |  | 19 | 30.25 | 31.16 | 30.68 |  |  | 42.28 | 42.45 | 42.41 | [35 empty] | THIRTY FIRST |  |  | RAGS |  |  | Central Landfill |  |  | 10
| 20 | 152 | 128 | 22 | 323 | 7 | 790 | 220 | 6 | 78 | 124 |  |  |  |  | 20 | 30.24 | 31.14 | 30.71 |  |  | 42.32 | 42.51 | 42.43 | [35 empty] | BCSR = Broward County Septage Receiving
| 21 | 130 | 186 | 38 | 362 | 7 | 770 | 216 | 7 | 79 | 125 |  |  |  |  | 21 | 30.48 | 31.55 | 30.99 |  |  | 42.42 | 42.64 | 42.49 | [34 empty] | c) | WEEK OF | MARCH |  | Type of Sludge |  |  | Disopsal Site |  |  | Gallons
| 22 | 119 | 114 | 20 |  | 7 | 810 | 216 | 7 | 79 | 131.3 |  |  |  |  | 22 | 27.33 | 30.7 | 29.28 |  |  | 37.6 | 42.62 | 39.28
| 23 | 86 | 134 | 14 |  | 7 | 800 | 214 | 6 | 78 | 130 |  |  |  |  | 23 | 27.2 | 30.69 | 29.39 |  |  | 36.92 | 42.15 | 40.54 | [35 empty] | FIRST THRU SEVENTH |  |  | VAC/Plastic & Rags |  |  | BCSR |  |  | 0
| 24 | 120 | 136 | 26 | 400 | 7 | 600 | 218 | 7 | 78 | 131.3 |  |  |  |  | 24 | 30.06 | 30.76 | 30.39 |  |  | 42.13 | 42.27 | 42.15
| 25 | 121 | 140 | 28 | 332 | 7 | 750 | 218 | 7 | 77 | 134.8 |  |  |  |  | 25 | 29.91 | 30.94 | 30.41 |  |  | 42.23 | 42.35 | 42.3 | [35 empty] | EIGHT THRU FORTEENTH |  |  | VAC/Plastic & Rags |  |  | BCSR |  |  | 4500
| 26 | 119 | 120 | 22 | 404 | 7 | 680 | 220 | 6 | 78 | 126 |  |  |  |  | 26 | 30.09 | 31.26 | 30.62 |  |  | 42.32 | 42.4 | 42.4 | [35 empty] | FIFTHTEENTH THRU
| 27 | 204 | 2588 | 976 | 682 | 7 | 840 | 250 | 5 | 79 | 132.5 |  |  |  |  | 27 | 30.25 | 31.38 | 30.74 |  |  | 42.37 | 42.45 | 42.46 | [35 empty] | TWENTY SECOND |  |  | VAC/Plastic & Rags |  |  | BSCR |  |  | 0
| 28 | 116 | 120 | 22 | 368 | 7.2 | 810 | 220 | 7 | 79 | 128.5 |  |  |  |  | 28 | 30.46 | 31.56 | 30.89 |  |  | 42.44 | 42.52 | 42.5 | [35 empty] | TWENTY THIRD THRU
| 29 | 99 | 106 | 16 |  | 7 | 770 | 208 | 6 | 77 | 132.3 |  |  |  |  | 29 | 27.41 | 30.78 | 29.09 |  |  | 40.28 | 42.57 | 41.22 | [35 empty] | THIRTY FIRST |  |  | VAC/Plastic & Rags |  |  | BSCR |  |  | 0
| 30 | 94 | 100 | 16 |  | 7 | 730 | 202 | 6 | 77 | 127.5 |  |  |  |  | 30 | 26.97 | 30.88 | 29.19 |  |  | 40.25 | 42.29 | 41.47 | [34 empty] | TOTALS
| 31 | 94 | 94 | 14 | 337 | 7 | 810 | 212 | 5 | 78 | 135.5 |  |  |  |  | 31 | 29.77 | 31.75 | 30.65 |  |  | 42.27 | 42.56 | 42.44 | [35 empty] | a) | 40 | cu.yds |  | GRIT |  | Signature
| TOTAL | 3275.6 | 6530 | 1676 | 7925 | 217.4 | 21800 | 6696 | 192 | 2418 | 3729 |  |  |  |  | TOTAL | 906.01 | 969.29 | 937.98 |  |  | 1270.64 | 1315.15 | 1294.77 | [35 empty] | b) | 40 | cu.yds |  | RAGS |  | Title
| AVERAGE | 105.6645 | 210.6452 | 54.0645 | 377.381 | 7.0129 | 703.2258 | 216 | 6.1935 | 78 | 120.2903 |  |  |  |  | AVERAGE | 29.2261 | 31.2674 | 30.2574 |  |  | 40.9884 | 42.4242 | 41.7668 | [35 empty] | c) | 4500 | gal. |  | VAC/Plastic & Rags |  | Date
[16 empty] | MAXIMUM | 30.72 | 32.09 | 31.19 |  |  | 42.44 | 42.64 | 42.5
[16 empty] | MINIMUM | 26.89 | 30.69 | 28.78 |  |  | 36.85 | 42.04 | 39.28 | [35 empty] | * Sludge Reports should be submitted along with the monthly operating reports to Broward County Department
of Natural Resource Protection, 218 S. W. 1st Avenue, Fort Lauderdale, Florida 33301
PAGE 3
PAGE 21
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
[5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [13 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
[5 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [13 empty] | MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
[5 empty] | MONTHLY OPERATIONAL REPORT | [13 empty] | MONITORING WELL THREE |  |  |  | 1/07/04 thru 1/06/09
[5 empty] | EFFLUENT DATA PART 1 | [11 empty] | MW-3 | I.D. #: 5066A11310 |  |  | PERMIT # 0054569-142-UO
RUN DATE
[16 empty] | 2026-07-30 |  | UPPER MONITOR ZONE |  |  |  |  | LOWER MONITOR ZONE
| RUN DATE | [15 empty] | MIN | MAX | AVG |  |  | MIN | MAX | AVG
| 2026-07-30 | [14 empty] | MARCH | FT HEAD | FT HEAD | FT HEAD |  |  | FT HEAD | FT HEAD | FT HEAD
[14 empty] | BOD | TSS | 2004 | ABOVE | ABOVE | ABOVE |  |  | ABOVE | ABOVE | ABOVE
| MARCH | EFFLUENT | EFFL. TSS | EFFL. SS | EFFLUENT | EFFL. | EFFL. | EFFL. | EFFL. | EFFL. | TDS |  |  | MONTHLY AVG OVER 30 | MONTHLY AVG OVER 30 |  | NGVD | NGVD | NGVD |  |  | NGVD | NGVD | NGVD
| 2004 | CBOD | TOTAL | FIXED | COD | CL_ | ALK. | TURB. | COND. | TEMP.(F) |  |  |  | 0 | 0 | 1 | 23.25 | 31.68 | 26.93 |  |  | 40.57 | 45.67 | 42.79
[14 empty] | WEKKLY OVER 45 | WEKKLY OVER 45 | 2 | 23.19 | 31.37 | 27.94 |  |  | 40.57 | 45.11 | 43.17
| 1 | 1.6 | 8 | 1 |  | 570 | 190 | 5.92 | 2390 | 79 | 1263 | 1 |  | 0 | 0 | 3 | 31.27 | 31.65 | 31.49 |  |  | 45.03 | 45.3 | 45.22
| 2 | 2 | 12 | 2 |  | 620 | 192 | 7.26 | 2370 | 79 | 1249 | 1 |  | SINGLE DAY OVER 60 | SINGLE DAY OVER 60 | 4 | 31.51 | 31.79 | 31.7 |  |  | 45.22 | 45.43 | 45.38
| 3 | 1.5 | 11 | 2 | 52.3 | 610 | 192 | 6.2 | 2330 | 80 | 1266 | 1 |  | 0 | 0 | 5 | 31.59 | 31.88 | 31.78 |  |  | 45.29 | 45.49 | 45.46
| 4 | 2.2 | 6 | 0 | 46.6 | 610 | 190 | 5.19 | 2390 | 80 | 1267 | 1 |  | 0 | 0 | 6 | 31.67 | 31.93 | 31.81 |  |  | 45.39 | 45.55 | 45.48
| 5 | 1.2 | 15 | 2 | 46.7 | 660 | 196 | 5.22 | 2370 | 80 | 1267 | 1 |  |  |  | 7 | 31.71 | 32 | 31.82 |  |  | 45.43 | 45.6 | 45.49
| 6 | 3.24 | 13 | 1 | 40.9 | 600 | 196 | 5.47 | 2360 | 81 | 1149 | 1 |  |  |  | 8 | 24.79 | 31.95 | 27.59 |  |  | 40.93 | 45.6 | 42.78
| 7 | 3.62 | 11 | 1 | 54.8 | 610 | 190 | 5.57 | 2250 | 81 | 1234 | 1 | 2.1943 | 2.1943 | 10.8571 | 9 | 24.55 | 31.95 | 29.34 |  |  | 40.88 | 45.38 | 43.81
| 8 | 2.8 | 11 | 2 |  | 580 | 194 | 7.34 | 2330 | 81 | 1206 | 1 |  | 2.3657 | 11.2857 | 10 | 31.8 | 31.98 | 31.92 |  |  | 45.33 | 45.41 | 45.44
| 9 | 2.8 | 12 | 2 |  | 650 | 190 | 6.51 | 2670 | 80 | 1210 | 1 |  | 2.48 | 11.2857 | 11 | 31.75 | 31.99 | 31.9 |  |  | 45.33 | 45.46 | 45.42
| 10 | 3 | 15 | 2 | 40.3 | 570 | 190 | 7.18 | 2680 | 80 | 1256 | 1 |  | 2.6943 | 11.8571 | 12 | 31.84 | 32.05 | 31.98 |  |  | 45.43 | 45.54 | 45.5
| 11 | 3.1 | 24 | 9 | 58.4 | 640 | 188 | 6.75 | 2620 | 80 | 1272 | 1 |  | 2.8229 | 14.4286 | 13 | 31.86 | 32.09 | 32 |  |  | 45.46 | 45.6 | 45.52
| 12 | 4.6 | 10 | 2 | 52.8 | 660 | 190 | 6.83 | 2630 | 80 | 1290 | 1 |  | 3.3086 | 13.7143 | 14 | 31.9 | 32.11 | 32 |  |  | 45.51 | 45.65 | 45.53
| 13 | 4.3 | 11 | 2 | 50.3 | 660 | 190 | 6.74 | 2650 | 80 | 1274 | 1 |  | 3.46 | 13.4286 | 15 | 19.56 | 32.15 | 23.94 |  |  | 38.51 | 45.7 | 41.02
| 14 | 3.8 | 12 | 2 | 53.6 | 760 | 192 | 6.73 | 2830 | 80 | 1274 | 1 | 3.4857 | 3.4857 | 13.5714 | 16 | 19.56 | 31.42 | 27.52 |  |  | 38.53 | 45.39 | 43.19
| 15 | 4 | 9 | 1 |  | 810 | 198 | 5.94 | 2840 | 81 | 1421 | 1 |  | 3.6571 | 13.2857 | 17 | 31.27 | 31.61 | 31.47 |  |  | 45.28 | 45.53 | 45.45
| 16 | 3.6 | 9 | 1 |  | 710 | 196 | 5.19 | 2910 | 81 | 1320 | 1 |  | 3.7714 | 12.8571 | 18 | 31.36 | 31.58 | 31.48 |  |  | 45.35 | 45.5 | 45.46
| 17 | 3.5 | 13 | 2 | 49.8 | 720 | 194 | 5.72 | 2880 | 81 | 1323 | 1 |  | 3.8429 | 12.5714 | 19 | 31.35 | 31.62 | 31.48 |  |  | 45.36 | 45.52 | 45.48
| 18 | 4 | 9 | 1 | 44.8 | 730 | 196 | 5.91 | 2890 | 81 | 1298 | 1 |  | 3.9714 | 10.4286 | 20 | 31.41 | 31.69 | 31.49 |  |  | 45.41 | 45.59 | 45.49
| 19 | 3.7 | 11 | 2 | 52.4 | 750 | 194 | 5.67 | 2890 | 81 | 1360 | 1 |  | 3.8429 | 10.5714 | 21 | 31.52 | 31.83 | 31.72 |  |  | 45.52 | 45.72 | 45.57
| 20 | 5 | 10 | 2 | 47.8 | 760 | 196 | 5.86 | 2900 | 81 | 1424 | 1 |  | 3.9429 | 10.4286 | 22 | 20.6 | 31.79 | 24.41 |  |  | 39.41 | 45.71 | 41.61
| 21 | 5.3 | 13 | 3 | 59.4 | 760 | 196 | 7.37 | 2990 | 81 | 1412 | 1 | 4.1571 | 4.1571 | 10.5714 | 23 | 20.44 | 31.26 | 27.58 |  |  | 39.36 | 45.17 | 43.16
| 22 | 4.7 | 17 | 4 |  | 820 | 196 | 9.03 | 3080 | 81 | 1532 | 1 |  | 4.2571 | 11.7143 | 24 | 31.15 | 31.42 | 31.27 |  |  | 45.17 | 45.31 | 45.19
| 23 | 5.4 | 11 | 2 |  | 850 | 196 | 7.3 | 3230 | 80 | 1654 | 1 |  | 4.5143 | 12 | 25 | 31.3 | 31.49 | 31.4 |  |  | 45.3 | 45.41 | 45.39
| 24 | 4.4 | 15 | 3 | 55.9 | 800 | 198 | 8.14 | 3140 | 80 | 1370 | 1 |  | 4.6429 | 12.2857 | 26 | 31.36 | 31.52 | 31.47 |  |  | 45.4 | 45.48 | 45.48
| 25 | 5.2 | 20 | 5 | 73.8 | 830 | 200 | 9.02 | 3140 | 80 | 1502 | 1 |  | 4.8143 | 13.8571 | 27 | 31.42 | 31.57 | 31.49 |  |  | 45.46 | 45.55 | 45.5
| 26 | 6.3 | 14 | 3 | 76.8 | 770 | 198 | 8.63 | 3210 | 81 | 1451 | 1 |  | 5.1857 | 14.2857 | 28 | 31.47 | 31.62 | 31.52 |  |  | 45.53 | 45.65 | 45.52
| 27 | 8 | 11 | 2 | 76.9 | 750 | 196 | 7.76 | 3160 | 81 | 1434 | 1 |  | 5.6143 | 14.4286 | 29 | 19.2 | 31.65 | 23.68 |  |  | 41.36 | 45.68 | 43
| 28 | 7 | 17 | 5 | 67.2 | 520 | 174 | 7.43 | 2810 | 81 | 1521 | 1 |  | 5.8571 | 15 | 30 | 19.15 | 31.07 | 26.4 |  |  | 41.39 | 45.22 | 43.64
| 29 | 5 | 12 | 3 |  | 730 | 186 | 7.4 | 2890 | 81 | 1460 | 1 |  | 5.9 | 14.2857 | 31 | 31.07 | 31.48 | 31.34 |  |  | 45.2 | 45.53 | 45.39
| 30 | 6 | 12 | 2 |  | 770 | 192 | 8.03 | 3000 | 81 | 1471 | 1 |  | 5.9857 | 14.4286 | TOTAL | 875.87 | 983.19 | 929.86 |  |  | 1353.91 | 1410.45 | 1382.53
| 31 | 5 | 10 | 2 | 63.4 | 820 | 194 | 6.41 | 3110 | 81 | 1502 | 1 | 5.7 | 6.0714 | 13.7143 | AVERAGE | 28.2539 | 31.7158 | 29.9955 |  |  | 43.6745 | 45.4984 | 44.5977
| TOTAL | 125.86 | 384 | 73 | 1164.9 | 21700 | 5980 | 209.72 | 85940 | 2495 | 41932 |  |  |  |  | MAXIMUM | 31.9 | 32.15 | 32 |  |  | 45.53 | 45.72 | 45.57
| AVERAGE | 4.06 | 12.3871 | 2.4333 | 55.4714 | 700 | 192.9032 | 6.7652 | 2772.2581 | 80.4839 | 1352.6452 |  |  | 4.1136 | 12.6857 | MINIMUM | 19.15 | 31.07 | 23.68 |  |  | 38.51 | 45.11 | 41.02
| MAXIMUM | 8 | 24
[5 empty] | PAGE 4 | [14 empty] | PAGE 22
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
[5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [13 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
[5 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [13 empty] | MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
[5 empty] | MONTHLY OPERATIONAL REPORT | [13 empty] | REGIONAL MONITORING WELL ONE
[5 empty] | EFFLUENT DATA PART 2 | [13 empty] | RMW-1 |  |  |  | 1/07/04 thru 1/06/09
[16 empty] | RUN DATE |  |  |  |  | PERMIT # 0054569-142-UO
[16 empty] | 2026-07-30 |  | UPPER MONITOR ZONE |  |  |  |  | LOWER MONITOR ZONE
RUN DATE | [16 empty] | MIN | MAX | AVG |  |  | MIN | MAX | AVG
2026-07-30 | [15 empty] | MARCH | FT HEAD | FT HEAD | FT HEAD |  |  | FT HEAD | FT HEAD | FT HEAD
[16 empty] | 2004 | ABOVE | ABOVE | ABOVE |  |  | ABOVE | ABOVE | ABOVE
| MARCH | EFF. BACT. | EFF. BACT. | FREE | TOTAL | EFFL. | EFF PH | EFF PH | EFF. SAP | AVG. | [6 empty] | NGVD | NGVD | NGVD |  |  | NGVD | NGVD | NGVD
| 2004 | TOTAL | FECAL | CL2 | CL2 | pH | MIN | MAX | TEMP.(C) | BLK. | [5 empty] | 1 | 42.59 | 44.52 | 43.48 |  |  | 21.05 | 23.12 | 22.29
[16 empty] | 2 | 42.48 | 44.11 | 43.44 |  |  | 21 | 21.78 | 21.48
| 1 | 143 | 0 | 0 | 0.7 | 6.5 | 6.5 | 6.5 | 2 | 52 | [5 empty] | 3 | 44.09 | 44.25 | 44.19 |  |  | 21.74 | 21.96 | 21.88
| 2 | 0 | 0 | 0 | 0.7 | 6.5 | 6.4 | 6.4 | 2 | 56 | [5 empty] | 4 | 44.22 | 44.36 | 44.3 |  |  | 21.92 | 22.07 | 22.01
| 3 | 200 | 9 | 0 | 0.5 | 6.5 | 6.4 | 6.5 | 2 | 53 | [5 empty] | 5 | 44.28 | 44.39 | 44.34 |  |  | 21.99 | 22.12 | 22.06
| 4 | 8000 | 89 | 0 | 0.6 | 6.5 | 6.4 | 6.5 | 3 | 40 | [5 empty] | 6 | 44.3 | 44.44 | 44.37 |  |  | 22.06 | 22.16 | 22.11
| 5 | 643 | 0 | 0 | 0.7 | 6.5 | 6.4 | 6.6 | 10 | 38 | [5 empty] | 7 | 44.33 | 44.47 | 44.41 |  |  | 22.07 | 22.22 | 22.14
| 6 | 45 | 0 | 0 | 0.6 | 6.4 | 6.4 | 6.5 | 8 | 48 | [5 empty] | 8 | 44.4 | 44.53 | 44.47 |  |  | 22.16 | 22.29 | 22.22
| 7 | 1750 | 0 | 0 | 0.8 | 6.5 | 6.4 | 6.5 | 5 | 45 | [5 empty] | 9 | 44.46 | 44.62 | 44.53 |  |  | 22.25 | 22.38 | 22.31
| 8 | 54 | 0 | 0 | 0.6 | 6.4 | 6.3 | 6.5 | 5 | 39 | [5 empty] | 10 | 44.43 | 44.6 | 44.52 |  |  | 22.19 | 22.4 | 22.3
| 9 | 230 | 0 | 0 | 0.6 | 6.4 | 6.2 | 6.5 | 2 | 41 | [5 empty] | 11 | 44.41 | 44.48 | 44.44 |  |  | 22.15 | 22.25 | 22.19
| 10 | 2100 | 0 | 0 | 0.6 | 6.5 | 6.2 | 6.6 | 2 | 28 | [5 empty] | 12 | 44.44 | 44.5 | 44.47 |  |  | 22.16 | 22.27 | 22.21
| 11 | 530 | 0 | 0 | 0.6 | 6.5 | 6.3 | 6.6 | 2 | 26 | [5 empty] | 13 | 44.44 | 44.54 | 44.48 |  |  | 22.14 | 22.3 | 22.21
| 12 | 339 | 0 | 0 | 0.4 | 6.5 | 6.4 | 6.5 | 5 | 30 | [5 empty] | 14 | 44.46 | 44.52 | 44.48 |  |  | 22.16 | 22.26 | 22.21
| 13 | 29500 | 0 | 0 | 0 | 6.4 | 6.2 | 6.4 | 0 | 40 | [5 empty] | 15 | 44.5 | 44.6 | 44.55 |  |  | 22.19 | 22.32 | 22.28
| 14 | 540 | 0 | 0 | 0.6 | 6.5 | 6.4 | 6.5 | 0 | 48 | [5 empty] | 16 | 44.58 | 44.75 | 44.67 |  |  | 22.27 | 22.49 | 22.4
| 15 | 3100 | 0 | 0 | 0.5 | 6.4 | 6.1 | 6.5 | 4 | 42 | [5 empty] | 17 | 44.58 | 44.75 | 44.67 |  |  | 22.3 | 22.46 | 22.39
| 16 | 1667 | 0 | 0 | 0.5 | 6.5 | 6.3 | 6.6 | 0 | 41 | [5 empty] | 18 | 44.48 | 44.63 | 44.56 |  |  | 22.21 | 22.32 | 22.27
| 17 | 3000 | 18 | 0 | 0.7 | 6.5 | 6.4 | 6.5 | 4 | 31 | [5 empty] | 19 | 44.45 | 44.57 | 44.51 |  |  | 22.18 | 22.25 | 22.22
| 18 | 833 | 36 | 0 | 0.4 | 6.6 | 6.5 | 6.6 | 4 | 27 | [5 empty] | 20 | 44.44 | 44.57 | 44.51 |  |  | 22.17 | 22.29 | 22.22
| 19 | 5667 | 3 | 0 | 0.4 | 6.5 | 6.4 | 6.5 | 5 | 27 | [5 empty] | 21 | 44.52 | 44.69 | 44.61 |  |  | 22.26 | 22.4 | 22.33
| 20 | 6667 | 0 | 0 | 0.6 | 6.4 | 6.3 | 6.5 | 5 | 29 | [5 empty] | 22 | 44.57 | 44.7 | 44.64 |  |  | 22.32 | 22.42 | 22.36
| 21 | 19000 | 0 | 0 | 0.6 | 6.5 | 6.4 | 6.9 | 5 | 45 | [5 empty] | 23 | 44.46 | 44.62 | 44.54 |  |  | 22.2 | 22.37 | 22.26
| 22 | 107 | 9 | 0 | 0.4 | 6.4 | 6.1 | 6.5 | 4 | 29 | [5 empty] | 24 | 44.43 | 44.53 | 44.49 |  |  | 22.14 | 22.25 | 22.18
| 23 | 600 | 0 | 0 | 0.9 | 6.4 | 6.3 | 6.6 | 2 | 31 | [5 empty] | 25 | 44.45 | 44.53 | 44.5 |  |  | 22.14 | 22.25 | 22.19
| 24 | 7000 | 0 | 0 | 0.4 | 6.5 | 6.3 | 6.6 | 1 | 23 | [5 empty] | 26 | 44.5 | 44.58 | 44.54 |  |  | 22.17 | 22.27 | 22.21
| 25 | 9500 | 9 | 0 | 0.5 | 6.5 | 6.4 | 6.5 | 0 | 17 | [5 empty] | 27 | 44.51 | 44.59 | 44.56 |  |  | 22.17 | 22.3 | 22.22
| 26 | 19500 | 0 | 0 | 0.5 | 6.5 | 6.4 | 6.6 | 5 | 19 | [5 empty] | 28 | 44.55 | 44.61 | 44.58 |  |  | 22.17 | 22.3 | 22.24
| 27 | TNTC | 750 | 0 | 0 | 6.5 | 6.4 | 6.5 | 5 | 21 | [5 empty] | 29 | 44.57 | 44.65 | 44.6 |  |  | 22.21 | 22.32 | 22.26
| 28 | TNTC | 0 | 0 | 0.6 | 6.5 | 6.5 | 6.5 | 5 | 32 | [5 empty] | 30 | 44.57 | 44.67 | 44.61 |  |  | 22.24 | 22.35 | 22.29
| 29 | 1333 | 0 | 0 | 0.3 | 6.4 | 6.5 | 6.4 | 2 | 24 | [5 empty] | 31 | 44.63 | 44.75 | 44.68 |  |  | 22.29 | 22.44 | 22.36
| 30 | 188 | 0 | 0 | 0.4 | 6.5 | 6.4 | 6.6 | 0 | 22 | [5 empty] | TOTAL | 1374.12 | 1381.12 | 1377.74 |  |  | 684.67 | 691.38 | 688.3
| 31 | 5400 | 0 | 0 | 0.5 | 6.5 | 6.4 | 6.6 | 1 | 23 | [5 empty] | AVERAGE | 44.3265 | 44.5523 | 44.4432 |  |  | 22.0861 | 22.3026 | 22.2032
| TOTAL | 127636 | 923 | 0 | 16.2 | 200.7 | 197 | 202.6 | 100 | 1067 | [5 empty] | MAXIMUM | 44.63 | 44.75 | 44.68 |  |  | 22.32 | 23.12 | 22.4
| AVERAGE | 4401.2414 | 29.7742 | 0 | 0.52258 | 6.4742 | 6.3548 | 6.5355 | 3.2258 | 34.4194 | [5 empty] | MINIMUM | 42.48 | 44.11 | 43.44 |  |  | 21 | 21.78 | 21.48
[7 empty] | 6.1 | 6.9
[7 empty] | MIN | MAX
PAGE 5
PAGE 23
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
NUTRIENTS
RUN DATE
| 2026-07-30 |  | INFLUENT | [5 empty] | EFFLUENT
| MARCH | INFLUENT | INFLUENT | INFLUENT | INFLUENT |  | EFFL. | EFFL. | EFFL. | EFFL.
| 2004 | NH-3 | N03-N | TKN | TOT P |  | NH-3 | N03-N | TKN | TOT P
1
2
| 3 | 19.06 | 0.02 | 23 | 3.5 |  | 14.06 | 0.326 | 14 | 0.78
| 4 | 18.7 | 0.02 | 22 | 2.9 |  | 14.45 | 0.344 | 13 | 0.73
| 5 | 18.39 | 0.02 | 17 | 2.9 |  | 14.82 | 0.243 | 17 | 0.66
| 6 | 17.76 | 0.02 | 19 | 3.1 |  | 12.67 | 0.195 | 12 | 0.91
| 7 | 17.63 | 0.02 | 18 | 3.1 |  | 14.63 | 0.216 | 16 | 0.82
8
9
| 10 | 19.36 | 0.02 | 22 | 3.1 |  | 15.53 | 0.24 | 15 | 0.95
| 11 | 19.18 | 0.02 | 20 | 3.2 |  | 15.41 | 0.279 | 14 | 1.8
| 12 | 19.49 | 0.02 | 20 | 3.1 |  | 15.32 | 0.234 | 13 | 1.2
| 13 | 18.05 | 0.02 | 21 | 2.8 |  | 14.59 | 0.294 | 15 | 1.1
| 14 | 19.18 | 0.02 | 22 | 3.3 |  | 14.25 | 0.504 | 15 | 1.1
15
16
| 17 | 18.79 | 0.02 | 21 | 3 |  | 14.35 | 0.559 | 16 | 1
| 18 | 18.18 | 0.02 | 22 | 2.9 |  | 14.94 | 0.588 | 13 | 1.6
| 19 | 19.09 | 0.02 | 22 | 3.2 |  | 14.8 | 0.228 | 15 | 1
| 20 | 18.83 | 0.02 | 22 | 3.4 |  | 13.69 | 0.227 | 16 | 1
| 21 | 18.99 | 0.02 | 31 | 3 |  | 12.98 | 0.628 | 15 | 0.98
22
23
| 24 | 19.44 | 0.02 | 22 | 3.3 |  | 14.79 | 0.272 | 17 | 1.9
| 25 | 18.42 | 0.02 | 27 | 3 |  | 14.69 | 0.261 | 16 | 2.2
| 26 | 18.27 | 0.02 | 25 | 3 |  | 14.37 | 0.199 | 18 | 1.5
| 27 | 17.48 | 0.02 | 20 | 2.7 |  | 13.05 | 0.215 | 15 | 1.4
| 28 | 17.43 | 0.02 | 24 | 3 |  | 12.15 | 0.566 | 14 | 1.2
29
30
| 31 | LS | LS | LS | LS |  | LS | LS | LS | LS
| TOTAL | 371.72 | 0.4 | 440 | 61.5 | TOT. | 285.54 | 6.618 | 299 | 23.83
| AVERAGE | 18.586 | 0.02 | 22 | 3.075 | AVG. | 14.277 | 0.3309 | 14.95 | 1.1915
PAGE 6
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
REACTOR ONE PROCESS
RUN DATE
| 2026-07-30 |  | TRAIN "A" | [5 empty] | TRAIN "B"
| MARCH | MLSS | MLVSS | SS | SVI |  | MLSS | MLVSS | SS | SVI
| 2004 | "A" | "A" | "A" | "A" |  | "B" | "B" | "B" | "B"
| 1 | O/S | O/S | O/S |  |  | 3760 | 3160 | 33 | 87.766
| 2 | O/S | O/S | O/S |  |  | 4340 | 3650 | 37 | 85.2535
| 3 | O/S | O/S | O/S |  |  | 3920 | 3180 | 35 | 89.2857
| 4 | O/S | O/S | O/S |  |  | 4060 | 3410 | 32 | 78.8177
| 5 | O/S | O/S | O/S |  |  | 2030 | 1600 | 32 | 157.6355
| 6 | O/S | O/S | O/S |  |  | 1960 | 1560 | 28 | 142.8571
| 7 | O/S | O/S | O/S |  |  | 3790 | 2980 | 34 | 89.7098
| 8 | O/S | O/S | O/S |  |  | 3450 | 2900 | 26 | 75.3623
| 9 | O/S | O/S | O/S |  |  | 3490 | 2930 | 30 | 85.9599
| 10 | O/S | O/S | O/S |  |  | 1900 | 1600 | 24 | 126.3158
| 11 | O/S | O/S | O/S |  |  | 1900 | 1500 | 18 | 94.7368
| 12 | O/S | O/S | O/S |  |  | 1730 | 1490 | 20 | 115.6069
| 13 | O/S | O/S | O/S |  |  | 2310 | 1940 | 27 | 116.8831
| 14 | O/S | O/S | O/S |  |  | 3040 | 2550 | 27 | 88.8158
| 15 | O/S | O/S | O/S |  |  | 3640 | 3060 | 26 | 71.4286
| 16 | O/S | O/S | O/S |  |  | 3340 | 2810 | 30 | 89.8204
| 17 | O/S | O/S | O/S |  |  | 3150 | 2650 | 25 | 79.3651
| 18 | O/S | O/S | O/S |  |  | 3460 | 2910 | 33 | 95.3757
| 19 | O/S | O/S | O/S |  |  | 2510 | 2090 | 25 | 99.6016
| 20 | O/S | O/S | O/S |  |  | 2490 | 2090 | 26 | 104.4177
| 21 | O/S | O/S | O/S |  |  | 3130 | 2630 | 25 | 79.8722
| 22 | O/S | O/S | O/S |  |  | 2580 | 2170 | 22 | 85.2713
| 23 | O/S | O/S | O/S |  |  | 1900 | 1600 | 14 | 73.6842
| 24 | O/S | O/S | O/S |  |  | 2000 | 1680 | 14 | 70
| 25 | O/S | O/S | O/S |  |  | 1440 | 1210 | 13 | 90.2778
| 26 | O/S | O/S | O/S |  |  | 1200 | 1090 | 15 | 125
| 27 | O/S | O/S | O/S |  |  | 1720 | 1440 | 18 | 104.6512
| 28 | O/S | O/S | O/S |  |  | 2810 | 2450 | 19 | 67.6157
| 29 | O/S | O/S | O/S |  |  | 2770 | 2330 | 21 | 75.8123
| 30 | O/S | O/S | O/S |  |  | 1850 | 1550 | 19 | 102.7027
| 31 | O/S | O/S | O/S |  |  | 2240 | 1880 | 19 | 84.8214
| TOTAL | 0 | 0 | 0 |  |  | 83910 | 70090 | 767
| AVERAGE | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 2706.7742 | 2260.9677 | 24.7419 | 91.4075
PAGE 7
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
REACTOR TWO PROCESS
RUN DATE
| 2026-07-30 |  | TRAIN "C" | [5 empty] | TRAIN "D"
| MARCH | MLSS | MLVSS | SS | SVI |  | MLSS | MLVSS | SS | SVI
| 2004 | "C" | "C" | "C" | "C" |  | "D" | "D" | "D" | "D"
| 1 | O/S | O/S | O/S |  |  | 3280 | 2760 | 32 | 97.561
| 2 | O/S | O/S | O/S |  |  | 3400 | 2860 | 34 | 100
| 3 | O/S | O/S | O/S |  |  | 2610 | 2220 | 32 | 122.6054
| 4 | O/S | O/S | O/S |  |  | 3020 | 2540 | 31 | 102.649
| 5 | O/S | O/S | O/S |  |  | 2660 | 2200 | 28 | 105.2632
| 6 | O/S | O/S | O/S |  |  | 2510 | 2070 | 30 | 119.5219
| 7 | O/S | O/S | O/S |  |  | 2880 | 2350 | 30 | 104.1667
| 8 | O/S | O/S | O/S |  |  | 2930 | 2460 | 26 | 88.7372
| 9 | O/S | O/S | O/S |  |  | 3030 | 2550 | 27 | 89.1089
| 10 | O/S | O/S | O/S |  |  | 2100 | 1760 | 23 | 109.5238
| 11 | O/S | O/S | O/S |  |  | 2260 | 1810 | 17 | 75.2212
| 12 | O/S | O/S | O/S |  |  | 1980 | 1680 | 26 | 131.3131
| 13 | O/S | O/S | O/S |  |  | 2680 | 2250 | 33 | 123.1343
| 14 | O/S | O/S | O/S |  |  | 3090 | 2600 | 28 | 90.6149
| 15 | O/S | O/S | O/S |  |  | 3350 | 2810 | 29 | 86.5672
| 16 | O/S | O/S | O/S |  |  | 2700 | 2270 | 30 | 111.1111
| 17 | O/S | O/S | O/S |  |  | 2770 | 2330 | 23 | 83.0325
| 18 | O/S | O/S | O/S |  |  | 2670 | 2240 | 31 | 116.1049
| 19 | O/S | O/S | O/S |  |  | 2340 | 1950 | 24 | 102.5641
| 20 | O/S | O/S | O/S |  |  | 2760 | 2320 | 30 | 108.6957
| 21 | O/S | O/S | O/S |  |  | 3050 | 2560 | 23 | 75.4098
| 22 | O/S | O/S | O/S |  |  | 2330 | 1960 | 22 | 94.4206
| 23 | O/S | O/S | O/S |  |  | 2140 | 1800 | 14 | 65.4206
| 24 | O/S | O/S | O/S |  |  | 2260 | 1900 | 15 | 66.3717
| 25 | O/S | O/S | O/S |  |  | 1480 | 1240 | 17 | 114.8649
| 26 | O/S | O/S | O/S |  |  | 1780 | 1620 | 16 | 89.8876
| 27 | O/S | O/S | O/S |  |  | 1780 | 1490 | 18 | 101.1236
| 28 | O/S | O/S | O/S |  |  | 3190 | 2740 | 20 | 62.6959
| 29 | O/S | O/S | O/S |  |  | 2930 | 2460 | 24 | 81.9113
| 30 | O/S | O/S | O/S |  |  | 1800 | 1510 | 20 | 111.1111
| 31 | O/S | O/S | O/S |  |  | 1980 | 1660 | 17 | 85.8586
| TOTAL | 0 | 0 | 0 |  |  | 79740 | 66970 | 770
| AVERAGE | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 2572.2581 | 2160.3226 | 24.8387 | 96.5638
PAGE 8
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
RAS SUMMARY
RUN DATE
2026-07-30
| MARCH | R-1 | R-2 | TOTAL | F/M | TOTAL | SLUDGE | % TOT | % FIX | % VOL.
| 2004 | TOT. RAS | TOT. RAS | MLVSS | RATIO | MLSS | AGE | RAS | RAS | RAS
|  | MGD | MGD
| 1 | 4.952 | 6.068 | 5920 | 0.38171 | 7040 | 1.9039 | 1.07 | 21.5 | 78.5
| 2 | 4.951 | 6.005 | 6510 | 0.36695 | 7740 | 1.944 | 1.15 | 22.4 | 77.6
| 3 | 5.498 | 5.495 | 5400 | 0.56013 | 6530 | 1.2541 | 0.97 | 20.7 | 79.3
| 4 | 5.381 | 5.894 | 5950 | 0.38984 | 7080 | 1.3466 | 0.96 | 20.8 | 79.2
| 5 | 5.733 | 5.659 | 3800 | 0.48094 | 4690 | 0.58104 | 1.01 | 20.8 | 79.2
| 6 | 5.361 | 5.444 | 3630 | 1.0411 | 4470 | 0.762 | 0.97 | 24.8 | 75.2
| 7 | 5.654 | 5.486 | 5330 | 1.0888 | 6670 | 0.60628 | 1 | 21.9 | 78.1
| 8 | 4.897 | 4.624 | 5360 | 0.68644 | 6380 | 2.1459 | 0.92 | 20.6 | 79.4
| 9 | 3.567 | 5.551 | 5480 | 0.77318 | 6520 | 1.3091 | 0.99 | 20.3 | 79.7
| 10 | 2.835 | 5.34 | 3360 | 1.2137 | 4000 | 0.6364 | 0.96 | 17.6 | 82.4
| 11 | 2.615 | 5.913 | 3310 | 0.70761 | 4160 | 1.4723 | 0.78 | 33.1 | 66.9
| 12 | 4.28 | 6.58 | 3170 | 1.0283 | 3710 | 0.8536 | 1.08 | 20.4 | 79.6
| 13 | 4.893 | 5.421 | 4190 | 1.297 | 4990 | 1.0913 | 1.05 | 21.7 | 78.3
| 14 | 5.119 | 4.914 | 5150 | 0.79669 | 6130 | 1.4791 | 0.82 | 22.4 | 77.6
| 15 | 5.728 | 6.082 | 5870 | 0.69431 | 6990 | 1.5524 | 1.05 | 20.7 | 79.3
| 16 | 7.5 | 6.109 | 5080 | 0.78947 | 6040 | 0.97893 | 0.96 | 20.7 | 79.3
| 17 | 6.342 | 5.416 | 4980 | 0.86287 | 5920 | 1.3535 | 0.82 | 21.1 | 78.9
| 18 | 5.926 | 5.982 | 5150 | 0.72495 | 6130 | 1.3272 | 0.9 | 20.5 | 79.5
| 19 | 5.608 | 6.379 | 4040 | 1.1185 | 4850 | 1.0554 | 1.31 | 21.4 | 78.6
| 20 | 5.023 | 5.931 | 4410 | 1.3229 | 5250 | 1.0686 | 0.95 | 21 | 79
| 21 | 5.465 | 5.475 | 5190 | 0.94912 | 6180 | 0.87686 | 0.8 | 20.8 | 79.2
| 22 | 4.741 | 6.215 | 4130 | 1.0808 | 4910 | 1.1482 | 0.84 | 22.4 | 77.6
| 23 | 4.118 | 5.782 | 3400 | 0.96612 | 4040 | 0.78934 | 0.79 | 0.23 | 99.77
| 24 | 4.324 | 6.026 | 3580 | 1.2834 | 4260 | 0.81807 | 0.7 | 22.7 | 77.3
| 25 | 4.315 | 6.443 | 2450 | 1.9102 | 2920 | 0.53926 | 0.71 | 23.8 | 76.2
| 26 | 4.425 | 6.017 | 2710 | 1.721 | 2980 | 0.63362 | 1.06 | 23.6 | 76.4
| 27 | 4.552 | 5.788 | 2930 | 2.7009 | 3500 | 0.034863 | 1.13 | 22.8 | 77.2
| 28 | 5.1 | 6.17 | 5190 | 0.83876 | 6000 | 1.3324 | 1.05 | 22.7 | 77.3
| 29 | 4.862 | 5.549 | 4790 | 0.7787 | 5700 | 1.4272 | 0.88 | 22.7 | 77.3
| 30 | 4.594 | 5.467 | 3060 | 1.1572 | 3650 | 0.96893 | 0.62 | 22 | 78
| 31 | 5.707 | 6.468 | 3540 | 0.9843 | 4220 | 1.2111 | 0.69 | 25.2 | 74.8
| TOTAL | 154.066 | 179.693 | 137060 |  | 163650 |  | 28.99 | 663.33 | 2436.67
| AVERAGE | 4.9699 | 5.7965 | 4421.2903 | 0.91078 | 5279.0323 | 0.65761 | 0.93516 | 21.3977 | 78.6023
PAGE 9
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
DEWATERING DATA
RUN DATE
| 2026-07-30 |  | FEED SLUDGE |  |  |  |  | FILTRATE RETURN
| MARCH | % TOT. | % FIX. | % VOL. | pH |  | % TOT. | % FIX. | % VOL. | pH
| 2004 | FEED | FEED | FEED |  |  | FILT. | FILT. | FILT.
| 1 | 1.38 | 21.7 | 78.3 | 6.7 |  | 0.19 | 68.4 | 31.6 | 7.18
| 2 | 1.24 | 22.6 | 77.4 | 6.69 |  | 0.21 | 57.1 | 42.9 | 7.14
| 3 | 1.15 | 20 | 80 | 6.69 |  | 0.21 | 57.1 | 42.9 | 7.13
| 4 | 1.29 | 20.9 | 79.1 | 6.71 |  | 0.23 | 65.2 | 34.8 | 7.18
5
6
| 7 | 1.19 | 22.7 | 77.3 | 6.59 |  | 0.16 | 75 | 25 | 6.96
| 8 | 1.35 | 22.2 | 77.8 | 6.72 |  | 0.2 | 65 | 35 | 7.17
| 9 | 1.34 | 20.9 | 79.1 | 6.7 |  | 0.2 | 60 | 40 | 7.18
| 10 | 1.29 | 22.5 | 77.5 | 6.71 |  | 0.21 | 66.7 | 33.3 | 7.18
| 11 | 1.08 | 27.8 | 72.2 | 6.48 |  | 0.21 | 71.4 | 28.6 | 6.91
12
13
| 14 | 1.03 | 26.2 | 73.8 | 6.74 |  | 0.19 | 68.4 | 31.6 | 7.16
| 15 | 1.44 | 20.1 | 79.9 | 6.36 |  | 0.23 | 56.5 | 43.5 | 6.78
| 16 | 1.1 | 20.9 | 79.1 | 6.4 |  | 0.24 | 58.3 | 41.7 | 6.82
17
| 18 | 1.1 | 20 | 80 | 6.47 |  | 0.24 | 62.5 | 37.5 | 6.89
19
20
| 21 | 1.7 | 21.2 | 78.8 | 6.61 |  | 0.21 | 57.1 | 42.9 | 7.01
| 22 | 1.18 | 24.6 | 75.4 | 6.44 |  | 0.23 | 73.9 | 26.1 | 6.85
| 23 | 1.11 | 0.29 | 99.71 | 6.51 |  | 0.25 | 0.17 | 99.83 | 6.9
| 24 | 1.18 | 21.2 | 78.8 | 6.59 |  | 0.25 | 60 | 40 | 6.91
| 25 | 0.96 | 27.1 | 72.9 | 6.58 |  | 0.29 | 58.6 | 41.4 | 6.89
26
27
| 28 | 1.31 | 22.1 | 77.9 | 6.34 |  | 0.23 | 56.5 | 43.5 | 6.92
| 29 | 1.23 | 22.8 | 77.2 | 6.57 |  | 0.24 | 58.3 | 41.7 | 7.09
| 30 | 1.33 | 21.1 | 78.9 | 6.48 |  | 0.26 | 53.8 | 46.2 | 6.91
| 31 | 0.89 | 27 | 73 | 6.44 |  | 0.23 | 65.2 | 34.8 | 6.98
| TOTAL | 26.87 | 475.89 | 1724.11 | 144.52 |  | 4.91 | 1315.17 | 884.83 | 154.14
| AVERAGE | 1.2214 | 21.6314 | 78.3686 | 6.5691 |  | 0.22318 | 59.7805 | 40.2195 | 7.0064
PAGE 10
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
SLUDGE VOLUME REMOVED
RUN DATE
2026-07-30
|  | MARCH | TRAILERS | TONS | DRY TONS | % LIME | % TOT. | % FIX. | % VOL.
|  | 2004 | REMOVED | SLUDGE | REMOVED | CAKE | CAKE | CAKE | CAKE
|  | 1 | 7 | 175 | 38.3256 |  | 17.35 | 13.4 | 86.6
|  | 2 | 7 | 175 | 32.6277 |  | 17.75 | 14.1 | 85.9
|  | 3 | 7 | 175 | 32.8492 |  | 18.34 | 13.8 | 86.2
|  | 4 | 7 | 175 | 35.8261 |  | 18.16 | 15.9 | 84.1
|  | 5 | 6 | 150
|  | 6 | 0 | 0
|  | 7 | 1 | 25 | 11.0163 |  | 16.61 | 13.8 | 86.2
|  | 8 | 6 | 150 | 34.3962 |  | 17.56 | 13.4 | 86.6
|  | 9 | 7 | 175 | 37.997 |  | 18.01 | 13.6 | 86.4
|  | 10 | 6 | 150 | 39.5916 |  | 19.03 | 16.5 | 83.5
|  | 11 | 7 | 175 | 32.6061 |  | 19.25 | 14.7 | 85.3
|  | 12 | 5 | 125
|  | 13 | 0 | 0
|  | 14 | 0 | 0 | 9.3204 |  | 17.71 | 12.7 | 87.3
|  | 15 | 6 | 150 | 41.0128 |  | 17.83 | 13.5 | 86.5
|  | 16 | 7 | 175 | 28.8522 |  | 17.82 | 14.9 | 85.1
|  | 17 | 6 | 150
|  | 18 | 6 | 150 | 30.5494 |  | 18.3 | 15.7 | 84.3
|  | 19 | 6 | 150
|  | 20 | 1 | 25
|  | 21 | 0 | 0 | 14.6742 |  | 17.46 | 14.3 | 85.7
|  | 22 | 6 | 150 | 39.414 |  | 17.83 | 13.3 | 86.7
|  | 23 | 7 | 175 | 37.3536 |  | 19.07 | 2.75 | 97.25
|  | 24 | 6 | 150 | 37.8394 |  | 18.61 | 14 | 86
|  | 25 | 7 | 175 | 32.7061 |  | 20.72 | 14.5 | 85.5
|  | 26 | 4 | 100
|  | 27 | 1 | 25
|  | 28 | 0 | 0 | 11.6356 |  | 18.62 | 14.2 | 85.8
|  | 29 | 3 | 75 | 25.4403 |  | 17.94 | 14.7 | 85.3
|  | 30 | 5 | 125 | 39.3773 |  | 17.85 | 13.8 | 86.2
|  | 31 | 5 | 125 | 28.0203 |  | 18.89 | 18.4 | 81.6
|  | TOTAL | 142 | 3550 | 671.4317 | 0 | 400.71 | 305.95 | 1894.05
|  | AVERAGE | 4.5806 | 114.5161 | 30.5196 | #DIV/0! | 18.2141 | 13.9068 | 86.0932
PAGE 11
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
CHEMICAL USEAGE
RUN DATE
2026-07-30
| MARCH | H2O2 | CL2 | POLYMER | POLYMER | LIME | GOX | O2 % | LOX | FPL
| 2004 | POUNDS | POUNDS | GALLONS | POUNDS | DELV. | TONS | PURITY | TONS | KW
| 1 | 1537 | 1080 | 93 | 775.62 | 0 | 27.9 | 100% | 193 | 28512
| 2 | 1357 | 1120 | 107 | 892.38 | 0 | 23.9 | 99% | 194 | 29234
| 3 | 1397 | 1440 | 120 | 1000.8 | 0 | 30.3 | 99% | 192 | 28431
| 4 | 1337 | 1180 | 57 | 475.38 | 0 | 30.3 | 99% | 184 | 21195
| 5 | 1058 | 1240 | 26 | 216.84 | 0 | 28.3 | 99% | 184 | 29895
| 6 | 1836 | 1260 | 38 | 316.92 | 0 | 27.5 | 98% | 184 | 29984
| 7 | 1916 | 1200 | 77 | 642.18 | 0 | 35.6 | 97% | 184 | 29682
| 8 | 1976 | 1240 | 45 | 375.3 | 0 | 27.2 | 98% | 185 | 29630
| 9 | 1836 | 1460 | 72 | 600.48 | 0 | 32 | 98% | 184 | 29081
| 10 | 2016 | 1200 | 96 | 800.64 | 0 | 20.6 | 99% | 184 | 29097
| 11 | 1576 | 1200 | 64 | 533.76 | 0 | 24.5 | 99% | 184 | 28981
| 12 | 1737 | 1160 | 13 | 108.42 | 0 | 28.8 | 96% | 184 | 28973
| 13 | 1656 | 1400 | 25 | 208.5 | 0 | 33.6 | 99% | 183 | 28937
| 14 | 1829 | 1260 | 40 | 333.6 | 0 | 28.8 | 97% | 184 | 29080
| 15 | 1556 | 1040 | 83 | 692.22 | 0 | 38 | 98% | 185 | 29037
| 16 | 1956 | 1300 | 99 | 825.66 | 0 | 28.5 | 93% | 185 | 27578
| 17 | 1777 | 1280 | 59 | 492.06 | 0 | 22.7 | 100% | 184 | 27645
| 18 | 1897 | 1040 | 68 | 567.12 | 0 | 19.6 | 99% | 183 | 27836
| 19 | 1687 | 1160 | 43 | 358.62 | 0 | 21.7 | 99% | 183.9 | 28425
| 20 | 1717 | 1160 | 9 | 75.06 | 0 | 23.5 | 100% | 184 | 28411
| 21 | 1827 | 1080 | 14 | 116.76 | 0 | 22.6 | 100% | 184 | 28547
| 22 | 1846 | 1180 | 126 | 1050.84 | 0 | 23 | 100% | 198 | 28535
| 23 | 1486 | 1320 | 71 | 592.14 | 0 | 19.8 | 100% | 192 | 28723
| 24 | 1637 | 1240 | 87 | 725.58 | 0 | 17.4 | 100% | 192 | 28760
| 25 | 1796 | 1160 | 49 | 408.66 | 0 | 18 | 100% | 196 | 28671
| 26 | 1287 | 1220 | 0 | 0 | 0 | 18.5 | 99% | 193 | 28600
| 27 | 1786 | 1280 | 29 | 241.86 | 0 | 20.5 | 100% | 196 | 28558
| 28 | 1487 | 1280 | 37 | 308.58 | 0 | 28.7 | 100% | 194 | 28262
| 29 | 1576 | 1080 | 40 | 333.6 | 0 | 25.1 | 100% | 195 | 28391
| 30 | 1268 | 1200 | 69 | 575.46 | 0 | 18.4 | 100% | 198 | 29184
| 31 | 1378 | 1200 | 81 | 675.54 | 0 | 18.5 | 100% | 200 | 31170
| TOTAL | 51028 | 37660 | 1837 | 15320.58 | 0 | 783.8 |  | 5845.9 | 887045
| AVERAGE | 1646.0645 | 1214.8387 | 59.2581 | 494.2123 | 0 | 25.2839 | 98.87% | 188.5774 | 28614.3548
PAGE 12
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL ONE
|  | RUN DATE |  |  | PERMIT NUMBER 0054569-142-UO
|  | 2026-07-30 |  |  | 1/07/04 thru 1/06/09 |  |  | I.D. #:5006A11308
|  | MARCH | % INFL. | MAX | MIN | WELL 1 | MAX | MIN | AVG
|  | 2004 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 21.62% | 12.03 | 0 | 7.55 | 56.87 | 34.59 | 46.99
|  | 2 | 26.74% | 12.28 | 5.26 | 9.05 | 58.84 | 40.13 | 48.3
|  | 3 | 26.24% | 13.28 | 4.71 | 8.54 | 61.62 | 39 | 47.2
|  | 4 | 25.35% | 12.22 | 3.96 | 8.33 | 57.45 | 37.72 | 47.05
|  | 5 | 25.62% | 11.7 | 3.97 | 8.29 | 56.56 | 37.68 | 46.94
|  | 6 | 27.59% | 13.37 | 5.31 | 8.82 | 61.64 | 39.93 | 48.26
|  | 7 | 27.18% | 11.6 | 5.44 | 8.53 | 56.3 | 39.78 | 47.4
|  | 8 | 25.48% | 11.09 | 4.73 | 8.05 | 55.64 | 38.86 | 46.41
|  | 9 | 25.42% | 10.91 | 3.79 | 8.03 | 53.73 | 37.41 | 46.23
|  | 10 | 25.41% | 10.19 | 3.73 | 8.08 | 50.93 | 37.14 | 46.03
|  | 11 | 25.51% | 10.15 | 4.09 | 8.06 | 50.78 | 37.81 | 45.88
|  | 12 | 25.65% | 10.17 | 3.7 | 8.17 | 50.81 | 37.11 | 46.18
|  | 13 | 27.18% | 13.37 | 5.36 | 8.66 | 62.81 | 40.38 | 47.63
|  | 14 | 28.45% | 13.8 | 5.69 | 9.11 | 62.42 | 40.56 | 48.57
|  | 15 | 24.22% | 11.88 | 4.31 | 7.99 | 56.88 | 38.62 | 46.01
|  | 16 | 23.64% | 10.88 | 4.12 | 7.75 | 53.4 | 38.35 | 45.39
|  | 17 | 21.22% | 10.85 | 0 | 6.92 | 53.91 | 34.56 | 44.68
|  | 18 | 24.51% | 10.45 | 4.48 | 8.02 | 53.96 | 38.37 | 45.92
|  | 19 | 21.84% | 18.13 | 0 | 7.11 | 80.5 | 34.21 | 45.54
|  | 20 | 24.74% | 11.47 | 4.83 | 8.07 | 56.27 | 38.94 | 45.98
|  | 21 | 20.12% | 12.11 | 0 | 6.48 | 57.93 | 34.29 | 43.9
|  | 22 | 21.14% | 9.69 | 0 | 6.74 | 49.6 | 34.23 | 44.15
|  | 23 | 28.55% | 15.06 | 4.49 | 9.27 | 69.19 | 38.12 | 49.35
|  | 24 | 26.3% | 10.19 | 5.22 | 8.56 | 50.72 | 39.54 | 46.88
|  | 25 | 26.43% | 13.2 | 5.26 | 8.69 | 61.84 | 39.79 | 47.44
|  | 26 | 25.51% | 12.75 | 4.53 | 8.5 | 59.89 | 38.65 | 47.13
|  | 27 | 20.77% | 12.88 | 0 | 6.85 | 60.41 | 34.36 | 45.14
|  | 28 | 24.99% | 10.14 | 4.31 | 7.97 | 51.15 | 38.31 | 45.96
|  | 29 | 21.92% | 10.16 | 0 | 7.02 | 51.13 | 34.44 | 45.14
|  | 30 | 25.39% | 10.95 | 4.53 | 8.13 | 54.08 | 38.51 | 46.48
|  | 31 | 26.72% | 10.16 | 5.44 | 8.42 | 50.96 | 40.18 | 46.76
|  | TOTAL | 771.5% | 367.11 | 111.26 | 249.76 | 1768.22 | 1171.57 | 1440.92
|  | AVERAGE | 24.89% | 11.8423 | 3.589 | 8.0568 | 57.0394 | 37.7926 | 46.4813
|  | MAXIMUM | 28.55% | 18.13 | 5.69 | 9.27 | 80.5 | 40.56 | 49.35
|  | MINIMUM | 20.12% | 9.69 | 0 | 6.48 | 49.6 | 34.21 | 43.9
PAGE 13
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL TWO
|  | RUN DATE |  |  | PERMIT NUMBER 0054569-142-UO
|  | 2026-07-30 |  |  | 1/07/04 thru 1/06/09 |  |  | I.D. #:5006A11309
|  | MARCH | % INFL. | MAX | MIN | WELL 2 | MAX | MIN | AVG
|  | 2004 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 27.15% | 12.23 | 5.5 | 9.48 | 55.9 | 39.43 | 48.45
|  | 2 | 22.19% | 12.52 | 0.02 | 7.51 | 57.68 | 34.89 | 45.38
|  | 3 | 26.64% | 13.58 | 4.53 | 8.67 | 60.41 | 38.24 | 46.28
|  | 4 | 25.56% | 12.39 | 3.49 | 8.4 | 56.35 | 36.98 | 46.13
|  | 5 | 25.77% | 11.94 | 3.61 | 8.34 | 55.46 | 36.96 | 46.06
|  | 6 | 27.91% | 13.55 | 5.31 | 8.92 | 60.56 | 39.15 | 47.34
|  | 7 | 19.22% | 11.72 | 0.02 | 6.03 | 55.27 | 34.96 | 43.53
|  | 8 | 25.64% | 11.23 | 4.41 | 8.1 | 54.68 | 38.09 | 45.5
|  | 9 | 25.54% | 11.03 | 3.12 | 8.07 | 52.71 | 36.66 | 45.33
|  | 10 | 25.41% | 10.28 | 3.06 | 8.08 | 49.96 | 36.38 | 45.11
|  | 11 | 25.57% | 10.34 | 3.62 | 8.08 | 49.88 | 37.04 | 44.99
|  | 12 | 25.78% | 10.31 | 3.02 | 8.21 | 49.91 | 36.36 | 45.32
|  | 13 | 27.43% | 13.59 | 5.14 | 8.74 | 61.67 | 39.58 | 46.74
|  | 14 | 28.98% | 14.1 | 5.57 | 9.28 | 35.86 | 39.77 | 47.74
|  | 15 | 24.43% | 12.19 | 4.02 | 8.06 | 56.05 | 37.9 | 45.29
|  | 16 | 23.74% | 11.01 | 3 | 7.78 | 52.54 | 37.08 | 44.72
|  | 17 | 24.99% | 11.01 | 4.75 | 8.15 | 53.08 | 38.77 | 45.37
|  | 18 | 24.7% | 10.66 | 4.08 | 8.08 | 53.01 | 37.72 | 45.17
|  | 19 | 24.95% | 15.92 | 0.02 | 8.12 | 68.87 | 36.07 | 45.64
|  | 20 | 24.92% | 11.67 | 4.55 | 8.13 | 55.31 | 38.2 | 45.14
|  | 21 | 24.75% | 12.4 | 4.74 | 7.97 | 56.89 | 38.4 | 44.71
|  | 22 | 24.81% | 9.73 | 4.83 | 7.91 | 48.75 | 38.54 | 44.57
|  | 23 | 10.75% | 10.16 | 0.03 | 3.49 | 49.42 | 34.62 | 39.82
|  | 24 | 26.73% | 10.32 | 5.1 | 8.7 | 49.72 | 38.74 | 45.95
|  | 25 | 26.8% | 13.51 | 5.21 | 8.81 | 60.6 | 39 | 46.49
|  | 26 | 25.78% | 12.96 | 4.26 | 8.59 | 58.72 | 37.85 | 46.18
|  | 27 | 27.17% | 13.09 | 5.62 | 8.96 | 59.27 | 39.81 | 46.96
|  | 28 | 25.02% | 10.26 | 3.91 | 7.98 | 50.12 | 37.55 | 45.06
|  | 29 | 26.92% | 10.27 | 4.7 | 8.62 | 50.14 | 38.7 | 46.11
|  | 30 | 25.52% | 11.04 | 4.23 | 8.17 | 53 | 37.74 | 45.55
|  | 31 | 21.96% | 10.22 | 0.02 | 6.92 | 49.94 | 34.85 | 44.13
|  | TOTAL | 772.7% | 365.23 | 113.49 | 250.35 | 1681.73 | 1166.03 | 1410.76
|  | AVERAGE | 24.93% | 11.7816 | 3.661 | 8.0758 | 54.2494 | 37.6139 | 45.5084
|  | MAXIMUM | 28.98% | 15.92 | 5.62 | 9.48 | 68.87 | 39.81 | 48.45
|  | MINIMUM | 10.75% | 9.73 | 0.02 | 3.49 | 35.86 | 34.62 | 39.82
PAGE 14
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL THREE
|  | RUN DATE |  |  | PERMIT NUMBER 0054569-142-UO
|  | 2026-07-30 |  |  | 1/07/04 thru 1/06/09 |  |  | I.D. #:5006A11310
|  | MARCH | % INFL. | MAX | MIN | WELL 3 | MAX | MIN | AVG
|  | 2004 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 23.85% | 10.82 | 4.84 | 8.33 | 57.14 | 40.38 | 49.62
|  | 2 | 23.73% | 11.11 | 2.38 | 8.03 | 59.13 | 39.74 | 48.44
|  | 3 | 19.48% | 11.95 | ER | 6.34 | 61.94 | 35.13 | 45.6
|  | 4 | 22.52% | 10.91 | 3.18 | 7.4 | 57.74 | 37.83 | 47.23
|  | 5 | 22.74% | 10.52 | 3.28 | 7.36 | 56.84 | 37.81 | 47.16
|  | 6 | 24.68% | 11.98 | 4.69 | 7.89 | 61.99 | 40.08 | 48.46
|  | 7 | 24.16% | 10.36 | 4.63 | 7.58 | 56.6 | 39.91 | 47.58
|  | 8 | 22.6% | 9.91 | 3.91 | 7.14 | 55.94 | 38.96 | 46.58
|  | 9 | 22.51% | 9.72 | 2.91 | 7.11 | 53.99 | 37.5 | 46.43
|  | 10 | 22.48% | 9.04 | 2.94 | 7.15 | 51.16 | 37.24 | 46.21
|  | 11 | 22.5% | 9.07 | 3.23 | 7.11 | 51.11 | 37.91 | 46.09
|  | 12 | 22.64% | 9.09 | 2.8 | 7.21 | 51.18 | 37.22 | 46.41
|  | 13 | 24.26% | 12.1 | 4.48 | 7.73 | 63.25 | 40.51 | 47.88
|  | 14 | 20.95% | 10.7 | ER | 6.71 | 57.1 | 35.19 | 46.05
|  | 15 | 21.25% | 10.64 | 3.58 | 7.01 | 57.34 | 38.75 | 46.32
|  | 16 | 20.41% | 9.42 | 3.48 | 6.69 | 53.72 | 38.74 | 45.72
|  | 17 | 21.4% | 9.5 | 4.07 | 6.98 | 54.31 | 39.64 | 46.39
|  | 18 | 21.27% | 9.1 | 3.47 | 6.96 | 54.25 | 38.57 | 46.22
|  | 19 | 21.63% | 16.66 | ER | 7.04 | 83.1 | 36.12 | 46.9
|  | 20 | 21.76% | 10.08 | 3.94 | 7.1 | 56.59 | 39.06 | 46.19
|  | 21 | 21.45% | 10.77 | 4 | 6.91 | 58.22 | 39.24 | 45.72
|  | 22 | 21.45% | 8.51 | 4.22 | 6.84 | 49.85 | 39.43 | 45.58
|  | 23 | 24.95% | 13.12 | 3.56 | 8.1 | 69.3 | 38.21 | 49.47
|  | 24 | 19.33% | 9.1 | ER | 6.29 | 50.97 | 34.94 | 45.29
|  | 25 | 22.9% | 11.11 | ER | 7.53 | 58.41 | 35.96 | 47.13
|  | 26 | 22.69% | 11.39 | 3.8 | 7.56 | 60.2 | 38.74 | 47.3
|  | 27 | 23.78% | 11.47 | 4.93 | 7.84 | 60.71 | 40.75 | 48.08
|  | 28 | 22.07% | 9.01 | 3.53 | 7.04 | 51.39 | 38.41 | 46.12
|  | 29 | 23.48% | 9.02 | 4.16 | 7.52 | 51.32 | 39.57 | 47.2
|  | 30 | 22.42% | 9.73 | 3.75 | 7.18 | 54.34 | 38.6 | 46.65
|  | 31 | 23.71% | 9.02 | 4.7 | 7.47 | 51.16 | 40.27 | 46.94
|  | TOTAL | 695.1% | 324.93 | 98.46 | 225.15 | 1770.29 | 1190.41 | 1452.96
|  | AVERAGE | 22.42% | 10.4816 | 3.7869 | 7.2629 | 57.1061 | 38.4003 | 46.8697
|  | MAXIMUM | 24.95% | 16.66 | 4.93 | 8.33 | 83.1 | 40.75 | 49.62
|  | MINIMUM | 19.33% | 8.51 | 2.38 | 6.29 | 49.85 | 34.94 | 45.29
PAGE 15
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL FOUR
|  | RUN DATE |  |  | PERMIT NUMBER 0054569-142-UO
|  | 2026-07-30 |  |  | 1/07/04 thru 1/06/09
|  | MARCH | % INFL. | MAX | MIN | WELL 4 | MAX | MIN | AVG
|  | 2004 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 0.3722% | 0.14 | 0.12 | 0.13 | 36.98 | 35.48 | 36.31
|  | 2 | 0.3841% | 0.14 | 0.12 | 0.13 | 37.1 | 35.37 | 36.15
|  | 3 | 0.3995% | 0.15 | 0.12 | 0.13 | 37.4 | 35 | 36.05
|  | 4 | 0.3956% | 0.15 | 0.12 | 0.13 | 37.17 | 35.17 | 36.21
|  | 5 | 0.4017% | 0.15 | 0.12 | 0.13 | 37.11 | 35.21 | 36.23
|  | 6 | 0.4067% | 0.15 | 0.12 | 0.13 | 37.11 | 34.98 | 36.05
|  | 7 | 0.4143% | 0.15 | 0.12 | 0.13 | 37.25 | 35.41 | 36.3
|  | 8 | 0.4115% | 0.15 | 0.12 | 0.13 | 37.29 | 35.37 | 36.33
|  | 9 | 0.4115% | 0.15 | 0.12 | 0.13 | 37.12 | 35.15 | 36.3
|  | 10 | 0.3773% | 0.15 | 0.11 | 0.12 | 36.83 | 35.08 | 36.17
|  | 11 | 0.3797% | 0.14 | 0.11 | 0.12 | 36.69 | 35.01 | 36.04
|  | 12 | 0.4082% | 0.15 | 0.12 | 0.13 | 36.71 | 34.9 | 36.1
|  | 13 | 0.4081% | 0.15 | 0.12 | 0.13 | 37 | 34.97 | 35.97
|  | 14 | 0.4059% | 0.14 | 0.12 | 0.13 | 50.93 | 34.52 | 35.87
|  | 15 | 17.55% | 13.17 | 0.12 | 5.79 | 53.05 | 35.31 | 41.96
|  | 16 | 30.72% | 13.69 | 5.85 | 10.07 | 53.61 | 39.33 | 45.96
|  | 17 | 31.86% | 13.73 | 6.69 | 10.39 | 54.17 | 40.16 | 46.67
|  | 18 | 28.03% | 13.23 | 0.12 | 9.17 | 54.23 | 35.42 | 45.4
|  | 19 | 28.88% | 14.31 | 0.13 | 9.4 | 55.59 | 35.9 | 45.51
|  | 20 | 26.76% | 14.44 | 0.12 | 8.73 | 56.53 | 35.31 | 44.91
|  | 21 | 31.64% | 15.35 | 6.4 | 10.19 | 57.95 | 39.79 | 45.98
|  | 22 | 31.71% | 12.23 | 6.67 | 10.11 | 50.1 | 40.02 | 45.95
|  | 23 | 23.93% | 18.47 | 0.12 | 7.77 | 68.42 | 36 | 45.52
|  | 24 | 0.3994% | 0.14 | 0.12 | 0.13 | 36.75 | 35.01 | 36.14
|  | 25 | 0.3954% | 0.14 | 0.12 | 0.13 | 37.02 | 34.8 | 36.07
|  | 26 | 0.3902% | 0.14 | 0.12 | 0.13 | 37.45 | 35.15 | 36.2
|  | 27 | 0.3943% | 0.14 | 0.12 | 0.13 | 37.65 | 35.46 | 36.35
|  | 28 | 0.4075% | 0.15 | 0.12 | 0.13 | 36.89 | 35.31 | 36.23
|  | 29 | 0.4059% | 0.13 | 0.12 | 0.13 | 36.84 | 35.57 | 36.33
|  | 30 | 0.406% | 0.15 | 0.12 | 0.13 | 37.03 | 35.4 | 36.3
|  | 31 | 0.4126% | 0.14 | 0.12 | 0.13 | 36.9 | 35.55 | 36.32
|  | TOTAL | 259.9% | 131.81 | 28.84 | 84.46 | 1332.87 | 1111.11 | 1203.88
|  | AVERAGE | 8.383% | 4.2519 | 0.93032 | 2.7245 | 42.9958 | 35.8423 | 38.8348
|  | MAXIMUM | 31.86% | 18.47 | 6.69 | 10.39 | 68.42 | 40.16 | 46.67
|  | MINIMUM | 0.3722% | 0.13 | 0.11 | 0.12 | 36.69 | 34.52 | 35.87
PAGE 16
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL FIVE
|  | RUN DATE |  |  | PERMIT NUMBER 0054569-142-UO
|  | 2026-07-30 |  |  | 1/07/04 thru 1/06/09 |  |  | I.D. #:5006A11311
|  | MARCH | % INFL. | MAX | MIN | WELL 5 | MAX | MIN | AVG
|  | 2004 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 23.91% | 10.67 | 5.13 | 8.35 | 56.7 | 40.16 | 49.23
|  | 2 | 23.05% | 10.9 | ER | 7.8 | 58.67 | 34.55 | 47.52
|  | 3 | 23.81% | 11.78 | 4.38 | 7.75 | 61.46 | 38.87 | 47.01
|  | 4 | 23.07% | 10.83 | 3.64 | 7.58 | 57.3 | 37.6 | 46.87
|  | 5 | 23.27% | 10.48 | 0.98 | 7.53 | 56.4 | 36.08 | 46.78
|  | 6 | 15.71% | 10.4 | ER | 5.02 | 56.02 | 33.54 | 42.9
|  | 7 | 24.41% | 10.31 | 4.87 | 7.66 | 56.08 | 39.66 | 47.2
|  | 8 | 22.98% | 9.85 | 4.26 | 7.26 | 55.39 | 38.77 | 46.21
|  | 9 | 22.92% | 9.66 | 3.28 | 7.24 | 53.43 | 37.4 | 46.13
|  | 10 | 22.86% | 9.04 | 3.3 | 7.27 | 50.77 | 37.19 | 45.92
|  | 11 | 22.94% | 9.04 | 3.66 | 7.25 | 50.72 | 37.82 | 45.77
|  | 12 | 23.08% | 9.05 | 3.19 | 7.35 | 50.71 | 37.06 | 46.11
|  | 13 | 17.01% | 10.02 | ER | 5.42 | 54.41 | 33.65 | 43.26
|  | 14 | 16.71% | 10.63 | ER | 5.35 | 56.67 | 33.36 | 43.17
|  | 15 | 9.79% | 10.65 | ER | 3.23 | 56.85 | 34.96 | 40.15
|  | 16 |  | ER | ER | ER | 36.15 | 34.39 | 35.3
|  | 17 |  | ER | ER | ER | 36.14 | 34.45 | 35.25
|  | 18 |  | ER | ER | ER | 35.86 | 33.06 | 34.87
|  | 19 | 2.335% | 16.13 | ER | 0.76 | 82.3 | 34.05 | 37.38
|  | 20 |  | ER | ER | ER | 36.31 | 33.29 | 35.02
|  | 21 |  | ER | ER | ER | 36.37 | 34.33 | 35.16
|  | 22 |  | ER | ER | ER | 35.67 | 34.25 | 35.09
|  | 23 | 8.563% | 8.92 | ER | 2.78 | 50.3 | 34.05 | 39.48
|  | 24 | 23.81% | 9.07 | 4.74 | 7.75 | 50.62 | 39.46 | 46.73
|  | 25 | 20.38% | 11.11 | ER | 6.7 | 58.66 | 33.51 | 45.51
|  | 26 | 23.08% | 11.38 | 4.16 | 7.69 | 59.74 | 38.58 | 46.99
|  | 27 | 24.08% | 11.44 | 5.17 | 7.94 | 60.25 | 40.52 | 47.74
|  | 28 | 22.63% | 9.08 | 3.9 | 7.22 | 50.89 | 38.24 | 45.79
|  | 29 | 23.89% | 9.09 | 4.53 | 7.65 | 50.92 | 39.4 | 46.91
|  | 30 | 22.95% | 9.73 | 4.1 | 7.35 | 53.91 | 38.5 | 46.32
|  | 31 | 24.09% | 9.04 | 4.91 | 7.59 | 50.8 | 40.12 | 46.59
|  | TOTAL | 511.3% | 258.3 | 68.2 | 165.49 | 1616.47 | 1130.87 | 1344.36
|  | AVERAGE | 20.45% | 10.332 | 4.0118 | 6.6196 | 52.1442 | 36.4797 | 43.3665
|  | MAXIMUM | 24.41% | 16.13 | 5.17 | 8.35 | 82.3 | 40.52 | 49.23
|  | MINIMUM | 2.335% | 8.92 | 0.98 | 0.76 | 35.67 | 33.06 | 34.87
PAGE 17
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
INJECTION WELL SUMMARY
RUN DATE
2026-07-30
| MARCH | INFLUENT | EFFLUENT | EFFLUENT | IW-1 | IW-2 | IW-3 | IW-4 | IW-5 | TOTAL
| 2004 | FLOW | FLOW | SS | LBS SS | LBS SS | LBS SS | LBS SS | LBS SS | LBS SS
|  | MGD | MGD
| 1 | 34.923 | 33.838 | 8 | 503.736 | 632.5056 | 555.7776 | 8.6736 | 557.112 | 2249.1312
| 2 | 33.842 | 32.431 | 12 | 905.724 | 751.6008 | 803.6424 | 13.0104 | 780.624 | 3241.5912
| 3 | 32.544 | 31.379 | 11 | 783.4596 | 795.3858 | 581.6316 | 11.9262 | 710.985 | 2871.462
| 4 | 32.86 | 31.864 | 6 | 416.8332 | 420.336 | 370.296 | 6.5052 | 379.3032 | 1586.7684
| 5 | 32.363 | 31.647 | 15 | 1037.079 | 1043.334 | 920.736 | 16.263 | 942.003 | 3943.152
| 6 | 31.963 | 30.711 | 13 | 956.2644 | 967.1064 | 855.4338 | 14.0946 | 544.2684 | 3323.073
| 7 | 31.38 | 29.895 | 11 | 782.5422 | 553.1922 | 695.3892 | 11.9262 | 702.7284 | 2733.852
| 8 | 31.59 | 30.65 | 11 | 738.507 | 743.094 | 655.0236 | 11.9262 | 666.0324 | 2802.657
| 9 | 31.592 | 30.542 | 12 | 803.6424 | 807.6456 | 711.5688 | 13.0104 | 724.5792 | 3047.436
| 10 | 31.801 | 30.659 | 15 | 1010.808 | 1010.808 | 894.465 | 15.012 | 909.477 | 3825.558
| 11 | 31.601 | 30.611 | 24 | 1613.2896 | 1617.2928 | 1423.1376 | 24.0192 | 1451.16 | 6104.88
| 12 | 31.848 | 31.085 | 10 | 681.378 | 684.714 | 601.314 | 10.842 | 612.99 | 2580.396
| 13 | 31.858 | 30.61 | 11 | 794.4684 | 801.8076 | 709.1502 | 11.9262 | 497.2308 | 2802.657
| 14 | 32.025 | 30.546 | 12 | 911.7288 | 928.7424 | 671.5368 | 13.0104 | 535.428 | 3047.436
| 15 | 32.993 | 32.012 | 9 | 599.7294 | 604.9836 | 526.1706 | 434.5974 | 242.4438 | 1973.3274
| 16 | 32.778 | 32.342 | 9 | 581.715 | 583.9668 | 502.1514 | 755.8542
| 17 | 32.612 | 32.394 | 13 | 750.2664 | 883.623 | 756.7716 | 1126.4838
| 18 | 32.716 | 32.194 | 9 | 601.9812 | 606.4848 | 522.4176 | 688.3002
| 19 | 32.551 | 32.845 | 11 | 652.2714 | 744.9288 | 645.8496 | 862.356 | 69.7224 | 2112.7722
| 20 | 32.624 | 31.957 | 10 | 673.038 | 678.042 | 592.14 | 728.082
| 21 | 32.208 | 31.516 | 13 | 702.5616 | 864.1074 | 749.1822 | 1104.7998
| 22 | 31.884 | 31.592 | 17 | 955.5972 | 1121.4798 | 969.7752 | 1433.3958
| 23 | 32.466 | 31.379 | 11 | 850.4298 | 320.1726 | 743.094 | 712.8198 | 255.0372 | 2168.7336
| 24 | 32.546 | 31.405 | 15 | 1070.856 | 1088.37 | 786.879 | 16.263 | 969.525 | 3915.63
| 25 | 32.876 | 31.835 | 20 | 1449.492 | 1469.508 | 1256.004 | 21.684 | 1117.56 | 5292.564
| 26 | 33.314 | 32.356 | 14 | 992.46 | 1002.9684 | 882.7056 | 15.1788 | 897.8844 | 3776.0184
| 27 | 32.973 | 31.698 | 11 | 628.419 | 821.9904 | 719.2416 | 11.9262 | 728.4156 | 2898.0666
| 28 | 31.898 | 30.252 | 17 | 1129.9866 | 1131.4044 | 998.1312 | 18.4314 | 1023.6516 | 4283.1738
| 29 | 32.025 | 30.923 | 12 | 702.5616 | 862.6896 | 752.6016 | 13.0104 | 765.612 | 3083.4648
| 30 | 32.02 | 30.911 | 12 | 813.6504 | 817.6536 | 718.5744 | 13.0104 | 735.588 | 3085.4664
| 31 | 31.508 | 30.499 | 10 | 702.228 | 577.128 | 622.998 | 10.842 | 633.006 | 2535.36
| TOTAL | 1004.182 | 974.578 | 384 | 25796.7042 | 25937.0664 | 23193.7902 | 8149.1808 | 17452.3674 | 79284.627
| AVERAGE | 32.393 | 31.438 | 12.3871 | 832.1517 | 836.6796 | 748.1868 | 262.8768 | 698.0947 | 3171.3851
PAGE 18
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
| RUN DATE |  |  |  | SOLIDS REMOVAL INVENTORY DATA SHEET
2026-07-30
| MARCH | TONS | CAKE |  |  |  | MARCH | RAGS | GRIT | OTHER
| 2004 | SLUDGE | TSS |  |  |  | 2004 |  |  | (vac)
| 1st - 7th | [5 empty] | 1st - 7th
| 1 | 175 | 17.35 |  |  |  | 1
| 2 | 175 | 17.75 |  |  |  | 2
| 3 | 175 | 18.34 |  |  |  | 3
| 4 | 175 | 18.16 |  |  |  | 4 |  | 10
| 5 | 150 |  |  |  |  | 5 | 10
| 6 | 0 |  |  |  |  | 6
| 7 | 25 | 16.61 |  |  |  | 7
| TOTAL = | 875 | 17.642 | = AVG. |  |  | TOTAL = | 10 | 10 | 0
| 8th - 14th | [5 empty] | 8th - 14th
| 8 | 150 | 17.56 |  |  |  | 8
| 9 | 175 | 18.01 |  |  |  | 9 |  |  | 4500
| 10 | 150 | 19.03 |  |  |  | 10
| 11 | 175 | 19.25 |  |  |  | 11 |  | 10
| 12 | 125 |  |  |  |  | 12 | 10
| 13 | 0 |  |  |  |  | 13
| 14 | 0 | 17.71 |  |  |  | 14
| TOTAL = | 775 | 18.312 | = AVG. |  |  | TOTAL = | 10 | 10 | 4500
| 15th - 22nd | [5 empty] | 15th-22nd
| 15 | 150 | 17.83 |  |  |  | 15
| 16 | 175 | 17.82 |  |  |  | 16
| 17 | 150 |  |  |  |  | 17
| 18 | 150 | 18.3 |  |  |  | 18
| 19 | 150 |  |  |  |  | 19 | 10 | 10
| 20 | 25 |  |  |  |  | 20
| 21 | 0 | 17.46 |  |  |  | 21
| 22 | 150 | 17.83 |  |  |  | 22
| TOTAL = | 950 | 17.848 | = AVG. |  |  | TOTAL = | 10 | 10 | 0
| 23rd - 31st | [5 empty] | 23rd-31st
| 23 | 175 | 19.07 |  |  |  | 23
| 24 | 150 | 18.61 |  |  |  | 24
| 25 | 175 | 20.72 |  |  |  | 25
| 26 | 100 |  |  |  |  | 26 | 10 | 10
| 27 | 25 |  |  |  |  | 27
| 28 | 0 | 18.62 |  |  |  | 28
| 29 | 75 | 17.94 |  |  |  | 29
| 30 | 125 | 17.85 |  |  |  | 30
| 31 | 125 | 18.89 |  |  |  | 31
| TOTAL = | 950 | 18.8143 | = AVG. |  |  | TOTAL = | 10 | 10 | 0
RAGS & GRIT go to Central LandFill
Other(VAC) go to BCSR
PAGE 19

## INJECTION PAGES
|  |  |  | UNDERGROUND INJECTION CONTROL | [10 empty] | UNDERGROUND INJECTION CONTROL | [10 empty] | UNDERGROUND INJECTION CONTROL
[15 empty] | MONTHLY OPERATING REPORT | [10 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES |  |  |  |  | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES |  |  |  |  | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [10 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [10 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-1 | [7 empty] | Wet Well Description: |  |  | Effuent Wet Well for IW-1, IW-2, IW3, IW-4 and IW-5 | [7 empty] | Monitoring Well Decription: |  |  | UPPER ZONE OF MONITORING WELL MW-1
Permit #: |  | 0054569-142-UO |  |  |  |  | Date of Issuance: |  | 2004-01-07 |  | Facility ID #: |  | 5006M02066 |  |  |  | Permit Number: |  |  | FLA041378 |  | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | 0054569-142-UO
[22 empty] | Monitoring Well ID #: |  |  | 5006A11311
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2009-01-06 | [7 empty] | Issue Date: |  |  | 1999-10-18 |  | As Identified in Permit: |  | Monitor Well MW-1 Upper Monitor Zone |  |  |  | Issue Date: |  |  | 2004-01-07
[22 empty] | Monitoring Well Interval: |  |  | 1288' to 1320'
Injection Well ID #: |  | 5006A11308 | [8 empty] | Wet Well ID #: |  | Well Facility U-001 |  |  |  | Expiration Date: |  |  | 2004-10-17 |  | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.7 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24 | Associated Injection Well(s):
Injection Interval: |  |  | 2799' to 3513' | [18 empty] | 500A11311 |  |  | INJECTION WELL IW-5
[11 empty] | Injection Well ID #: |  |  | Injection Well Description
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s): | [10 empty] | 5006A11308 |  |  | INJECTION WELL IW-1
[11 empty] | 5006A11309 |  |  | INJECTION WELL IW-2 | [7 empty] | REPORT MONTH / YEAR: |  | 2004-03-01 | DATE OF SAP / RECORDING: |  |  | 2004-03-02 | 2004-03-09 | 2004-03-16 | 2004-03-23 | 2004-03-30
Monitoring Zone ID #: | [5 empty] | Description |  |  |  |  | 5006A11310 |  |  | INJECTION WELL IW-3
[11 empty] | N/A |  |  | INJECTION WELL IW-4 | [7 empty] | OPERATOR'S NAME: |  |  | BAYLER, J.
UO-06-279401 |  | UPPER ZONE OF MONITORING WELL MW-2 | [8 empty] | 5006A11311 |  |  | INJECTION WELL IW-5
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A
UO-06-279401 |  | LOWER ZONE OF MONITORING WELL MW-2
[11 empty] | THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [10 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [10 empty] | REPORT MONTH / YEAR: |  | 2004-03-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous |  |  | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2004-03-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous |  |  | OPERATOR'S NAME: |  |  | BAYLER, J.
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
OPERATOR'S NAME: |  |  | BAYLER, J. | [7 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A | [7 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4474-A | [7 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: |  |  |  | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 48.77 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 46.4 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: |  |  |  | PARAMETER |  |  |  | Sampling Frequency |  |  |  | VALUE |  | UNITS | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 48.1655 | PSIG
[11 empty] | Nitrogen, Total as N |  |  |  |  | Daily/Monthly Average |  |  | 15.2809 |  | mg/L as N | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[11 empty] | Nitrogen, Nitrate, Total as N |  |  |  |  | Daily/Monthly Average |  |  | 0.3309 |  | mg/L as N | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7166 | mg/l
Total monthly flow | [7 empty] | 249.76 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 3840 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [7 empty] | Nitrogen, Total Kjeildahl as N |  |  |  |  | Daily/Monthly Average |  |  | 14.95 |  | mg/L as N | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.8476 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 18.13 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.998 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 80.5 |  | PSIG | pH |  |  |  |  | Daily/Monthly Average |  |  | 6.4742 |  | s.u. | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 8.06 | Std units
Monthly average of the daily flow rates | [7 empty] | 8.0568 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 11848 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 10.5597 |  | MG | Phosphorus, Total as P |  |  |  |  | Daily/Monthly Average |  |  | 1.1915 |  | mg/L as P | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 1.768 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 73.6 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [10 empty] | Total Dissolved Solids (TDS) |  |  |  |  | Daily/Monthly Average |  |  | 1352.6452 |  | mg/L | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.01 | mg/l
Monthly average pressure | [7 empty] | 46.4813 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 848.8 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 35.5 |  | PSIG | Residue, Total filterable (TSS dried at 180 C) |  |  |  |  | Daily/Monthly Average |  |  | 12.3871 |  | mg/L | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[11 empty] | Specific Conductance (Temperature Compensated) |  |  |  |  | Daily/Monthly Average |  |  | 2772.2581 |  | umhos/cm | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just | [6 empty] | Temperature, Water |  |  |  |  | Daily/Monthly Average |  |  | 80.4839 |  | deg C
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [9 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just |  |  | Date: |  |  |  |  | (Signature):
Date:
(Signature):
|  |  |  | UNDERGROUND INJECTION CONTROL | [21 empty] | UNDERGROUND INJECTION CONTROL
|  |  |  | MONTHLY OPERATING REPORT | [21 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES | [15 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [21 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-2 | [18 empty] | Monitoring Well Decription: |  |  | LOWER ZONE OF MONITORING WELL MW-1
Permit #: |  | 0054569-142-UO |  |  |  |  | Date of Issuance: |  | 2004-01-07 | [12 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | 0054569-142-UO
[22 empty] | Monitoring Well ID #: |  |  | 5006A11311
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2009-01-06 | [12 empty] | As Identified in Permit: |  | Monitor Well MW-1 Lower Monitor Zone |  |  |  | Issue Date: |  |  | 2004-01-07
[22 empty] | Monitoring Well Interval: |  |  | 1449' to 1557'
Injection Well ID #: |  | 5006A11309 | [19 empty] | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.7 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24
Injection Interval: |  |  | 2798' to 3518' | [18 empty] | 500A11311 |  |  | INJECTION WELL IW-5
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s):
[22 empty] | REPORT MONTH / YEAR: |  | 2004-03-01 | DATE OF SAP / RECORDING: |  |  | 2004-03-02 | 2004-03-09 | 2004-03-16 | 2004-03-23 | 2004-03-30
Monitoring Zone ID #: | [5 empty] | Description
[22 empty] | OPERATOR'S NAME: |  |  | BAYLER, J.
UO-06-279401 |  | UPPER ZONE OF MONITORING WELL MW-2
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A
UO-06-279401 |  | LOWER ZONE OF MONITORING WELL MW-2
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [21 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2004-03-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
OPERATOR'S NAME: |  |  | BAYLER, J. | [18 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4474-A | [18 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 42.01 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 37.25 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: | [14 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 40.9332 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 9413.4 | mg/l
Total monthly flow | [7 empty] | 250.35 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 5120 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [18 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 9.56 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 15.92 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 9.74 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 68.87 |  | PSIG | [11 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7.448 | Std units
Monthly average of the daily flow rates | [7 empty] | 8.0758 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 15714 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 10.5766 |  | MG | [11 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 1.768 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 73 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [21 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.01 | mg/l
Monthly average pressure | [7 empty] | 45.5084 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 783.6 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 36 |  | PSIG | [11 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [21 empty] | (Signature):
Date:
|  |  |  | UNDERGROUND INJECTION CONTROL | [21 empty] | UNDERGROUND INJECTION CONTROL
|  |  |  | MONTHLY OPERATING REPORT | [21 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES | [15 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [21 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-3 | [18 empty] | Monitoring Well Decription: |  |  | UPPER ZONE OF MONITORING WELL MW-2
Permit #: |  | 0054569-142-UO |  |  |  |  | Date of Issuance: |  | 2004-01-07 | [12 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | 0054569-142-UO
[22 empty] | Monitoring Well ID #: |  |  | 5006A11308 & 309
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2009-01-06 | [12 empty] | As Identified in Permit: |  | Monitor Well MW-2 Upper Monitor Zone |  |  |  | Issue Date: |  |  | 2004-01-07
[22 empty] | Monitoring Well Interval: |  |  | 1300' to 1344'
Injection Well ID #: |  | 5006A11310 | [19 empty] | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.7 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24
Injection Interval: |  |  | 2800' to 3977' | [18 empty] | 5006A11308 |  |  | INJECTION WELL IW-1
[22 empty] | 5006A11309 |  |  | INJECTION WELL IW-2
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s):
[22 empty] | REPORT MONTH / YEAR: |  | 2004-03-01 | DATE OF SAP / RECORDING: |  |  | 2004-03-02 | 2004-03-09 | 2004-03-16 | 2004-03-23 | 2004-03-30
Monitoring Zone ID #: | [5 empty] | Description
[22 empty] | OPERATOR'S NAME: |  |  | BAYLER, J.
UO-06-279510 |  | UPPER ZONE OF MONITORING WELL MW-3
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A
UO-06-279510 |  | LOWER ZONE OF MONITORING WELL MW-3
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [21 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2004-03-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
OPERATOR'S NAME: |  |  | BAYLER, J. | [18 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4474-A | [18 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 32.09 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 26.89 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: | [14 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 30.2574 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7113.2 | mg/l
Total monthly flow | [7 empty] | 225.15 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 3700 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [18 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.8462 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 16.66 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.014 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 83.1 |  | PSIG | [11 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 8.118 | Std units
Monthly average of the daily flow rates | [7 empty] | 7.2629 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 11598 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 9.514 |  | MG | [11 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 1.768 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 72.6 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [21 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.01 | mg/l
Monthly average pressure | [7 empty] | 46.8697 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 829.2 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 36.1 |  | PSIG | [11 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [21 empty] | (Signature):
Date:
|  |  |  | UNDERGROUND INJECTION CONTROL | [21 empty] | UNDERGROUND INJECTION CONTROL
|  |  |  | MONTHLY OPERATING REPORT | [21 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES | [15 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [21 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-4 | [18 empty] | Monitoring Well Decription: |  |  | LOWER ZONE OF MONITORING WELL MW-2
Permit #: |  | 0054569-142-UO |  |  |  |  | Date of Issuance: |  | 2004-01-07 | [12 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | 0054569-142-UO
[22 empty] | Monitoring Well ID #: |  |  | 5006A11308 & 309
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2009-01-06 | [12 empty] | As Identified in Permit: |  | Monitor Well MW-2 Lower Monitor Zone |  |  |  | Issue Date: |  |  | 2004-01-07
[22 empty] | Monitoring Well Interval: |  |  | 1970' to 2025'
Injection Well ID #: |  | N/A | [19 empty] | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.7 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24
Injection Interval: |  |  | 2804' to 3977' | [18 empty] | 5006A11308 |  |  | INJECTION WELL IW-1
[22 empty] | 5006A11309 |  |  | INJECTION WELL IW-2
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s):
[22 empty] | REPORT MONTH / YEAR: |  | 2004-03-01 | DATE OF SAP / RECORDING: |  |  | 2004-03-02 | 2004-03-09 | 2004-03-16 | 2004-03-23 | 2004-03-30
Monitoring Zone ID #: | [5 empty] | Description
[22 empty] | OPERATOR'S NAME: |  |  | BAYLER, J.
UO-06-279510 |  | UPPER ZONE OF MONITORING WELL MW-3
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A
UO-06-279510 |  | LOWER ZONE OF MONITORING WELL MW-3
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [21 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2004-03-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
OPERATOR'S NAME: |  |  | BAYLER, J. | [18 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4474-A | [18 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 42.64 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 36.85 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: | [14 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 41.7668 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 30924 | mg/l
Total monthly flow | [7 empty] | 84.46 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 17640 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [18 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.358 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 18.47 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 2.28 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 68.42 |  | PSIG | [11 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7.492 | Std units
Monthly average of the daily flow rates | [7 empty] | 2.7245 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 46000 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 3.557 |  | MG | [11 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 1.768 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 70.8 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [21 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.01 | mg/l
Monthly average pressure | [7 empty] | 38.8348 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 2554 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 35.6 |  | PSIG | [11 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [21 empty] | (Signature):
Date:
|  |  |  | UNDERGROUND INJECTION CONTROL | [21 empty] | UNDERGROUND INJECTION CONTROL
|  |  |  | MONTHLY OPERATING REPORT | [21 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES | [15 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [21 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-5 | [18 empty] | Monitoring Well Decription: |  |  | UPPER ZONE OF MONITORING WELL MW-3
Permit #: |  | 0054569-142-UO |  |  |  |  | Date of Issuance: |  | 2004-01-07 | [12 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | 0054569-142-UO
[22 empty] | Monitoring Well ID #: |  |  | 5006A11310
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2009-01-06 | [12 empty] | As Identified in Permit: |  | Monitor Well MW-3 Upper Monitor Zone |  |  |  | Issue Date: |  |  | 2004-01-07
[22 empty] | Monitoring Well Interval: |  |  | 1300' to 1349'
Injection Well ID #: |  | 5006A11311 | [19 empty] | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.7 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24
Injection Interval: |  |  | 2818' to 3462' | [18 empty] | 5006A11310 |  |  | INJECTION WELL IW-3
[22 empty] | N/A |  |  | INJECTION WELL IW-4
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s):
[22 empty] | REPORT MONTH / YEAR: |  | 2004-03-01 | DATE OF SAP / RECORDING: |  |  | 2004-03-02 | 2004-03-09 | 2004-03-16 | 2004-03-23 | 2004-03-30
Monitoring Zone ID #: | [5 empty] | Description
[22 empty] | OPERATOR'S NAME: |  |  | BAYLER, J.
UO-06-279512 |  | UPPER ZONE OF MONITORING WELL MW-1
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A
UO-06-279512 |  | LOWER ZONE OF MONITORING WELL MW-1
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [21 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2004-03-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
OPERATOR'S NAME: |  |  | BAYLER, J. | [18 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4474-A | [18 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 32.15 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 19.15 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: | [14 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 29.9955 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7092 | mg/l
Total monthly flow | [7 empty] | 165.49 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 3760 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [18 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.8608 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 16.13 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.026 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 82.3 |  | PSIG | [11 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 8.11 | Std units
Monthly average of the daily flow rates | [7 empty] | 6.6196 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 11690 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 8.6787 |  | MG | [11 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 1.768 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 70.4 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [21 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.01 | mg/l
Monthly average pressure | [7 empty] | 43.3665 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 829.8 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 34.5 |  | PSIG | [11 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [21 empty] | (Signature):
Date:
UNDERGROUND INJECTION CONTROL
MONTHLY OPERATING REPORT
[22 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
[22 empty] | Monitoring Well Decription: |  |  | LOWER ZONE OF MONITORING WELL MW-3
[22 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | 0054569-142-UO
[22 empty] | Monitoring Well ID #: |  |  | 5006A11310
[22 empty] | As Identified in Permit: |  | Monitor Well MW-3 Lower Monitor Zone |  |  |  | Issue Date: |  |  | 2004-01-07
[22 empty] | Monitoring Well Interval: |  |  | 1970 to 2027'
Associated Injection Well(s):
[22 empty] | Injection Well ID #: |  |  | Injection Well Description
[22 empty] | 5006A11310 |  |  | INJECTION WELL IW-3
[22 empty] | N/A |  |  | INJECTION WELL IW-4
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
[22 empty] | REPORT MONTH / YEAR: |  | 2004-03-01 | DATE OF SAP / RECORDING: |  |  | 2004-03-02 | 2004-03-09 | 2004-03-16 | 2004-03-23 | 2004-03-30
[22 empty] | OPERATOR'S NAME: |  |  | BAYLER, J.
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
[22 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
[22 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
[22 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 45.72 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 38.51 | PSIG
[22 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 44.5977 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
[22 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 28168.4 | mg/l
[22 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 16200 | mg/l
[22 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 2.41 | mg/l
[22 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 2.94 | mg/l
[22 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7.484 | Std units
[22 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 42340 | umho/cm
[22 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
[22 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 69.4 | deg. F
[22 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.0106 | mg/l
[22 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 2444 | mg/l
[22 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
Date:

## DEP FORMS
Department of Environmental Protection Discharge Monitoring Report - Part A
When Completed mail this report to: Department of Environmental Protection, Wastewater Facilities Management Section, MS 3551, 2600 Blair Stone Road, Tallahassee, FL 32399-2400
PERMITEE NAME: | City of Fort Lauderdale |  |  |  |  | PERMIT NUMBER: |  | FLA041378 |  | REPORT: | Monthly
MAILING ADDRESS: | 949 NW 38th Street |  |  |  |  | LIMIT: |  | Final |  | GROUP: | Domestic
| Fort Lauderdale, FL 33309 |  |  |  |  | CLASS SIZE: |  | N/A |  | GMS TEST SITE
[6 empty] | GMS ID NO. |  | 5006M02066 |  | NO:
FACILITY: | City of Fort Lauderdale G. T. Lohmeyer WWTF |  |  |  |  | MONITORING GROUP NUMBER: |  | U-001
LOCATION: | 1765 SE 18th Street |  |  |  |  | PLANT SIZE/TREATMENT TYPE: |  | IIA
Fort Lauderdale, FL 33316
COUNTY: | Broward | [5 empty] | MONITORING PERIOD: |  |  | 2004-03-01
Parameter |  | Quantity of Loading |  | Units |  | Quality or Concentration |  | Units | No. Ex. | Frequency of Analysis | Sample Type
Flow | Sample Measurement | 10.5597 | 8.0568 | [5 empty] | 0
PARM Code 50050 1 Mon.Site No. EFF-002 | Permit Requirement | 18.3 (Peak Hour.) | Report (Mo. Avg.) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
Flow | Sample Measurement | 10.5766 | 8.0758 | [5 empty] | 0
PARM Code 50050 1 Mon.Site No. EFF-003 | Permit Requirement | 18.3 (Peak Hour.) | Report (Mo. Avg.) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
Flow | Sample Measurement | 9.514 | 7.2629 | [5 empty] | 0
PARM Code 50050 1 Mon.Site No. EFF-004 | Permit Requirement | 18.3 (Peak Hour.) | Report (Mo. Avg.) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
Flow | Sample Measurement | 3.557 | 2.7245 | [5 empty] | 0
PARM Code 50050 1 Mon.Site No. EFF-005 | Permit Requirement | 18.0 (Peak Hour.) | Report (Mo. Avg.) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
Flow | Sample Measurement | 8.6787 | 6.6196 | [5 empty] | 0
PARM Code 50050 1 Mon.Site No. EFF-006 | Permit Requirement | 18.3 (Peak Hour.) | Report (Mo. Avg.) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
I certify under penalty of law that I have personally examined and am familiar with the informantion submitted herein; and based on my inquiry of those individuals immeadiately responsible for obtaining the information, I believe the submitted
information is true, accurate and complete. I am aware that there are significant penalties for submitting false information including the possiblity of fine and imprisonment.
NAME/TITLE OF PRINCIPAL EXECUTIVE OFFICER OR AUTHORIZED AGENT |  |  |  | SIGNATURE OF PRINCIPAL EXECUTIVE OFFICER OR AUTHORIZED AGENT |  |  |  |  | TELEPHONE |  | DATE (YY/MM/DD)
954-523-1002 ext 2021
REGIONAL WASTEWATER FACILITIES MANAGER
COMMENTS AND EXPLANATION OF ANY VIOLATIONS (Reference all attachments here):
Version 8/13/99
Department of Environmental Protection Discharge Monitoring Report - Part A (Continued)
[12 empty] | PERMITEE NAME: | City of Fort Lauderdale G. T. Lohmeyer WWTF |  |  |  | PERMIT NUMBER: |  | FLA041378 | MONITORING GROUP NUMBER: U-001 |  |  | REPORT: | Monthly
[20 empty] | MONITORING PERIOD: |  |  |  | 2004-03-01
[12 empty] | Parameter |  |  | Quantity of Loading |  | Units |  | Quality or Concentration |  | Units | No. Ex. | Frequency of Analysis | Sample Type
[12 empty] | BOD, Carbonaceous 5 day, 20C |  | Sample Measurement |  |  |  | 4.3 |  |  |  | 0
[12 empty] | PARM Code 80082 Y Mon.Site No. EFF-001 |  | Permit Requirement |  |  |  | 20.0 (An.Avg.) |  |  | mg/l |  | Daily | 24-hour FPC
[12 empty] | BOD, Carbonaceous 5 day, 20C |  | Sample Measurement |  |  |  | 4.06 | 4.1136 | 8 |  | 0
[12 empty] | PARM Code 80082 1 Mon.Site No. EFF-001 |  | Permit Requirement |  |  |  | 30.0 (Mo.Avg.) | 45.0 (Week.Avg.) | 60.0 (Max.) | mg/l |  | Daily | 24-hour FPC
[12 empty] | Solids, Total Suspended |  | Sample Measurement |  |  |  | 14.6 |  |  |  | 0
[12 empty] | PARM Code 00530 Y Mon.Site No. EFF-001 |  | Permit Requirement |  |  |  | 20.0 (An.Avg.) |  |  | mg/l |  | Daily | 24-hour FPC
[12 empty] | Solids, Total Suspended |  | Sample Measurement |  |  |  | 12.3871 | 12.6857 | 24 |  | 0
[12 empty] | PARM Code 00530 1 Mon.Site No. EFF-001 |  | Permit Requirement |  |  |  | 30.0 (Mo.Avg.) | 45.0 (Week.Avg.) | 60.0 (Max.) | mg/l |  | Daily | 24-hour FPC
[12 empty] | pH |  | Sample Measurement |  |  |  | 6.1 |  |  |  | 0
[12 empty] | PARM Code 00400 1 Mon.Site No. EFF-001 |  | Permit Requirement |  |  |  | 6.0 (Min.) |  |  | s.u. |  | Continuous | Meter
[12 empty] | Flow |  | Sample Measurement | 34.55 | 32.393 | [5 empty] | 0
[12 empty] | PARM Code 50050 G Mon.Site No. INF-001 |  | Permit Requirement | 43.0 (3-Mo.Avg.) | Report (Mo.Avg.) | mgd | [5 empty] | Continuous | Flow meters with 24-hour recording chart
[12 empty] | BOD, Carbonaceous 5 day, 20C |  | Sample Measurement |  |  |  | 105.6645 |  |  |  | N/A
[12 empty] | PARM Code 80082 G Mon.Site No. INF-002 |  | Permit Requirement |  |  |  | Report (Mo.Avg.) |  |  | mg/l |  | Daily | 24-hour FPC
[12 empty] | Solids, Total Suspended |  | Sample Measurement |  |  |  | 210.6452 |  |  |  | N/A
[12 empty] | PARM Code 00530 G Mon.Site No. INF-002 |  | Permit Requirement |  |  |  | Report (Mo.Avg.) |  |  | mg/l |  | Daily | 24-hour FPC
Version 8/13/99

## JULIAN CONVERT
2004-03-01 | 38047 | 1999-01-01 | 1886
FROM DATE ON "DATA INPUT" PAGE | [5 empty] | 2004-03-01
2004
MONTHYY.PAR RANGE TO COMPILE (JULIAN DAY VALUES) FOR SPLIT PROGRAM ARE | [7 empty] | 61 | THROUGH | 1918
|  | 3 | MARCH
[5 empty] | 2004-03-01 | 2004-03-01 | 3
2004-03-01 |  |  |  |  | 1 | JANUARY |  | 1995 | 1995-01-01
[5 empty] | 2 | FEBRUARY |  | 1996 | 1996-01-01
[5 empty] | 3 | MARCH |  | 1997 | 1997-01-01
MARCH |  | 1 |  | 3 | 4 | APRIL |  | 1998 | 1998-01-01
|  | 0 |  | 0 | 5 | MAY |  | 1999 | 1999-01-01
|  | 1 |  |  | 6 | JUNE |  | 2000 | 2000-01-01
|  | 0 |  |  | 7 | JULY |  | 2001 | 2001-01-01
|  | 1 |  | 0 | 8 | AUGUST |  | 2002 | 2002-01-01
|  |  |  | 3 | 9 | SEPTEMBER |  | 2003 | 2003-01-01
[5 empty] | 10 | OCTOBER |  | 2004 | 2004-01-01
[5 empty] | 11 | NOVEMBER |  | 2005 | 2005-01-01
2004 |  |  |  |  | 12 | DECEMBER |  | 2006 | 2006-01-01
38047 | [6 empty] | MARCH | 2007 | 2007-01-01
37987 | [7 empty] | 2008 | 2008-01-01
60 | 1 |  | 1 | 61 | Monday
| 2 |  | 2 | 62 | Tuesday
| 3 |  | 3 | 63 | Wednesday
| 4 |  | 4 | 64 | Thursday
| 5 |  | 5 | 65 | Friday
| 6 |  | 6 | 66 | Saturday
| 7 |  | 7 | 67 | Sunday
| 8 |  | 8 | 68 | Monday
| 9 |  | 9 | 69 | Tuesday
| 10 |  | 10 | 70 | Wednesday
| 11 |  | 11 | 71 | Thursday
| 12 |  | 12 | 72 | Friday
| 13 |  | 13 | 73 | Saturday
| 14 |  | 14 | 74 | Sunday
| 15 |  | 15 | 75 | Monday
| 16 |  | 16 | 76 | Tuesday
| 17 |  | 17 | 77 | Wednesday
| 18 |  | 18 | 78 | Thursday
| 19 |  | 19 | 79 | Friday
| 20 |  | 20 | 80 | Saturday
| 21 |  | 21 | 81 | Sunday
| 22 |  | 22 | 82 | Monday
| 23 |  | 23 | 83 | Tuesday
| 24 |  | 24 | 84 | Wednesday
| 25 |  | 25 | 85 | Thursday
| 26 |  | 26 | 86 | Friday
| 27 |  | 27 | 87 | Saturday
| 28 |  | 28 | 88 | Sunday
| 29 |  | 29 | 89 | Monday
| 30 |  | 30 | 90 | Tuesday
| 31 |  | 31 | 91 | Wednesday
31