## DATA INPUT
ENTER THE AVERAGE MONTHLY INFLUENT FLOW
INTO THE CORROSPONDING BOXES BELOW:
MAY | 42.135 | APRIL | 33.738
ENTER THE PRESENT MONTH AND YEAR IN BOX BELOW (A5) | [5 empty] | JUNE
2003-06-01 | [5 empty] | 2003
IW-1 | IW-2 | IW-3 | IW-4 | IW-5
37 | 37.4 | 37 | 37.5 | 36.6 | 2003-06-12
|  | ENTER INJECTION WELL SHUT-IN PRESSURE ABOVE |  |  | ENTER DATE OF SHUT-IN READINGS
ENTER SLUDGE DISPOSAL SITE FOR EACH WEEK BELOW
| WEEK 1 | WEEK 2 | WEEK 3 | WEEK 4
1 st | Nutri-Cylcle Inc. | Nutri-Cylcle Inc. | Nutri-Cylcle Inc. | Nutri-Cylcle Inc.
2 nd | Arcadia, FL | Arcadia, FL | Arcadia, FL | Arcadia, FL
RAW DATA REPORT ENTRY CATEGORIES
GTL PLANT DAILY PROCESS SUMMARY
[6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
TOTAL RAW INFLUENT FLOW (MGD) | [5 empty] | 54.147 | 51.048 | 48.411 | 46.308 | 44.458 | 42.631 | 42.761 | 42.609 | 44.692 | 45.837 | 43.556 | 41.885 | 40.372 | 38.806 | 38.11 | 38.023 | 37.372 | 36.836 | 40.665 | 48.883 | 47.538 | 42.878 | 42.285 | 41.12 | 39.699 | 37.917 | 39.118 | 38.744 | 36.673 | 36.218
TOTAL EFFLUENT FLOW (MGD) | [5 empty] | 50.564 | 47.969 | 45.478 | 43.496 | 41.983 | 40.591 | 40.183 | 40.283 | 42.84 | 43.119 | 41.082 | 39.625 | 38.549 | 36.801 | 35.598 | 36.054 | 35.567 | 35.119 | 38.864 | 46.26 | 44.813 | 40.102 | 40.133 | 38.649 | 37.709 | 36.115 | 37.67 | 36.781 | 34.474 | 34.37
MAXIMUM HOURLY RAW INFLUENT FLOW (MGD) | [5 empty] | 2.509 | 2.359 | 2.268 | 2.189 | 2.169 | 2.08 | 2.294 | 2.082 | 2.243 | 2.223 | 2.133 | 2.101 | 1.984 | 1.94 | 1.942 | 1.89 | 1.819 | 1.787 | 2.46 | 2.504 | 2.398 | 2.084 | 2.009 | 2.001 | 1.932 | 1.907 | 2.077 | 1.948 | 1.905 | 1.835
MAXIMUM INSTANANEOUS PEAK RAW INFUENT FLOW (MGD) | [5 empty] | 66.375 | 64.625 | 62.125 | 61.625 | 58.969 | 59.281 | 61.844 | 61.531 | 63.813 | 63 | 60.063 | 60.375 | 57.781 | 57.375 | 58.656 | 57.75 | 57.125 | 57.125 | 67.406 | 65.75 | 64.844 | 58.438 | 56.219 | 57.25 | 56.594 | 54.875 | 60.188 | 54.531 | 55.844 | 55.469
MINIMUM INSTANANEOUS PEAK RAW INFUENT FLOW (MGD) | [5 empty] | 38.406 | 30.188 | 27.563 | 23.75 | 25.594 | 19.125 | 18.25 | 17.188 | 16.875 | 20.906 | 19.469 | 15.531 | 16.031 | 13.063 | 13.781 | 14.875 | 12.375 | 16.094 | 12.938 | 27.063 | 22.344 | 25.656 | 5.268 | 21.031 | 16.969 | 18.156 | 12.188 | 16.375 | 16 | 13.969
TOTAL RETURN ACTIVATED SLUDGE FLOW (MGD) | [5 empty] | 13.5 | 13.476 | 13.068 | 12.867 | 13.331 | 13.886 | 13.926 | 13.889 | 13.482 | 13.69 | 13.42 | 13.51 | 13.768 | 13.46 | 13.014 | 13.524 | 13.862 | 13.679 | 13.38 | 13.625 | 12.886 | 13.368 | 13.021 | 13.021 | 13.021 | 13.021 | 13.021 | 13.22 | 13.021 | 14.36
TOTAL WASTE FLOW TO DEWATERING PROCESS (MG) | [5 empty] | ER | 0.516 | 0.633 | 0.643 | 0.62 | 0.167 | 0 | 0.274 | 0.717 | 0.588 | 0.739 | 0.548 | 0.185 | 0 | 0.6 | 0.454 | 0.418 | 0.642 | 0.597 | 0.265 | 0 | 0 | 0.47 | 0.718 | 0.693 | 0.643 | 0.605 | NR | 0.546 | 0
TOTAL DAILY RAINFALL | [5 empty] | 0 | 0 | 0 | 0.2 | 0.13 | 0 | 1.76 | 0.23 | 0.24 | 0.01 | 0.33 | 0 | 0.15 | 0 | 0.25 | 0 | 0.14 | 0 | 1.75 | 1 | 0.15 | 0.7 | 0.55 | 0 | 0 | 0 | 1.65 | 0.03 | 0 | 0
RAW INFLUENT pH | [5 empty] | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.1 | 7.1 | 7.1 | 7.2 | 7.2 | 7.2 | 7.1 | 7 | 7.1 | 7 | 7.1 | 7.1 | 7.2 | 7.2 | 7.2 | 7.1 | 7.1 | 7 | 7.1 | 7.2 | 7.2 | 6.6
RAW INFLUENT HYDROGEN SULFIDE (PPM) | [5 empty] | 2 | 4 | 4 | 4 | 3 | 4 | 3 | 5 | 5 | 4 | 3 | 4 | 5 | 0 | 5 | 5 | 5 | 6 | 6 | 4 | 6 | 7 | 4 | 4 | 6 | 6 | 5 | 5 | 5 | 7
RAW INFLUENT TEMPERATURE (F ) | [5 empty] | 82 | 85 | 85 | 85 | 85 | 85 | 84 | 84 | 83 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 83 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
TOTAL DAILY KILOWATTS (FPL POWER CONSUMPTION) | [5 empty] | 32305 | 33124 | 32951 | 32070 | 32926 | 28710 | 29892 | 28293 | 32239 | 32867 | 32760 | 29969 | 28887 | 26304 | 30070 | 29376 | 30017 | 28898 | 33688 | 37490 | 34471 | 33646 | 34432 | 31717 | 31096 | ER | 29594 | 26305 | 28506 | 12966
GTL PLANT DAILY PROCESS SUMMARY
(CONTINUED)
[6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
FINAL EFFLUENT FREE CHLORINE RESIDUAL (PPM) | [5 empty] | 0.1 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0
FINAL EFFLUENT TOTAL CHLORINE RESIDUAL (PPM) | [5 empty] | 1 | 1.1 | 1.1 | 1 | 1.1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 0.8 | 0.9 | 0.9 | 0.8 | 0.9 | 0.8 | 1 | 0.9 | 0.9 | 0.9 | 0.5 | 0.9 | 0.8 | 0.9 | 0.7 | 0.8 | 0.8 | 0.7 | 0.8
FINAL EFFLUENT pH (daily average) | [5 empty] | 6.6 | 6.7 | 6.7 | 6.7 | 6.7 | 6.6 | 6.6 | 6.6 | 6.7 | 6.7 | 6.7 | 6.6 | 6.6 | 6.6 | 6.6 | 6.8 | 6.8 | 6.8 | 6.7 | 6.7 | 6.6 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.6 | 6.6 | 6.7 | 6.7
FINAL EFFLUENT pH (daily minimum) | [5 empty] | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.5 | 6.5 | 6.6 | 6.6 | 6.6 | 6.8 | 6.7 | 6.6 | 6.7 | 6.6 | 6.7 | 6.6 | 6.7 | 6.6 | 6.6 | 6.5 | 6.5 | 6.5 | 6.5
FINAL EFFLUENT pH (daily maximum) | [5 empty] | 6.7 | 6.8 | 6.8 | 6.7 | 6.7 | 6.7 | 6.7 | 6.6 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.7 | 6.7 | 7 | 7.1 | 6.8 | 6.8 | 6.8 | 6.7 | 6.7 | 6.9 | 6.8 | 6.8 | 6.8 | 6.8 | 6.6 | 6.7 | 6.7
FINAL EFFLUENT TEMPARTURE (F ) | [5 empty] | 82 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 82 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 83 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
AVERAGE CLARIFIER BLANKET DEPTH (INCHES) | [5 empty] | 47 | 43 | 42 | 43 | 40 | 44 | 50 | 49 | 50 | 48 | 46 | 44 | 48 | 52 | 52 | 45 | 48 | 44 | 38 | 43 | 45 | 41 | 45 | 40 | 33 | 30 | 39 | 45 | 37 | 38
FINAL EFFLUENT SAMPLE TEMPARTURE (C ) | [5 empty] | 0 | 8 | 3 | 2 | 1 | 8 | 8 | 1 | 10 | 1 | 3 | 10 | 8 | 7 | 7 | 10 | 0 | OS | 4 | 7 | 7 | 4 | 3 | 3 | 4 | 4 | 7 | 8 | 8 | 8
TOTAL RETURN ACTIVATED SLUDGE FLOW TO REACTOR ONE (MGD) | [5 empty] | 6.616 | 6.511 | 6.456 | 6.394 | 6.426 | 6.611 | 6.607 | 6.544 | 6.382 | 6.616 | 6.572 | 6.502 | 6.453 | 6.523 | 6.537 | 6.479 | 6.634 | 6.478 | 6.462 | 6.421 | 6.421 | 6.425 | 6.511 | 6.511 | 6.511 | 6.511 | 6.511 | 6.511 | 6.511 | 7.18
TOTAL RETURN ACTIVATED SLUDGE FLOW TO REACTOR TWO (MGD) | [5 empty] | 6.892 | 6.966 | 6.612 | 6.473 | 6.905 | 7.275 | 7.319 | 7.345 | 7.1 | 7.073 | 6.848 | 7.011 | 7.315 | 6.928 | 6.478 | 7.046 | 7.228 | 7.201 | 6.961 | 7.204 | 6.467 | 6.944 | 6.511 | 6.511 | 6.511 | 6.511 | 6.511 | 6.511 | 6.511 | 7.18
GTL PLANT DAILY PROCESS SUMMARY
CONTINUED
[6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
TOTAL DAILY TRUCKING LOAD OF DEWATERED SLUDGE REMOVED | [5 empty] | 2 | 5 | 6 | 6 | 6 | 4 | 0 | 1 | 5 | 4 | 6 | 5 | 5 | 0 | 1 | 6 | 6 | 6 | 6 | 4 | 0 | 0 | 2 | 6 | 6 | 5 | 4 | 0 | 1 | 5
TOTAL DAILY HYDROGEN PEROXIDE CONSUMED (LBS) | [5 empty] | 549 | 0 | 1886 | 2265 | 2295 | 1856 | 1047 | 130 | 1567 | 1547 | 1408 | 1517 | 1367 | 1357 | 1208 | 958 | 1178 | 659 | 1716 | 1507 | 1467 | 1078 | 1087 | 1208 | 1618 | 1228 | 1218 | 1187 | 1228 | 1228
TOTAL DAILY CHLORINE CONSUMED (LBS) | [5 empty] | 1940 | 1480 | 1500 | 1440 | 1440 | 1180 | 1360 | 1160 | 1140 | 1140 | 1100 | 1120 | 1120 | 1160 | 1040 | 1320 | 1280 | 1200 | 1200 | 1100 | 1200 | 560 | 1420 | 1060 | 1140 | 880 | 1100 | 1080 | 1100 | 820
TOTAL DAILY POLYMER CONSUMED (GALS) | [5 empty] | 0 | 129 | 57 | 67 | 99 | 41 | 0 | 43 | 38 | 81 | 48 | 38 | 47 | 21 | 11 | 30 | 68 | 74 | 50 | 0 | 0 | 0 | 21 | 81 | 66 | 36 | 3 | 4 | 34 | 0
TOTAL TONS OF LIME DELIVERED DAILY | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTAL DAILY GASIOUS OXYGEN PRODUCED (TONS) | [5 empty] | 33 | 40 | 40 | 37 | 35 | 37.2 | 35 | 35 | 39.9 | 40 | 40 | 40 | 37.5 | 34.6 | 36 | 36 | 31 | 28 | 32 | 32 | 26 | 28.6 | 30 | 30 | 39 | 37 | 29 | 32.3 | 32 | 37
AVERAGE PERCENT OXYGEN PRODUCT PURITY | [5 empty] | 99 | 100 | 99 | 99 | 100 | 99.7 | 99 | 100 | 99.5 | 100 | 99 | 99 | 99.5 | 100 | 99 | 99 | 100 | 100 | 100 | 99 | 100 | 99.9 | 100 | 100 | 99 | 99 | 87.7 | 99.8 | 100 | 99
TOTAL DAILY LIQUID OXYGEN IN STORAGE (TONS) | [5 empty] | 121 | 121 | 122 | 121 | 120 | 120 | 120 | 121 | 121 | 123 | 122 | 121 | 122 | 122 | 123 | 124 | 124 | 124 | 124 | 124 | 125 | 125 | 126 | 127 | 127 | 127 | 112 | 127 | 128 | 128
MONITORING WELL PRESSURE DATA
MONITORING WELL ONE UPPER/LOWER LEVEL
| MW-1 |  | UPPER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
MINIMUM | [5 empty] | 48.28 | 46.49 | 46.96 | 48.23 | 48.21 | 48.22 | 48.21 | 48.18 | 43.79 | 44.33 | 48.14 | 48.17 | 48.17 | 48.16 | 48.17 | 44.51 | 46.53 | 46.57 | 46.59 | 46.61 | 46.61 | 46.66 | 46.66 | 46.74 | 48.17 | 48.25 | 48.29 | 48.28 | 48.17 | 42.64
MAXIMUM | [5 empty] | 48.55 | 48.53 | 48.46 | 48.45 | 48.45 | 48.44 | 48.46 | 48.46 | 48.48 | 48.64 | 48.58 | 48.6 | 48.63 | 48.59 | 48.55 | 48.5 | 46.9 | 46.82 | 46.83 | 46.87 | 46.89 | 46.91 | 46.93 | 48.66 | 48.48 | 48.58 | 48.63 | 48.57 | 48.48 | 48.38
AVERAGE | [5 empty] | 48.47 | 47.47 | 47.92 | 48.36 | 48.32 | 48.35 | 48.35 | 48.35 | 45.39 | 47.12 | 48.37 | 48.38 | 48.38 | 48.36 | 48.36 | 45.95 | 46.63 | 46.66 | 46.67 | 46.75 | 46.78 | 46.84 | 46.84 | 47.93 | 48.36 | 48.43 | 48.47 | 48.47 | 48.35 | 44.65
| MW-1 |  | LOWER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
MINIMUM | [5 empty] | ER | ER | ER | ER | ER | 41.32 | 41.31 | 41.3 | 25.76 | 25.77 | 41.09 | 41.23 | 41.29 | 41.3 | 41.28 | 27.58 | 27.52 | 28.18 | 28.17 | 28.29 | 28.31 | 28.36 | 27.49 | 27.5 | 40.98 | 41.09 | 41.2 | 41.19 | 41.23 | 27.48
MAXIMUM | [5 empty] | ER | ER | ER | ER | 41.42 | 41.46 | 41.49 | 41.52 | 41.49 | 41.22 | 41.33 | 41.39 | 41.48 | 41.44 | 41.41 | 41.38 | 28.23 | 28.3 | 28.39 | 28.52 | 28.59 | 28.57 | 28.45 | 41.01 | 41.17 | 41.32 | 41.4 | 41.41 | 41.34 | 41.29
AVERAGE | [5 empty] | ER | ER | ER | ER | 26.2 | 41.45 | 41.44 | 41.49 | 30.11 | 36.41 | 41.28 | 41.37 | 41.4 | 41.42 | 41.42 | 31.76 | 28.01 | 28.21 | 28.29 | 28.39 | 28.42 | 28.45 | 27.8 | 37.24 | 41.02 | 41.3 | 41.35 | 41.37 | 41.32 | 31.71
MONITORING WELL TWO UPPER/LOWER LEVEL
| MW-2 |  | UPPER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
MINIMUM | bar: 1 to 30
MAXIMUM | [5 empty] | ER | ER | ER | ER | 30.9 | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER
AVERAGE | bar: 1 to 30
| MW-2 |  | LOWER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
MINIMUM | [5 empty] | 42.14 | 34.54 | 34.46 | 41.92 | ER | 42.07 | 42.11 | 42.15 | 29.51 | 29.53 | 41.73 | 41.94 | 42.02 | 42.03 | 42.07 | 30.58 | 30.57 | 41.51 | 41.67 | 41.77 | 41.82 | 41.87 | 29.4 | 29.41 | 41.75 | 41.93 | 42.06 | 42.07 | 42.04 | 30.68
MAXIMUM | [5 empty] | 42.26 | 42.26 | 41.92 | 42.07 | 42.12 | 42.19 | 42.25 | 42.3 | 42.33 | 41.79 | 42.07 | 42.18 | 42.24 | 42.24 | 42.24 | 42.23 | 41.55 | 41.72 | 41.81 | 41.88 | 41.98 | 42.01 | 42.03 | 41.77 | 42 | 42.15 | 42.24 | 42.22 | 42.18 | 42.16
AVERAGE | [5 empty] | 42.15 | 37.77 | 39.61 | 41.97 | ER | 42.07 | 42.11 | 42.21 | 33.27 | 37.9 | 41.9 | 42.01 | 42.05 | 42.07 | 42.09 | 34.21 | 38.53 | 41.54 | 41.7 | 41.88 | 41.92 | 41.98 | 33.22 | 38.2 | 41.88 | 42 | 42.04 | 42.08 | 42.07 | 34.12
MONITORING WELL THREE UPPER/LOWER LEVEL
| MW-3 |  | UPPER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
MINIMUM | [5 empty] | 31.28 | 18.72 | 18.59 | 30.74 | 30.84 | 30.9 | 30.89 | 30.93 | 19.87 | 19.87 | 30.65 | 30.88 | 30.94 | 30.96 | 31 | 20.08 | 19.96 | 30.8 | 30.97 | 31.09 | 31.14 | 31.24 | 27.18 | 27.15 | 31.56 | 31.75 | 31.85 | 31.85 | 31.79 | 17.66
MAXIMUM | [5 empty] | 31.46 | 31.45 | 30.81 | 30.96 | 31.01 | 31.11 | 31.13 | 31.17 | 31.17 | 30.78 | 31.09 | 31.19 | 31.26 | 31.25 | 31.25 | 31.23 | 30.92 | 31.09 | 31.18 | 31.29 | 31.42 | 31.47 | 31.45 | 31.64 | 31.88 | 32.02 | 32.1 | 32.06 | 31.97 | 31.91
AVERAGE | [5 empty] | 31.33 | 23.99 | 27.04 | 30.87 | 30.96 | 30.99 | 31.01 | 31.04 | 23.14 | 27.19 | 30.87 | 31 | 31.07 | 31.07 | 31.06 | 23.57 | 27.82 | 30.95 | 31.05 | 31.16 | 31.27 | 31.39 | 28.52 | 30.22 | 31.76 | 31.87 | 31.96 | 31.97 | 31.89 | 22.07
| MW-3 |  | LOWER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
MINIMUM | [5 empty] | 45.28 | 37.66 | 37.62 | 45 | 45.13 | 45.19 | 45.24 | 45.28 | 34.78 | 34.79 | 44.84 | 45.06 | 45.16 | 45.18 | 45.23 | 38.44 | 38.42 | 44.27 | 44.44 | 44.54 | 44.6 | 44.65 | 36.06 | 36.07 | 44.88 | 45.06 | 45.2 | 45.22 | 45.21 | 36.85
MAXIMUM | [5 empty] | 45.39 | 45.39 | 45 | 45.16 | 45.22 | 45.33 | 45.38 | 45.45 | 45.45 | 44.9 | 45.18 | 45.29 | 45.35 | 45.34 | 45.36 | 45.35 | 44.29 | 44.46 | 44.56 | 44.67 | 44.76 | 44.8 | 44.79 | 44.91 | 45.15 | 45.27 | 45.37 | 45.35 | 45.31 | 45.29
AVERAGE | [5 empty] | 45.37 | 40.83 | 42.77 | 45 | 45.11 | 45.26 | 45.38 | 45.4 | 37.93 | 41.68 | 44.99 | 45.16 | 45.3 | 45.3 | 45.31 | 40.67 | 42.55 | 44.4 | 44.5 | 44.53 | 44.59 | 44.72 | 38.62 | 42.41 | 44.99 | 45.12 | 45.34 | 45.36 | 45.29 | 39.55
MONITORING WELL RMW-1 UPPER/LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
[5 empty] | JULIAN DATE | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180 | 181
| RMW-1 |  | UPPER LEVEL
MINIMUM | [5 empty] | 44.19 | 38.11 | 38.03 | 43.67 | 43.84 | 43.93 | 43.97 | 44 | 44 | 43.98 | 44 | 44.03 | 43.97 | 43.9 | 43.93 | 43.96 | 44.02 | 44.06 | 44.09 | 44.15 | 44.06 | 44.05 | 43.99 | 43.91 | 43.9 | 43.9 | 43.95 | 43.9 | 43.83 | 35.69
MAXIMUM | [5 empty] | 44.3 | 44.29 | 43.69 | 43.86 | 43.95 | 44 | 44.05 | 44.08 | 44.11 | 44.09 | 44.15 | 44.16 | 44.13 | 44.07 | 44.05 | 44.07 | 44.11 | 44.14 | 44.2 | 44.22 | 44.19 | 44.14 | 44.11 | 44.05 | 44.01 | 44.02 | 44.06 | 44.05 | 43.98 | 43.93
AVERAGE | [5 empty] | 44.25 | 40.65 | 42.11 | 43.79 | 43.9 | 43.96 | 44.01 | 44.04 | 44.05 | 44.04 | 44.08 | 44.09 | 44.05 | 43.99 | 44 | 44.03 | 44.07 | 44.1 | 44.14 | 44.18 | 44.14 | 44.09 | 44.05 | 43.97 | 43.95 | 43.97 | 44.01 | 43.97 | 43.9 | 38.63
| RMW-1 |  | LOWER LEVEL
MINIMUM | [5 empty] | 21.92 | 20.43 | 20.49 | 21.46 | 21.59 | 21.66 | 21.7 | 21.7 | 21.72 | 21.72 | 21.76 | 21.76 | 21.75 | 21.73 | 21.76 | 21.78 | 21.81 | 21.81 | 21.88 | 21.89 | 21.88 | 21.9 | 21.88 | 21.84 | 21.82 | 21.85 | 21.89 | 21.85 | 21.76 | 19.02
MAXIMUM | [5 empty] | 22.04 | 22.05 | 21.46 | 21.62 | 21.68 | 21.76 | 21.8 | 21.84 | 21.85 | 21.86 | 21.91 | 21.9 | 21.88 | 21.86 | 21.88 | 21.9 | 21.9 | 21.95 | 21.97 | 22.01 | 22.01 | 22 | 22.01 | 21.97 | 21.94 | 21.99 | 22 | 21.97 | 21.91 | 21.85
AVERAGE | [5 empty] | 21.98 | 21.23 | 21.06 | 21.54 | 21.64 | 21.71 | 21.75 | 21.77 | 21.79 | 21.8 | 21.84 | 21.84 | 21.83 | 21.8 | 21.81 | 21.82 | 21.86 | 21.9 | 21.93 | 21.96 | 21.94 | 21.95 | 21.95 | 21.91 | 21.89 | 21.92 | 21.95 | 21.92 | 21.83 | 20.42
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
| INJECTION WELL ONE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 11.82 | 13.92 | 13.94 | 13.92 | 13.8 | 13.52 | 15.49 | 13.52 | 13.95 | 13.85 | 13.81 | 16.01 | 13.11 | 12.87 | 12.4 | 14.22 | 12.59 | 11.9 | 16.88 | 16.84 | 15.11 | 13.07 | 13.08 | 13.73 | 12.55 | 14.17 | 13.25 | 13.24 | 12.35 | 14.48
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 8.09 | 6.94 | 8.79 | 7.59 | 7.36 | 7.16 | 6.61 | 6.44 | 6.29 | 7.89 | 7.12 | 0.01 | 6.15 | 5.83 | 5.21 | 5.66 | 5.67 | 5.51 | 5.84 | 8.44 | 7.69 | 7.8 | 7.12 | 6.64 | 6.16 | 5.87 | 5.58 | 6.56 | 5.47 | 3.98
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 10.36 | 11.5 | 12 | 11.48 | 11.04 | 10.65 | 10.56 | 10.58 | 11.1 | 11.34 | 10.8 | 8.97 | 10.13 | 9.64 | 9.36 | 9.45 | 9.33 | 9.17 | 10.3 | 12.26 | 11.79 | 10.53 | 10.57 | 10.25 | 9.87 | 9.46 | 9.9 | 9.61 | 9.02 | 9
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | ER | ER | ER | ER | 59.14 | 61.78 | 70.4 | 61.56 | 63.67 | 62.5 | 62.64 | 70.3 | 60.18 | 58.99 | 58.65 | 63.88 | 62.42 | 56.5 | 74.6 | 74.4 | 67.17 | 61.4 | 61.4 | 65.19 | 58.5 | 66.93 | 61.02 | 63.66 | 60.68 | 66.91
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | ER | ER | ER | ER | ER | 44.62 | 43.48 | 43.25 | 42.79 | 46.37 | 44.55 | 36.72 | 42.21 | 42.05 | 40.38 | 41.44 | 41.16 | 41.48 | 41.64 | 47.57 | 45.76 | 45.95 | 44.77 | 43.66 | 42.87 | 41.98 | 41.46 | 42.96 | 40.92 | 40.3
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | ER | ER | ER | ER | 28.25 | 53.23 | 53.13 | 53.1 | 54.72 | 55.26 | 53.81 | 50.49 | 51.82 | 50.67 | 49.92 | 50.12 | 49.78 | 49.35 | 52.76 | 58.21 | 56.91 | 53.38 | 53.33 | 52.21 | 51.33 | 50.13 | 51.14 | 50.34 | 48.88 | 49.17
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
| INJECTION WELL TWO |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 11.74 | 13.72 | 13.75 | 13.79 | 13.78 | 13.53 | 15.43 | 13.38 | 13.92 | 13.77 | 13.73 | 16.27 | 13.02 | 12.78 | 12.34 | 14.06 | 12.42 | 11.86 | 16.73 | 16.62 | 14.92 | 12.99 | 12.99 | 12.03 | 12.86 | 14.35 | 13.47 | 13.46 | 12.57 | 14.82
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 8.11 | 6.77 | 8.73 | 7.47 | 7.35 | 7.24 | 6.46 | 6.26 | 6.18 | 7.88 | 7.14 | 3.86 | 6.02 | 5.57 | 5 | 5.39 | 5.49 | 5.29 | 5.61 | 8.35 | 7.74 | 7.78 | 0.05 | ER | 6.07 | 5.77 | 5.49 | 6.63 | 5.29 | 4.06
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 10.37 | 11.42 | 11.92 | 11.39 | 11.02 | 10.61 | 10.53 | 10.56 | 11.08 | 11.33 | 10.78 | 10.97 | 10.08 | 9.58 | 9.3 | 9.39 | 9.27 | 9.14 | 10.23 | 12.2 | 11.72 | 10.49 | 4.13 | ER | 10.03 | 9.63 | 10.08 | 9.8 | 9.15 | 9.11
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 55.08 | 61.55 | 61.41 | 61.44 | 61.51 | 60.68 | 69.05 | 60.47 | 62.46 | 61.37 | 61.52 | 69.97 | 59.11 | 55.58 | 57.6 | 62.73 | 61.27 | 55.49 | 73.2 | 73 | 65.99 | 60.29 | 60.25 | 60.3 | 57.45 | 65.65 | 59.92 | 62.49 | 59.59 | 65.7
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 46.1 | 43.77 | 47.56 | 44.81 | 44.25 | 43.81 | 42.66 | 42.46 | 42.02 | 45.51 | 43.76 | 43.06 | 41.43 | 41.27 | 39.63 | 40.71 | 40.41 | 40.75 | 40.89 | 46.69 | 44.94 | 45.1 | 43.91 | 37.48 | 42.06 | 41.22 | 40.7 | 42.19 | 40.2 | 39.59
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 51.37 | 54.72 | 55.93 | 54.43 | 53.42 | 52.27 | 52.16 | 52.15 | 53.73 | 54.27 | 52.84 | 53.5 | 50.88 | 49.74 | 49 | 49.23 | 48.89 | 48.46 | 51.79 | 57.16 | 55.9 | 52.41 | 52.34 | 51.03 | 50.4 | 49.22 | 50.22 | 49.45 | 48.01 | 48.3
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
| INJECTION WELL THREE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 10.16 | 12.42 | 12.44 | 12.44 | 12.44 | 12.14 | 13.85 | 12.07 | 12.56 | 12.41 | 12.38 | 14.49 | 11.79 | 11.53 | 11.14 | 12.73 | 11.24 | 10.71 | 15.16 | 15.03 | 13.53 | 11.7 | 11.69 | 12.31 | 11.36 | 12.71 | 11.81 | 11.8 | 11 | 13.01
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 6.98 | 5.92 | 7.88 | 6.74 | 6.64 | 6.48 | 5.81 | 5.63 | 5.54 | 7.06 | 6.34 | ER | 5.43 | 5.05 | 4.41 | 4.84 | 4.89 | 4.71 | 5.01 | 7.48 | 6.84 | 6.96 | 6.29 | 5.85 | 5.43 | 5.11 | 4.87 | 5.74 | 4.6 | 3.41
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 8.97 | 10.19 | 10.76 | 10.28 | 9.93 | 9.56 | 9.5 | 9.5 | 9.97 | 10.19 | 9.7 | 9.63 | 9.11 | 8.63 | 8.35 | 8.43 | 8.31 | 8.18 | 9.21 | 11.02 | 10.59 | 9.44 | 9.47 | 9.19 | 8.86 | 8.47 | 8.86 | 8.6 | 8.04 | 8.01
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 56.29 | 63.07 | 62.95 | 62.99 | 62.97 | 62.16 | 70.9 | 61.92 | 64.06 | 62.89 | 63.02 | 71.7 | 60.55 | 59.33 | 58.99 | 64.28 | 62.77 | 56.78 | 75.2 | 75 | 67.59 | 61.8 | 61.75 | 65.45 | 58.82 | 67.31 | 61.36 | 64.01 | 61.01 | 67.3
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 47.1 | 44.69 | 48.66 | 45.85 | 45.27 | 44.78 | 43.64 | 43.42 | 42.95 | 46.55 | 44.73 | 37.36 | 42.35 | 42.19 | 40.5 | 41.59 | 41.3 | 41.64 | 41.79 | 47.77 | 45.93 | 46.14 | 44.93 | 43.82 | 42.99 | 42.11 | 41.6 | 43.11 | 41.07 | 40.44
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 52.49 | 56.02 | 57.3 | 55.72 | 54.7 | 53.51 | 53.39 | 53.35 | 54.99 | 55.56 | 54.06 | 54.31 | 52.1 | 50.89 | 50.12 | 50.34 | 49.99 | 49.58 | 53.02 | 58.56 | 57.25 | 53.66 | 53.6 | 52.44 | 51.53 | 50.36 | 51.37 | 50.57 | 49.08 | 49.37
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
FUTURE
| INJECTION WELL FOUR |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 13.59 | 13.51 | 0.15 | 0.15 | 0.15 | 0.15 | 0.14 | 0.15 | 0.16 | 0.16 | 0.15 | 0.16 | 0.16 | 0.16 | 0.15 | 0.16 | 0.16 | 0.16 | 0.16 | 0.15 | 0.16 | 0.16 | 0.14 | 0.15 | ER | ER | ER | ER | ER | ER
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 9.77 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.12 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.14 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | ER | ER | ER | ER | ER | ER | ER
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 12.12 | 4.73 | 0.13 | 0.14 | 0.13 | 0.14 | 0.13 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.13 | ER | ER | ER | ER | ER | ER | ER
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | ER | ER | ER | ER | 37.52 | 37.54 | 37.88 | 37.65 | 37.71 | 37.68 | 37.62 | 38.18 | 37.6 | 62.5 | 37.29 | 37.65 | 37.39 | 37.37 | 38.35 | 38.63 | 38.3 | 37.85 | 37.71 | 37.76 | 37.52 | 37.98 | 37.61 | 37.78 | 37.59 | 38.14
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | ER | ER | ER | ER | ER | 36.45 | 36.34 | 36.29 | 36.43 | 36.6 | 36.55 | 36.42 | 36.32 | 36.26 | 36.01 | 36 | 36.03 | 36.07 | 36.06 | 36.67 | 36.66 | 36.76 | 36.66 | 36.51 | 36.37 | 36.29 | 36.25 | 36.42 | 36.18 | 36.11
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | ER | ER | ER | ER | 17.54 | 37.09 | 36.99 | 37.01 | 37.14 | 37.19 | 37.13 | 37.12 | 37.04 | 36.87 | 36.75 | 36.81 | 36.8 | 36.77 | 36.99 | 37.51 | 37.58 | 37.3 | 37.25 | 37.14 | 37.07 | 36.98 | 37.03 | 36.96 | 36.85 | 36.9
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
| INJECTION WELL FIVE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 10.04 | 12.37 | 12.24 | 12.23 | 12.23 | 12 | 13.67 | 11.92 | 12.3 | 12.21 | 12.17 | 14.07 | 11.63 | 11.37 | 11.02 | 12.45 | 11.13 | 10.56 | 14.77 | 14.68 | 13.2 | 11.52 | 11.54 | 12.03 | 11.14 | 12.53 | 11.66 | 11.72 | 10.96 | 12.78
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 7.09 | 6.1 | 8.03 | 6.93 | 6.83 | 6.69 | 6.08 | 5.91 | 5.82 | 7.22 | 6.56 | 4.89 | 5.74 | 5.38 | 4.77 | 5.13 | 5.2 | 5.02 | 5.26 | 7.63 | 7.06 | 7.14 | 6.5 | 6.11 | 5.69 | 5.36 | 5.19 | 6.08 | 4.99 | 3.52
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 8.93 | 10.14 | 10.7 | 10.23 | 9.89 | 9.56 | 9.48 | 9.49 | 9.93 | 10.12 | 9.68 | 9.86 | 9.1 | 8.67 | 8.41 | 8.49 | 8.38 | 8.26 | 9.19 | 10.86 | 10.46 | 9.42 | 9.44 | 9.18 | 8.88 | 8.51 | 8.87 | 8.63 | 8.13 | 8.1
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 56.1 | 63.09 | 62.79 | 62.41 | 62.56 | 60.22 | 68.67 | 61.56 | 63.37 | 62.83 | 62.29 | 70.1 | 59.87 | 58.04 | 57.76 | 62.78 | 59.12 | 55.58 | 74.3 | 74.7 | 66.88 | 60.15 | 58.71 | 61.53 | 57.52 | 63.96 | 59.51 | 60.72 | 56.54 | 63.74
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 41.01 | 43.36 | 47.41 | 40.56 | 44.73 | 44 | 38.26 | 42.68 | 42.46 | 45.27 | 44.48 | 42.77 | 35.42 | 40.86 | 34.45 | 41.21 | 40.73 | 41.05 | 39.08 | 46.01 | 45.62 | 45.3 | 43.51 | 42.83 | 42.01 | 36.75 | 40.37 | 42.27 | 40.57 | 39.08
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 51.39 | 54.93 | 56.19 | 54.37 | 53.49 | 52.23 | 52.04 | 52.12 | 53.65 | 54.15 | 52.62 | 53.38 | 50.47 | 49.29 | 48.42 | 48.74 | 48.34 | 48.12 | 51.44 | 56.92 | 55.34 | 51.74 | 51.77 | 50.93 | 49.89 | 48.85 | 49.9 | 49.06 | 47.54 | 47.75
GTL DAILY LABORATORY ANALYSIS REPORT DATA
| RAW INFLUENT DATA |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
RAW TOTAL SUSPENDED SOLIDS | [5 empty] | 86 | 90 | 90 | 74 | 92 | 64 | 132 | 86 | 128 | 33 | 96 | 88 | 90 | 94 | 102 | 98 | 46 | 80 | 110 | 59 | 80 | 70 | 86 | 76 | 82 | 100 | 100 | 92 | 116 | 96
RAW FIXED SUSPENDED SOLIDS | [5 empty] | 16 | 14 | 14 | 2 | 16 | 10 | 20 | 16 |  | 2 | 18 | 14 | 7 | 17 | 18 | 18 | 8 | 4 | 20 | 12 | 12 | 14 | 12 | 6 | 6 | 20 | 10 | 18 | 22 | 20
RAW ALKILINITY | [5 empty] | 202 | 196 | 198 | 196 | 198 | 212 | 200 | 196 | 188 | 190 | 190 | 190 | 192 | 188 | 192 | 202 | 192 | 196 | 204 | 202 | 200 | 192 | 206 | 202 | 194 | 196 | 198 | 196 | 218 | 208
RAW CHLORIDES | [5 empty] | 420 | 450 | 460 | 470 | 480 | 470 | 430 | 480 | 500 | 500 | 480 | 500 | 470 | 460 | 600 | 580 | 550 | 510 | 500 | 560 | 540 | 500 | 490 | 510 | 520 | 560 | 580 | 600 | 600 | 640
RAW COD | [5 empty] | 190 |  |  | 192 | 223 | 254 | 221 | 244 |  |  | 132 | 202 | 122 | 163 | 255 |  |  | 183 | 162 | 164 | 252 | 203 |  |  | 208 | 242 | 221 | 238 | 213
RAW CBOD | [5 empty] | 43.9 | 31.8 | 51 | 61.4 | 46.6 | 56 | 76 | 80.5 | 46 | 33 | 55 | 58.7 | 63.2 | 64 | 68.6 | 62.1 | 88 | 66.1 | 77.7 | 76 | 56 | 54.8 | 66 | 66 | 54 | 55 | 86 | 62 | 84 | 69
| EFFLUENT DATA |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
EFFLUENT TOTAL DISSOLVED SOLIDS | [5 empty] | 765 | 950 | 879 | 1060 | 963 | 864 | 1119 | 928 | 983 | 1193 | 1014 | 1368 | 1174 | 1008 | 1058 | 1076 | 1056 | 1100 | 1076 | 945 | 951 | 949 | 1050 | 1034 | 1145 | 1231 | 1152 | 970 | 1115 | 1044
EFFLUENT TOTAL SUSPENDED SOLIDS | [5 empty] | 10 | 9 | 11 | 10 | 15 | 18 | 16 | 12 | 10 | 8 | 8 | 11 | 11 | 10 | 10 | 12 | 20 | 15 | 10 | 10 | 14 | 10 | 11 | 11 | 12 | 15 | 14 | 11 | 11 | 12
EFFLUENT FIXED SUSPENDED SOLIDS | [5 empty] | 2 | 0 | 3 | 1 | 5 | 3 | 3 | 3 |  | 1 | 1 | 3 | 1 | 2 | 2 | 4 | 6 | 1 | 2 | 2 | 5 | 2 | 1 | 1 | 1 | 3 | 3 | 3 | 3 | 3
EFFLUENT ALKILINITY | [5 empty] | 184 | 184 | 192 | 188 | 190 | 198 | 194 | 188 | 174 | 174 | 184 | 188 | 188 | 184 | 180 | 198 | 180 | 188 | 188 | 186 | 190 | 182 | 182 | 190 | 194 | 190 | 192 | 186 | 188 | 194
EFFLUENT TURBIDITY | [5 empty] | 7.58 | 7.44 | 8.01 | 7.66 | 9.76 | 6.4 | 7.67 | 6.76 | 6.47 | 6.72 | 6.23 | 6.49 | 6.47 | 6.32 | 5.65 | 6.83 | 5.73 | 6.08 | 6.09 | 6.11 | 7.21 | 6.72 | 6.65 | 6.2 | 5.81 | 6.28 | 6.87 | 6.75 | 4.86 | 4.47
EFFLUENT CHLORIDES | [5 empty] | 390 | 410 | 420 | 450 | 450 | 530 | 440 | 530 | 440 | 480 | 470 | 460 | 470 | 470 | 500 | 570 | 550 | 540 | 520 | 550 | 490 | 490 | 500 | 520 | 510 | 530 | 580 | 580 | 590 | 590
EFFLUENT CONDUCTIVITY | [5 empty] | 1567 | 1690 | 1816 | 1881 | 1920 | 1970 | 2020 | 1965 | 1948 | 1924 | 1975 | 2030 | 1945 | 1960 | 2000 | 2150 | 2330 | 2120 | 2070 | 2000 | 1930 | 1979 | 2020 | 2050 | 2060 | 2160 | 2160 | 2040 | 2180 | 2190
EFFLUENT TOTAL BACTERIA COUNT | [5 empty] | 430 | 250 | 196 | 70 | 63 | 360 | 152 | 27 | 53 | 5500 | 22000 | 40000 | 438 | 536 | 5500 | 170 | TNTC | 280 | 98 | 290 | 3800 | 12500 | 8000 | 290 | 420 | 0 | TNTC | 223 | 0 | 180
EFFLUENT FECAL BACTERIA COUNT | [5 empty] | 0 | 0 | 0 | 36 | 9 | 0 | 0 | 0 | 9 | 0 | 9 | 9 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 9 | 0 | 402 | 0 | 0 | 0 | 0 | TNTC | 0 | 0 | 0
EFFLUENT COD | [5 empty] | 38 |  |  | 58.6 | 50.7 | 47.8 | 47 | 47 |  |  | 39.8 | 46.9 | 40.4 | 44.8 | 47.1 |  |  | 48.5 | 36.9 | 40.4 | 35.5 | 36.6 |  |  | 41.2 | 44.1 | 38.6 | 42.4 | 39.5
EFFLUENT CBOD | [5 empty] | 2.56 | 3.78 | 5.1 | 4.79 | 7.24 | 5.5 | 3.7 | 3.85 | 3.2 | 4.5 | 5.47 | 4.42 | 5.35 | 4.9 | 2.48 | 4.22 | 3.2 | 2.2 | 3.5 | 3.9 | 5.4 | 3.88 | 3.9 | 3.7 | 4.9 | 4 | 5 | 3 | 2 | 2
LABORATORY NUTRIENT DATA
RAW INFLUENT | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
RAW AMMONIA (PPM) | [5 empty] | 9.91 |  |  | 11.45 | 11.94 | 13.57 | 12.05 | 11.97 |  |  | 11.98 | 12.25 | 13.24 | 12.64 | 13 |  |  | 14.12 | 13.41 | 10.83 | 11.41 | 11.07 |  |  | 12.98 | 13.32 | 13.62 | 13.25 | 11.52
RAW NITRATES (PPM) | [5 empty] | 0.072 |  |  | 0.28 | 0.175 | 0.002 | 0.154 | 0.025 |  |  | 0.115 | 0.337 | 0.002 | 0.551 | 0.373 |  |  | 0.35 | 0.167 | 0.002 | 0.002 | 0.212 |  |  | 0.279 | 0.288 | 0.002 | 0.002 | 0.002
RAW TOTAL KNEDJAHL NITRIGEN | [5 empty] | 13.29 |  |  | 15.09 | 15.88 | 17.58 | 16.05 | 15.64 |  |  | 15.97 | 16.59 | 19.08 | 17.17 | 17.23 |  |  | 21.02 | 18.81 | 16.99 | 18.51 | 18.18 |  |  | 21.3 | 21.07 | 20.42 | 20.43 | 20.98
RAW TOTAL PHOSPHORUS | [5 empty] | 1.49 |  |  | 1.64 | 1.69 | 2.08 | 1.86 | 1.82 |  |  | 1.66 | 1.92 | 1.93 | 1.95 | 2.13 |  |  | 2.47 | 2.21 | 1.86 | 2.17 | 2.01 |  |  | 2.44 | 2.53 | 2.39 | 2.43 | 2.67
EFFLUENT | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
EFFLUENT AMMONIA (PPM) | [5 empty] | 7.12 |  |  | 9.6 | 9.8 | 10.29 | 9.14 | 9.3 |  |  | 9.81 | 8.9 | 10.51 | 9.89 | 9.12 |  |  | 11.73 | 10.7 | 8.46 | 8.15 | 8.96 |  |  | 11.23 | 10.41 | 10.76 | 10.07 | 9.52
EFFLUENT NITRATES (PPM) | [5 empty] | 0.098 |  |  | 0.21 | 0.238 | 0.182 | 0.184 | 0.256 |  |  | 0.275 | 0.663 | 0.287 | 0.273 | 0.601 |  |  | 0.279 | 0.204 | 0.177 | 0.195 | 0.201 |  |  | 0.248 | 0.22 | 0.219 | 0.24 | 0.266
EFFLUENT TOTAL KNEDJAHL NITRIGEN | [5 empty] | 9.86 |  |  | 13.16 | 13 | 14.28 | 12.52 | 12.91 |  |  | 13.06 | 12.96 | 14.1 | 13.48 | 13.33 |  |  | 16.12 | 15.15 | 12.16 | 12.23 | 13.13 |  |  | 15.92 | 15.14 | 14.77 | 14.27 | 13.23
EFFLUENT TOTAL PHOSPHORUS | [5 empty] | 0.571 |  |  | 0.725 | 0.597 | 0.958 | 0.54 | 0.412 |  |  | 0.651 | 0.662 | 0.685 | 0.82 | 0.762 |  |  | 0.872 | 0.963 | 0.969 | 1.23 | 0.992 |  |  | 0.905 | 1.19 | 1.03 | 0.884 | 0.821
LABORATORY REACTOR PROCESSES DATA
| REACTOR ONE TRAIN A |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
MIXED-LIQUIR SUSPENDED SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
AVERAGE SETTLABLE SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
MIXED LIQUIR VOLITLE SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
| REACTOR ONE TRAIN B |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
MIXED-LIQUIR SUSPENDED SOLIDS | [5 empty] | 2640 | 2430 | 2760 | 2770 | 2900 | 3430 | 2420 | 3120 | 2510 | 2820 | 2730 | 3130 | 3100 | 2840 | 2830 | 2730 | 2880 | 2850 | 2680 | 2410 | 1640 | 3120 | 2450 | 2680 | 1820 | 3050 | 3260 | 2620 | 2740 | 2080
AVERAGE SETTLABLE SOLIDS | [5 empty] | 24 | 26 | 27 | 27 | 27 | 34 | 30 | 31 | 30 | 32 | 26 | 32 | 32 | 29 | 25 | 34 | 37 | 33 | 36 | 28 | 26 | 37 | 32 | 32 | 17 | 30 | 31 | 27 | 26 | 23
MIXED LIQUIR VOLITLE SOLIDS | [5 empty] | 2110 | 2000 | 2210 | 2320 | 2320 | 2830 | 2010 | 2500 | 2060 | 2370 | 2180 | 2500 | 2480 | 2270 | 2260 | 2180 | 2440 | 2440 | 2140 | 1920 | 1530 | 2500 | 2050 | 2260 | 1540 | 2440 | 2630 | 2100 | 2190 | 1660
LABORATORY REACTOR PROCESSES DATA
CONTINUED
| REACTOR TWO TRAIN C |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
MIXED-LIQUIR SUSPENDED SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
AVERAGE SETTLABLE SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
MIXED LIQUIR VOLITLE SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
| REACTOR TWO TRAIN D |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
MIXED-LIQUIR SUSPENDED SOLIDS | [5 empty] | 2380 | 2740 | 2600 | 2680 | 2650 | 2730 | 2420 | 3460 | 2940 | 3290 | 2580 | 2960 | 2900 | 2690 | 3000 | 3060 | 3110 | 2980 | 2590 | 2310 | 1850 | 2770 | 2790 | 2970 | 2960 | 3010 | 3100 | 2820 | 2960 | 2530
AVERAGE SETTLABLE SOLIDS | [5 empty] | 24 | 28 | 25 | 24 | 25 | 32 | 31 | 31 | 28 | 30 | 26 | 31 | 31 | 27 | 25 | 37 | 37 | 32 | 33 | 27 | 25 | 35 | 30 | 30 | 26 | 30 | 31 | 27 | 26 | 26
MIXED LIQUIR VOLITLE SOLIDS | [5 empty] | 1900 | 2260 | 2080 | 2130 | 2120 | 2260 | 2030 | 2770 | 2350 | 2740 | 2060 | 2370 | 2310 | 2150 | 2400 | 2450 | 2580 | 2520 | 2070 | 1870 | 1670 | 2220 | 2340 | 2480 | 2460 | 2410 | 2490 | 2260 | 2370 | 2020
LABORATORY RETURN ACTIVATED SLUDGE AND WASTE SLUDGE DATA
| RETURN ACTIVATED SLUDGE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
PERCENT RETURN SLUDGE TOTAL SUSPENDED SOLIDS | [5 empty] | 1.26 | 0.94 | 0.93 | 0.92 | 1.1 | 0.7 | 1.72 | 1.15 | 1.06 | 0.53 | 0.75 | 0.86 | 0.91 | 0.91 | 1.11 | 1.13 | 0.9 | 1.01 | 1.04 | 1.08 | 1.04 | 1.02 | 1.08 | 1.05 | 0.72 | 0.88 | 1.04 | 0.91 | 0.98 | 0.94
PERCENT RETURN SLUDGE FIXED SUSPENDED SOLIDS | [5 empty] | 20.7 | 22.6 | 23.8 | 22.6 | 20.7 | 23.5 | 6.28 | 19.3 | 19.7 | 25.5 | 22.7 | 26.5 | 25.3 | 24.1 | 21 | 19.5 | 21.1 | 21.3 | 19.9 | 20 | 23 | 19.2 | 20.7 | 21.8 | 22.9 | 26.1 | 24.3 | 26.5 | 22.4 | 23.2
|  | WASTE SLUDGE |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
PERCENT WASTE FEED TOTAL SUSPENDED SOLDS | [5 empty] | 1.53 | 1.6 | 1.34 | 1.48 | 1.47 |  |  | 1.25 | 1.56 | 1.41 | 1.3 | 1.43 |  |  | 1.03 | 1.12 | 1.3 | 1.1 | 1.31 |  |  |  | 1.32 | 1.43 | 1.26 | 1.22 |  |  | 0.99 | 1.6
PERCENT WASTE FEED FIXED SUSPENDED SOLIDS | [5 empty] | 21.6 | 21.9 | 23.1 | 22.3 | 21.08 |  |  | 21.6 | 19.2 | 23.4 | 20.8 | 23.8 |  |  | 24.3 | 24.1 | 22.3 | 23.6 | 21.4 |  |  |  | 21.2 | 21.7 | 22.2 | 23 |  |  | 23.2 | 20
WASTE FEED SLUDGE pH | [5 empty] | 6.7 | 6.41 | 6.98 | 6.56 | 6.68 |  |  | 6.69 | 6.5 | 6.99 | 6.71 | 6.64 |  |  | 6.72 | 6.74 | 6.5 | 6.68 | 6.74 |  |  |  | 6.78 | 6.52 | 6.6 | 6.78 |  |  | 6.8 | 6.8
DEWATERING FILTRATE TOTAL SUSPENDED SOLIDS | [5 empty] | 0.2 | 0.24 | 0.24 | 0.33 | 0.24 |  |  | 0.24 | 0.27 | 0.19 | 0.19 | 0.23 |  |  | 0.23 | 0.23 | 0.22 | 0.23 | 0.27 |  |  |  | 0.2 | 0.19 | 0.2 | 0.23 |  |  | 0.18 | 0.28
DEWATERING FILTRATE FIXED SUSPENDED SOLIDS | [5 empty] | 50 | 45.8 | 45.8 | 39.4 | 50 |  |  | 45.8 | 37 | 68.4 | 57.9 | 65.2 |  |  | 52.2 | 47.8 | 54.5 | 56.5 | 48.1 |  |  |  | 55 | 68.4 | 60 | 65.2 |  |  | 61.1 | 57.1
DEWATERING FILTRATE pH | [5 empty] | 7.19 | 7.02 | 7.3 | 7.04 | 7.11 |  |  | 7.19 | 6.85 | 7.33 | 7.18 | 7.18 |  |  | 7.2 | 7.21 | 6.9 | 7.6 | 7.19 |  |  |  | 7.49 | 6.94 | 7 | 7.19 |  |  | 7.21 | 7.39
| DEWATERED CAKE SLUDGE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
PERCENT TOTAL SOLIDS PRESS CAKE | [5 empty] | 18.35 | 18.66 | 18.55 | 17.44 | 18.44 |  |  | 17.02 | 17.55 | 17.52 | 17.98 | 17.84 |  |  | 17.04 | 16.64 | 16.96 | 17.51 | 16.94 |  |  |  | 17.59 | 17.63 | 17.62 | 17.87 |  |  | 17.21 | 16.37
PERCENT FIXED SOLIDS PRESS CAKE | [5 empty] | 19.2 | 17.6 | 19.6 | 18.2 | 16.26 |  |  | 18.6 | 15.7 | 17.6 | 16.2 | 18.9 |  |  | 15.5 | 14.9 | 18.2 | 14.8 | 15.8 |  |  |  | 18.8 | 19.2 | 16.4 | 14.3 |  |  | 14.2 | 15.1
PERCENT TOTAL SOLIDS LIME CAKE
OTHER SLUDGE REMOVAL
[6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
GRIT (CU.YDS.) | [5 empty] | 2: 10; 5: 10; 19: 10; 20: 10
RAGS (CU.YDS.) | [5 empty] | 6: 10; 13: 10; 27: 10
VACUUM DEBRIS (EST. GAL) | [5 empty] | 18: 4500
MONITORING WELLS LABORATORY DATA
| MONITOR WELL ONE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
UPPER LEVEL
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
MONITORING WELLS LABORATORY DATA
| MONITOR WELL TWO |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
UPPER LEVEL
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
MONITORING WELLS LABORATORY DATA
| MONITOR WELL THREE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
FUTURE
UPPER LEVEL
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
MONITORING WELLS LABORATORY DATA
| REGIONAL MONITOR WELL ONE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
UPPER LEVEL
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
JUNE |  | 0 |  | 0
|  | 1 |  | 2
0
0
|  | 0 |  | 0
2
[5 empty] | 1st WEEK | 1: 2nd WEEK; 2: 3rd WEEK; 3: 4th WEEK
| 1 |  | 1 |  | 1 | 1: 8; 2: 15; 3: 23
| 2 |  | 2 |  | 2 | 1: 9; 2: 16; 3: 24
| 3 |  | 3 |  | 3 | 1: 10; 2: 17; 3: 25
| 4 |  | 4 |  | 4 | 1: 11; 2: 18; 3: 26
| 5 |  | 5 |  | 5 | 1: 12; 2: 19; 3: 27
| 6 |  | 6 |  | 6 | 1: 13; 2: 20; 3: 28
| 7 |  | 7 |  | 7 | 1: 14; 2: 21; 3: 29
| 8 |  | 8 |  |  | 2: 22; 3: 30
| 9 |  | 9
| 10 |  | 10
| 11 |  | 11
| 12 |  | 12
| 13 |  | 13
| 14 |  | 14
| 15 |  | 15
| 16 |  | 16
| 17 |  | 17
| 18 |  | 18
| 19 |  | 19
| 20 |  | 20
| 21 |  | 21
| 22 |  | 22
| 23 |  | 23
| 24 |  | 24
| 25 |  | 25
| 26 |  | 26
| 27 |  | 27
| 28 |  | 28
29
30
| APRIL | MARCH | FEBRUARY
| AUGUST | JULY | JUNE
| DECEMBER | NOVEMBER | OCTOBER
| FEBRUARY | JANUARY | DECEMBER
| JANUARY | DECEMBER | NOVEMBER
| JUNE | MAY | APRIL
| JULY | JUNE | MAY | MAY
| MARCH | FEBRUARY | JANUARY | APRIL
| MAY | APRIL | MARCH
| NOVEMBER | OCTOBER | SEPTEMBER
| OCTOBER | SEPTEMBER | AUGUST
| SEPTEMBER | AUGUST | JULY
| HYDROGEN PEROXIDE |  | 0.1395
| CHLORINE |  | 0.1475
| POLYMER |  | 0.61
| FPL |  | 0.055
[6 empty] | 1st WEEK |  |  | 2nd WEEK |  |  | 3rd WEEK |  |  | 4th WEEK
[7 empty] | G | H | I | J
[5 empty] | MW1 UP | 1: 311
312
313
314
315
316
317
318

## MONITOR DATA
UNDERGROUND INJECTION CONTROL SECTION
MONTHLY OPERATING REPORT DATA SUMMARY
FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT MONTH/YEAR |  |  | JUNE |  | 2003
I.D. NUMBER: 5006M02066 | [5 empty] | LEAD OPERATOR: |  |  |  | MIKE JUST
TELEPHONE NUMBER: (954) 523-1002
MONITORING WELL 1 DATA | [6 empty] | I.D. # 5006A11311
MW-1
PERMIT/CERTIFICATION NUMBER | [6 empty] | UO-06-279512
PERMIT EXPIRATION DATE |  | 2002-07-21
UPPER MONITORING INTERVAL | [6 empty] | 1,288' - 1,320' |  |  |  | Ft. bls.
Sample Date |  | 2003-06-03 |  | 2003-06-10 |  | 2003-06-17 |  | 2003-06-24
Submittal Date |  | 2003-06-04 |  | 2003-06-11 |  | 2003-06-18 |  | 2003-06-25
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 48.66 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 42.64 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 74 |  | 73 |  | 73 |  | 72 |  |  | degrees (F) |  | 73
TDS |  | 7386 |  | 7476 |  | 7641 |  | 7623 |  |  | mg/l |  | 7531.5
CHLORIDE |  | 3900 |  | 3800 |  | 3900 |  | 3850 |  |  | mg/l |  | 3862.5
AMMONIA-N |  | 0.694 |  | 0.9 |  | 0.89 |  | 0.873 |  |  | mg/l |  | 0.83925
TKN |  | 1.36 |  | 1.53 |  | 1.58 |  | 1.44 |  |  | mg/l |  | 1.4775
pH |  | 7.88 |  | 7.87 |  | 7.84 |  | 7.84 |  |  | Std units |  | 7.8575
CONDUCTIVITY |  | 12040 |  | 12050 |  | 12020 |  | 12040 |  |  | umho/cm |  | 12037.5
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.05 | < | 0.05 | < | 0.05 | < | 0.05 |  |  | mg/l |  | 0.05
SULFATE |  | 850 |  | 750 |  | 800 |  | 650 |  |  | mg/l |  | 762.5
C.O.D. 'S |  | 170 |  | 160 |  | 190 |  | 180 |  |  | mg/l |  | 175
IRON |  | 0.71 |  | 0.33 |  | 0.55 |  | 1.1 |  |  | mg/l |  | 0.6725
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
LOWER MONITORING INTERVAL | [6 empty] | 1,449' - 1,557' |  |  |  | Ft. bls
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 41.52 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 25.76 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 73 |  | 74 |  | 72 |  | 72 |  |  | degrees (F) |  | 72.75
TDS |  | 9400 |  | 9523 |  | 9636 |  | 9353 |  |  | mg/l |  | 9478
CHLORIDE |  | 5100 |  | 5100 |  | 5100 |  | 5100 |  |  | mg/l |  | 5100
AMMONIA-N |  | 9.5 |  | 9.49 |  | 9.49 |  | 9.41 |  |  | mg/l |  | 9.4725
TKN |  | 11.24 |  | 11.84 |  | 11.5 |  | 11.43 |  |  | mg/l |  | 11.5025
pH |  | 7.34 |  | 7.2 |  | 7.23 |  | 7.37 |  |  | Std units |  | 7.285
CONDUCTIVITY |  | 15600 |  | 15390 |  | 15550 |  | 15490 |  |  | umho/cm |  | 15507.5
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.05 | < | 0.05 | < | 0.05 | < | 0.05 |  |  | mg/l |  | 0.05
SULFATE |  | 750 |  | 800 |  | 800 |  | 650 |  |  | mg/l |  | 750
C.O.D. 'S |  | 300 |  | 260 |  | 240 |  | 290 |  |  | mg/l |  | 272.5
IRON |  | 0.02 |  | 0.01 |  | 0.01 |  | 0.01 |  |  | mg/l |  | 0.0125
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
PAGE 24
UNDERGROUND INJECTION CONTROL SECTION
MONTHLY OPERATING REPORT DATA SUMMARY
FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT MONTH/YEAR |  |  | JUNE |  | 2003
I.D. NUMBER: 5006M02066 | [5 empty] | LEAD OPERATOR: |  |  |  | MIKE JUST
TELEPHONE NUMBER: (954) 523-1002
MONITORING WELL 2 DATA | [6 empty] | I.D. # 5006A11308 & 309
MW-2
PERMIT/CERTIFICATION NUMBER | [6 empty] | UO-06-279401 & 508
PERMIT EXPIRATION DATE |  | 2002-07-21
UPPER MONITORING INTERVAL | [6 empty] | 1,300' - 1,344' |  |  |  | Ft. bls.
Sample Date |  | 2003-06-03 |  | 2003-06-10 |  | 2003-06-17 |  | 2003-06-24
Submittal Date |  | 2003-06-04 |  | 2003-06-11 |  | 2003-06-18 |  | 2003-06-25
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 30.9 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 0 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 71 |  | 72 |  | 71 |  | 71 |  |  | degrees (F) |  | 71.25
TDS |  | 7240 |  | 7223 |  | 7442 |  | 7267 |  |  | mg/l |  | 7293
CHLORIDE |  | 3650 |  | 3900 |  | 3850 |  | 3750 |  |  | mg/l |  | 3787.5
AMMONIA-N |  | 0.724 |  | 0.88 |  | 0.89 |  | 1.05 |  |  | mg/l |  | 0.886
TKN |  | 1.48 |  | 1.72 |  | 1.7 |  | 1.46 |  |  | mg/l |  | 1.59
pH |  | 7.98 |  | 8.03 |  | 7.95 |  | 8.07 |  |  | Std units |  | 8.0075
CONDUCTIVITY |  | 11810 |  | 11830 |  | 11760 |  | 11830 |  |  | umho/cm |  | 11807.5
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.05 | < | 0.05 | < | 0.05 | < | 0.05 |  |  | mg/l |  | 0.05
SULFATE |  | 850 |  | 800 |  | 850 |  | 650 |  |  | mg/l |  | 787.5
C.O.D. 'S |  | 170 |  | 170 |  | 190 |  | 190 |  |  | mg/l |  | 180
IRON |  | 2.74 |  | 1.89 |  | 0.96 |  | 1.35 |  |  | mg/l |  | 1.735
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
LOWER MONITORING INTERVAL | [6 empty] | 1,970' - 2,025' |  |  |  | Ft. bls
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 42.33 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 29.4 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 70 |  | 70 |  | 72 |  | 70 |  |  | degrees (F) |  | 70.5
TDS |  | 31537 |  | 32088 |  | 32470 |  | 31965 |  |  | mg/l |  | 32015
CHLORIDE |  | 18200 |  | 18800 |  | 17600 |  | 17600 |  |  | mg/l |  | 18050
AMMONIA-N |  | 1.41 |  | 1.23 |  | 1.23 |  | 1.42 |  |  | mg/l |  | 1.3225
TKN |  | 1.8 |  | 2.05 |  | 2.06 |  | 1.99 |  |  | mg/l |  | 1.975
pH |  | 7.36 |  | 7.3 |  | 7.26 |  | 7.34 |  |  | Std units |  | 7.315
CONDUCTIVITY |  | 47100 |  | 47300 |  | 46900 |  | 47100 |  |  | umho/cm |  | 47100
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.05 | < | 0.111 | < | 0.05 | < | 0.05 |  |  | mg/l |  | 0.06525
SULFATE |  | 2300 |  | 2300 |  | 2300 |  | 2900 |  |  | mg/l |  | 2450
C.O.D. 'S |  | 840 |  | 780 |  | 860 |  | 870 |  |  | mg/l |  | 837.5
IRON |  | 0.04 |  | 0.05 |  | 0.04 |  | 0.04 |  |  | mg/l |  | 0.0425
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
PAGE 25
UNDERGROUND INJECTION CONTROL SECTION
MONTHLY OPERATING REPORT DATA SUMMARY
FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT MONTH/YEAR |  |  | JUNE |  | 2003
I.D. NUMBER: 5006M02066 | [5 empty] | LEAD OPERATOR: |  |  |  | MIKE JUST
TELEPHONE NUMBER: (954) 523-1002
MONITORING WELL 2 DATA | [6 empty] | I.D. # 5006A11310
MW-3
PERMIT/CERTIFICATION NUMBER | [6 empty] | UO-06-279510
PERMIT EXPIRATION DATE |  | 2002-07-21
UPPER MONITORING INTERVAL | [6 empty] | 1,300' - 1,349' |  |  |  | Ft. bls.
Sample Date |  | 2003-06-03 |  | 2003-06-10 |  | 2003-06-17 |  | 2003-06-24
Submittal Date |  | 2003-06-04 |  | 2003-06-11 |  | 2003-06-18 |  | 2003-06-25
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 32.1 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 17.66 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 76 |  | 71 |  | 70 |  | 70 |  |  | degrees (F) |  | 71.75
TDS |  | 7290 |  | 7539 |  | 7478 |  | 7461 |  |  | mg/l |  | 7442
CHLORIDE |  | 3800 |  | 3900 |  | 3850 |  | 3850 |  |  | mg/l |  | 3850
AMMONIA-N |  | 1.07 |  | 0.89 |  | 0.87 |  | 1.05 |  |  | mg/l |  | 0.97
TKN |  | 1.4 |  | 1.5 |  | 1.53 |  | 1.51 |  |  | mg/l |  | 1.485
pH |  | 8.16 |  | 8.24 |  | 8.06 |  | 8.21 |  |  | Std units |  | 8.1675
CONDUCTIVITY |  | 11880 |  | 12080 |  | 11910 |  | 11990 |  |  | umho/cm |  | 11965
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.05 | < | 0.05 | < | 0.05 | < | 0.05 |  |  | mg/l |  | 0.05
SULFATE |  | 800 |  | 750 |  | 800 |  | 800 |  |  | mg/l |  | 787.5
C.O.D. 'S |  | 170 |  | 180 |  | 190 |  | 190 |  |  | mg/l |  | 182.5
IRON |  | 1.02 |  | 1.63 |  | 1.66 |  | 1.12 |  |  | mg/l |  | 1.3575
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
LOWER MONITORING INTERVAL | [6 empty] | 1,970' - 2,027' |  |  |  | Ft. bls
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 45.45 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 34.78 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 74 |  | 69 |  | 69 |  | 69 |  |  | degrees (F) |  | 70.25
TDS |  | 28930 |  | 28033 |  | 29750 |  | 28459 |  |  | mg/l |  | 28793
CHLORIDE |  | 16600 |  | 17800 |  | 16000 |  | 16000 |  |  | mg/l |  | 16600
AMMONIA-N |  | 2.42 |  | 2.27 |  | 2.25 |  | 2.59 |  |  | mg/l |  | 2.3825
TKN |  | 3.02 |  | 3.08 |  | 3.26 |  | 3.49 |  |  | mg/l |  | 3.2125
pH |  | 7.47 |  | 7.43 |  | 7.34 |  | 7.41 |  |  | Std units |  | 7.4125
CONDUCTIVITY |  | 43600 |  | 43600 |  | 43200 |  | 42800 |  |  | umho/cm |  | 43300
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.05 | < | 0.05 | < | 0.05 | < | 0.05 |  |  | mg/l |  | 0.05
SULFATE |  | 2000 |  | 2200 |  | 2200 |  | 2100 |  |  | mg/l |  | 2125
C.O.D. 'S |  | 660 |  | 820 |  | 850 |  | 960 |  |  | mg/l |  | 822.5
IRON |  | 0.02 |  | 0.04 |  | 0.02 |  | 0.03 |  |  | mg/l |  | 0.0275
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
PAGE 26
UNDERGROUND INJECTION CONTROL SECTION
MONTHLY OPERATING REPORT DATA SUMMARY
FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT MONTH/YEAR |  |  | JUNE |  | 2003
I.D. NUMBER: 5006M02066 | [5 empty] | LEAD OPERATOR: |  |  |  | MIKE JUST
TELEPHONE NUMBER: (954) 523-1002
REGIONAL MONITORING WELL DATA
RMW-1
PERMIT NUMBER | [6 empty] | UC06-249353
PERMIT EXPIRATION DATE |  | 1997-04-27
UPPER MONITORING INTERVAL | [6 empty] | 1300' - 1339' |  |  |  | Ft. bls.
Sample Date |  | 2003-06-03
Submittal Date |  | 2003-06-04
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 44.3 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 35.69 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 71 | [8 empty] | degrees (F) |  | 71
TDS |  | 5664 | [8 empty] | mg/l |  | 5664
CHLORIDE |  | 2900 | [8 empty] | mg/l |  | 2900
AMMONIA-N |  | 0.8 | [8 empty] | mg/l |  | 0.8
TKN |  | 1.09 | [8 empty] | mg/l |  | 1.09
pH |  | 8.34 | [8 empty] | Std units |  | 8.34
CONDUCTIVITY |  | 9370 | [8 empty] | umho/cm |  | 9370
FECAL COLIFORM |  | 0 | [8 empty] | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.05 | [8 empty] | mg/l |  | 0.05
SULFATE |  | 950 | [8 empty] | mg/l |  | 950
C.O.D. 'S |  | 130 | [8 empty] | mg/l |  | 130
IRON |  | 0.42 | [8 empty] | mg/l |  | 0.42
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
LOWER MONITORING INTERVAL | [6 empty] | 1500' - 1600' |  |  |  | Ft. bls
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 22.05 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 19.02 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 70 | [8 empty] | degrees (F) |  | 70
TDS |  | 26590 | [8 empty] | mg/l |  | 26590
CHLORIDE |  | 15400 | [8 empty] | mg/l |  | 15400
AMMONIA-N |  | 0.431 | [8 empty] | mg/l |  | 0.431
TKN |  | 0.432 | [8 empty] | mg/l |  | 0.432
pH |  | 7.84 | [8 empty] | Std units |  | 7.84
CONDUCTIVITY |  | 41300 | [8 empty] | umho/cm |  | 41300
FECAL COLIFORM |  | 0 | [8 empty] | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.05 | [8 empty] | mg/l |  | 0.05
SULFATE |  | 1150 | [8 empty] | mg/l |  | 1150
C.O.D. 'S |  | 640 | [8 empty] | mg/l |  | 640
IRON |  | 0.06 | [8 empty] | mg/l |  | 0.06
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
PAGE 27
Formulas:
LEAD OPERATOR: = [LEAD OPERATOR:, row above]+1

## WELL PRN DATA
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 1 |  |  | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180 | 181
152 | 11.82 | 8.09 | 10.36 | ER | ER | ER
153 | 13.92 | 6.94 | 11.5 | ER | ER | ER |  |  | FLOW
154 | 13.94 | 8.79 | 12 | ER | ER | ER | I |  | MAX | 11.82 | 13.92 | 13.94 | 13.92 | 13.8 | 13.52 | 15.49 | 13.52 | 13.95 | 13.85 | 13.81 | 16.01 | 13.11 | 12.87 | 12.4 | 14.22 | 12.59 | 11.9 | 16.88 | 16.84 | 15.11 | 13.07 | 13.08 | 13.73 | 12.55 | 14.17 | 13.25 | 13.24 | 12.35 | 14.48
155 | 13.92 | 7.59 | 11.48 | ER | ER | ER | N |  | MIN | 8.09 | 6.94 | 8.79 | 7.59 | 7.36 | 7.16 | 6.61 | 6.44 | 6.29 | 7.89 | 7.12 | 0.01 | 6.15 | 5.83 | 5.21 | 5.66 | 5.67 | 5.51 | 5.84 | 8.44 | 7.69 | 7.8 | 7.12 | 6.64 | 6.16 | 5.87 | 5.58 | 6.56 | 5.47 | 3.98
156 | 13.8 | 7.36 | 11.04 | 59.14 | ER | 28.25 | J |  | TOT | 10.36 | 11.5 | 12 | 11.48 | 11.04 | 10.65 | 10.56 | 10.58 | 11.1 | 11.34 | 10.8 | 8.97 | 10.13 | 9.64 | 9.36 | 9.45 | 9.33 | 9.17 | 10.3 | 12.26 | 11.79 | 10.53 | 10.57 | 10.25 | 9.87 | 9.46 | 9.9 | 9.61 | 9.02 | 9
157 | 13.52 | 7.16 | 10.65 | 61.78 | 44.62 | 53.23 | E | INJECTION WELL ONE
158 | 15.49 | 6.61 | 10.56 | 70.4 | 43.48 | 53.13 | C |  | PSI
159 | 13.52 | 6.44 | 10.58 | 61.56 | 43.25 | 53.1 | T |  | MAX | ER | ER | ER | ER | 59.14 | 61.78 | 70.4 | 61.56 | 63.67 | 62.5 | 62.64 | 70.3 | 60.18 | 58.99 | 58.65 | 63.88 | 62.42 | 56.5 | 74.6 | 74.4 | 67.17 | 61.4 | 61.4 | 65.19 | 58.5 | 66.93 | 61.02 | 63.66 | 60.68 | 66.91
160 | 13.95 | 6.29 | 11.1 | 63.67 | 42.79 | 54.72 | O |  | MIN | ER | ER | ER | ER | ER | 44.62 | 43.48 | 43.25 | 42.79 | 46.37 | 44.55 | 36.72 | 42.21 | 42.05 | 40.38 | 41.44 | 41.16 | 41.48 | 41.64 | 47.57 | 45.76 | 45.95 | 44.77 | 43.66 | 42.87 | 41.98 | 41.46 | 42.96 | 40.92 | 40.3
161 | 13.85 | 7.89 | 11.34 | 62.5 | 46.37 | 55.26 | N |  | AVG | ER | ER | ER | ER | 28.25 | 53.23 | 53.13 | 53.1 | 54.72 | 55.26 | 53.81 | 50.49 | 51.82 | 50.67 | 49.92 | 50.12 | 49.78 | 49.35 | 52.76 | 58.21 | 56.91 | 53.38 | 53.33 | 52.21 | 51.33 | 50.13 | 51.14 | 50.34 | 48.88 | 49.17
162 | 13.81 | 7.12 | 10.8 | 62.64 | 44.55 | 53.81
163 | 16.01 | 0.01 | 8.97 | 70.3 | 36.72 | 50.49 | W
164 | 13.11 | 6.15 | 10.13 | 60.18 | 42.21 | 51.82 | E
165 | 12.87 | 5.83 | 9.64 | 58.99 | 42.05 | 50.67 | L
166 | 12.4 | 5.21 | 9.36 | 58.65 | 40.38 | 49.92 | L
167 | 14.22 | 5.66 | 9.45 | 63.88 | 41.44 | 50.12 | O
168 | 12.59 | 5.67 | 9.33 | 62.42 | 41.16 | 49.78 | N
169 | 11.9 | 5.51 | 9.17 | 56.5 | 41.48 | 49.35 | E
170 | 16.88 | 5.84 | 10.3 | 74.6 | 41.64 | 52.76
171 | 16.84 | 8.44 | 12.26 | 74.4 | 47.57 | 58.21 | D
172 | 15.11 | 7.69 | 11.79 | 67.17 | 45.76 | 56.91 | A
173 | 13.07 | 7.8 | 10.53 | 61.4 | 45.95 | 53.38 | T
174 | 13.08 | 7.12 | 10.57 | 61.4 | 44.77 | 53.33 | A
175 | 13.73 | 6.64 | 10.25 | 65.19 | 43.66 | 52.21
176 | 12.55 | 6.16 | 9.87 | 58.5 | 42.87 | 51.33
177 | 14.17 | 5.87 | 9.46 | 66.93 | 41.98 | 50.13
178 | 13.25 | 5.58 | 9.9 | 61.02 | 41.46 | 51.14
179 | 13.24 | 6.56 | 9.61 | 63.66 | 42.96 | 50.34
180 | 12.35 | 5.47 | 9.02 | 60.68 | 40.92 | 48.88
181 | 14.48 | 3.98 | 9 | 66.91 | 40.3 | 49.17
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 2 |  |  | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180 | 181
152 | 11.74 | 8.11 | 10.37 | 55.08 | 46.1 | 51.37
153 | 13.72 | 6.77 | 11.42 | 61.55 | 43.77 | 54.72 |  |  | FLOW
154 | 13.75 | 8.73 | 11.92 | 61.41 | 47.56 | 55.93 | I |  | MAX | 11.74 | 13.72 | 13.75 | 13.79 | 13.78 | 13.53 | 15.43 | 13.38 | 13.92 | 13.77 | 13.73 | 16.27 | 13.02 | 12.78 | 12.34 | 14.06 | 12.42 | 11.86 | 16.73 | 16.62 | 14.92 | 12.99 | 12.99 | 12.03 | 12.86 | 14.35 | 13.47 | 13.46 | 12.57 | 14.82
155 | 13.79 | 7.47 | 11.39 | 61.44 | 44.81 | 54.43 | N |  | MIN | 8.11 | 6.77 | 8.73 | 7.47 | 7.35 | 7.24 | 6.46 | 6.26 | 6.18 | 7.88 | 7.14 | 3.86 | 6.02 | 5.57 | 5 | 5.39 | 5.49 | 5.29 | 5.61 | 8.35 | 7.74 | 7.78 | 0.05 | ER | 6.07 | 5.77 | 5.49 | 6.63 | 5.29 | 4.06
156 | 13.78 | 7.35 | 11.02 | 61.51 | 44.25 | 53.42 | J |  | TOT | 10.37 | 11.42 | 11.92 | 11.39 | 11.02 | 10.61 | 10.53 | 10.56 | 11.08 | 11.33 | 10.78 | 10.97 | 10.08 | 9.58 | 9.3 | 9.39 | 9.27 | 9.14 | 10.23 | 12.2 | 11.72 | 10.49 | 4.13 | ER | 10.03 | 9.63 | 10.08 | 9.8 | 9.15 | 9.11
157 | 13.53 | 7.24 | 10.61 | 60.68 | 43.81 | 52.27 | E | INJECTION WELL TWO
158 | 15.43 | 6.46 | 10.53 | 69.05 | 42.66 | 52.16 | C |  | PSI
159 | 13.38 | 6.26 | 10.56 | 60.47 | 42.46 | 52.15 | T |  | MAX | 55.08 | 61.55 | 61.41 | 61.44 | 61.51 | 60.68 | 69.05 | 60.47 | 62.46 | 61.37 | 61.52 | 69.97 | 59.11 | 55.58 | 57.6 | 62.73 | 61.27 | 55.49 | 73.2 | 73 | 65.99 | 60.29 | 60.25 | 60.3 | 57.45 | 65.65 | 59.92 | 62.49 | 59.59 | 65.7
160 | 13.92 | 6.18 | 11.08 | 62.46 | 42.02 | 53.73 | I |  | MIN | 46.1 | 43.77 | 47.56 | 44.81 | 44.25 | 43.81 | 42.66 | 42.46 | 42.02 | 45.51 | 43.76 | 43.06 | 41.43 | 41.27 | 39.63 | 40.71 | 40.41 | 40.75 | 40.89 | 46.69 | 44.94 | 45.1 | 43.91 | 37.48 | 42.06 | 41.22 | 40.7 | 42.19 | 40.2 | 39.59
161 | 13.77 | 7.88 | 11.33 | 61.37 | 45.51 | 54.27 | O |  | AVG | 51.37 | 54.72 | 55.93 | 54.43 | 53.42 | 52.27 | 52.16 | 52.15 | 53.73 | 54.27 | 52.84 | 53.5 | 50.88 | 49.74 | 49 | 49.23 | 48.89 | 48.46 | 51.79 | 57.16 | 55.9 | 52.41 | 52.34 | 51.03 | 50.4 | 49.22 | 50.22 | 49.45 | 48.01 | 48.3
162 | 13.73 | 7.14 | 10.78 | 61.52 | 43.76 | 52.84 | N
163 | 16.27 | 3.86 | 10.97 | 69.97 | 43.06 | 53.5
164 | 13.02 | 6.02 | 10.08 | 59.11 | 41.43 | 50.88 | W
165 | 12.78 | 5.57 | 9.58 | 57.92 | 41.27 | 49.74 | E
166 | 12.34 | 5 | 9.3 | 57.6 | 39.63 | 49 | L
167 | 14.06 | 5.39 | 9.39 | 62.73 | 40.71 | 49.23 | L
168 | 12.42 | 5.49 | 9.27 | 61.27 | 40.41 | 48.89
169 | 11.86 | 5.29 | 9.14 | 55.49 | 40.75 | 48.46 | T
170 | 16.73 | 5.61 | 10.23 | 73.2 | 40.89 | 51.79 | W
171 | 16.62 | 8.35 | 12.2 | 73 | 46.69 | 57.16 | O
172 | 14.92 | 7.74 | 11.72 | 65.99 | 44.94 | 55.9
173 | 12.99 | 7.78 | 10.49 | 60.29 | 45.1 | 52.41 | D
174 | 12.99 | 0.05 | 4.13 | 60.25 | 43.91 | 52.34 | A
175 | 12.03 | ER | ER | 60.3 | 37.48 | 51.03 | T
176 | 12.86 | 6.07 | 10.03 | 57.45 | 42.06 | 50.4 | A
177 | 14.35 | 5.77 | 9.63 | 65.65 | 41.22 | 49.22
178 | 13.47 | 5.49 | 10.08 | 59.92 | 40.7 | 50.22
179 | 13.46 | 6.63 | 9.8 | 62.49 | 42.19 | 49.45
180 | 12.57 | 5.29 | 9.15 | 59.59 | 40.2 | 48.01
181 | 14.82 | 4.06 | 9.11 | 65.7 | 39.59 | 48.3
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 3 |  |  | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180 | 181
152 | 10.16 | 6.98 | 8.97 | 56.29 | 47.1 | 52.49
153 | 12.42 | 5.92 | 10.19 | 63.07 | 44.69 | 56.02 |  |  | FLOW
154 | 12.44 | 7.88 | 10.76 | 62.95 | 48.66 | 57.3 | I |  | MAX | 10.16 | 12.42 | 12.44 | 12.44 | 12.44 | 12.14 | 13.85 | 12.07 | 12.56 | 12.41 | 12.38 | 14.49 | 11.79 | 11.53 | 11.14 | 12.73 | 11.24 | 10.71 | 15.16 | 15.03 | 13.53 | 11.7 | 11.69 | 12.31 | 11.36 | 12.71 | 11.81 | 11.8 | 11 | 13.01
155 | 12.44 | 6.74 | 10.28 | 62.99 | 45.85 | 55.72 | N |  | MIN | 6.98 | 5.92 | 7.88 | 6.74 | 6.64 | 6.48 | 5.81 | 5.63 | 5.54 | 7.06 | 6.34 | ER | 5.43 | 5.05 | 4.41 | 4.84 | 4.89 | 4.71 | 5.01 | 7.48 | 6.84 | 6.96 | 6.29 | 5.85 | 5.43 | 5.11 | 4.87 | 5.74 | 4.6 | 3.41
156 | 12.44 | 6.64 | 9.93 | 62.97 | 45.27 | 54.7 | J |  | TOT | 8.97 | 10.19 | 10.76 | 10.28 | 9.93 | 9.56 | 9.5 | 9.5 | 9.97 | 10.19 | 9.7 | 9.63 | 9.11 | 8.63 | 8.35 | 8.43 | 8.31 | 8.18 | 9.21 | 11.02 | 10.59 | 9.44 | 9.47 | 9.19 | 8.86 | 8.47 | 8.86 | 8.6 | 8.04 | 8.01
157 | 12.14 | 6.48 | 9.56 | 62.16 | 44.78 | 53.51 | E | INJECTION WELL THREE
158 | 13.85 | 5.81 | 9.5 | 70.9 | 43.64 | 53.39 | C |  | PSI
159 | 12.07 | 5.63 | 9.5 | 61.92 | 43.42 | 53.35 | T |  | MAX | 56.29 | 63.07 | 62.95 | 62.99 | 62.97 | 62.16 | 70.9 | 61.92 | 64.06 | 62.89 | 63.02 | 71.7 | 60.55 | 59.33 | 58.99 | 64.28 | 62.77 | 56.78 | 75.2 | 75 | 67.59 | 61.8 | 61.75 | 65.45 | 58.82 | 67.31 | 61.36 | 64.01 | 61.01 | 67.3
160 | 12.56 | 5.54 | 9.97 | 64.06 | 42.95 | 54.99 | I |  | MIN | 47.1 | 44.69 | 48.66 | 45.85 | 45.27 | 44.78 | 43.64 | 43.42 | 42.95 | 46.55 | 44.73 | 37.36 | 42.35 | 42.19 | 40.5 | 41.59 | 41.3 | 41.64 | 41.79 | 47.77 | 45.93 | 46.14 | 44.93 | 43.82 | 42.99 | 42.11 | 41.6 | 43.11 | 41.07 | 40.44
161 | 12.41 | 7.06 | 10.19 | 62.89 | 46.55 | 55.56 | O |  | AVG | 52.49 | 56.02 | 57.3 | 55.72 | 54.7 | 53.51 | 53.39 | 53.35 | 54.99 | 55.56 | 54.06 | 54.31 | 52.1 | 50.89 | 50.12 | 50.34 | 49.99 | 49.58 | 53.02 | 58.56 | 57.25 | 53.66 | 53.6 | 52.44 | 51.53 | 50.36 | 51.37 | 50.57 | 49.08 | 49.37
162 | 12.38 | 6.34 | 9.7 | 63.02 | 44.73 | 54.06 | N
163 | 14.49 | ER | 9.63 | 71.7 | 37.36 | 54.31
164 | 11.79 | 5.43 | 9.11 | 60.55 | 42.35 | 52.1 | W
165 | 11.53 | 5.05 | 8.63 | 59.33 | 42.19 | 50.89 | E
166 | 11.14 | 4.41 | 8.35 | 58.99 | 40.5 | 50.12 | L
167 | 12.73 | 4.84 | 8.43 | 64.28 | 41.59 | 50.34 | L
168 | 11.24 | 4.89 | 8.31 | 62.77 | 41.3 | 49.99
169 | 10.71 | 4.71 | 8.18 | 56.78 | 41.64 | 49.58 | T
170 | 15.16 | 5.01 | 9.21 | 75.2 | 41.79 | 53.02 | H
171 | 15.03 | 7.48 | 11.02 | 75 | 47.77 | 58.56 | R
172 | 13.53 | 6.84 | 10.59 | 67.59 | 45.93 | 57.25 | E
173 | 11.7 | 6.96 | 9.44 | 61.8 | 46.14 | 53.66 | E
174 | 11.69 | 6.29 | 9.47 | 61.75 | 44.93 | 53.6
175 | 12.31 | 5.85 | 9.19 | 65.45 | 43.82 | 52.44 | D
176 | 11.36 | 5.43 | 8.86 | 58.82 | 42.99 | 51.53 | A
177 | 12.71 | 5.11 | 8.47 | 67.31 | 42.11 | 50.36 | T
178 | 11.81 | 4.87 | 8.86 | 61.36 | 41.6 | 51.37 | A
179 | 11.8 | 5.74 | 8.6 | 64.01 | 43.11 | 50.57
180 | 11 | 4.6 | 8.04 | 61.01 | 41.07 | 49.08
181 | 13.01 | 3.41 | 8.01 | 67.3 | 40.44 | 49.37
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 4 |  |  | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180 | 181
152 | 13.59 | 9.77 | 12.12 | ER | ER | ER
153 | 13.51 | 0.13 | 4.73 | ER | ER | ER |  |  | FLOW
154 | 0.15 | 0.13 | 0.13 | ER | ER | ER | I |  | MAX | 13.59 | 13.51 | 0.15 | 0.15 | 0.15 | 0.15 | 0.14 | 0.15 | 0.16 | 0.16 | 0.15 | 0.16 | 0.16 | 0.16 | 0.15 | 0.16 | 0.16 | 0.16 | 0.16 | 0.15 | 0.16 | 0.16 | 0.14 | 0.15 | ER | ER | ER | ER | ER | ER
155 | 0.15 | 0.13 | 0.14 | ER | ER | ER | N |  | MIN | 9.77 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.12 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.14 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | ER | ER | ER | ER | ER | ER | ER
156 | 0.15 | 0.13 | 0.13 | 37.52 | ER | 17.54 | J |  | TOT | 12.12 | 4.73 | 0.13 | 0.14 | 0.13 | 0.14 | 0.13 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.13 | ER | ER | ER | ER | ER | ER | ER
157 | 0.15 | 0.13 | 0.14 | 37.54 | 36.45 | 37.09 | E | INJECTION WELL FOUR
158 | 0.14 | 0.12 | 0.13 | 37.88 | 36.34 | 36.99 | C |  | PSI
159 | 0.15 | 0.13 | 0.14 | 37.65 | 36.29 | 37.01 | T |  | MAX | ER | ER | ER | ER | 37.52 | 37.54 | 37.88 | 37.65 | 37.71 | 37.68 | 37.62 | 38.18 | 37.6 | 62.5 | 37.29 | 37.65 | 37.39 | 37.37 | 38.35 | 38.63 | 38.3 | 37.85 | 37.71 | 37.76 | 37.52 | 37.98 | 37.61 | 37.78 | 37.59 | 38.14
160 | 0.16 | 0.13 | 0.14 | 37.71 | 36.43 | 37.14 | I |  | MIN | ER | ER | ER | ER | ER | 36.45 | 36.34 | 36.29 | 36.43 | 36.6 | 36.55 | 36.42 | 36.32 | 36.26 | 36.01 | 36 | 36.03 | 36.07 | 36.06 | 36.67 | 36.66 | 36.76 | 36.66 | 36.51 | 36.37 | 36.29 | 36.25 | 36.42 | 36.18 | 36.11
161 | 0.16 | 0.13 | 0.14 | 37.68 | 36.6 | 37.19 | O |  | AVG | ER | ER | ER | ER | 17.54 | 37.09 | 36.99 | 37.01 | 37.14 | 37.19 | 37.13 | 37.12 | 37.04 | 36.87 | 36.75 | 36.81 | 36.8 | 36.77 | 36.99 | 37.51 | 37.58 | 37.3 | 37.25 | 37.14 | 37.07 | 36.98 | 37.03 | 36.96 | 36.85 | 36.9
162 | 0.15 | 0.13 | 0.14 | 37.62 | 36.55 | 37.13 | N
163 | 0.16 | 0.13 | 0.14 | 38.18 | 36.42 | 37.12
164 | 0.16 | 0.13 | 0.14 | 37.6 | 36.32 | 37.04 | W
165 | 0.16 | 0.13 | 0.14 | 37.44 | 36.26 | 36.87 | E
166 | 0.15 | 0.13 | 0.14 | 37.29 | 36.01 | 36.75 | L
167 | 0.16 | 0.13 | 0.14 | 37.65 | 36 | 36.81 | L
168 | 0.16 | 0.14 | 0.14 | 37.39 | 36.03 | 36.8
169 | 0.16 | 0.13 | 0.14 | 37.37 | 36.07 | 36.77 | F
170 | 0.16 | 0.13 | 0.14 | 38.35 | 36.06 | 36.99 | O
171 | 0.15 | 0.13 | 0.14 | 38.63 | 36.67 | 37.51 | U
172 | 0.16 | 0.13 | 0.14 | 38.3 | 36.66 | 37.58 | R
173 | 0.16 | 0.13 | 0.14 | 37.85 | 36.76 | 37.3
174 | 0.14 | 0.13 | 0.13 | 37.71 | 36.66 | 37.25 | D
175 | 0.15 | ER | ER | 37.76 | 36.51 | 37.14 | A
176 | ER | ER | ER | 37.52 | 36.37 | 37.07 | T
177 | ER | ER | ER | 37.98 | 36.29 | 36.98 | A
178 | ER | ER | ER | 37.61 | 36.25 | 37.03
179 | ER | ER | ER | 37.78 | 36.42 | 36.96
180 | ER | ER | ER | 37.59 | 36.18 | 36.85
181 | ER | ER | ER | 38.14 | 36.11 | 36.9
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 5 |  |  | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180 | 181
152 | 10.04 | 7.09 | 8.93 | 56.1 | 41.01 | 51.39
153 | 12.37 | 6.1 | 10.14 | 63.09 | 43.36 | 54.93 |  |  | FLOW
154 | 12.24 | 8.03 | 10.7 | 62.79 | 47.41 | 56.19 | I |  | MAX | 10.04 | 12.37 | 12.24 | 12.23 | 12.23 | 12 | 13.67 | 11.92 | 12.3 | 12.21 | 12.17 | 14.07 | 11.63 | 11.37 | 11.02 | 12.45 | 11.13 | 10.56 | 14.77 | 14.68 | 13.2 | 11.52 | 11.54 | 12.03 | 11.14 | 12.53 | 11.66 | 11.72 | 10.96 | 12.78
155 | 12.23 | 6.93 | 10.23 | 62.41 | 40.56 | 54.37 | N |  | MIN | 7.09 | 6.1 | 8.03 | 6.93 | 6.83 | 6.69 | 6.08 | 5.91 | 5.82 | 7.22 | 6.56 | 4.89 | 5.74 | 5.38 | 4.77 | 5.13 | 5.2 | 5.02 | 5.26 | 7.63 | 7.06 | 7.14 | 6.5 | 6.11 | 5.69 | 5.36 | 5.19 | 6.08 | 4.99 | 3.52
156 | 12.23 | 6.83 | 9.89 | 62.56 | 44.73 | 53.49 | J |  | TOT | 8.93 | 10.14 | 10.7 | 10.23 | 9.89 | 9.56 | 9.48 | 9.49 | 9.93 | 10.12 | 9.68 | 9.86 | 9.1 | 8.67 | 8.41 | 8.49 | 8.38 | 8.26 | 9.19 | 10.86 | 10.46 | 9.42 | 9.44 | 9.18 | 8.88 | 8.51 | 8.87 | 8.63 | 8.13 | 8.1
157 | 12 | 6.69 | 9.56 | 60.22 | 44 | 52.23 | E | INJECTION WELL FIVE
158 | 13.67 | 6.08 | 9.48 | 68.67 | 38.26 | 52.04 | C |  | PSI
159 | 11.92 | 5.91 | 9.49 | 61.56 | 42.68 | 52.12 | T |  | MAX | 56.1 | 63.09 | 62.79 | 62.41 | 62.56 | 60.22 | 68.67 | 61.56 | 63.37 | 62.83 | 62.29 | 70.1 | 59.87 | 58.04 | 57.76 | 62.78 | 59.12 | 55.58 | 74.3 | 74.7 | 66.88 | 60.15 | 58.71 | 61.53 | 57.52 | 63.96 | 59.51 | 60.72 | 56.54 | 63.74
160 | 12.3 | 5.82 | 9.93 | 63.37 | 42.46 | 53.65 | I |  | MIN | 41.01 | 43.36 | 47.41 | 40.56 | 44.73 | 44 | 38.26 | 42.68 | 42.46 | 45.27 | 44.48 | 42.77 | 35.42 | 40.86 | 34.45 | 41.21 | 40.73 | 41.05 | 39.08 | 46.01 | 45.62 | 45.3 | 43.51 | 42.83 | 42.01 | 36.75 | 40.37 | 42.27 | 40.57 | 39.08
161 | 12.21 | 7.22 | 10.12 | 62.83 | 45.27 | 54.15 | O |  | AVG | 51.39 | 54.93 | 56.19 | 54.37 | 53.49 | 52.23 | 52.04 | 52.12 | 53.65 | 54.15 | 52.62 | 53.38 | 50.47 | 49.29 | 48.42 | 48.74 | 48.34 | 48.12 | 51.44 | 56.92 | 55.34 | 51.74 | 51.77 | 50.93 | 49.89 | 48.85 | 49.9 | 49.06 | 47.54 | 47.75
162 | 12.17 | 6.56 | 9.68 | 62.29 | 44.48 | 52.62 | N
163 | 14.07 | 4.89 | 9.86 | 70.1 | 42.77 | 53.38
164 | 11.63 | 5.74 | 9.1 | 59.87 | 35.42 | 50.47 | W
165 | 11.37 | 5.38 | 8.67 | 58.04 | 40.86 | 49.29 | E
166 | 11.02 | 4.77 | 8.41 | 57.76 | 34.45 | 48.42 | L
167 | 12.45 | 5.13 | 8.49 | 62.78 | 41.21 | 48.74 | L
168 | 11.13 | 5.2 | 8.38 | 59.12 | 40.73 | 48.34
169 | 10.56 | 5.02 | 8.26 | 55.58 | 41.05 | 48.12 | F
170 | 14.77 | 5.26 | 9.19 | 74.3 | 39.08 | 51.44 | I
171 | 14.68 | 7.63 | 10.86 | 74.7 | 46.01 | 56.92 | V
172 | 13.2 | 7.06 | 10.46 | 66.88 | 45.62 | 55.34 | E
173 | 11.52 | 7.14 | 9.42 | 60.15 | 45.3 | 51.74
174 | 11.54 | 6.5 | 9.44 | 58.71 | 43.51 | 51.77 | D
175 | 12.03 | 6.11 | 9.18 | 61.53 | 42.83 | 50.93 | A
176 | 11.14 | 5.69 | 8.88 | 57.52 | 42.01 | 49.89 | T
177 | 12.53 | 5.36 | 8.51 | 63.96 | 36.75 | 48.85 | A
178 | 11.66 | 5.19 | 8.87 | 59.51 | 40.37 | 49.9
179 | 11.72 | 6.08 | 8.63 | 60.72 | 42.27 | 49.06
180 | 10.96 | 4.99 | 8.13 | 56.54 | 40.57 | 47.54
181 | 12.78 | 3.52 | 8.1 | 63.74 | 39.08 | 47.75

## RMW PRN DATA
julian | u-avg | u-min | u-max | l-avg | l-min | l-max
152 | 21.98 | 21.92 | 22.04 | 44.25 | 44.19 | 44.3 | R |  |  | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180 | 181
153 | 21.23 | 20.43 | 22.05 | 40.65 | 38.11 | 44.29 | E
154 | 21.06 | 20.49 | 21.46 | 42.11 | 38.03 | 43.69 | G |  | LOW
155 | 21.54 | 21.46 | 21.62 | 43.79 | 43.67 | 43.86 | I |  | MIN | 21.92 | 20.43 | 20.49 | 21.46 | 21.59 | 21.66 | 21.7 | 21.7 | 21.72 | 21.72 | 21.76 | 21.76 | 21.75 | 21.73 | 21.76 | 21.78 | 21.81 | 21.81 | 21.88 | 21.89 | 21.88 | 21.9 | 21.88 | 21.84 | 21.82 | 21.85 | 21.89 | 21.85 | 21.76 | 19.02
156 | 21.64 | 21.59 | 21.68 | 43.9 | 43.84 | 43.95 | O |  | MAX | 22.04 | 22.05 | 21.46 | 21.62 | 21.68 | 21.76 | 21.8 | 21.84 | 21.85 | 21.86 | 21.91 | 21.9 | 21.88 | 21.86 | 21.88 | 21.9 | 21.9 | 21.95 | 21.97 | 22.01 | 22.01 | 22 | 22.01 | 21.97 | 21.94 | 21.99 | 22 | 21.97 | 21.91 | 21.85
157 | 21.71 | 21.66 | 21.76 | 43.96 | 43.93 | 44 | N |  | AVG | 21.98 | 21.23 | 21.06 | 21.54 | 21.64 | 21.71 | 21.75 | 21.77 | 21.79 | 21.8 | 21.84 | 21.84 | 21.83 | 21.8 | 21.81 | 21.82 | 21.86 | 21.9 | 21.93 | 21.96 | 21.94 | 21.95 | 21.95 | 21.91 | 21.89 | 21.92 | 21.95 | 21.92 | 21.83 | 20.42
158 | 21.75 | 21.7 | 21.8 | 44.01 | 43.97 | 44.05 | A | RMW
159 | 21.77 | 21.7 | 21.84 | 44.04 | 44 | 44.08 | L |  | UP
160 | 21.79 | 21.72 | 21.85 | 44.05 | 44 | 44.11 |  |  | MIN | 44.19 | 38.11 | 38.03 | 43.67 | 43.84 | 43.93 | 43.97 | 44 | 44 | 43.98 | 44 | 44.03 | 43.97 | 43.9 | 43.93 | 43.96 | 44.02 | 44.06 | 44.09 | 44.15 | 44.06 | 44.05 | 43.99 | 43.91 | 43.9 | 43.9 | 43.95 | 43.9 | 43.83 | 35.69
161 | 21.8 | 21.72 | 21.86 | 44.04 | 43.98 | 44.09 | M |  | MAX | 44.3 | 44.29 | 43.69 | 43.86 | 43.95 | 44 | 44.05 | 44.08 | 44.11 | 44.09 | 44.15 | 44.16 | 44.13 | 44.07 | 44.05 | 44.07 | 44.11 | 44.14 | 44.2 | 44.22 | 44.19 | 44.14 | 44.11 | 44.05 | 44.01 | 44.02 | 44.06 | 44.05 | 43.98 | 43.93
162 | 21.84 | 21.76 | 21.91 | 44.08 | 44 | 44.15 | O |  | AVG | 44.25 | 40.65 | 42.11 | 43.79 | 43.9 | 43.96 | 44.01 | 44.04 | 44.05 | 44.04 | 44.08 | 44.09 | 44.05 | 43.99 | 44 | 44.03 | 44.07 | 44.1 | 44.14 | 44.18 | 44.14 | 44.09 | 44.05 | 43.97 | 43.95 | 43.97 | 44.01 | 43.97 | 43.9 | 38.63
163 | 21.84 | 21.76 | 21.9 | 44.09 | 44.03 | 44.16 | N
164 | 21.83 | 21.75 | 21.88 | 44.05 | 43.97 | 44.13 | I
165 | 21.8 | 21.73 | 21.86 | 43.99 | 43.9 | 44.07 | T
166 | 21.81 | 21.76 | 21.88 | 44 | 43.93 | 44.05 | O
167 | 21.82 | 21.78 | 21.9 | 44.03 | 43.96 | 44.07 | R
168 | 21.86 | 21.81 | 21.9 | 44.07 | 44.02 | 44.11
169 | 21.9 | 21.81 | 21.95 | 44.1 | 44.06 | 44.14 | W
170 | 21.93 | 21.88 | 21.97 | 44.14 | 44.09 | 44.2 | E
171 | 21.96 | 21.89 | 22.01 | 44.18 | 44.15 | 44.22 | L
172 | 21.94 | 21.88 | 22.01 | 44.14 | 44.06 | 44.19 | L
173 | 21.95 | 21.9 | 22 | 44.09 | 44.05 | 44.14
174 | 21.95 | 21.88 | 22.01 | 44.05 | 43.99 | 44.11
175 | 21.91 | 21.84 | 21.97 | 43.97 | 43.91 | 44.05 | R
176 | 21.89 | 21.82 | 21.94 | 43.95 | 43.9 | 44.01 | M
177 | 21.92 | 21.85 | 21.99 | 43.97 | 43.9 | 44.02 | W
178 | 21.95 | 21.89 | 22 | 44.01 | 43.95 | 44.06
179 | 21.92 | 21.85 | 21.97 | 43.97 | 43.9 | 44.05 | O
180 | 21.83 | 21.76 | 21.91 | 43.9 | 43.83 | 43.98 | N
181 | 20.42 | 19.02 | 21.85 | 38.63 | 35.69 | 43.93 | E
152 | ER | ER | ER | 48.47 | 48.28 | 48.55 | M |  |  | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180 | 181
153 | ER | ER | ER | 47.47 | 46.49 | 48.53 | O
154 | ER | ER | ER | 47.92 | 46.96 | 48.46 | N |  | LOW
155 | ER | ER | ER | 48.36 | 48.23 | 48.45 | I |  | MIN | ER | ER | ER | ER | ER | 41.32 | 41.31 | 41.3 | 25.76 | 25.77 | 41.09 | 41.23 | 41.29 | 41.3 | 41.28 | 27.58 | 27.52 | 28.18 | 28.17 | 28.29 | 28.31 | 28.36 | 27.49 | 27.5 | 40.98 | 41.09 | 41.2 | 41.19 | 41.23 | 27.48
156 | 26.2 | ER | 41.42 | 48.32 | 48.21 | 48.45 | T |  | MAX | ER | ER | ER | ER | 41.42 | 41.46 | 41.49 | 41.52 | 41.49 | 41.22 | 41.33 | 41.39 | 41.48 | 41.44 | 41.41 | 41.38 | 28.23 | 28.3 | 28.39 | 28.52 | 28.59 | 28.57 | 28.45 | 41.01 | 41.17 | 41.32 | 41.4 | 41.41 | 41.34 | 41.29
157 | 41.45 | 41.32 | 41.46 | 48.35 | 48.22 | 48.44 | O |  | AVG | ER | ER | ER | ER | 26.2 | 41.45 | 41.44 | 41.49 | 30.11 | 36.41 | 41.28 | 41.37 | 41.4 | 41.42 | 41.42 | 31.76 | 28.01 | 28.21 | 28.29 | 28.39 | 28.42 | 28.45 | 27.8 | 37.24 | 41.02 | 41.3 | 41.35 | 41.37 | 41.32 | 31.71
158 | 41.44 | 41.31 | 41.49 | 48.35 | 48.21 | 48.46 | R | MW-1
159 | 41.49 | 41.3 | 41.52 | 48.35 | 48.18 | 48.46 |  |  | UP
160 | 30.11 | 25.76 | 41.49 | 45.39 | 43.79 | 48.48 | W |  | MIN | 48.28 | 46.49 | 46.96 | 48.23 | 48.21 | 48.22 | 48.21 | 48.18 | 43.79 | 44.33 | 48.14 | 48.17 | 48.17 | 48.16 | 48.17 | 44.51 | 46.53 | 46.57 | 46.59 | 46.61 | 46.61 | 46.66 | 46.66 | 46.74 | 48.17 | 48.25 | 48.29 | 48.28 | 48.17 | 42.64
161 | 36.41 | 25.77 | 41.22 | 47.12 | 44.33 | 48.64 | E |  | MAX | 48.55 | 48.53 | 48.46 | 48.45 | 48.45 | 48.44 | 48.46 | 48.46 | 48.48 | 48.64 | 48.58 | 48.6 | 48.63 | 48.59 | 48.55 | 48.5 | 46.9 | 46.82 | 46.83 | 46.87 | 46.89 | 46.91 | 46.93 | 48.66 | 48.48 | 48.58 | 48.63 | 48.57 | 48.48 | 48.38
162 | 41.28 | 41.09 | 41.33 | 48.37 | 48.14 | 48.58 | L |  | AVG | 48.47 | 47.47 | 47.92 | 48.36 | 48.32 | 48.35 | 48.35 | 48.35 | 45.39 | 47.12 | 48.37 | 48.38 | 48.38 | 48.36 | 48.36 | 45.95 | 46.63 | 46.66 | 46.67 | 46.75 | 46.78 | 46.84 | 46.84 | 47.93 | 48.36 | 48.43 | 48.47 | 48.47 | 48.35 | 44.65
163 | 41.37 | 41.23 | 41.39 | 48.38 | 48.17 | 48.6 | L
164 | 41.4 | 41.29 | 41.48 | 48.38 | 48.17 | 48.63
165 | 41.42 | 41.3 | 41.44 | 48.36 | 48.16 | 48.59 | O
166 | 41.42 | 41.28 | 41.41 | 48.36 | 48.17 | 48.55 | N
167 | 31.76 | 27.58 | 41.38 | 45.95 | 44.51 | 48.5 | E
168 | 28.01 | 27.52 | 28.23 | 46.63 | 46.53 | 46.9
169 | 28.21 | 28.18 | 28.3 | 46.66 | 46.57 | 46.82 | I
170 | 28.29 | 28.17 | 28.39 | 46.67 | 46.59 | 46.83 | N
171 | 28.39 | 28.29 | 28.52 | 46.75 | 46.61 | 46.87 | J
172 | 28.42 | 28.31 | 28.59 | 46.78 | 46.61 | 46.89 | E
173 | 28.45 | 28.36 | 28.57 | 46.84 | 46.66 | 46.91 | C
174 | 27.8 | 27.49 | 28.45 | 46.84 | 46.66 | 46.93 | T
175 | 37.24 | 27.5 | 41.01 | 47.93 | 46.74 | 48.66 | I
176 | 41.02 | 40.98 | 41.17 | 48.36 | 48.17 | 48.48 | O
177 | 41.3 | 41.09 | 41.32 | 48.43 | 48.25 | 48.58 | N
178 | 41.35 | 41.2 | 41.4 | 48.47 | 48.29 | 48.63
179 | 41.37 | 41.19 | 41.41 | 48.47 | 48.28 | 48.57 | W
180 | 41.32 | 41.23 | 41.34 | 48.35 | 48.17 | 48.48 | E
181 | 31.71 | 27.48 | 41.29 | 44.65 | 42.64 | 48.38 | L
L
152 | 42.15 | 42.14 | 42.26 | ER | ER | ER | M |  |  | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180 | 181
153 | 37.77 | 34.54 | 42.26 | ER | ER | ER | O
154 | 39.61 | 34.46 | 41.92 | ER | ER | ER | N |  | LOW
155 | 41.97 | 41.92 | 42.07 | ER | ER | ER | I |  | MIN | 42.14 | 34.54 | 34.46 | 41.92 | ER | 42.07 | 42.11 | 42.15 | 29.51 | 29.53 | 41.73 | 41.94 | 42.02 | 42.03 | 42.07 | 30.58 | 30.57 | 41.51 | 41.67 | 41.77 | 41.82 | 41.87 | 29.4 | 29.41 | 41.75 | 41.93 | 42.06 | 42.07 | 42.04 | 30.68
156 | ER | ER | 42.12 | ER | ER | 30.9 | T |  | MAX | 42.26 | 42.26 | 41.92 | 42.07 | 42.12 | 42.19 | 42.25 | 42.3 | 42.33 | 41.79 | 42.07 | 42.18 | 42.24 | 42.24 | 42.24 | 42.23 | 41.55 | 41.72 | 41.81 | 41.88 | 41.98 | 42.01 | 42.03 | 41.77 | 42 | 42.15 | 42.24 | 42.22 | 42.18 | 42.16
157 | 42.07 | 42.07 | 42.19 | ER | ER | ER | O |  | AVG | 42.15 | 37.77 | 39.61 | 41.97 | ER | 42.07 | 42.11 | 42.21 | 33.27 | 37.9 | 41.9 | 42.01 | 42.05 | 42.07 | 42.09 | 34.21 | 38.53 | 41.54 | 41.7 | 41.88 | 41.92 | 41.98 | 33.22 | 38.2 | 41.88 | 42 | 42.04 | 42.08 | 42.07 | 34.12
158 | 42.11 | 42.11 | 42.25 | ER | ER | ER | R | MW-2
159 | 42.21 | 42.15 | 42.3 | ER | ER | ER |  |  | UP
160 | 33.27 | 29.51 | 42.33 | ER | ER | ER | W |  | MIN | bar: 152 to 181
161 | 37.9 | 29.53 | 41.79 | ER | ER | ER | E |  | MAX | ER | ER | ER | ER | 30.9 | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER
162 | 41.9 | 41.73 | 42.07 | ER | ER | ER | L |  | AVG | bar: 152 to 181
163 | 42.01 | 41.94 | 42.18 | ER | ER | ER | L
164 | 42.05 | 42.02 | 42.24 | ER | ER | ER
165 | 42.07 | 42.03 | 42.24 | ER | ER | ER | T
166 | 42.09 | 42.07 | 42.24 | ER | ER | ER | W
167 | 34.21 | 30.58 | 42.23 | ER | ER | ER | O
168 | 38.53 | 30.57 | 41.55 | ER | ER | ER
169 | 41.54 | 41.51 | 41.72 | ER | ER | ER | I
170 | 41.7 | 41.67 | 41.81 | ER | ER | ER | N
171 | 41.88 | 41.77 | 41.88 | ER | ER | ER | J
172 | 41.92 | 41.82 | 41.98 | ER | ER | ER | E
173 | 41.98 | 41.87 | 42.01 | ER | ER | ER | C
174 | 33.22 | 29.4 | 42.03 | ER | ER | ER | T
175 | 38.2 | 29.41 | 41.77 | ER | ER | ER | I
176 | 41.88 | 41.75 | 42 | ER | ER | ER | O
177 | 42 | 41.93 | 42.15 | ER | ER | ER | N
178 | 42.04 | 42.06 | 42.24 | ER | ER | ER
179 | 42.08 | 42.07 | 42.22 | ER | ER | ER | W
180 | 42.07 | 42.04 | 42.18 | ER | ER | ER | E
181 | 34.12 | 30.68 | 42.16 | ER | ER | ER | L
L
152 | 45.37 | 45.28 | 45.39 | 31.33 | 31.28 | 31.46 | M |  |  | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180 | 181
153 | 40.83 | 37.66 | 45.39 | 23.99 | 18.72 | 31.45 | O
154 | 42.77 | 37.62 | 45 | 27.04 | 18.59 | 30.81 | N |  | LOW
155 | 45 | 45 | 45.16 | 30.87 | 30.74 | 30.96 | I |  | MIN | 45.28 | 37.66 | 37.62 | 45 | 45.13 | 45.19 | 45.24 | 45.28 | 34.78 | 34.79 | 44.84 | 45.06 | 45.16 | 45.18 | 45.23 | 38.44 | 38.42 | 44.27 | 44.44 | 44.54 | 44.6 | 44.65 | 36.06 | 36.07 | 44.88 | 45.06 | 45.2 | 45.22 | 45.21 | 36.85
156 | 45.11 | 45.13 | 45.22 | 30.96 | 30.84 | 31.01 | T |  | MAX | 45.39 | 45.39 | 45 | 45.16 | 45.22 | 45.33 | 45.38 | 45.45 | 45.45 | 44.9 | 45.18 | 45.29 | 45.35 | 45.34 | 45.36 | 45.35 | 44.29 | 44.46 | 44.56 | 44.67 | 44.76 | 44.8 | 44.79 | 44.91 | 45.15 | 45.27 | 45.37 | 45.35 | 45.31 | 45.29
157 | 45.26 | 45.19 | 45.33 | 30.99 | 30.9 | 31.11 | O |  | AVG | 45.37 | 40.83 | 42.77 | 45 | 45.11 | 45.26 | 45.38 | 45.4 | 37.93 | 41.68 | 44.99 | 45.16 | 45.3 | 45.3 | 45.31 | 40.67 | 42.55 | 44.4 | 44.5 | 44.53 | 44.59 | 44.72 | 38.62 | 42.41 | 44.99 | 45.12 | 45.34 | 45.36 | 45.29 | 39.55
158 | 45.38 | 45.24 | 45.38 | 31.01 | 30.89 | 31.13 | R | MW-3
159 | 45.4 | 45.28 | 45.45 | 31.04 | 30.93 | 31.17 |  |  | UP
160 | 37.93 | 34.78 | 45.45 | 23.14 | 19.87 | 31.17 | W |  | MIN | 31.28 | 18.72 | 18.59 | 30.74 | 30.84 | 30.9 | 30.89 | 30.93 | 19.87 | 19.87 | 30.65 | 30.88 | 30.94 | 30.96 | 31 | 20.08 | 19.96 | 30.8 | 30.97 | 31.09 | 31.14 | 31.24 | 27.18 | 27.15 | 31.56 | 31.75 | 31.85 | 31.85 | 31.79 | 17.66
161 | 41.68 | 34.79 | 44.9 | 27.19 | 19.87 | 30.78 | E |  | MAX | 31.46 | 31.45 | 30.81 | 30.96 | 31.01 | 31.11 | 31.13 | 31.17 | 31.17 | 30.78 | 31.09 | 31.19 | 31.26 | 31.25 | 31.25 | 31.23 | 30.92 | 31.09 | 31.18 | 31.29 | 31.42 | 31.47 | 31.45 | 31.64 | 31.88 | 32.02 | 32.1 | 32.06 | 31.97 | 31.91
162 | 44.99 | 44.84 | 45.18 | 30.87 | 30.65 | 31.09 | L |  | AVG | 31.33 | 23.99 | 27.04 | 30.87 | 30.96 | 30.99 | 31.01 | 31.04 | 23.14 | 27.19 | 30.87 | 31 | 31.07 | 31.07 | 31.06 | 23.57 | 27.82 | 30.95 | 31.05 | 31.16 | 31.27 | 31.39 | 28.52 | 30.22 | 31.76 | 31.87 | 31.96 | 31.97 | 31.89 | 22.07
163 | 45.16 | 45.06 | 45.29 | 31 | 30.88 | 31.19 | L
164 | 45.3 | 45.16 | 45.35 | 31.07 | 30.94 | 31.26
165 | 45.3 | 45.18 | 45.34 | 31.07 | 30.96 | 31.25 | T
166 | 45.31 | 45.23 | 45.36 | 31.06 | 31 | 31.25 | H
167 | 40.67 | 38.44 | 45.35 | 23.57 | 20.08 | 31.23 | R
168 | 42.55 | 38.42 | 44.29 | 27.82 | 19.96 | 30.92 | E
169 | 44.4 | 44.27 | 44.46 | 30.95 | 30.8 | 31.09 | E
170 | 44.5 | 44.44 | 44.56 | 31.05 | 30.97 | 31.18
171 | 44.53 | 44.54 | 44.67 | 31.16 | 31.09 | 31.29 | I
172 | 44.59 | 44.6 | 44.76 | 31.27 | 31.14 | 31.42 | N
173 | 44.72 | 44.65 | 44.8 | 31.39 | 31.24 | 31.47 | J
174 | 38.62 | 36.06 | 44.79 | 28.52 | 27.18 | 31.45 | E
175 | 42.41 | 36.07 | 44.91 | 30.22 | 27.15 | 31.64 | C
176 | 44.99 | 44.88 | 45.15 | 31.76 | 31.56 | 31.88 | T
177 | 45.12 | 45.06 | 45.27 | 31.87 | 31.75 | 32.02 | I
178 | 45.34 | 45.2 | 45.37 | 31.96 | 31.85 | 32.1 | O
179 | 45.36 | 45.22 | 45.35 | 31.97 | 31.85 | 32.06 | N
180 | 45.29 | 45.21 | 45.31 | 31.89 | 31.79 | 31.97
181 | 39.55 | 36.85 | 45.29 | 22.07 | 17.66 | 31.91 | W
E
L
L

## SHIFT DATA
PERSONNEL LIST
|  | SHIFT CODE | OPERATOR NAME |  | CERTIFICATION NUMBER |  | SOCIAL SECURITY NUMBER
CHIEF OPERATORS
HOSTNICK, N. | CO# 3207-A | 3 | BAYLER, J. | 3 | CO# 4474-A | "A" |  | "A" | 4474 | 3207 | 2D | J. BAROFSKY | 5096-C
McGEARY, J. | CO# 4545-A | 1 | HOSTNICK, N. | 1 | CO# 3207-A | "A" |  | "A" | 3207 | 4545 | 5 | S. HULL | 5613-C
BAYLER, J. | CO# 4474-A | 2 | McGEARY, J. | 2 | CO# 4545-A | "A" |  | "A" | 4545 | 4474 | 4 | VACANT | X
VACANT | CO# XXXX-X | 5 | POMEROY, D. | 5 | CO# 421-B | "A" |  | "X" | 2052 | 421 | 3 | J. TINKER | 3291-C
POMEROY, D. | CO# 421-B | 4 | VACANT | 4 | CO# XXXX-X | "X" |  | "A" | 421 | 2052 | 1 | G. SLAYTON | 2606-B
[11 empty] | 2 | H. WALKER | 4700-A
OPERATOR II' S
JONES, K. | CO# 2466-B | 2D | BAROFSKY, J. | 2D | CO# 5096-C | [5 empty] | 5 | J. BENTLEY | X
HULL, S. | CO# 5613-C | 5 | BENTLEY, J. | 5 | CO# 9366-C | [5 empty] | 1D | S. CURMODE | X
THOMAS, P. | CO# 12833 C | 4 | CURMODE, S. | 4 | CO# 9379-A | [5 empty] | 4 | K. HENDERSON | 5087-B
CURMODE, S. | CO# 9379-A | 2 | HULL, S. | 2 | CO# 5613-C | [5 empty] | 3D | K. JONES | 2466-C
BENTLEY, J. | CO# 9366-C | 1 | JONES, K. | 1 | CO# 2466-B | [5 empty] | 3 | G. KLEYNHANS | 7367-C
BAROFSKY, J. | CO# 5096-C | 3 | THOMAS, P. | 3 | CO# 12833 C | [5 empty] | 2 | A. MORROW | 9164-C
[11 empty] | 1 | J. RAINFORTH | 2718-C
OPERATOR I' S
HENDERSON, K. | CO# 5087-B | 3 | FREIDLAND, M. | 3 | CO# XXXX-X
NOBERT, B. | CO# 9661-C | 1 | HENDERSON, K. | 1 | CO# 5087-B
KOKLAS, D. | CO# XXXX-X | 2 | KOKLAS, D. | 2 | CO# XXXX-X
FREIDLAND, M. | CO# XXXX-X | 1D | NOBERT, B. | 1D | CO# 9661-C
SANDERS, C. | CO# XXXX-X | 4 | PEUGEOT, P. | 4 | CO# 12817-C
PEUGEOT, P. | CO# 12817-C | 3D | SANDERS, C. | 3D | CO# XXXX-X
VERBOSH, R. | CO# 12667-C | 5 | VERBOSH, R. | 5 | CO# 12667-C

## COVER PAGE
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
|  | JUNE |  | 2003
| OPERATOR | TITLE | CERTIFICATE # | TOTAL COST |  |  | 65402.2668
1 ST SHIFT | HOSTNICK, N. | CHIEF | CO# 3207-A | PEAK TO FLOW RATIO |  |  | 1.2795
2230-0630 | JONES, K. | OP. II | CO# 2466-B
| HENDERSON, K. | OP. I | CO# 5087-B |  | TOTAL SUSPENDED SOLIDS
| NOBERT, B. | OP. I DEWAT | CO# 9661-C |  |  |  | LBS/DAY
|  |  |  | RAW INFLUENT |  |  | 31012.4346
2 ND SHIFT |  |  |  | FINAL EFFLUENT |  |  | 4200.0907
0630-1430 | McGEARY, J. | CHIEF | CO# 4545-A |  | TOTAL CBOD
| HULL, S. | OP. II RELIEF | CO# 5613-C |  |  |  | LBS/DAY
| BAROFSKY, J. | OP. II DEWAT | CO# 5096-C | RAW INFLUENT |  |  | 21864.0017
| KOKLAS, D. | OP. I RELIEF | CO# XXXX-X | FINAL EFFLUENT |  |  | 1431.0897
CHEMICALS
3 RD SHIFT | BAYLER, J. | CHIEF | CO# 4474-A |  |  | COST | POUNDS
1430-2230 | THOMAS, P. | OP. II | CO# 12833 C | HYDROGEN PEROXIDE |  | 5379.678 | 38564
| FREIDLAND, M. | OP. I | CO# XXXX-X | CHLORINE |  | 5277.55 | 35780
| SANDERS, C. | OP. I DEWAT | CO# XXXX-X | POLYMER |  | 6038.7438 | 9899.58
SLUDGE REMOVED
4 TH SHIFT | VACANT | CHIEF | CO# XXXX-X |  |  |  | TONS
WEEKEND | CURMODE, S. | OP. II | CO# 9379-A | DRY TONS |  |  | 607.7679
2230-1030 | PEUGEOT, P. | OP. I | CO# 12817-C |  | ENERGY
[6 empty] | COST | KILOWATTS
5 TH SHIFT | POMEROY, D. | CHIEF | CO# 421-B | FPL CONSUMPTION |  | 48706.295 | 885569
WEEKEND | BENTLEY, J. | OP. II | CO# 9366-C
1030-2230 | VERBOSH, R. | OP. I | CO# 12667-C | POPULATION EQUIVALENCE |  |  | 128611.7745
This Monthly Operation Report prepared by: |  |  | BAYLER, J. | CO# 4474-A
State DEP Plant Classification: Class "A" Level "II"
I certify that I am familiar with the information contained in this report and that to the best of my knowledge and
belief, such information is true, complete and accurate.
Facilitiy Manager's Signature: ____________________________________ CO# __________________
Division Manager's Signature: ____________________________________ CO# __________________
Please direct all inquiries reguarding this report to the City Official Mailing Address:
Director of Public Services |  |  | Phone (954) 776-5151
City of Fort Lauderdale
P.O. Drawer 14250 |  |  | Copies mailed: Date ________________ To: DEP _____
Fort Lauderdale, Florida | [5 empty] | DNRP _____
33302
PAGE 1

## PRINT PAGES
UNDERGROUND INJECTION CONTROL SECTION
[28 empty] | MONTHLY OPERATING REPORT DATA SUMMARY | [13 empty] | DEP From # 17-801.900 (1) | [11 empty] | DEP From # 17-801.900 (1) | [19 empty] | DAILY SAMPLE RESULTS - PART B
[25 empty] | FACILITY: GEORGE T. LOHMEYER WWTP |  |  |  |  | REPORT DATE: |  | JUNE | 2003 | [8 empty] | Form Title:Domestic Wastewater Treatment | [11 empty] | Form Title:Domestic Wastewater Treatment
[25 empty] | I.D. NUMBER: 5006M02066 |  |  |  | CHIEF OPERATOR: |  |  | BAYLER, J. | CO# 4474-A | [8 empty] | Plant Monthly Operating Report | [11 empty] | Plant Monthly Operating Report | [15 empty] | Permit Number: |  | FLA041378 |  |  |  |  | Three-month Average Daily Flow: | [5 empty] | 39.3977
[25 empty] | TELEPHONE NUMBER: (954) 523-1002 | [16 empty] | Effective Date: July 1, 1991 | [11 empty] | Effective Date: July 1, 1991 | [15 empty] | Monitoring Period |  | From: | 2003-06-01 | To: | 2003-07-01 |  | (TMADF):/Permitted Capacity)x100: | [5 empty] | 91.62%
[19 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [8 empty] | INJECTION WELL DATA | [13 empty] | DEP Application No. __________________ | [11 empty] | DEP Application No. __________________ | [11 empty] | Department of Natural Resource Protection
[5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [13 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [6 empty] | IW-1 | IW-2 | IW-3 |  | IW-4 | IW-5 | [35 empty] | Laboratory/Licensing/Enforcement |  |  |  | Flow | Flow | Flow | Flow | Flow | Flow | CBOD5 | CBOD5 | TSS | TSS | pH | pH | TDS | NH-3 | TKN | pH | cond. | temp. | TP
[5 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [13 empty] | MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING | [5 empty] | PERMIT/CERTIFICATION NUMBER: | UO-06-279401 | UO-06-279508 | UO-06-279510 |  | UC 06-264391 | UO-06-2795112 | [19 empty] | DOMESTIC WASTEWATER TREATMENT PLANT | [11 empty] | BROWARD COUNTY DEPARTMENT OF NATURAL RESOURCE PROTECTION | [5 empty] | 218 S. W. 1st Avenue |  |  | (MGD) | (MGD) | (MGD) | (MGD) | (MGD) | (mg/l) | (mg/l) | (mg/l) | (mg/l) | (Min) | (Max) | mg/L | mg/L | mg/L | units | umho/ | F | mg/L
[5 empty] | MONTHLY OPERATIONAL REPORT | [13 empty] | MONITORING WELL ONE |  |  |  | 7/21/97 thru 7/21/02 |  | PERMIT EXPIRATION DATE: | 2002-07-27 | 2002-07-27 | 2002-07-27 |  | 2000-11-30 | 2002-07-27 | [19 empty] | MONTHLY OPERATING REPORT | [11 empty] | WASTEWATER TREATMENT PLANT | [5 empty] | Fort Lauderdale, FL 33301 | [17 empty] | cm
[5 empty] | PROCESS DATA | [11 empty] | MW-1 | I.D. #: 5066A11311 |  |  | PERMIT/CERT. #: UO-06-279512 |  |  |  | CASING DEPTH | 2799' | 2798' | 2800' |  | 2804' | 2818' | [8 empty] | DOMESTIC WASTEWATER TREATMENT PLANT |  |  |  |  | (34) | [8 empty] | MONTH: | JUNE |  | YEAR: | 2003 |  |  |  |  | MONTHLY SLUDGE REPORTS | [5 empty] | Tel. No. (954) 765-4804 | Code | 50050 | 50050 | 50050 | 50050 | 50050 | 50050 | 80082 | 80082 | 00530 | 00530 | 00400 | 00400
| RUN DATE | [14 empty] | RUN DATE | [8 empty] | TOTAL DEPTH | 3513' | 3518' | 3977' |  | 3305' | 3462' | [8 empty] | MONTHLY OPERATING REPORT |  |  |  |  | DAY OF | FLOW | CHLORINE | CHLORINE | CBOD5 | TSS | CBOD5 | TSS | PH |  |  | EFFLUENT NUTRIENTS (MG/L) |  |  | I. | [10 empty] | Mon. Site | INF-001 | EFF-002 | EFF-003 | EFF-004 | EFF-005 | EFF-006 | INF-002 | EFF-001 | INF-002 | EFF-001 | EFF-001 | EFF-001
| 2026-07-30 | [14 empty] | 2026-07-30 |  | UPPER MONITOR ZONE |  |  |  |  | LOWER MONITOR ZONE |  | AVERAGE DAILY FLOW: | 10.334 | 10.1831 | 9.2983 |  | 0.8587 | 9.2997 | MGD | [7 empty] | Part II - General Information |  |  |  |  | THE |  | RESIDUAL | RESIDUAL | INFLUENT | INFLUENT | EFFLUENT | EFFLUENT | EFFLUENT | TKN | NH3-N | NITRATE | TOTAL | FECAL | Plant Name: | GEORGE T. LOHMEYER WASTEWATER TREATMENT FACILITY | [6 empty] | MONTH: | JUNE |  | 1 | 54.147 | 10.36 | 10.37 | 8.97 | 12.12 | 8.93 | 43.9 | 2.56 | 86 | 10 | 6.6 | 6.6 | 765 | 7.12 | 9.86 | 6.6 | 1567 | 82 | 0.571
[17 empty] | MIN | MAX | AVG |  |  | MIN | MAX | AVG | **MAX DAILY FLOW PER MO (mg): | 12.26 | 12.2 | 11.02 |  | 12.12 | 10.86 | MG | [12 empty] | MONTH | (MGD) | AFTER | AFTER DE- | [8 empty] | P | COLIFORM | II. | [7 empty] | YEAR: | 2003 |  | 2 | 51.048 | 11.5 | 11.42 | 10.19 | 4.73 | 10.14 | 31.8 | 3.78 | 90 | 9 | 6.6 | 6.6 | 950 |  |  | 6.7 | 1690 | 85
| JUNE | INFLUENT | HOURLY | INFLUENT | INFLUENT | RAS | PERCENT | WAS | RAIN | SPARE | [5 empty] | JUNE | FT HEAD | FT HEAD | FT HEAD |  |  | FT HEAD | FT HEAD | FT HEAD | ** PEAK HR FLOW (MGD) ON MAX DAY: | 14.7456 | 14.524 | 13.2701 |  | 1.0081 | 13.2793 | MGD |  | (1) Month: |  | JUNE |  | Year: | 2003 |  | Parameter | Units | STORET | Value |  |  | CONTACT | CHLORINATION | MG/L | MG/L | MG/L | MG/L | [6 empty] | A) | Sludge Treatment Provided: |  |  |  |  | B) | Sludge Dewater Processes |  |  |  | 3 | 48.411 | 12 | 11.92 | 10.76 | 0.13 | 10.7 | 51 | 5.1 | 90 | 11 | 6.6 | 6.8 | 879 |  |  | 6.7 | 1816 | 85
| 2003 | FLOW | MAXIMUM | MAXIMUM | MINIMUM | FLOW | RAS | FLOW | INCHES | [6 empty] | 2003 | ABOVE | ABOVE | ABOVE |  |  | ABOVE | ABOVE | ABOVE | MAX SUSTAINED INJECTION PRESSURE: | 74.6 | 73.2 | 75.2 |  | 62.5 | 74.7 | PSIG |  | (2) Plant's DEP Identification Number: |  |  |  |  | 5006M02066 |  |  |  | Code |  | 1 | 54.147 | 1 |  | 43.9 | 86 | 2.56 | 10 | 6.6 | 9.86 | 7.12 | 0.098 | 0.571 | 0 |  |  | Aerobic Digestion | [5 empty] | Thickner |  |  | 4 | 46.308 | 11.48 | 11.39 | 10.28 | 0.14 | 10.23 | 61.4 | 4.79 | 74 | 10 | 6.6 | 6.7 | 1060 | 9.6 | 13.16 | 6.7 | 1881 | 85 | 0.725
|  | MGD | MGD | MGD | MGD | MGD |  | MGD | [8 empty] | NGVD | NGVD | NGVD |  |  | NGVD | NGVD | NGVD | MONTHLY AVG. INJECTION PRESSURE: | 51.2092 | 51.774 | 52.9743 |  | 36.3004 | 51.5023 | PSIG |  | (3) Plant Name: |  |  |  | George T. Lohmeyer Regional Wastewater |  |  | (16) Monthly average daily flow | mgd | 050053 | 42.32 | 2 | 51.048 | 1.1 |  | 31.8 | 90 | 3.78 | 9 | 6.7 |  |  |  |  | 0 |  |  | Anaerobic Digestion | [5 empty] | DGA___X___Filter Press |  |  | 5 | 44.458 | 11.04 | 11.02 | 9.93 | 0.13 | 9.89 | 46.6 | 7.24 | 92 | 15 | 6.6 | 6.7 | 963 | 9.8 | 13 | 6.7 | 1920 | 85 | 0.597
| 1 | 54.147 | 2.509 | 66.375 | 38.406 | 13.5 | 24.93% | ER | 0 |  |  | 1 |  |  |  | 1 | 48.28 | 48.55 | 48.53 |  |  | ER | ER | ER | *** MAX INJECTION PRESSURE PERMITTED: | 99 | 99 | 99 |  | 99 | 99 | PSIG |  |  |  |  | Treatment Facility |  |  |  | (17) Permitted capacity | mgd | - | 43 | 3 | 48.411 | 1.1 |  | 51 | 90 | 5.1 | 11 | 6.7 |  |  |  |  | 0 |  |  | Other | [5 empty] | Centrifuge Drying Beds, Bed #______ |  |  | 6 | 42.631 | 10.65 | 10.61 | 9.56 | 0.14 | 9.56 | 56 | 5.5 | 64 | 18 | 6.6 | 6.7 | 864 | 10.29 | 14.28 | 6.6 | 1970 | 85 | 0.958
| 2 | 51.048 | 2.359 | 64.625 | 30.188 | 13.476 | 26.4% | 0.516 | 0 |  |  | 2 |  |  |  | 2 | 46.49 | 48.53 | 48.47 |  |  | ER | ER | ER | ***NOTE: (INJECTION PRESSURE NOT TO EXCEED 66% TESTED PRESSURE | [8 empty] | (4) Plant Address: |  |  | 1765 S.E. 18th Street at |  |  |  | (18) Three-month average daily flow | mgd | - | 39.3977 | 4 | 46.308 | 1 |  | 61.4 | 74 | 4.79 | 10 | 6.7 | 13.16 | 9.6 | 0.21 | 0.725 | 36 | [8 empty] | Heat Treatment____No Treatment |  |  | 7 | 42.761 | 10.56 | 10.53 | 9.5 | 0.13 | 9.48 | 76 | 3.7 | 132 | 16 | 6.6 | 6.7 | 1119 | 9.14 | 12.52 | 6.6 | 2020 | 85 | 0.54
| 3 | 48.411 | 2.268 | 62.125 | 27.563 | 13.068 | 26.99% | 0.633 | 0 |  |  | 3 |  |  |  | 3 | 46.96 | 48.46 | 47.92 |  |  | ER | ER | ER | TESTED CASING PRESSURE DURING MIT | 150 | 150 | 150 |  | 150 | 150 | PSIG |  |  |  |  | Eisenhower Boulevard |  |  |  | (19) Percent of permitted capacity | % | - | 91.62% | 5 | 44.458 | 1.1 |  | 46.6 | 92 | 7.24 | 15 | 6.7 | 13 | 9.8 | 0.238 | 0.597 | 9 | [7 empty] | x | Other: | LIME STABILIZATION |  | 8 | 42.609 | 10.58 | 10.56 | 9.5 | 0.14 | 9.49 | 80.5 | 3.85 | 86 | 12 | 6.6 | 6.6 | 928 | 9.3 | 12.91 | 6.6 | 1965 | 85 | 0.412
| 4 | 46.308 | 2.189 | 61.625 | 23.75 | 12.867 | 27.79% | 0.643 | 0.2 |  |  | 4 |  |  |  | 4 | 48.23 | 48.45 | 48.36 |  |  | ER | ER | ER | [9 empty] | (5) City: |  | Fort Lauderdale |  |  |  |  | (20) CBOD5 Effluent | mg/L | 080082 | 4.0547 | 6 | 42.631 | 0.9 |  | 56 | 64 | 5.5 | 18 | 6.6 | 14.28 | 10.29 | 0.182 | 0.958 | 0 | [9 empty] | CLASS "AA" |  | 9 | 44.692 | 11.1 | 11.08 | 9.97 | 0.14 | 9.93 | 46 | 3.2 | 128 | 10 | 6.6 | 6.8 | 983 |  |  | 6.7 | 1948 | 82
| 5 | 44.458 | 2.169 | 58.969 | 25.594 | 13.331 | 29.99% | 0.62 | 0.13 |  |  | 5 |  |  |  | 5 | 48.21 | 48.45 | 48.32 |  |  | ER | 41.42 | 26.2 |  |  | MONITORING WELL DATA | [6 empty] | (6) County: |  | Broward |  |  |  |  | (21) CBOD5 Effluent | lbs/day | - | 1431.0897 | 7 | 42.761 | 0.9 |  | 76 | 132 | 3.7 | 16 | 6.6 | 12.52 | 9.14 | 0.184 | 0.54 | 0 | III. | Final Sludge Disposal: | [7 empty] | RMF-Azurix (Nutri-Cycle) |  | 10 | 45.837 | 11.34 | 11.33 | 10.19 | 0.14 | 10.12 | 33 | 4.5 | 33 | 8 | 6.6 | 6.8 | 1193 |  |  | 6.7 | 1924 | 85
| 6 | 42.631 | 2.08 | 59.281 | 19.125 | 13.886 | 32.57% | 0.167 | 0 |  |  | 6 |  |  |  | 6 | 48.22 | 48.44 | 48.35 |  |  | 41.32 | 41.46 | 41.45 |  | MW-1 | MW-2 | MW-3 |  | RMW-1 |  |  |  | (7) Phone Number: |  |  | (954) 523-1002 |  |  |  | (22) TSS Effluent | mg/L | 900201 | 11.9 | 8 | 42.609 | 0.9 |  | 80.5 | 86 | 3.85 | 12 | 6.6 | 12.91 | 9.3 | 0.256 | 0.412 | 0 | A) | Liquid Sludge Disposal: | [9 empty] | 11 | 43.556 | 10.8 | 10.78 | 9.7 | 0.14 | 9.68 | 55 | 5.47 | 96 | 8 | 6.6 | 6.8 | 1014 | 9.81 | 13.06 | 6.7 | 1975 | 85 | 0.651
| 7 | 42.761 | 2.294 | 61.844 | 18.25 | 13.926 | 32.57% | 0 | 1.76 |  |  | 7 |  |  |  | 7 | 48.21 | 48.46 | 48.35 |  |  | 41.31 | 41.49 | 41.44 | PERMIT NUMBER | UO-06-279512 | UO-06-279401 | UO-06-279510 |  | UC06-249353 |  |  |  | (8) Permit Number: |  |  | FLA041378 |  |  |  | (23) TSS Effluent | lbs/day | - | 4200.0907 | 9 | 44.692 | 0.9 |  | 46 | 128 | 3.2 | 10 | 6.7 |  |  |  |  | 9 |  | WEEK OF | JUNE | GALLONS | % SOLIDS |  |  | HAULERS |  |  | DISPOSAL SITE | 12 | 41.885 | 8.97 | 10.97 | 9.63 | 0.14 | 9.86 | 58.7 | 4.42 | 88 | 11 | 6.5 | 6.8 | 1368 | 8.9 | 12.96 | 6.6 | 2030 | 85 | 0.662
| 8 | 42.609 | 2.082 | 61.531 | 17.188 | 13.889 | 32.6% | 0.274 | 0.23 |  |  | 8 |  |  |  | 8 | 48.18 | 48.46 | 48.35 |  |  | 41.3 | 41.52 | 41.49 | UPPER MONITORING INTERVAL | 1288'-1320' | 1300'-1344' | 1300'-1349' |  | 1300'-1339' |  | Ft. bls. |  | (9) Plant Type: |  |  | Oxygen Activated Sludge |  |  |  | (24) Minimum pH |  | - | 6.5 | 10 | 45.837 | 0.9 |  | 33 | 33 | 4.5 | 8 | 6.7 |  |  |  |  | 0 | [11 empty] | 13 | 40.372 | 10.13 | 10.08 | 9.11 | 0.14 | 9.1 | 63.2 | 5.35 | 90 | 11 | 6.5 | 6.8 | 1174 | 10.51 | 14.1 | 6.6 | 1945 | 85 | 0.685
| 9 | 44.692 | 2.243 | 63.813 | 16.875 | 13.482 | 30.17% | 0.717 | 0.24 |  |  | 9 |  |  |  | 9 | 43.79 | 48.48 | 45.39 |  |  | 25.76 | 41.49 | 30.11 | MONTHLY MAX DAILY PRESSURE | 48.66 | 30.9 | 32.1 |  | 44.3 |  | FT. HEAD |  | (10) Test Site Identification Number: |  |  |  |  | 5006X10744 |  | (25) Maximum pH |  | - | 7.1 | 11 | 43.556 | 1 |  | 55 | 96 | 5.47 | 8 | 6.7 | 13.06 | 9.81 | 0.275 | 0.651 | 9 |  | FIRST THRU SEVENTH | [9 empty] | 14 | 38.806 | 9.64 | 9.58 | 8.63 | 0.14 | 8.67 | 64 | 4.9 | 94 | 10 | 6.6 | 6.7 | 1174 | 9.89 | 13.48 | 6.6 | 1960 | 85 | 0.82
| 10 | 45.837 | 2.223 | 63 | 20.906 | 13.69 | 29.87% | 0.588 | 0.01 |  |  | 10 |  |  |  | 10 | 44.33 | 48.64 | 47.12 |  |  | 25.77 | 41.22 | 36.41 | MONTHLY MIN DAILY PRESSURE | 42.64 | 0 | 17.66 |  | 35.69 |  | FT. HEAD |  | (11) Fecal Coliform Method | [6 empty] | (26) Total N | mg/L | 000600 | 13.8236 | 12 | 41.885 | 0.8 |  | 58.7 | 88 | 4.42 | 11 | 6.6 | 12.96 | 8.9 | 0.663 | 0.662 | 9 | [11 empty] | 15 | 38.11 | 9.36 | 9.3 | 8.35 | 0.14 | 8.41 | 68.6 | 2.48 | 102 | 10 | 6.6 | 6.7 | 1058 | 9.12 | 13.33 | 6.6 | 2000 | 85 | 0.762
| 11 | 43.556 | 2.133 | 60.063 | 19.469 | 13.42 | 30.81% | 0.739 | 0.33 |  |  | 11 |  |  |  | 11 | 48.14 | 48.58 | 48.37 |  |  | 41.09 | 41.33 | 41.28 | TDS (MONTHLY AVERAGE) | 7531.5 | 7293 | 7442 |  | 5664 |  | mg/l |  |  | XX | Membrane Filter |  |  |  |  | (27) TKN | mg/L | 000625 | 13.561 | 13 | 40.372 | 0.9 |  | 63.2 | 90 | 5.35 | 11 | 6.6 | 14.1 | 10.51 | 0.287 | 0.685 | 0 |  | EIGHT THRU FORTEENTH | [9 empty] | 16 | 38.023 | 9.45 | 9.39 | 8.43 | 0.14 | 8.49 | 62.1 | 4.22 | 98 | 12 | 6.6 | 7 | 1076 |  |  | 6.8 | 2150 | 85
| 12 | 41.885 | 2.101 | 60.375 | 15.531 | 13.51 | 32.25% | 0.548 | 0 |  |  | 12 |  |  |  | 12 | 48.17 | 48.6 | 48.38 |  |  | 41.23 | 41.39 | 41.37 | CHLORIDE (MONTHLY AVERAGE) | 3862.5 | 3787.5 | 3850 |  | 2900 |  | mg/l |  |  |  | Most Probable Number |  |  |  |  | (28) Ammonia (NH3 - N) | mg/L | 000610 | 9.689 | 14 | 38.806 | 0.9 |  | 64 | 94 | 4.9 | 10 | 6.6 | 13.48 | 9.89 | 0.273 | 0.82 | 0 |  | FIFTHTEENTH THRU | [9 empty] | 17 | 37.372 | 9.33 | 9.27 | 8.31 | 0.14 | 8.38 | 88 | 3.2 | 46 | 20 | 6.8 | 7.1 | 1056 |  |  | 6.8 | 2330 | 85
| 13 | 40.372 | 1.984 | 57.781 | 16.031 | 13.768 | 34.1% | 0.185 | 0.15 |  |  | 13 |  |  |  | 13 | 48.17 | 48.63 | 48.38 |  |  | 41.29 | 41.48 | 41.4 | AMMONIA-N (MONTHLY AVERAGE) | 0.83925 | 0.886 | 0.97 |  | 0.8 |  | mg/l |  | (12) Type of Effluent Disposal or Reclaimed Water Reuse | [6 empty] | (29) Nitrate | mg/L | 071850 | 0.26267 | 15 | 38.11 | 0.8 |  | 68.6 | 102 | 2.48 | 10 | 6.6 | 13.33 | 9.12 | 0.601 | 0.762 | 0 |  | TWENTY SECOND | [9 empty] | 18 | 36.836 | 9.17 | 9.14 | 8.18 | 0.14 | 8.26 | 66.1 | 2.2 | 80 | 15 | 6.7 | 6.8 | 1100 | 11.73 | 16.12 | 6.8 | 2120 | 85 | 0.872
| 14 | 38.806 | 1.94 | 57.375 | 13.063 | 13.46 | 34.69% | 0 | 0 |  |  | 14 |  |  |  | 14 | 48.16 | 48.59 | 48.36 |  |  | 41.3 | 41.44 | 41.42 | TKN (MONTHLY AVERAGE) | 1.4775 | 1.59 | 1.485 |  | 1.09 |  | mg/l |  |  |  | Deep Well Injection |  |  |  |  | (30) Total Phosphorus | mg/L | 000665 | 0.8209 | 16 | 38.023 | 0.9 |  | 62.1 | 98 | 4.22 | 12 | 6.8 |  |  |  |  | 0 |  | TWENTY THIRD THRU | [9 empty] | 19 | 40.665 | 10.3 | 10.23 | 9.21 | 0.14 | 9.19 | 77.7 | 3.5 | 110 | 10 | 6.6 | 6.8 | 1076 | 10.7 | 15.15 | 6.7 | 2070 | 85 | 0.963
| 15 | 38.11 | 1.942 | 58.656 | 13.781 | 13.014 | 34.15% | 0.6 | 0.25 |  |  | 15 |  |  |  | 15 | 48.17 | 48.55 | 48.36 |  |  | 41.28 | 41.41 | 41.42 | pH (MONTHLY AVERAGE) | 7.8575 | 8.0075 | 8.1675 |  | 8.34 |  | Std units |  | (13) Limited Wet Wheather Discharge Activated | [6 empty] | (31) Minimum Chlorine Residual | mg/L | - | 0.5 | 17 | 37.372 | 0.8 |  | 88 | 46 | 3.2 | 20 | 6.8 |  |  |  |  | 98 |  | THIRTY FIRST | [9 empty] | 20 | 48.883 | 12.26 | 12.2 | 11.02 | 0.14 | 10.86 | 76 | 3.9 | 59 | 10 | 6.7 | 6.8 | 945 | 8.46 | 12.16 | 6.7 | 2000 | 85 | 0.969
| 16 | 38.023 | 1.89 | 57.75 | 14.875 | 13.524 | 35.57% | 0.454 | 0 |  |  | 16 |  |  |  | 16 | 44.51 | 48.5 | 45.95 |  |  | 27.58 | 41.38 | 31.76 | CONDUCTIVITY (MONTHLY AVERAGE) | 12037.5 | 11807.5 | 11965 |  | 9370 |  | umho/cm |  |  |  | YES |  | XX | Not Applicable |  | (32) Maximum Chlorine Residual | mg/L | - | 1.1 | 18 | 36.836 | 1 |  | 66.1 | 80 | 2.2 | 15 | 6.8 | 16.12 | 11.73 | 0.279 | 0.872 | 0 | [11 empty] | 21 | 47.538 | 11.79 | 11.72 | 10.59 | 0.14 | 10.46 | 56 | 5.4 | 80 | 14 | 6.6 | 6.7 | 951 | 8.15 | 12.23 | 6.6 | 1930 | 85 | 1.23
| 17 | 37.372 | 1.819 | 57.125 | 12.375 | 13.862 | 37.09% | 0.418 | 0.14 |  |  | 17 |  |  |  | 17 | 46.53 | 46.9 | 46.63 |  |  | 27.52 | 28.23 | 28.01 | FECAL COLIFORM (MONTHLY AVERAGE) | 0 | 0 | 0 |  | 0 |  | # col/100ml |  |  |  | NO |  |  |  |  | (33) Other Effluent Parameters |  |  |  | 19 | 40.665 | 0.9 |  | 77.7 | 110 | 3.5 | 10 | 6.7 | 15.15 | 10.7 | 0.204 | 0.963 | 0 | B) | Solid Sludge Hauled from Plant: | [9 empty] | 22 | 42.878 | 10.53 | 10.49 | 9.44 | 0.14 | 9.42 | 54.8 | 3.88 | 70 | 10 | 6.7 | 6.7 | 949 | 8.96 | 13.13 | 6.7 | 1979 | 83 | 0.992
| 18 | 36.836 | 1.787 | 57.125 | 16.094 | 13.679 | 37.13% | 0.642 | 0 |  |  | 18 |  |  |  | 18 | 46.57 | 46.82 | 46.66 |  |  | 28.18 | 28.3 | 28.21 | TEMPERATURE (MONTHLY AVERAGE) | 73 | 71.25 | 71.75 |  | 71 |  | deg. F | [12 empty] | 20 | 48.883 | 0.9 |  | 76 | 59 | 3.9 | 10 | 6.7 | 12.16 | 8.46 | 0.177 | 0.969 | 9 |  | WEEK OF | JUNE | TONS |  | % SOLIDS |  | HAULERS |  |  | DISPOSAL SITE | 23 | 42.285 | 10.57 | 4.13 | 9.47 | 0.13 | 9.44 | 66 | 3.9 | 86 | 11 | 6.6 | 6.9 | 1050 |  |  | 6.7 | 2020 | 85
| 19 | 40.665 | 2.46 | 67.406 | 12.938 | 13.38 | 32.9% | 0.597 | 1.75 |  |  | 19 |  |  |  | 19 | 46.59 | 46.83 | 46.67 |  |  | 28.17 | 28.39 | 28.29 | TOTAL PHOSPHOROUS (MONTHLY AVG.) | 0.05 | 0.05 | 0.05 |  | 0.05 |  | mg/l |  | (14) Cumulative Days of Wet Wheather Discharge | [10 empty] | 21 | 47.538 | 0.9 |  | 56 | 80 | 5.4 | 14 | 6.6 | 12.23 | 8.15 | 0.195 | 1.23 | 0 | [10 empty] | Nutri-Cylcle Inc. | 24 | 41.12 | 10.25 | ER | 9.19 | ER | 9.18 | 66 | 3.7 | 76 | 11 | 6.7 | 6.8 | 1034 |  |  | 6.7 | 2050 | 85
| 20 | 48.883 | 2.504 | 65.75 | 27.063 | 13.625 | 27.87% | 0.265 | 1 |  |  | 20 |  |  |  | 20 | 46.61 | 46.87 | 46.75 |  |  | 28.29 | 28.52 | 28.39 | SULFATE (MONTHLY AVERAGE) | 762.5 | 787.5 | 787.5 |  | 950 |  | mg/l |  |  |  | N/A | [8 empty] | 22 | 42.878 | 0.5 |  | 54.8 | 70 | 3.88 | 10 | 6.7 | 13.13 | 8.96 | 0.201 | 0.992 | 402 |  | FIRST THRU SEVENTH |  | 725 |  | 18.288 |  | AZURIX |  |  | Arcadia, FL | 25 | 39.699 | 9.87 | 10.03 | 8.86 | ER | 8.88 | 54 | 4.9 | 82 | 12 | 6.6 | 6.8 | 1145 | 11.23 | 15.92 | 6.7 | 2060 | 85 | 0.905
| 21 | 47.538 | 2.398 | 64.844 | 22.344 | 12.886 | 27.11% | 0 | 0.15 |  |  | 21 |  |  |  | 21 | 46.61 | 46.89 | 46.78 |  |  | 28.31 | 28.59 | 28.42 | C.O.D. (MONTHLY AVERAGE) | 175 | 180 | 182.5 |  | 130 |  | mg/l |  | (15) Plant Staffing: | [10 empty] | 23 | 42.285 | 0.9 |  | 66 | 86 | 3.9 | 11 | 6.7 |  |  |  |  | 0 | [10 empty] | Nutri-Cylcle Inc. | 26 | 37.917 | 9.46 | 9.63 | 8.47 | ER | 8.51 | 55 | 4 | 100 | 15 | 6.6 | 6.8 | 1231 | 10.41 | 15.14 | 6.7 | 2160 | 85 | 1.19
| 22 | 42.878 | 2.084 | 58.438 | 25.656 | 13.368 | 31.18% | 0 | 0.7 |  |  | 22 |  |  |  | 22 | 46.66 | 46.91 | 46.84 |  |  | 28.36 | 28.57 | 28.45 | IRON (MONTHLY AVERAGE) | 0.6725 | 1.735 | 1.3575 |  | 0.42 |  | mg/l | [12 empty] | 24 | 41.12 | 0.8 |  | 66 | 76 | 3.7 | 11 | 6.7 |  |  |  |  | 0 |  | EIGHT THRU FORTEENTH |  | 650 |  | 17.582 |  | AZURIX |  |  | Arcadia, FL | 27 | 39.118 | 9.9 | 10.08 | 8.86 | ER | 8.87 | 86 | 5 | 100 | 14 | 6.5 | 6.8 | 1152 | 10.76 | 14.77 | 6.6 | 2160 | 85 | 1.03
| 23 | 42.285 | 2.009 | 56.219 | 5.268 | 13.021 | 30.79% | 0.47 | 0.55 |  |  | 23 |  |  |  | 23 | 46.66 | 46.93 | 46.84 |  |  | 27.49 | 28.45 | 27.8 | SULFIDE (MONTHLY AVERAGE) | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! |  | mg/l |  |  | Day Shift Operator: |  |  | Class | "A" | Cert. No. | 4545 |  |  |  | 25 | 39.699 | 0.9 |  | 54 | 82 | 4.9 | 12 | 6.7 | 15.92 | 11.23 | 0.248 | 0.905 | 0 |  | FIFTHTEENTH THRU | [8 empty] | Nutri-Cylcle Inc. | 28 | 38.744 | 9.61 | 9.8 | 8.6 | ER | 8.63 | 62 | 3 | 92 | 11 | 6.5 | 6.6 | 970 | 10.07 | 14.27 | 6.6 | 2040 | 85 | 0.884
| 24 | 41.12 | 2.001 | 57.25 | 21.031 | 13.021 | 31.67% | 0.718 | 0 |  |  | 24 |  |  |  | 24 | 46.74 | 48.66 | 47.93 |  |  | 27.5 | 41.01 | 37.24 | LOWER MONITORING INTERVAL | 1449'-1557' | 1970'-2025' | 1970'-2027' |  | 1500'-1600' |  | Ft. bls | [12 empty] | 26 | 37.917 | 0.7 |  | 55 | 100 | 4 | 15 | 6.7 | 15.14 | 10.41 | 0.22 | 1.19 | 0 |  | TWENTY SECOND |  | 725 |  | 17.582 |  | AZURIX |  |  | Arcadia, FL | 29 | 36.673 | 9.02 | 9.15 | 8.04 | ER | 8.13 | 84 | 2 | 116 | 11 | 6.5 | 6.7 | 1115 | 9.52 | 13.23 | 6.7 | 2180 | 85 | 0.821
| 25 | 39.699 | 1.932 | 56.594 | 16.969 | 13.021 | 32.8% | 0.693 | 0 |  |  | 25 |  |  |  | 25 | 48.17 | 48.48 | 48.36 |  |  | 40.98 | 41.17 | 41.02 | MONTHLY MAX DAILY PRESSURE | 41.52 | 42.33 | 45.45 |  | 22.05 |  | FT. HEAD |  |  | Evening Shift Operator: |  |  | Class | "A" | Cert. No. | 4474 |  |  |  | 27 | 39.118 | 0.8 |  | 86 | 100 | 5 | 14 | 6.6 | 14.77 | 10.76 | 0.219 | 1.03 | TNTC |  | TWENTY THIRD THRU | [8 empty] | Nutri-Cylcle Inc. | 30 | 36.218 | 9 | 9.11 | 8.01 | ER | 8.1 | 69 | 2 | 96 | 12 | 6.5 | 6.7 | 1044 |  |  | 6.7 | 2190 | 85
| 26 | 37.917 | 1.907 | 54.875 | 18.156 | 13.021 | 34.34% | 0.643 | 0 |  |  | 26 |  |  |  | 26 | 48.25 | 48.58 | 48.43 |  |  | 41.09 | 41.32 | 41.3 | MONTHLY MIN DAILY PRESSURE | 25.76 | 29.4 | 34.78 |  | 19.02 |  | FT. HEAD | [12 empty] | 28 | 38.744 | 0.8 |  | 62 | 92 | 3 | 11 | 6.6 | 14.27 | 10.07 | 0.24 | 0.884 | 0 |  | THIRTY FIRST |  | 725 |  | 17.3817 |  | AZURIX |  |  | Arcadia, FL | 31
| 27 | 39.118 | 2.077 | 60.188 | 12.188 | 13.021 | 33.29% | 0.605 | 1.65 |  |  | 27 |  |  |  | 27 | 48.29 | 48.63 | 48.47 |  |  | 41.2 | 41.4 | 41.35 | TDS (MONTHLY AVERAGE) | 9478 | 32015 | 28793 |  | 26590 |  | mg/l |  |  | Night Shift Operator: |  |  | Class | "A" | Cert. No. | 3207 |  |  |  | 29 | 36.673 | 0.7 |  | 84 | 116 | 2 | 11 | 6.7 | 13.23 | 9.52 | 0.266 | 0.821 | 0 | C) | Monthly quantities of solid sludge stockpiled at plant.Solid Sludge Hauled from Plant: | [9 empty] | TOT | 1269.6 | 310.02 | 295.31 | 278.95 | 19.75 | 278.99 | 1858.4 | 121.64 | 2636 | 357 | 198 | 202.8 | 31386 | 203.47 | 284.78 | 200.2 | 60050 | 2542 | 17.239
| 28 | 38.744 | 1.948 | 54.531 | 16.375 | 13.22 | 34.12% | NR | 0.03 |  |  | 28 |  |  |  | 28 | 48.28 | 48.57 | 48.47 |  |  | 41.19 | 41.41 | 41.37 | CHLORIDE (MONTHLY AVERAGE) | 5100 | 18050 | 16600 |  | 15400 |  | mg/l | [12 empty] | 30 | 36.218 | 0.8 |  | 69 | 96 | 2 | 12 | 6.7 |  |  |  |  | 0 |  | 1) | Additions |  |  | Cubic Yards | [5 empty] | AVG | 42.32 | 10.334 | 10.1831 | 9.2983 | 0.8587 | 9.2997 | 61.9467 | 4.0547 | 87.8667 | 11.9 | 6.6 | 6.76 | 1046.2 | 9.689 | 13.561 | 6.6733 | 2001.6667 | 84.7333 | 0.8209
| 29 | 36.673 | 1.905 | 55.844 | 16 | 13.021 | 35.51% | 0.546 | 0 |  |  | 29 |  |  |  | 29 | 48.17 | 48.48 | 48.35 |  |  | 41.23 | 41.34 | 41.32 | AMMONIA-N (MONTHLY AVERAGE) | 9.4725 | 1.3225 | 2.3825 |  | 0.431 |  | mg/l |  |  | Lead Operator:_________________________________ | [28 empty] | Tons | [5 empty] | MAX | 54.147 | 12.26 | 12.2 | 11.02 | 12.12 | 10.86 | 88 | 7.24 | 132 | 20 | 6.8 | 7.1 | 1368 | 11.73 | 16.12 | 6.8 | 2330 | 85 | 1.23
| 30 | 36.218 | 1.835 | 55.469 | 13.969 | 14.36 | 39.65% | 0 | 0 |  |  | 30 |  |  |  | 30 | 42.64 | 48.38 | 44.65 |  |  | 27.48 | 41.29 | 31.71 | TKN (MONTHLY AVERAGE) | 11.5025 | 1.975 | 3.2125 |  | 0.432 |  | mg/l | [5 empty] | Signature |  | Cert. No. |  |  |  |  | Lead Operator : This is to certify that I am familar with the information contained on this report and that to the best of | [14 empty] | 2) | Removals |  |  | Cubic Yards | [5 empty] | MIN | 36.218 | 8.97 | 4.13 | 8.01 | 0.13 | 8.1 | 31.8 | 2 | 33 | 8 | 6.5 | 6.6 | 765 | 7.12 | 9.86 | 6.6 | 1567 | 82 | 0.412
[25 empty] | pH (MONTHLY AVERAGE) | 7.285 | 7.315 | 7.4125 |  | 7.84 |  | Std units | [12 empty] | my knowledge and belief, this information is true, complete and accuate. | [16 empty] | X |  | Tons | [6 empty] | item #1 | 14.7456 | 14.524 | 13.2701 | 1.0081 | 13.2793 | MAX HOURLY FLOW (MG) = |  |  |  | 2.509 | ON THE | 1 | DAY OF THIS MONTH
| TOTAL | 1269.6 | 63.072 | 1796.846 | 567.021 | 402.317 |  | 12.281 | 9.27 | [6 empty] | TOTAL | 1412.99 | 1444.3 | 1428.79 |  |  | 866.22 | 985.02 | 928.63 | CONDUCTIVITY (MONTHLY AVERAGE) | 15507.5 | 47100 | 43300 |  | 41300 |  | umho/cm | [33 empty] | Signature |  |  |  |  | item #2 | 51.2092 | 51.774 | 52.9743 | 36.3004 | 51.5023
| AVERAGE | 42.32 | 2.1024 | 59.8949 | 18.9007 | 13.4106 | 31.69% | 0.53396 | 0.309 | [6 empty] | AVERAGE | 47.0997 | 48.1433 | 47.6263 |  |  | 34.6488 | 37.8854 | 35.7165 | FECAL COLIFORM (MONTHLY AVERAGE) | 0 | 0 | 0 |  | 0 |  | # col/100ml | [12 empty] | Signed: ____________________________ Date: ___________________ | [20 empty] | Title |  |  |  |  | item #3 | 37 | 37.4 | 37 | 37.5 | 36.6
[16 empty] | MAXIMUM | 48.29 | 48.66 | 48.53 |  |  | 41.32 | 41.52 | 41.49 | TEMPERATURE (MONTHLY AVERAGE) | 72.75 | 70.5 | 70.25 |  | 70 |  | deg. F | [33 empty] | Date |  |  |  | item #1 | =monthly maximum of the daily flows (MG), with peakhour flow (MGD) on the day of the month with maximum flow = | [14 empty] | 2.509 | MG/hour multiplied by
[16 empty] | MINIMUM | 42.64 | 46.82 | 44.65 |  |  | 25.76 | 28.23 | 26.2 | TOTAL PHOSPHOROUS (MONTHLY AVG.) | 0.05 | 0.06525 | 0.05 |  | 0.05 |  | mg/l | [12 empty] | Name: Michael A. Just | [14 empty] | * Sludge Reports should be submitted along with the monthly operating reports to Broward County Department | [10 empty] | the % of average % of TOTAL RAW FLOW to each Injection well.
[25 empty] | SULFATE (MONTHLY AVERAGE) | 750 | 2450 | 2125 |  | 1150 |  | mg/l | [27 empty] | of Natural Resource Protection, 218 S. W. 1st Avenue, Fort Lauderdale, Florida 33301 | [9 empty] | item #2 | =monthly average injection well pressure at injection well (psig)
[25 empty] | C.O.D. (MONTHLY AVERAGE) | 272.5 | 837.5 | 822.5 |  | 640 |  | mg/l | [12 empty] | Company Name: City of Fort Lauderdale Telephone No. (954) 523-1002 | [24 empty] | item #3 | =monthly wellhead pressure with no flow (shut-in pressure,psig)
[25 empty] | IRON (MONTHLY AVERAGE) | 0.0125 | 0.0425 | 0.0275 |  | 0.06 |  | mg/l | [37 empty] | PLANT STAFFING
[5 empty] | PAGE 2 | [19 empty] | SULFIDE (MONTHLY AVERAGE) | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! |  | mg/l | [37 empty] | Day Shift Operator |  |  | Class: | "A" | Certificate No. | 4545 | Name: |  | McGEARY, J.
[70 empty] | Evening Shift Operator |  |  | Class: | "A" | Certificate No. | 4474 | Name: |  | BAYLER, J.
[20 empty] | PAGE 20 | [49 empty] | Night Shift Operator |  |  | Class: | "A" | Certificate No. | 3207 | Name: |  | HOSTNICK, N.
[70 empty] | Lead Operator |  |  | Class: | "A" | Certificate No. | 2769 | Name: |  | JUST, M.
[70 empty] | Type of Effluent Disposal or Reclaimed Water Reuse: |  |  |  |  | DEEPWELL INJECTION
[70 empty] | Permited Wet Weather Discharge Activated: |  |  |  | YES: |  | NO: |  |  | Not Applicable |  | X
If Yes, cumulative days of wet weather:
Attach additional sheets if necessary to list all certified operators. See page 1 "COVER PAGE" of supplental attachements.
DEP form 62-620.910(10), effective November 29, 1994
[19 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [46 empty] | Department of Natural Resource Protection
[5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [13 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [46 empty] | Division of Pollution Prevention and Remediation Programs
[5 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [13 empty] | MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING | [49 empty] | 218 S. W. 1st Avenue
[5 empty] | MONTHLY OPERATIONAL REPORT | [13 empty] | MONITORING WELL TWO |  |  |  | 7/21/97 thru 7/21/02 | [38 empty] | SLUDGE HAULERS MONTHLY REPORT | [6 empty] | Fort Lauderdale, FL 33301
[5 empty] | INFLUENT DATA | [11 empty] | MW-2 | I.D. #: 5066A11308 & 09 |  |  | PERMIT/CERT. #: UO-06-279401 & 508 | [40 empty] | BROWARD COUNTY CODE SECTION 27-356 (d)(4)(1) | [5 empty] | Tel. No. (954) 523-1002
| RUN DATE | [14 empty] | RUN DATE | [51 empty] | *FAX (954) 519-1245
| 2026-07-30 | [14 empty] | 2026-07-30 |  | UPPER MONITOR ZONE |  |  |  |  | LOWER MONITOR ZONE
[17 empty] | MIN | MAX | AVG |  |  | MIN | MAX | AVG | [34 empty] | Plant Name: | GEORGE T. LOHMEYER WASTEWATER TREATMENT FACILITY
| JUNE | RAW | RAW TSS | RAW SS | RAW | RAW | RAW | RAW | RAW | RAW | [5 empty] | JUNE | FT HEAD | FT HEAD | FT HEAD |  |  | FT HEAD | FT HEAD | FT HEAD | [34 empty] | Address: | 1765 S.E. 18th Street at Eisenhower Boulevard | [6 empty] | MONTH: | JUNE
| 2003 | CBOD | TOTAL | FIXED | COD | pH | CL_ | ALK. | H2S | TEMP.(F) | [5 empty] | 2003 | ABOVE | ABOVE | ABOVE |  |  | ABOVE | ABOVE | ABOVE | [34 empty] | Phone: | (954) 523-1002 * FAX (954) 468-1577 | [6 empty] | YEAR: | 2003
[17 empty] | NGVD | NGVD | NGVD |  |  | NGVD | NGVD | NGVD
| 1 | 43.9 | 86 | 16 | 190 | 7.2 | 420 | 202 | 2 | 82 | [5 empty] | 1 | ER | ER | ER |  |  | 42.14 | 42.26 | 42.15 | [34 empty] | a) | WEEK OF | JUNE |  | Type of Sludge |  |  | Disopsal Site |  |  | Cubic Yards
| 2 | 31.8 | 90 | 14 |  | 7.2 | 450 | 196 | 4 | 85 | [5 empty] | 2 | ER | ER | ER |  |  | 34.54 | 42.26 | 37.77
| 3 | 51 | 90 | 14 |  | 7.2 | 460 | 198 | 4 | 85 | [5 empty] | 3 | ER | ER | ER |  |  | 34.46 | 41.92 | 39.61 | [35 empty] | FIRST THRU SEVENTH |  |  | GRIT |  |  | Central Landfill |  |  | 20
| 4 | 61.4 | 74 | 2 | 192 | 7.2 | 470 | 196 | 4 | 85 | [5 empty] | 4 | ER | ER | ER |  |  | 41.92 | 42.07 | 41.97
| 5 | 46.6 | 92 | 16 | 223 | 7.2 | 480 | 198 | 3 | 85 | [5 empty] | 5 | ER | 30.9 | ER |  |  | ER | 42.12 | ER | [35 empty] | EIGHT THRU FORTEENTH |  |  | GRIT |  |  | Central Landfill |  |  | 0
| 6 | 56 | 64 | 10 | 254 | 7.2 | 470 | 212 | 4 | 85 | [5 empty] | 6 | ER | ER | ER |  |  | 42.07 | 42.19 | 42.07 | [35 empty] | FIFTHTEENTH THRU
| 7 | 76 | 132 | 20 | 221 | 7.2 | 430 | 200 | 3 | 84 | [5 empty] | 7 | ER | ER | ER |  |  | 42.11 | 42.25 | 42.11 | [35 empty] | TWENTY SECOND |  |  | GRIT |  |  | Central Landfill |  |  | 20
| 8 | 80.5 | 86 | 16 | 244 | 7.2 | 480 | 196 | 5 | 84 | [5 empty] | 8 | ER | ER | ER |  |  | 42.15 | 42.3 | 42.21 | [35 empty] | TWENTY THIRD THRU
| 9 | 46 | 128 |  |  | 7.1 | 500 | 188 | 5 | 83 | [5 empty] | 9 | ER | ER | ER |  |  | 29.51 | 42.33 | 33.27 | [35 empty] | THIRTY FIRST |  |  | GRIT |  |  | Central Landfill |  |  | 0
| 10 | 33 | 33 | 2 |  | 7.1 | 500 | 190 | 4 | 85 | [5 empty] | 10 | ER | ER | ER |  |  | 29.53 | 41.79 | 37.9
| 11 | 55 | 96 | 18 | 132 | 7.1 | 480 | 190 | 3 | 85 | [5 empty] | 11 | ER | ER | ER |  |  | 41.73 | 42.07 | 41.9 | [34 empty] | b) | WEEK OF | JUNE |  | Type of Sludge |  |  | Disopsal Site |  |  | Cubic Yards
| 12 | 58.7 | 88 | 14 | 202 | 7.2 | 500 | 190 | 4 | 85 | [5 empty] | 12 | ER | ER | ER |  |  | 41.94 | 42.18 | 42.01
| 13 | 63.2 | 90 | 7 | 122 | 7.2 | 470 | 192 | 5 | 85 | [5 empty] | 13 | ER | ER | ER |  |  | 42.02 | 42.24 | 42.05 | [35 empty] | FIRST THRU SEVENTH |  |  | RAGS |  |  | Central Landfill |  |  | 10
| 14 | 64 | 94 | 17 | 163 | 7.2 | 460 | 188 | 0 | 85 | [5 empty] | 14 | ER | ER | ER |  |  | 42.03 | 42.24 | 42.07
| 15 | 68.6 | 102 | 18 | 255 | 7.1 | 600 | 192 | 5 | 85 | [5 empty] | 15 | ER | ER | ER |  |  | 42.07 | 42.24 | 42.09 | [35 empty] | EIGHT THRU FORTEENTH |  |  | RAGS |  |  | Central Landfill |  |  | 10
| 16 | 62.1 | 98 | 18 |  | 7 | 580 | 202 | 5 | 85 | [5 empty] | 16 | ER | ER | ER |  |  | 30.58 | 42.23 | 34.21 | [35 empty] | FIFTHTEENTH THRU
| 17 | 88 | 46 | 8 |  | 7.1 | 550 | 192 | 5 | 85 | [5 empty] | 17 | ER | ER | ER |  |  | 30.57 | 41.55 | 38.53 | [35 empty] | TWENTY SECOND |  |  | RAGS |  |  | Central Landfill |  |  | 0
| 18 | 66.1 | 80 | 4 | 183 | 7 | 510 | 196 | 6 | 85 | [5 empty] | 18 | ER | ER | ER |  |  | 41.51 | 41.72 | 41.54 | [35 empty] | TWENTY THIRD THRU
| 19 | 77.7 | 110 | 20 | 162 | 7.1 | 500 | 204 | 6 | 85 | [5 empty] | 19 | ER | ER | ER |  |  | 41.67 | 41.81 | 41.7 | [35 empty] | THIRTY FIRST |  |  | RAGS |  |  | Central Landfill |  |  | 10
| 20 | 76 | 59 | 12 | 164 | 7.1 | 560 | 202 | 4 | 85 | [5 empty] | 20 | ER | ER | ER |  |  | 41.77 | 41.88 | 41.88 | [35 empty] | BCSR = Broward County Septage Receiving
| 21 | 56 | 80 | 12 | 252 | 7.2 | 540 | 200 | 6 | 85 | [5 empty] | 21 | ER | ER | ER |  |  | 41.82 | 41.98 | 41.92 | [34 empty] | c) | WEEK OF | JUNE |  | Type of Sludge |  |  | Disopsal Site |  |  | Gallons
| 22 | 54.8 | 70 | 14 | 203 | 7.2 | 500 | 192 | 7 | 83 | [5 empty] | 22 | ER | ER | ER |  |  | 41.87 | 42.01 | 41.98
| 23 | 66 | 86 | 12 |  | 7.2 | 490 | 206 | 4 | 85 | [5 empty] | 23 | ER | ER | ER |  |  | 29.4 | 42.03 | 33.22 | [35 empty] | FIRST THRU SEVENTH |  |  | VAC/Plastic & Rags |  |  | BCSR |  |  | 0
| 24 | 66 | 76 | 6 |  | 7.1 | 510 | 202 | 4 | 85 | [5 empty] | 24 | ER | ER | ER |  |  | 29.41 | 41.77 | 38.2
| 25 | 54 | 82 | 6 | 208 | 7.1 | 520 | 194 | 6 | 85 | [5 empty] | 25 | ER | ER | ER |  |  | 41.75 | 42 | 41.88 | [35 empty] | EIGHT THRU FORTEENTH |  |  | VAC/Plastic & Rags |  |  | BCSR |  |  | 0
| 26 | 55 | 100 | 20 | 242 | 7 | 560 | 196 | 6 | 85 | [5 empty] | 26 | ER | ER | ER |  |  | 41.93 | 42.15 | 42 | [35 empty] | FIFTHTEENTH THRU
| 27 | 86 | 100 | 10 | 221 | 7.1 | 580 | 198 | 5 | 85 | [5 empty] | 27 | ER | ER | ER |  |  | 42.06 | 42.24 | 42.04 | [35 empty] | TWENTY SECOND |  |  | VAC/Plastic & Rags |  |  | BSCR |  |  | 4500
| 28 | 62 | 92 | 18 | 238 | 7.2 | 600 | 196 | 5 | 85 | [5 empty] | 28 | ER | ER | ER |  |  | 42.07 | 42.22 | 42.08 | [35 empty] | TWENTY THIRD THRU
| 29 | 84 | 116 | 22 | 213 | 7.2 | 600 | 218 | 5 | 85 | [5 empty] | 29 | ER | ER | ER |  |  | 42.04 | 42.18 | 42.07 | [35 empty] | THIRTY FIRST |  |  | VAC/Plastic & Rags |  |  | BSCR |  |  | 0
| 30 | 69 | 96 | 20 |  | 6.6 | 640 | 208 | 7 | 85 | [5 empty] | 30 | ER | ER | ER |  |  | 30.68 | 42.16 | 34.12 | [34 empty] | TOTALS
[60 empty] | a) | 40 | cu.yds |  | GRIT |  | Signature
| TOTAL | 1858.4 | 2636 | 386 | 4284 | 213.8 | 15410 | 5934 | 136 | 2541 | [5 empty] | TOTAL | 0 | 30.9 | 0 |  |  | 1117.35 | 1262.39 | 1166.55 | [35 empty] | b) | 30 | cu.yds |  | RAGS |  | Title
| AVERAGE | 61.9467 | 87.8667 | 13.3103 | 204 | 7.1267 | 513.6667 | 197.8 | 4.6897 | 84.7 | [5 empty] | AVERAGE | #DIV/0! | 30.9 | #DIV/0! |  |  | 38.5293 | 42.0797 | 40.2259 | [35 empty] | c) | 4500 | gal. |  | VAC/Plastic & Rags |  | Date
[16 empty] | MAXIMUM | 0 | 30.9 | 0 |  |  | 42.15 | 42.33 | 42.21
[16 empty] | MINIMUM | 0 | 30.9 | 0 |  |  | 29.4 | 41.55 | 33.22 | [35 empty] | * Sludge Reports should be submitted along with the monthly operating reports to Broward County Department
of Natural Resource Protection, 218 S. W. 1st Avenue, Fort Lauderdale, Florida 33301
PAGE 3
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
[5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [13 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
[5 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [13 empty] | MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
[5 empty] | MONTHLY OPERATIONAL REPORT | [13 empty] | MONITORING WELL THREE |  |  |  | 7/21/97 thru 7/21/02
[5 empty] | EFFLUENT DATA PART 1 | [11 empty] | MW-3 | I.D. #: 5066A11310 |  |  | PERMIT/CERT. #: UO-06-279510
RUN DATE
[16 empty] | 2026-07-30 |  | UPPER MONITOR ZONE |  |  |  |  | LOWER MONITOR ZONE
| RUN DATE | [15 empty] | MIN | MAX | AVG |  |  | MIN | MAX | AVG
| 2026-07-30 | [14 empty] | JUNE | FT HEAD | FT HEAD | FT HEAD |  |  | FT HEAD | FT HEAD | FT HEAD
[14 empty] | BOD | TSS | 2003 | ABOVE | ABOVE | ABOVE |  |  | ABOVE | ABOVE | ABOVE
| JUNE | EFFLUENT | EFFL. TSS | EFFL. SS | EFFLUENT | EFFL. | EFFL. | EFFL. | EFFL. | EFFL. | TDS |  |  | MONTHLY AVG OVER 30 | MONTHLY AVG OVER 30 |  | NGVD | NGVD | NGVD |  |  | NGVD | NGVD | NGVD
| 2003 | CBOD | TOTAL | FIXED | COD | CL_ | ALK. | TURB. | COND. | TEMP.(F) |  |  |  | 0 | 0 | 1 | 31.28 | 31.46 | 31.33 |  |  | 45.28 | 45.39 | 45.37
[14 empty] | WEKKLY OVER 45 | WEKKLY OVER 45 | 2 | 18.72 | 31.45 | 23.99 |  |  | 37.66 | 45.39 | 40.83
| 1 | 2.56 | 10 | 2 | 38 | 390 | 184 | 7.58 | 1567 | 82 | 765 | 1 |  | 0 | 0 | 3 | 18.59 | 30.81 | 27.04 |  |  | 37.62 | 45 | 42.77
| 2 | 3.78 | 9 | 0 |  | 410 | 184 | 7.44 | 1690 | 85 | 950 | 1 |  | SINGLE DAY OVER 60 | SINGLE DAY OVER 60 | 4 | 30.74 | 30.96 | 30.87 |  |  | 45 | 45.16 | 45
| 3 | 5.1 | 11 | 3 |  | 420 | 192 | 8.01 | 1816 | 85 | 879 | 1 |  | 0 | 0 | 5 | 30.84 | 31.01 | 30.96 |  |  | 45.13 | 45.22 | 45.11
| 4 | 4.79 | 10 | 1 | 58.6 | 450 | 188 | 7.66 | 1881 | 85 | 1060 | 1 |  | 0 | 0 | 6 | 30.9 | 31.11 | 30.99 |  |  | 45.19 | 45.33 | 45.26
| 5 | 7.24 | 15 | 5 | 50.7 | 450 | 190 | 9.76 | 1920 | 85 | 963 | 1 |  |  |  | 7 | 30.89 | 31.13 | 31.01 |  |  | 45.24 | 45.38 | 45.38
| 6 | 5.5 | 18 | 3 | 47.8 | 530 | 198 | 6.4 | 1970 | 85 | 864 | 1 |  |  |  | 8 | 30.93 | 31.17 | 31.04 |  |  | 45.28 | 45.45 | 45.4
| 7 | 3.7 | 16 | 3 | 47 | 440 | 194 | 7.67 | 2020 | 85 | 1119 | 1 | 4.6671 | 4.6671 | 12.7143 | 9 | 19.87 | 31.17 | 23.14 |  |  | 34.78 | 45.45 | 37.93
| 8 | 3.85 | 12 | 3 | 47 | 530 | 188 | 6.76 | 1965 | 85 | 928 | 1 |  | 4.8514 | 13 | 10 | 19.87 | 30.78 | 27.19 |  |  | 34.79 | 44.9 | 41.68
| 9 | 3.2 | 10 |  |  | 440 | 174 | 6.47 | 1948 | 82 | 983 | 1 |  | 4.7686 | 13.1429 | 11 | 30.65 | 31.09 | 30.87 |  |  | 44.84 | 45.18 | 44.99
| 10 | 4.5 | 8 | 1 |  | 480 | 174 | 6.72 | 1924 | 85 | 1193 | 1 |  | 4.6829 | 12.7143 | 12 | 30.88 | 31.19 | 31 |  |  | 45.06 | 45.29 | 45.16
| 11 | 5.47 | 8 | 1 | 39.8 | 470 | 184 | 6.23 | 1975 | 85 | 1014 | 1 |  | 4.78 | 12.4286 | 13 | 30.94 | 31.26 | 31.07 |  |  | 45.16 | 45.35 | 45.3
| 12 | 4.42 | 11 | 3 | 46.9 | 460 | 188 | 6.49 | 2030 | 85 | 1368 | 1 |  | 4.3771 | 11.8571 | 14 | 30.96 | 31.25 | 31.07 |  |  | 45.18 | 45.34 | 45.3
| 13 | 5.35 | 11 | 1 | 40.4 | 470 | 188 | 6.47 | 1945 | 85 | 1174 | 1 |  | 4.3557 | 10.8571 | 15 | 31 | 31.25 | 31.06 |  |  | 45.23 | 45.36 | 45.31
| 14 | 4.9 | 10 | 2 | 44.8 | 470 | 184 | 6.32 | 1960 | 85 | 1174 | 1 | 4.5271 | 4.5271 | 10 | 16 | 20.08 | 31.23 | 23.57 |  |  | 38.44 | 45.35 | 40.67
| 15 | 2.48 | 10 | 2 | 47.1 | 500 | 180 | 5.65 | 2000 | 85 | 1058 | 1 |  | 4.3314 | 9.7143 | 17 | 19.96 | 30.92 | 27.82 |  |  | 38.42 | 44.29 | 42.55
| 16 | 4.22 | 12 | 4 |  | 570 | 198 | 6.83 | 2150 | 85 | 1076 | 1 |  | 4.4771 | 10 | 18 | 30.8 | 31.09 | 30.95 |  |  | 44.27 | 44.46 | 44.4
| 17 | 3.2 | 20 | 6 |  | 550 | 180 | 5.73 | 2330 | 85 | 1056 | 1 |  | 4.2914 | 11.7143 | 19 | 30.97 | 31.18 | 31.05 |  |  | 44.44 | 44.56 | 44.5
| 18 | 2.2 | 15 | 1 | 48.5 | 540 | 188 | 6.08 | 2120 | 85 | 1100 | 1 |  | 3.8243 | 12.7143 | 20 | 31.09 | 31.29 | 31.16 |  |  | 44.54 | 44.67 | 44.53
| 19 | 3.5 | 10 | 2 | 36.9 | 520 | 188 | 6.09 | 2070 | 85 | 1076 | 1 |  | 3.6929 | 12.5714 | 21 | 31.14 | 31.42 | 31.27 |  |  | 44.6 | 44.76 | 44.59
| 20 | 3.9 | 10 | 2 | 40.4 | 550 | 186 | 6.11 | 2000 | 85 | 945 | 1 |  | 3.4857 | 12.4286 | 22 | 31.24 | 31.47 | 31.39 |  |  | 44.65 | 44.8 | 44.72
| 21 | 5.4 | 14 | 5 | 35.5 | 490 | 190 | 7.21 | 1930 | 85 | 951 | 1 | 3.5571 | 3.5571 | 13 | 23 | 27.18 | 31.45 | 28.52 |  |  | 36.06 | 44.79 | 38.62
| 22 | 3.88 | 10 | 2 | 36.6 | 490 | 182 | 6.72 | 1979 | 83 | 949 | 1 |  | 3.7571 | 13 | 24 | 27.15 | 31.64 | 30.22 |  |  | 36.07 | 44.91 | 42.41
| 23 | 3.9 | 11 | 1 |  | 500 | 182 | 6.65 | 2020 | 85 | 1050 | 1 |  | 3.7114 | 12.8571 | 25 | 31.56 | 31.88 | 31.76 |  |  | 44.88 | 45.15 | 44.99
| 24 | 3.7 | 11 | 1 |  | 520 | 190 | 6.2 | 2050 | 85 | 1034 | 1 |  | 3.7829 | 11.5714 | 26 | 31.75 | 32.02 | 31.87 |  |  | 45.06 | 45.27 | 45.12
| 25 | 4.9 | 12 | 1 | 41.2 | 510 | 194 | 5.81 | 2060 | 85 | 1145 | 1 |  | 4.1686 | 11.1429 | 27 | 31.85 | 32.1 | 31.96 |  |  | 45.2 | 45.37 | 45.34
| 26 | 4 | 15 | 3 | 44.1 | 530 | 190 | 6.28 | 2160 | 85 | 1231 | 1 |  | 4.24 | 11.8571 | 28 | 31.85 | 32.06 | 31.97 |  |  | 45.22 | 45.35 | 45.36
| 27 | 5 | 14 | 3 | 38.6 | 580 | 192 | 6.87 | 2160 | 85 | 1152 | 1 |  | 4.3971 | 12.4286 | 29 | 31.79 | 31.97 | 31.89 |  |  | 45.21 | 45.31 | 45.29
| 28 | 3 | 11 | 3 | 42.4 | 580 | 186 | 6.75 | 2040 | 85 | 970 | 1 |  | 4.0543 | 12 | 30 | 17.66 | 31.91 | 22.07 |  |  | 36.85 | 45.29 | 39.55
| 29 | 2 | 11 | 3 | 39.5 | 590 | 188 | 4.86 | 2180 | 85 | 1115 | 1 |  | 3.7857 | 12.1429
| 30 | 2 | 12 | 3 |  | 590 | 194 | 4.47 | 2190 | 85 | 1044 | 1 |  | 3.5143 | 12.2857 | TOTAL | 843.13 | 940.72 | 890.1 |  |  | 1275.35 | 1353.52 | 1313.43
[12 empty] | 0 | 3.5978 | 3.4833 | 12.5 | AVERAGE | 28.1043 | 31.3573 | 29.67 |  |  | 42.5117 | 45.1173 | 43.781
| TOTAL | 121.64 | 357 | 70 | 911.8 | 15020 | 5618 | 198.29 | 60050 | 2542 | 31386 |  |  |  |  | MAXIMUM | 31.85 | 32.1 | 31.97 |  |  | 45.28 | 45.45 | 45.4
| AVERAGE | 4.0547 | 11.9 | 2.5 | 43.419 | 500.6667 | 187.2667 | 6.6097 | 2001.6667 | 84.7333 | 1046.2 |  |  | 4.1426 | 12.0257 | MINIMUM | 17.66 | 30.78 | 22.07 |  |  | 34.78 | 44.29 | 37.93
| MAXIMUM | 7.24 | 20
[5 empty] | PAGE 4 | [14 empty] | PAGE 22
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
[5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [13 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
[5 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [13 empty] | MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
[5 empty] | MONTHLY OPERATIONAL REPORT | [13 empty] | REGIONAL MONITORING WELL ONE
[5 empty] | EFFLUENT DATA PART 2 | [13 empty] | RMW-1
[16 empty] | RUN DATE |  |  | UC06-249353
[16 empty] | 2026-07-30 |  | UPPER MONITOR ZONE |  |  |  |  | LOWER MONITOR ZONE
RUN DATE | [16 empty] | MIN | MAX | AVG |  |  | MIN | MAX | AVG
2026-07-30 | [15 empty] | JUNE | FT HEAD | FT HEAD | FT HEAD |  |  | FT HEAD | FT HEAD | FT HEAD
[16 empty] | 2003 | ABOVE | ABOVE | ABOVE |  |  | ABOVE | ABOVE | ABOVE
| JUNE | EFF. BACT. | EFF. BACT. | FREE | TOTAL | EFFL. | EFF PH | EFF PH | EFF. SAP | AVG. | [6 empty] | NGVD | NGVD | NGVD |  |  | NGVD | NGVD | NGVD
| 2003 | TOTAL | FECAL | CL2 | CL2 | pH | MIN | MAX | TEMP.(C) | BLK. | [5 empty] | 1 | 44.19 | 44.3 | 44.25 |  |  | 21.92 | 22.04 | 21.98
[16 empty] | 2 | 38.11 | 44.29 | 40.65 |  |  | 20.43 | 22.05 | 21.23
| 1 | 430 | 0 | 0.1 | 1 | 6.6 | 6.6 | 6.6 | 0 | 47 | [5 empty] | 3 | 38.03 | 43.69 | 42.11 |  |  | 20.49 | 21.46 | 21.06
| 2 | 250 | 0 | 0 | 1.1 | 6.7 | 6.6 | 6.6 | 8 | 43 | [5 empty] | 4 | 43.67 | 43.86 | 43.79 |  |  | 21.46 | 21.62 | 21.54
| 3 | 196 | 0 | 0 | 1.1 | 6.7 | 6.6 | 6.8 | 3 | 42 | [5 empty] | 5 | 43.84 | 43.95 | 43.9 |  |  | 21.59 | 21.68 | 21.64
| 4 | 70 | 36 | 0 | 1 | 6.7 | 6.6 | 6.7 | 2 | 43 | [5 empty] | 6 | 43.93 | 44 | 43.96 |  |  | 21.66 | 21.76 | 21.71
| 5 | 63 | 9 | 0 | 1.1 | 6.7 | 6.6 | 6.7 | 1 | 40 | [5 empty] | 7 | 43.97 | 44.05 | 44.01 |  |  | 21.7 | 21.8 | 21.75
| 6 | 360 | 0 | 0.1 | 0.9 | 6.6 | 6.6 | 6.7 | 8 | 44 | [5 empty] | 8 | 44 | 44.08 | 44.04 |  |  | 21.7 | 21.84 | 21.77
| 7 | 152 | 0 | 0.1 | 0.9 | 6.6 | 6.6 | 6.7 | 8 | 50 | [5 empty] | 9 | 44 | 44.11 | 44.05 |  |  | 21.72 | 21.85 | 21.79
| 8 | 27 | 0 | 0 | 0.9 | 6.6 | 6.6 | 6.6 | 1 | 49 | [5 empty] | 10 | 43.98 | 44.09 | 44.04 |  |  | 21.72 | 21.86 | 21.8
| 9 | 53 | 9 | 0 | 0.9 | 6.7 | 6.6 | 6.8 | 10 | 50 | [5 empty] | 11 | 44 | 44.15 | 44.08 |  |  | 21.76 | 21.91 | 21.84
| 10 | 5500 | 0 | 0 | 0.9 | 6.7 | 6.6 | 6.8 | 1 | 48 | [5 empty] | 12 | 44.03 | 44.16 | 44.09 |  |  | 21.76 | 21.9 | 21.84
| 11 | 22000 | 9 | 0 | 1 | 6.7 | 6.6 | 6.8 | 3 | 46 | [5 empty] | 13 | 43.97 | 44.13 | 44.05 |  |  | 21.75 | 21.88 | 21.83
| 12 | 40000 | 9 | 0 | 0.8 | 6.6 | 6.5 | 6.8 | 10 | 44 | [5 empty] | 14 | 43.9 | 44.07 | 43.99 |  |  | 21.73 | 21.86 | 21.8
| 13 | 438 | 0 | 0.1 | 0.9 | 6.6 | 6.5 | 6.8 | 8 | 48 | [5 empty] | 15 | 43.93 | 44.05 | 44 |  |  | 21.76 | 21.88 | 21.81
| 14 | 536 | 0 | 0.1 | 0.9 | 6.6 | 6.6 | 6.7 | 7 | 52 | [5 empty] | 16 | 43.96 | 44.07 | 44.03 |  |  | 21.78 | 21.9 | 21.82
| 15 | 5500 | 0 | 0 | 0.8 | 6.6 | 6.6 | 6.7 | 7 | 52 | [5 empty] | 17 | 44.02 | 44.11 | 44.07 |  |  | 21.81 | 21.9 | 21.86
| 16 | 170 | 0 | 0 | 0.9 | 6.8 | 6.6 | 7 | 10 | 45 | [5 empty] | 18 | 44.06 | 44.14 | 44.1 |  |  | 21.81 | 21.95 | 21.9
| 17 | TNTC | 98 | 0 | 0.8 | 6.8 | 6.8 | 7.1 | 0 | 48 | [5 empty] | 19 | 44.09 | 44.2 | 44.14 |  |  | 21.88 | 21.97 | 21.93
| 18 | 280 | 0 | 0 | 1 | 6.8 | 6.7 | 6.8 | OS | 44 | [5 empty] | 20 | 44.15 | 44.22 | 44.18 |  |  | 21.89 | 22.01 | 21.96
| 19 | 98 | 0 | 0 | 0.9 | 6.7 | 6.6 | 6.8 | 4 | 38 | [5 empty] | 21 | 44.06 | 44.19 | 44.14 |  |  | 21.88 | 22.01 | 21.94
| 20 | 290 | 9 | 0.1 | 0.9 | 6.7 | 6.7 | 6.8 | 7 | 43 | [5 empty] | 22 | 44.05 | 44.14 | 44.09 |  |  | 21.9 | 22 | 21.95
| 21 | 3800 | 0 | 0.1 | 0.9 | 6.6 | 6.6 | 6.7 | 7 | 45 | [5 empty] | 23 | 43.99 | 44.11 | 44.05 |  |  | 21.88 | 22.01 | 21.95
| 22 | 12500 | 402 | 0 | 0.5 | 6.7 | 6.7 | 6.7 | 4 | 41 | [5 empty] | 24 | 43.91 | 44.05 | 43.97 |  |  | 21.84 | 21.97 | 21.91
| 23 | 8000 | 0 | 0 | 0.9 | 6.7 | 6.6 | 6.9 | 3 | 45 | [5 empty] | 25 | 43.9 | 44.01 | 43.95 |  |  | 21.82 | 21.94 | 21.89
| 24 | 290 | 0 | 0 | 0.8 | 6.7 | 6.7 | 6.8 | 3 | 40 | [5 empty] | 26 | 43.9 | 44.02 | 43.97 |  |  | 21.85 | 21.99 | 21.92
| 25 | 420 | 0 | 0 | 0.9 | 6.7 | 6.6 | 6.8 | 4 | 33 | [5 empty] | 27 | 43.95 | 44.06 | 44.01 |  |  | 21.89 | 22 | 21.95
| 26 | 0 | 0 | 0 | 0.7 | 6.7 | 6.6 | 6.8 | 4 | 30 | [5 empty] | 28 | 43.9 | 44.05 | 43.97 |  |  | 21.85 | 21.97 | 21.92
| 27 | TNTC | TNTC | 0 | 0.8 | 6.6 | 6.5 | 6.8 | 7 | 39 | [5 empty] | 29 | 43.83 | 43.98 | 43.9 |  |  | 21.76 | 21.91 | 21.83
| 28 | 223 | 0 | 0.1 | 0.8 | 6.6 | 6.5 | 6.6 | 8 | 45 | [5 empty] | 30 | 35.69 | 43.93 | 38.63 |  |  | 19.02 | 21.85 | 20.42
| 29 | 0 | 0 | 0 | 0.7 | 6.7 | 6.5 | 6.7 | 8 | 37
| 30 | 180 | 0 | 0 | 0.8 | 6.7 | 6.5 | 6.7 | 8 | 38 | [5 empty] | TOTAL | 1299.01 | 1322.26 | 1310.21 |  |  | 648.01 | 656.77 | 652.54
[16 empty] | AVERAGE | 43.3003 | 44.0753 | 43.6737 |  |  | 21.6003 | 21.8923 | 21.7513
| TOTAL | 101826 | 581 | 0.8 | 26.5 | 200.2 | 198 | 202.8 | 154 | 1309 | [5 empty] | MAXIMUM | 44.19 | 44.3 | 44.25 |  |  | 21.92 | 22.05 | 21.98
| AVERAGE | 3636.6429 | 20.0345 | 0.026667 | 0.88333 | 6.6733 | 6.6 | 6.76 | 4.9677 | 43.6333 | [5 empty] | MINIMUM | 35.69 | 43.69 | 38.63 |  |  | 19.02 | 21.46 | 20.42
[7 empty] | 6.5 | 7.1
[7 empty] | MIN | MAX
PAGE 5
PAGE 23
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
NUTRIENTS
RUN DATE
| 2026-07-30 |  | INFLUENT | [5 empty] | EFFLUENT
| JUNE | INFLUENT | INFLUENT | INFLUENT | INFLUENT |  | EFFL. | EFFL. | EFFL. | EFFL.
| 2003 | NH-3 | N03-N | TKN | TOT P |  | NH-3 | N03-N | TKN | TOT P
| 1 | 9.91 | 0.072 | 13.29 | 1.49 |  | 7.12 | 0.098 | 9.86 | 0.571
2
3
| 4 | 11.45 | 0.28 | 15.09 | 1.64 |  | 9.6 | 0.21 | 13.16 | 0.725
| 5 | 11.94 | 0.175 | 15.88 | 1.69 |  | 9.8 | 0.238 | 13 | 0.597
| 6 | 13.57 | 0.002 | 17.58 | 2.08 |  | 10.29 | 0.182 | 14.28 | 0.958
| 7 | 12.05 | 0.154 | 16.05 | 1.86 |  | 9.14 | 0.184 | 12.52 | 0.54
| 8 | 11.97 | 0.025 | 15.64 | 1.82 |  | 9.3 | 0.256 | 12.91 | 0.412
9
10
| 11 | 11.98 | 0.115 | 15.97 | 1.66 |  | 9.81 | 0.275 | 13.06 | 0.651
| 12 | 12.25 | 0.337 | 16.59 | 1.92 |  | 8.9 | 0.663 | 12.96 | 0.662
| 13 | 13.24 | 0.002 | 19.08 | 1.93 |  | 10.51 | 0.287 | 14.1 | 0.685
| 14 | 12.64 | 0.551 | 17.17 | 1.95 |  | 9.89 | 0.273 | 13.48 | 0.82
| 15 | 13 | 0.373 | 17.23 | 2.13 |  | 9.12 | 0.601 | 13.33 | 0.762
16
17
| 18 | 14.12 | 0.35 | 21.02 | 2.47 |  | 11.73 | 0.279 | 16.12 | 0.872
| 19 | 13.41 | 0.167 | 18.81 | 2.21 |  | 10.7 | 0.204 | 15.15 | 0.963
| 20 | 10.83 | 0.002 | 16.99 | 1.86 |  | 8.46 | 0.177 | 12.16 | 0.969
| 21 | 11.41 | 0.002 | 18.51 | 2.17 |  | 8.15 | 0.195 | 12.23 | 1.23
| 22 | 11.07 | 0.212 | 18.18 | 2.01 |  | 8.96 | 0.201 | 13.13 | 0.992
23
24
| 25 | 12.98 | 0.279 | 21.3 | 2.44 |  | 11.23 | 0.248 | 15.92 | 0.905
| 26 | 13.32 | 0.288 | 21.07 | 2.53 |  | 10.41 | 0.22 | 15.14 | 1.19
| 27 | 13.62 | 0.002 | 20.42 | 2.39 |  | 10.76 | 0.219 | 14.77 | 1.03
| 28 | 13.25 | 0.002 | 20.43 | 2.43 |  | 10.07 | 0.24 | 14.27 | 0.884
| 29 | 11.52 | 0.002 | 20.98 | 2.67 |  | 9.52 | 0.266 | 13.23 | 0.821
30
| TOTAL | 259.53 | 3.392 | 377.28 | 43.35 | TOT. | 203.47 | 5.516 | 284.78 | 17.239
| AVERAGE | 12.3586 | 0.16152 | 17.9657 | 2.0643 | AVG. | 9.689 | 0.26267 | 13.561 | 0.8209
PAGE 6
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
REACTOR ONE PROCESS
RUN DATE
| 2026-07-30 |  | TRAIN "A" | [5 empty] | TRAIN "B"
| JUNE | MLSS | MLVSS | SS | SVI |  | MLSS | MLVSS | SS | SVI
| 2003 | "A" | "A" | "A" | "A" |  | "B" | "B" | "B" | "B"
| 1 | O/S | O/S | O/S |  |  | 2640 | 2110 | 24 | 90.9091
| 2 | O/S | O/S | O/S |  |  | 2430 | 2000 | 26 | 106.9959
| 3 | O/S | O/S | O/S |  |  | 2760 | 2210 | 27 | 97.8261
| 4 | O/S | O/S | O/S |  |  | 2770 | 2320 | 27 | 97.4729
| 5 | O/S | O/S | O/S |  |  | 2900 | 2320 | 27 | 93.1034
| 6 | O/S | O/S | O/S |  |  | 3430 | 2830 | 34 | 99.1254
| 7 | O/S | O/S | O/S |  |  | 2420 | 2010 | 30 | 123.9669
| 8 | O/S | O/S | O/S |  |  | 3120 | 2500 | 31 | 99.359
| 9 | O/S | O/S | O/S |  |  | 2510 | 2060 | 30 | 119.5219
| 10 | O/S | O/S | O/S |  |  | 2820 | 2370 | 32 | 113.4752
| 11 | O/S | O/S | O/S |  |  | 2730 | 2180 | 26 | 95.2381
| 12 | O/S | O/S | O/S |  |  | 3130 | 2500 | 32 | 102.2364
| 13 | O/S | O/S | O/S |  |  | 3100 | 2480 | 32 | 103.2258
| 14 | O/S | O/S | O/S |  |  | 2840 | 2270 | 29 | 102.1127
| 15 | O/S | O/S | O/S |  |  | 2830 | 2260 | 25 | 88.3392
| 16 | O/S | O/S | O/S |  |  | 2730 | 2180 | 34 | 124.5421
| 17 | O/S | O/S | O/S |  |  | 2880 | 2440 | 37 | 128.4722
| 18 | O/S | O/S | O/S |  |  | 2850 | 2440 | 33 | 115.7895
| 19 | O/S | O/S | O/S |  |  | 2680 | 2140 | 36 | 134.3284
| 20 | O/S | O/S | O/S |  |  | 2410 | 1920 | 28 | 116.1826
| 21 | O/S | O/S | O/S |  |  | 1640 | 1530 | 26 | 158.5366
| 22 | O/S | O/S | O/S |  |  | 3120 | 2500 | 37 | 118.5897
| 23 | O/S | O/S | O/S |  |  | 2450 | 2050 | 32 | 130.6122
| 24 | O/S | O/S | O/S |  |  | 2680 | 2260 | 32 | 119.403
| 25 | O/S | O/S | O/S |  |  | 1820 | 1540 | 17 | 93.4066
| 26 | O/S | O/S | O/S |  |  | 3050 | 2440 | 30 | 98.3607
| 27 | O/S | O/S | O/S |  |  | 3260 | 2630 | 31 | 95.092
| 28 | O/S | O/S | O/S |  |  | 2620 | 2100 | 27 | 103.0534
| 29 | O/S | O/S | O/S |  |  | 2740 | 2190 | 26 | 94.8905
| 30 | O/S | O/S | O/S |  |  | 2080 | 1660 | 23 | 110.5769
|  | O/S | O/S | O/S
| TOTAL | 0 | 0 | 0 |  |  | 81440 | 66440 | 881
| AVERAGE | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 2714.6667 | 2214.6667 | 29.3667 | 108.1778
PAGE 7
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
REACTOR TWO PROCESS
RUN DATE
| 2026-07-30 |  | TRAIN "C" | [5 empty] | TRAIN "D"
| JUNE | MLSS | MLVSS | SS | SVI |  | MLSS | MLVSS | SS | SVI
| 2003 | "C" | "C" | "C" | "C" |  | "D" | "D" | "D" | "D"
| 1 | O/S | O/S | O/S |  |  | 2380 | 1900 | 24 | 100.8403
| 2 | O/S | O/S | O/S |  |  | 2740 | 2260 | 28 | 102.1898
| 3 | O/S | O/S | O/S |  |  | 2600 | 2080 | 25 | 96.1538
| 4 | O/S | O/S | O/S |  |  | 2680 | 2130 | 24 | 89.5522
| 5 | O/S | O/S | O/S |  |  | 2650 | 2120 | 25 | 94.3396
| 6 | O/S | O/S | O/S |  |  | 2730 | 2260 | 32 | 117.2161
| 7 | O/S | O/S | O/S |  |  | 2420 | 2030 | 31 | 128.0992
| 8 | O/S | O/S | O/S |  |  | 3460 | 2770 | 31 | 89.5954
| 9 | O/S | O/S | O/S |  |  | 2940 | 2350 | 28 | 95.2381
| 10 | O/S | O/S | O/S |  |  | 3290 | 2740 | 30 | 91.1854
| 11 | O/S | O/S | O/S |  |  | 2580 | 2060 | 26 | 100.7752
| 12 | O/S | O/S | O/S |  |  | 2960 | 2370 | 31 | 104.7297
| 13 | O/S | O/S | O/S |  |  | 2900 | 2310 | 31 | 106.8966
| 14 | O/S | O/S | O/S |  |  | 2690 | 2150 | 27 | 100.3717
| 15 | O/S | O/S | O/S |  |  | 3000 | 2400 | 25 | 83.3333
| 16 | O/S | O/S | O/S |  |  | 3060 | 2450 | 37 | 120.915
| 17 | O/S | O/S | O/S |  |  | 3110 | 2580 | 37 | 118.9711
| 18 | O/S | O/S | O/S |  |  | 2980 | 2520 | 32 | 107.3826
| 19 | O/S | O/S | O/S |  |  | 2590 | 2070 | 33 | 127.4131
| 20 | O/S | O/S | O/S |  |  | 2310 | 1870 | 27 | 116.8831
| 21 | O/S | O/S | O/S |  |  | 1850 | 1670 | 25 | 135.1351
| 22 | O/S | O/S | O/S |  |  | 2770 | 2220 | 35 | 126.3538
| 23 | O/S | O/S | O/S |  |  | 2790 | 2340 | 30 | 107.5269
| 24 | O/S | O/S | O/S |  |  | 2970 | 2480 | 30 | 101.0101
| 25 | O/S | O/S | O/S |  |  | 2960 | 2460 | 26 | 87.8378
| 26 | O/S | O/S | O/S |  |  | 3010 | 2410 | 30 | 99.6678
| 27 | O/S | O/S | O/S |  |  | 3100 | 2490 | 31 | 100
| 28 | O/S | O/S | O/S |  |  | 2820 | 2260 | 27 | 95.7447
| 29 | O/S | O/S | O/S |  |  | 2960 | 2370 | 26 | 87.8378
| 30 | O/S | O/S | O/S |  |  | 2530 | 2020 | 26 | 102.7668
|  | O/S | O/S | O/S
| TOTAL | 0 | 0 | 0 |  |  | 83830 | 68140 | 870
| AVERAGE | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 2794.3333 | 2271.3333 | 29 | 103.7815
PAGE 8
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
RAS SUMMARY
RUN DATE
2026-07-30
| JUNE | R-1 | R-2 | TOTAL | F/M | TOTAL | SLUDGE | % TOT | % FIX | % VOL.
| 2003 | TOT. RAS | TOT. RAS | MLVSS | RATIO | MLSS | AGE | RAS | RAS | RAS
|  | MGD | MGD
| 1 | 6.616 | 6.892 | 4010 | 0.69739 | 5020 | 0.91633 | 1.26 | 20.7 | 79.3
| 2 | 6.511 | 6.966 | 4260 | 0.44831 | 5170 | 0.95651 | 0.94 | 22.6 | 77.4
| 3 | 6.456 | 6.612 | 4290 | 0.67708 | 5360 | 1.0457 | 0.93 | 23.8 | 76.2
| 4 | 6.394 | 6.473 | 4450 | 0.7517 | 5450 | 1.3518 | 0.92 | 22.6 | 77.4
| 5 | 6.426 | 6.905 | 4440 | 0.54895 | 5550 | 1.1534 | 1.1 | 20.7 | 79.3
| 6 | 6.611 | 7.275 | 5090 | 0.55179 | 6160 | 1.9191 | 0.7 | 23.5 | 76.5
| 7 | 6.607 | 7.319 | 4040 | 0.94637 | 4840 | 0.72886 | 1.72 | 6.28 | 93.72
| 8 | 6.544 | 7.345 | 5270 | 0.76572 | 6580 | 1.5263 | 1.15 | 19.3 | 80.7
| 9 | 6.382 | 7.1 | 4410 | 0.54844 | 5450 | 0.8098 | 1.06 | 19.7 | 80.3
| 10 | 6.616 | 7.073 | 5110 | 0.34825 | 6110 | 3.4334 | 0.53 | 25.5 | 74.5
| 11 | 6.572 | 6.848 | 4240 | 0.6647 | 5310 | 1.0794 | 0.75 | 22.7 | 77.3
| 12 | 6.502 | 7.011 | 4870 | 0.59395 | 6090 | 1.4044 | 0.86 | 26.5 | 73.5
| 13 | 6.453 | 7.315 | 4790 | 0.62668 | 6000 | 1.4036 | 0.91 | 25.3 | 74.7
| 14 | 6.523 | 6.928 | 4420 | 0.66106 | 5530 | 1.2886 | 0.91 | 24.1 | 75.9
| 15 | 6.537 | 6.478 | 4660 | 0.66002 | 5830 | 1.2748 | 1.11 | 21 | 79
| 16 | 6.479 | 7.046 | 4630 | 0.59998 | 5790 | 1.3208 | 1.13 | 19.5 | 80.5
| 17 | 6.634 | 7.228 | 5020 | 0.77074 | 5990 | 2.9617 | 0.9 | 21.1 | 78.9
| 18 | 6.478 | 7.201 | 4960 | 0.57753 | 5830 | 1.6816 | 1.01 | 21.3 | 78.7
| 19 | 6.462 | 6.961 | 4210 | 0.88296 | 5270 | 1.0014 | 1.04 | 19.9 | 80.1
| 20 | 6.421 | 7.204 | 3790 | 1.1532 | 4720 | 1.3911 | 1.08 | 20 | 80
| 21 | 6.421 | 6.467 | 3200 | 0.97872 | 3490 | 0.78003 | 1.04 | 23 | 77
| 22 | 6.425 | 6.944 | 4720 | 0.58567 | 5890 | 1.668 | 1.02 | 19.2 | 80.8
| 23 | 6.511 | 6.511 | 4390 | 0.74791 | 5240 | 1.2248 | 1.08 | 20.7 | 79.3
| 24 | 6.511 | 6.511 | 4740 | 0.6736 | 5650 | 1.5367 | 1.05 | 21.8 | 78.2
| 25 | 6.511 | 6.511 | 4000 | 0.63051 | 4780 | 1.2481 | 0.72 | 22.9 | 77.1
| 26 | 6.511 | 6.511 | 4850 | 0.50587 | 6060 | 1.3585 | 0.88 | 26.1 | 73.9
| 27 | 6.511 | 6.511 | 5120 | 0.77301 | 6360 | 1.382 | 1.04 | 24.3 | 75.7
| 28 | 6.511 | 6.511 | 4360 | 0.64817 | 5440 | 1.2973 | 0.91 | 26.5 | 73.5
| 29 | 6.511 | 6.511 | 4560 | 0.79477 | 5700 | 1.1389 | 0.98 | 22.4 | 77.6
| 30 | 7.18 | 7.18 | 3680 | 0.79893 | 4610 | 1.127 | 0.94 | 23.2 | 76.8
| TOTAL | 195.827 | 206.348 | 134580 |  | 165270 |  | 29.67 | 656.18 | 2343.82
| AVERAGE | 6.5276 | 6.8783 | 4486 | 0.68752 | 5509 | 1.2593 | 0.989 | 21.8727 | 78.1273
PAGE 9
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
DEWATERING DATA
RUN DATE
| 2026-07-30 |  | FEED SLUDGE |  |  |  |  | FILTRATE RETURN
| JUNE | % TOT. | % FIX. | % VOL. | pH |  | % TOT. | % FIX. | % VOL. | pH
| 2003 | FEED | FEED | FEED |  |  | FILT. | FILT. | FILT.
| 1 | 1.53 | 21.6 | 78.4 | 6.7 |  | 0.2 | 50 | 50 | 7.19
| 2 | 1.6 | 21.9 | 78.1 | 6.41 |  | 0.24 | 45.8 | 54.2 | 7.02
| 3 | 1.34 | 23.1 | 76.9 | 6.98 |  | 0.24 | 45.8 | 54.2 | 7.3
| 4 | 1.48 | 22.3 | 77.7 | 6.56 |  | 0.33 | 39.4 | 60.6 | 7.04
| 5 | 1.47 | 21.08 | 78.92 | 6.68 |  | 0.24 | 50 | 50 | 7.11
6
7
| 8 | 1.25 | 21.6 | 78.4 | 6.69 |  | 0.24 | 45.8 | 54.2 | 7.19
| 9 | 1.56 | 19.2 | 80.8 | 6.5 |  | 0.27 | 37 | 63 | 6.85
| 10 | 1.41 | 23.4 | 76.6 | 6.99 |  | 0.19 | 68.4 | 31.6 | 7.33
| 11 | 1.3 | 20.8 | 79.2 | 6.71 |  | 0.19 | 57.9 | 42.1 | 7.18
| 12 | 1.43 | 23.8 | 76.2 | 6.64 |  | 0.23 | 65.2 | 34.8 | 7.18
13
14
| 15 | 1.03 | 24.3 | 75.7 | 6.72 |  | 0.23 | 52.2 | 47.8 | 7.2
| 16 | 1.12 | 24.1 | 75.9 | 6.74 |  | 0.23 | 47.8 | 52.2 | 7.21
| 17 | 1.3 | 22.3 | 77.7 | 6.5 |  | 0.22 | 54.5 | 45.5 | 6.9
| 18 | 1.1 | 23.6 | 76.4 | 6.68 |  | 0.23 | 56.5 | 43.5 | 7.6
| 19 | 1.31 | 21.4 | 78.6 | 6.74 |  | 0.27 | 48.1 | 51.9 | 7.19
20
21
22
| 23 | 1.32 | 21.2 | 78.8 | 6.78 |  | 0.2 | 55 | 45 | 7.49
| 24 | 1.43 | 21.7 | 78.3 | 6.52 |  | 0.19 | 68.4 | 31.6 | 6.94
| 25 | 1.26 | 22.2 | 77.8 | 6.6 |  | 0.2 | 60 | 40 | 7
| 26 | 1.22 | 23 | 77 | 6.78 |  | 0.23 | 65.2 | 34.8 | 7.19
27
28
| 29 | 0.99 | 23.2 | 76.8 | 6.8 |  | 0.18 | 61.1 | 38.9 | 7.21
| 30 | 1.6 | 20 | 80 | 6.8 |  | 0.28 | 57.1 | 42.9 | 7.39
| TOTAL | 28.05 | 465.78 | 1634.22 | 140.52 |  | 4.83 | 1131.2 | 968.8 | 150.71
| AVERAGE | 1.3357 | 22.18 | 77.82 | 6.6914 |  | 0.23 | 53.8667 | 46.1333 | 7.1767
PAGE 10
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
SLUDGE VOLUME REMOVED
RUN DATE
2026-07-30
|  | JUNE | TRAILERS | TONS | DRY TONS | % LIME | % TOT. | % FIX. | % VOL.
|  | 2003 | REMOVED | SLUDGE | REMOVED | CAKE | CAKE | CAKE | CAKE
|  | 1 | 2 | 50 |  |  | 18.35 | 19.2 | 80.8
|  | 2 | 5 | 125 | 34.4275 |  | 18.66 | 17.6 | 82.4
|  | 3 | 6 | 150 | 35.3708 |  | 18.55 | 19.6 | 80.4
|  | 4 | 6 | 150 | 39.6834 |  | 17.44 | 18.2 | 81.8
|  | 5 | 6 | 150 | 38.0054 |  | 18.44 | 16.26 | 83.74
|  | 6 | 4 | 100
|  | 7 | 0 | 0
|  | 8 | 1 | 25 | 14.2822 |  | 17.02 | 18.6 | 81.4
|  | 9 | 5 | 125 | 46.6423 |  | 17.55 | 15.7 | 84.3
|  | 10 | 4 | 100 | 34.5726 |  | 17.52 | 17.6 | 82.4
|  | 11 | 6 | 150 | 40.0612 |  | 17.98 | 16.2 | 83.8
|  | 12 | 5 | 125 | 32.6778 |  | 17.84 | 18.9 | 81.1
|  | 13 | 5 | 125
|  | 14 | 0 | 0
|  | 15 | 1 | 25 | 25.7706 |  | 17.04 | 15.5 | 84.5
|  | 16 | 6 | 150 | 21.2036 |  | 16.64 | 14.9 | 85.1
|  | 17 | 6 | 150 | 22.6598 |  | 16.96 | 18.2 | 81.8
|  | 18 | 6 | 150 | 29.4485 |  | 17.51 | 14.8 | 85.2
|  | 19 | 6 | 150 | 32.6123 |  | 16.94 | 15.8 | 84.2
|  | 20 | 4 | 100
|  | 21 | 0 | 0
|  | 22 | 0 | 0
|  | 23 | 2 | 50 | 25.8707 |  | 17.59 | 18.8 | 81.2
|  | 24 | 6 | 150 | 42.8151 |  | 17.63 | 19.2 | 80.8
|  | 25 | 6 | 150 | 36.4116 |  | 17.62 | 16.4 | 83.6
|  | 26 | 5 | 125 | 32.712 |  | 17.87 | 14.3 | 85.7
|  | 27 | 4 | 100
|  | 28 | 0 | 0
|  | 29 | 1 | 25 | 22.5405 |  | 17.21 | 14.2 | 85.8
|  | 30 | 5 | 125 | 0 |  | 16.37 | 15.1 | 84.9
|  | TOTAL | 113 | 2825 | 607.7679 | 0 | 368.73 | 355.06 | 1744.94
|  | AVERAGE | 3.7667 | 94.1667 | 30.3884 | #DIV/0! | 17.5586 | 16.9076 | 83.0924
PAGE 11
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
CHEMICAL USEAGE
RUN DATE
2026-07-30
| JUNE | H2O2 | CL2 | POLYMER | POLYMER | LIME | GOX | O2 % | LOX | FPL
| 2003 | POUNDS | POUNDS | GALLONS | POUNDS | DELV. | TONS | PURITY | TONS | KW
| 1 | 549 | 1940 | 0 | 0 | 0 | 33 | 99% | 121 | 32305
| 2 | 0 | 1480 | 129 | 1075.86 | 0 | 40 | 100% | 121 | 33124
| 3 | 1886 | 1500 | 57 | 475.38 | 0 | 40 | 99% | 122 | 32951
| 4 | 2265 | 1440 | 67 | 558.78 | 0 | 37 | 99% | 121 | 32070
| 5 | 2295 | 1440 | 99 | 825.66 | 0 | 35 | 100% | 120 | 32926
| 6 | 1856 | 1180 | 41 | 341.94 | 0 | 37.2 | 99.7% | 120 | 28710
| 7 | 1047 | 1360 | 0 | 0 | 0 | 35 | 99% | 120 | 29892
| 8 | 130 | 1160 | 43 | 358.62 | 0 | 35 | 100% | 121 | 28293
| 9 | 1567 | 1140 | 38 | 316.92 | 0 | 39.9 | 99.5% | 121 | 32239
| 10 | 1547 | 1140 | 81 | 675.54 | 0 | 40 | 100% | 123 | 32867
| 11 | 1408 | 1100 | 48 | 400.32 | 0 | 40 | 99% | 122 | 32760
| 12 | 1517 | 1120 | 38 | 316.92 | 0 | 40 | 99% | 121 | 29969
| 13 | 1367 | 1120 | 47 | 391.98 | 0 | 37.5 | 99.5% | 122 | 28887
| 14 | 1357 | 1160 | 21 | 175.14 | 0 | 34.6 | 100% | 122 | 26304
| 15 | 1208 | 1040 | 11 | 91.74 | 0 | 36 | 99% | 123 | 30070
| 16 | 958 | 1320 | 30 | 250.2 | 0 | 36 | 99% | 124 | 29376
| 17 | 1178 | 1280 | 68 | 567.12 | 0 | 31 | 100% | 124 | 30017
| 18 | 659 | 1200 | 74 | 617.16 | 0 | 28 | 100% | 124 | 28898
| 19 | 1716 | 1200 | 50 | 417 | 0 | 32 | 100% | 124 | 33688
| 20 | 1507 | 1100 | 0 | 0 | 0 | 32 | 99% | 124 | 37490
| 21 | 1467 | 1200 | 0 | 0 | 0 | 26 | 100% | 125 | 34471
| 22 | 1078 | 560 | 0 | 0 | 0 | 28.6 | 99.9% | 125 | 33646
| 23 | 1087 | 1420 | 21 | 175.14 | 0 | 30 | 100% | 126 | 34432
| 24 | 1208 | 1060 | 81 | 675.54 | 0 | 30 | 100% | 127 | 31717
| 25 | 1618 | 1140 | 66 | 550.44 | 0 | 39 | 99% | 127 | 31096
| 26 | 1228 | 880 | 36 | 300.24 | 0 | 37 | 99% | 127 | ER
| 27 | 1218 | 1100 | 3 | 25.02 | 0 | 29 | 87.7% | 112 | 29594
| 28 | 1187 | 1080 | 4 | 33.36 | 0 | 32.3 | 99.8% | 127 | 26305
| 29 | 1228 | 1100 | 34 | 283.56 | 0 | 32 | 100% | 128 | 28506
| 30 | 1228 | 820 | 0 | 0 | 0 | 37 | 99% | 128 | 12966
| TOTAL | 38564 | 35780 | 1187 | 9899.58 | 0 | 1040.1 |  | 3692 | 885569
| AVERAGE | 1285.4667 | 1192.6667 | 39.5667 | 329.986 | 0 | 34.67 | 99.14% | 123.0667 | 30536.8621
PAGE 12
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL ONE
|  | RUN DATE |  |  | PERMIT NUMBER UO-06-279401
|  | 2026-07-30 |  |  | 7/21/97 thru 7/21/02 |  |  | I.D. #:5006A11308
|  | JUNE | % INFL. | MAX | MIN | WELL 1 | MAX | MIN | AVG
|  | 2003 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 19.13% | 11.82 | 8.09 | 10.36 | ER | ER | ER
|  | 2 | 22.53% | 13.92 | 6.94 | 11.5 | ER | ER | ER
|  | 3 | 24.79% | 13.94 | 8.79 | 12 | ER | ER | ER
|  | 4 | 24.79% | 13.92 | 7.59 | 11.48 | ER | ER | ER
|  | 5 | 24.83% | 13.8 | 7.36 | 11.04 | 59.14 | ER | 28.25
|  | 6 | 24.98% | 13.52 | 7.16 | 10.65 | 61.78 | 44.62 | 53.23
|  | 7 | 24.7% | 15.49 | 6.61 | 10.56 | 70.4 | 43.48 | 53.13
|  | 8 | 24.83% | 13.52 | 6.44 | 10.58 | 61.56 | 43.25 | 53.1
|  | 9 | 24.84% | 13.95 | 6.29 | 11.1 | 63.67 | 42.79 | 54.72
|  | 10 | 24.74% | 13.85 | 7.89 | 11.34 | 62.5 | 46.37 | 55.26
|  | 11 | 24.8% | 13.81 | 7.12 | 10.8 | 62.64 | 44.55 | 53.81
|  | 12 | 21.42% | 16.01 | 0.01 | 8.97 | 70.3 | 36.72 | 50.49
|  | 13 | 25.09% | 13.11 | 6.15 | 10.13 | 60.18 | 42.21 | 51.82
|  | 14 | 24.84% | 12.87 | 5.83 | 9.64 | 58.99 | 42.05 | 50.67
|  | 15 | 24.56% | 12.4 | 5.21 | 9.36 | 58.65 | 40.38 | 49.92
|  | 16 | 24.85% | 14.22 | 5.66 | 9.45 | 63.88 | 41.44 | 50.12
|  | 17 | 24.97% | 12.59 | 5.67 | 9.33 | 62.42 | 41.16 | 49.78
|  | 18 | 24.89% | 11.9 | 5.51 | 9.17 | 56.5 | 41.48 | 49.35
|  | 19 | 25.33% | 16.88 | 5.84 | 10.3 | 74.6 | 41.64 | 52.76
|  | 20 | 25.08% | 16.84 | 8.44 | 12.26 | 74.4 | 47.57 | 58.21
|  | 21 | 24.8% | 15.11 | 7.69 | 11.79 | 67.17 | 45.76 | 56.91
|  | 22 | 24.56% | 13.07 | 7.8 | 10.53 | 61.4 | 45.95 | 53.38
|  | 23 | 25% | 13.08 | 7.12 | 10.57 | 61.4 | 44.77 | 53.33
|  | 24 | 24.93% | 13.73 | 6.64 | 10.25 | 65.19 | 43.66 | 52.21
|  | 25 | 24.86% | 12.55 | 6.16 | 9.87 | 58.5 | 42.87 | 51.33
|  | 26 | 24.95% | 14.17 | 5.87 | 9.46 | 66.93 | 41.98 | 50.13
|  | 27 | 25.31% | 13.25 | 5.58 | 9.9 | 61.02 | 41.46 | 51.14
|  | 28 | 24.8% | 13.24 | 6.56 | 9.61 | 63.66 | 42.96 | 50.34
|  | 29 | 24.6% | 12.35 | 5.47 | 9.02 | 60.68 | 40.92 | 48.88
|  | 30 | 24.85% | 14.48 | 3.98 | 9 | 66.91 | 40.3 | 49.17
|  | TOTAL | 734.6% | 413.39 | 191.47 | 310.02 | 1654.47 | 1070.34 | 1331.44
|  | AVERAGE | 24.49% | 13.7797 | 6.3823 | 10.334 | 63.6335 | 42.8136 | 51.2092
|  | MAXIMUM | 25.33% | 16.88 | 8.79 | 12.26 | 74.6 | 47.57 | 58.21
|  | MINIMUM | 19.13% | 11.82 | 0.01 | 8.97 | 56.5 | 36.72 | 28.25
PAGE 13
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL TWO
|  | RUN DATE |  |  | PERMIT NUMBER UO-06-279508
|  | 2026-07-30 |  |  | 7/21/97 thru 7/21/02 |  |  | I.D. #:5006A11309
|  | JUNE | % INFL. | MAX | MIN | WELL 2 | MAX | MIN | AVG
|  | 2003 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 19.15% | 11.74 | 8.11 | 10.37 | 55.08 | 46.1 | 51.37
|  | 2 | 22.37% | 13.72 | 6.77 | 11.42 | 61.55 | 43.77 | 54.72
|  | 3 | 24.62% | 13.75 | 8.73 | 11.92 | 61.41 | 47.56 | 55.93
|  | 4 | 24.6% | 13.79 | 7.47 | 11.39 | 61.44 | 44.81 | 54.43
|  | 5 | 24.79% | 13.78 | 7.35 | 11.02 | 61.51 | 44.25 | 53.42
|  | 6 | 24.89% | 13.53 | 7.24 | 10.61 | 60.68 | 43.81 | 52.27
|  | 7 | 24.63% | 15.43 | 6.46 | 10.53 | 69.05 | 42.66 | 52.16
|  | 8 | 24.78% | 13.38 | 6.26 | 10.56 | 60.47 | 42.46 | 52.15
|  | 9 | 24.79% | 13.92 | 6.18 | 11.08 | 62.46 | 42.02 | 53.73
|  | 10 | 24.72% | 13.77 | 7.88 | 11.33 | 61.37 | 45.51 | 54.27
|  | 11 | 24.75% | 13.73 | 7.14 | 10.78 | 61.52 | 43.76 | 52.84
|  | 12 | 26.19% | 16.27 | 3.86 | 10.97 | 69.97 | 43.06 | 53.5
|  | 13 | 24.97% | 13.02 | 6.02 | 10.08 | 59.11 | 41.43 | 50.88
|  | 14 | 24.69% | 12.78 | 5.57 | 9.58 | 55.58 | 41.27 | 49.74
|  | 15 | 24.4% | 12.34 | 5 | 9.3 | 57.6 | 39.63 | 49
|  | 16 | 24.7% | 14.06 | 5.39 | 9.39 | 62.73 | 40.71 | 49.23
|  | 17 | 24.8% | 12.42 | 5.49 | 9.27 | 61.27 | 40.41 | 48.89
|  | 18 | 24.81% | 11.86 | 5.29 | 9.14 | 55.49 | 40.75 | 48.46
|  | 19 | 25.16% | 16.73 | 5.61 | 10.23 | 73.2 | 40.89 | 51.79
|  | 20 | 24.96% | 16.62 | 8.35 | 12.2 | 73 | 46.69 | 57.16
|  | 21 | 24.65% | 14.92 | 7.74 | 11.72 | 65.99 | 44.94 | 55.9
|  | 22 | 24.46% | 12.99 | 7.78 | 10.49 | 60.29 | 45.1 | 52.41
|  | 23 | 9.767% | 12.99 | 0.05 | 4.13 | 60.25 | 43.91 | 52.34
|  | 24 |  | 12.03 | ER | ER | 60.3 | 37.48 | 51.03
|  | 25 | 25.27% | 12.86 | 6.07 | 10.03 | 57.45 | 42.06 | 50.4
|  | 26 | 25.4% | 14.35 | 5.77 | 9.63 | 65.65 | 41.22 | 49.22
|  | 27 | 25.77% | 13.47 | 5.49 | 10.08 | 59.92 | 40.7 | 50.22
|  | 28 | 25.29% | 13.46 | 6.63 | 9.8 | 62.49 | 42.19 | 49.45
|  | 29 | 24.95% | 12.57 | 5.29 | 9.15 | 59.59 | 40.2 | 48.01
|  | 30 | 25.15% | 14.82 | 4.06 | 9.11 | 65.7 | 39.59 | 48.3
|  | TOTAL | 699.5% | 411.1 | 179.05 | 295.31 | 1862.12 | 1278.94 | 1553.22
|  | AVERAGE | 24.12% | 13.7033 | 6.1741 | 10.1831 | 62.0707 | 42.6313 | 51.774
|  | MAXIMUM | 26.19% | 16.73 | 8.73 | 12.2 | 73.2 | 47.56 | 57.16
|  | MINIMUM | 9.767% | 11.74 | 0.05 | 4.13 | 55.08 | 37.48 | 48.01
PAGE 14
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL THREE
|  | RUN DATE |  |  | PERMIT NUMBER UO-06-279510
|  | 2026-07-30 |  |  | 7/21/97 thru 7/21/02 |  |  | I.D. #:5006A11310
|  | JUNE | % INFL. | MAX | MIN | WELL 3 | MAX | MIN | AVG
|  | 2003 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 16.57% | 10.16 | 6.98 | 8.97 | 56.29 | 47.1 | 52.49
|  | 2 | 19.96% | 12.42 | 5.92 | 10.19 | 63.07 | 44.69 | 56.02
|  | 3 | 22.23% | 12.44 | 7.88 | 10.76 | 62.95 | 48.66 | 57.3
|  | 4 | 22.2% | 12.44 | 6.74 | 10.28 | 62.99 | 45.85 | 55.72
|  | 5 | 22.34% | 12.44 | 6.64 | 9.93 | 62.97 | 45.27 | 54.7
|  | 6 | 22.42% | 12.14 | 6.48 | 9.56 | 62.16 | 44.78 | 53.51
|  | 7 | 22.22% | 13.85 | 5.81 | 9.5 | 70.9 | 43.64 | 53.39
|  | 8 | 22.3% | 12.07 | 5.63 | 9.5 | 61.92 | 43.42 | 53.35
|  | 9 | 22.31% | 12.56 | 5.54 | 9.97 | 64.06 | 42.95 | 54.99
|  | 10 | 22.23% | 12.41 | 7.06 | 10.19 | 62.89 | 46.55 | 55.56
|  | 11 | 22.27% | 12.38 | 6.34 | 9.7 | 63.02 | 44.73 | 54.06
|  | 12 | 22.99% | 14.49 | ER | 9.63 | 71.7 | 37.36 | 54.31
|  | 13 | 22.57% | 11.79 | 5.43 | 9.11 | 60.55 | 42.35 | 52.1
|  | 14 | 22.24% | 11.53 | 5.05 | 8.63 | 59.33 | 42.19 | 50.89
|  | 15 | 21.91% | 11.14 | 4.41 | 8.35 | 58.99 | 40.5 | 50.12
|  | 16 | 22.17% | 12.73 | 4.84 | 8.43 | 64.28 | 41.59 | 50.34
|  | 17 | 22.24% | 11.24 | 4.89 | 8.31 | 62.77 | 41.3 | 49.99
|  | 18 | 22.21% | 10.71 | 4.71 | 8.18 | 56.78 | 41.64 | 49.58
|  | 19 | 22.65% | 15.16 | 5.01 | 9.21 | 75.2 | 41.79 | 53.02
|  | 20 | 22.54% | 15.03 | 7.48 | 11.02 | 75 | 47.77 | 58.56
|  | 21 | 22.28% | 13.53 | 6.84 | 10.59 | 67.59 | 45.93 | 57.25
|  | 22 | 22.02% | 11.7 | 6.96 | 9.44 | 61.8 | 46.14 | 53.66
|  | 23 | 22.4% | 11.69 | 6.29 | 9.47 | 61.75 | 44.93 | 53.6
|  | 24 | 22.35% | 12.31 | 5.85 | 9.19 | 65.45 | 43.82 | 52.44
|  | 25 | 22.32% | 11.36 | 5.43 | 8.86 | 58.82 | 42.99 | 51.53
|  | 26 | 22.34% | 12.71 | 5.11 | 8.47 | 67.31 | 42.11 | 50.36
|  | 27 | 22.65% | 11.81 | 4.87 | 8.86 | 61.36 | 41.6 | 51.37
|  | 28 | 22.2% | 11.8 | 5.74 | 8.6 | 64.01 | 43.11 | 50.57
|  | 29 | 21.92% | 11 | 4.6 | 8.04 | 61.01 | 41.07 | 49.08
|  | 30 | 22.12% | 13.01 | 3.41 | 8.01 | 67.3 | 40.44 | 49.37
|  | TOTAL | 661.1% | 370.05 | 167.94 | 278.95 | 1914.22 | 1306.27 | 1589.23
|  | AVERAGE | 22.04% | 12.335 | 5.791 | 9.2983 | 63.8073 | 43.5423 | 52.9743
|  | MAXIMUM | 22.99% | 15.16 | 7.88 | 11.02 | 75.2 | 48.66 | 58.56
|  | MINIMUM | 16.57% | 10.16 | 3.41 | 8.01 | 56.29 | 37.36 | 49.08
PAGE 15
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL FOUR
|  | RUN DATE |  |  | PERMIT NUMBER UC-06-264391 (IW-4)
2026-07-30
|  | JUNE | % INFL. | MAX | MIN | WELL 4 | MAX | MIN | AVG
|  | 2003 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 22.38% | 13.59 | 9.77 | 12.12 | ER | ER | ER
|  | 2 | 9.266% | 13.51 | 0.13 | 4.73 | ER | ER | ER
|  | 3 | 0.2685% | 0.15 | 0.13 | 0.13 | ER | ER | ER
|  | 4 | 0.3023% | 0.15 | 0.13 | 0.14 | ER | ER | ER
|  | 5 | 0.2924% | 0.15 | 0.13 | 0.13 | 37.52 | ER | 17.54
|  | 6 | 0.3284% | 0.15 | 0.13 | 0.14 | 37.54 | 36.45 | 37.09
|  | 7 | 0.304% | 0.14 | 0.12 | 0.13 | 37.88 | 36.34 | 36.99
|  | 8 | 0.3286% | 0.15 | 0.13 | 0.14 | 37.65 | 36.29 | 37.01
|  | 9 | 0.3133% | 0.16 | 0.13 | 0.14 | 37.71 | 36.43 | 37.14
|  | 10 | 0.3054% | 0.16 | 0.13 | 0.14 | 37.68 | 36.6 | 37.19
|  | 11 | 0.3214% | 0.15 | 0.13 | 0.14 | 37.62 | 36.55 | 37.13
|  | 12 | 0.3342% | 0.16 | 0.13 | 0.14 | 38.18 | 36.42 | 37.12
|  | 13 | 0.3468% | 0.16 | 0.13 | 0.14 | 37.6 | 36.32 | 37.04
|  | 14 | 0.3608% | 0.16 | 0.13 | 0.14 | 62.5 | 36.26 | 36.87
|  | 15 | 0.3674% | 0.15 | 0.13 | 0.14 | 37.29 | 36.01 | 36.75
|  | 16 | 0.3682% | 0.16 | 0.13 | 0.14 | 37.65 | 36 | 36.81
|  | 17 | 0.3746% | 0.16 | 0.14 | 0.14 | 37.39 | 36.03 | 36.8
|  | 18 | 0.3801% | 0.16 | 0.13 | 0.14 | 37.37 | 36.07 | 36.77
|  | 19 | 0.3443% | 0.16 | 0.13 | 0.14 | 38.35 | 36.06 | 36.99
|  | 20 | 0.2864% | 0.15 | 0.13 | 0.14 | 38.63 | 36.67 | 37.51
|  | 21 | 0.2945% | 0.16 | 0.13 | 0.14 | 38.3 | 36.66 | 37.58
|  | 22 | 0.3265% | 0.16 | 0.13 | 0.14 | 37.85 | 36.76 | 37.3
|  | 23 | 0.3074% | 0.14 | 0.13 | 0.13 | 37.71 | 36.66 | 37.25
|  | 24 |  | 0.15 | ER | ER | 37.76 | 36.51 | 37.14
|  | 25 |  | ER | ER | ER | 37.52 | 36.37 | 37.07
|  | 26 |  | ER | ER | ER | 37.98 | 36.29 | 36.98
|  | 27 |  | ER | ER | ER | 37.61 | 36.25 | 37.03
|  | 28 |  | ER | ER | ER | 37.78 | 36.42 | 36.96
|  | 29 |  | ER | ER | ER | 37.59 | 36.18 | 36.85
|  | 30 |  | ER | ER | ER | 38.14 | 36.11 | 36.9
|  | TOTAL | 38.5% | 30.49 | 12.63 | 19.75 | 1006.8 | 908.71 | 943.81
|  | AVERAGE | 1.674% | 1.2704 | 0.54913 | 0.8587 | 38.7231 | 36.3484 | 36.3004
|  | MAXIMUM | 22.38% | 13.59 | 9.77 | 12.12 | 62.5 | 36.76 | 37.58
|  | MINIMUM | 0.2685% | 0.14 | 0.12 | 0.13 | 37.29 | 36 | 17.54
PAGE 16
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL FIVE
|  | RUN DATE |  |  | PERMIT NUMBER UO-06-279512
|  | 2026-07-30 |  |  | 7/21/97 thru 7/21/02 |  |  | I.D. #:5006A11311
|  | JUNE | % INFL. | MAX | MIN | WELL 5 | MAX | MIN | AVG
|  | 2003 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 16.49% | 10.04 | 7.09 | 8.93 | 56.1 | 41.01 | 51.39
|  | 2 | 19.86% | 12.37 | 6.1 | 10.14 | 63.09 | 43.36 | 54.93
|  | 3 | 22.1% | 12.24 | 8.03 | 10.7 | 62.79 | 47.41 | 56.19
|  | 4 | 22.09% | 12.23 | 6.93 | 10.23 | 62.41 | 40.56 | 54.37
|  | 5 | 22.25% | 12.23 | 6.83 | 9.89 | 62.56 | 44.73 | 53.49
|  | 6 | 22.42% | 12 | 6.69 | 9.56 | 60.22 | 44 | 52.23
|  | 7 | 22.17% | 13.67 | 6.08 | 9.48 | 68.67 | 38.26 | 52.04
|  | 8 | 22.27% | 11.92 | 5.91 | 9.49 | 61.56 | 42.68 | 52.12
|  | 9 | 22.22% | 12.3 | 5.82 | 9.93 | 63.37 | 42.46 | 53.65
|  | 10 | 22.08% | 12.21 | 7.22 | 10.12 | 62.83 | 45.27 | 54.15
|  | 11 | 22.22% | 12.17 | 6.56 | 9.68 | 62.29 | 44.48 | 52.62
|  | 12 | 23.54% | 14.07 | 4.89 | 9.86 | 70.1 | 42.77 | 53.38
|  | 13 | 22.54% | 11.63 | 5.74 | 9.1 | 59.87 | 35.42 | 50.47
|  | 14 | 22.34% | 11.37 | 5.38 | 8.67 | 58.04 | 40.86 | 49.29
|  | 15 | 22.07% | 11.02 | 4.77 | 8.41 | 57.76 | 34.45 | 48.42
|  | 16 | 22.33% | 12.45 | 5.13 | 8.49 | 62.78 | 41.21 | 48.74
|  | 17 | 22.42% | 11.13 | 5.2 | 8.38 | 59.12 | 40.73 | 48.34
|  | 18 | 22.42% | 10.56 | 5.02 | 8.26 | 55.58 | 41.05 | 48.12
|  | 19 | 22.6% | 14.77 | 5.26 | 9.19 | 74.3 | 39.08 | 51.44
|  | 20 | 22.22% | 14.68 | 7.63 | 10.86 | 74.7 | 46.01 | 56.92
|  | 21 | 22% | 13.2 | 7.06 | 10.46 | 66.88 | 45.62 | 55.34
|  | 22 | 21.97% | 11.52 | 7.14 | 9.42 | 60.15 | 45.3 | 51.74
|  | 23 | 22.32% | 11.54 | 6.5 | 9.44 | 58.71 | 43.51 | 51.77
|  | 24 | 22.32% | 12.03 | 6.11 | 9.18 | 61.53 | 42.83 | 50.93
|  | 25 | 22.37% | 11.14 | 5.69 | 8.88 | 57.52 | 42.01 | 49.89
|  | 26 | 22.44% | 12.53 | 5.36 | 8.51 | 63.96 | 36.75 | 48.85
|  | 27 | 22.67% | 11.66 | 5.19 | 8.87 | 59.51 | 40.37 | 49.9
|  | 28 | 22.27% | 11.72 | 6.08 | 8.63 | 60.72 | 42.27 | 49.06
|  | 29 | 22.17% | 10.96 | 4.99 | 8.13 | 56.54 | 40.57 | 47.54
|  | 30 | 22.36% | 12.78 | 3.52 | 8.1 | 63.74 | 39.08 | 47.75
|  | TOTAL | 661.6% | 364.14 | 179.92 | 278.99 | 1867.4 | 1254.11 | 1545.07
|  | AVERAGE | 22.05% | 12.138 | 5.9973 | 9.2997 | 62.2467 | 41.8037 | 51.5023
|  | MAXIMUM | 23.54% | 14.77 | 8.03 | 10.86 | 74.7 | 47.41 | 56.92
|  | MINIMUM | 16.49% | 10.04 | 3.52 | 8.1 | 55.58 | 34.45 | 47.54
PAGE 17
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
INJECTION WELL SUMMARY
RUN DATE
2026-07-30
| JUNE | INFLUENT | EFFLUENT | EFFLUENT | IW-1 | IW-2 | IW-3 | IW-4 | IW-5 | TOTAL
| 2003 | FLOW | FLOW | SS | LBS SS | LBS SS | LBS SS | LBS SS | LBS SS | LBS SS
|  | MGD | MGD
| 1 | 54.147 | 50.564 | 10 | 864.024 | 864.858 | 748.098 | 1010.808 | 744.762 | 3221.742
| 2 | 51.048 | 47.969 | 9 | 863.19 | 857.1852 | 764.8614 | 355.0338 | 761.1084 | 3246.345
| 3 | 48.411 | 45.478 | 11 | 1100.88 | 1093.5408 | 987.1224 | 11.9262 | 981.618 | 4163.1612
| 4 | 46.308 | 43.496 | 10 | 957.432 | 949.926 | 857.352 | 11.676 | 853.182 | 3617.892
| 5 | 44.458 | 41.983 | 15 | 1381.104 | 1378.602 | 1242.243 | 16.263 | 1237.239 | 5239.188
| 6 | 42.631 | 40.591 | 18 | 1598.778 | 1592.7732 | 1435.1472 | 21.0168 | 1435.1472 | 6061.8456
| 7 | 42.761 | 40.183 | 16 | 1409.1264 | 1405.1232 | 1267.68 | 17.3472 | 1265.0112 | 5346.9408
| 8 | 42.609 | 40.283 | 12 | 1058.8464 | 1056.8448 | 950.76 | 14.0112 | 949.7592 | 4016.2104
| 9 | 44.692 | 42.84 | 10 | 925.74 | 924.072 | 831.498 | 11.676 | 828.162 | 3509.472
| 10 | 45.837 | 43.119 | 8 | 756.6048 | 755.9376 | 679.8768 | 9.3408 | 675.2064 | 2867.6256
| 11 | 43.556 | 41.082 | 8 | 720.576 | 719.2416 | 647.184 | 9.3408 | 645.8496 | 2732.8512
| 12 | 41.885 | 39.625 | 11 | 822.9078 | 1006.3878 | 883.4562 | 12.8436 | 904.5564 | 3617.3082
| 13 | 40.372 | 38.549 | 11 | 929.3262 | 924.7392 | 835.7514 | 12.8436 | 834.834 | 3524.6508
| 14 | 38.806 | 36.801 | 10 | 803.976 | 798.972 | 719.742 | 11.676 | 723.078 | 3045.768
| 15 | 38.11 | 35.598 | 10 | 780.624 | 775.62 | 696.39 | 11.676 | 701.394 | 2954.028
| 16 | 38.023 | 36.054 | 12 | 945.756 | 939.7512 | 843.6744 | 14.0112 | 849.6792 | 3578.8608
| 17 | 37.372 | 35.567 | 20 | 1556.244 | 1546.236 | 1386.108 | 23.352 | 1397.784 | 5886.372
| 18 | 36.836 | 35.119 | 15 | 1147.167 | 1143.414 | 1023.318 | 17.514 | 1033.326 | 4347.225
| 19 | 40.665 | 38.864 | 10 | 859.02 | 853.182 | 768.114 | 11.676 | 766.446 | 3246.762
| 20 | 48.883 | 46.26 | 10 | 1022.484 | 1017.48 | 919.068 | 11.676 | 905.724 | 3864.756
| 21 | 47.538 | 44.813 | 14 | 1376.6004 | 1368.4272 | 1236.4884 | 16.3464 | 1221.3096 | 5202.8256
| 22 | 42.878 | 40.102 | 10 | 878.202 | 874.866 | 787.296 | 11.676 | 785.628 | 3325.992
| 23 | 42.285 | 40.133 | 11 | 969.6918 | 378.8862 | 868.7778 | 11.9262 | 866.0256 | 3083.3814
| 24 | 41.12 | 38.649 | 11 | 940.335 |  | 843.0906 |  | 842.1732
| 25 | 39.699 | 37.709 | 12 | 987.7896 | 1003.8024 | 886.7088 |  | 888.7104 | 3767.0112
| 26 | 37.917 | 36.115 | 15 | 1183.446 | 1204.713 | 1059.597 |  | 1064.601 | 4512.357
| 27 | 39.118 | 37.67 | 14 | 1155.924 | 1176.9408 | 1034.4936 |  | 1035.6612 | 4403.0196
| 28 | 38.744 | 36.781 | 11 | 881.6214 | 899.052 | 788.964 |  | 791.7162 | 3361.3536
| 29 | 36.673 | 34.474 | 11 | 827.4948 | 839.421 | 737.5896 |  | 745.8462 | 3150.3516
| 30 | 36.218 | 34.37 | 12 | 900.72 | 911.7288 | 801.6408 |  | 810.648 | 3424.7376
| TOTAL | 1269.6 | 1200.841 | 357 | 30605.6316 | 29261.724 | 27532.0914 | 1655.6568 | 27546.186 | 112320.0342
| AVERAGE | 42.32 | 40.028 | 11.9 | 1020.1877 | 1009.025 | 917.7364 | 71.9851 | 918.2062 | 3873.1046
PAGE 18
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
| RUN DATE |  |  |  | SOLIDS REMOVAL INVENTORY DATA SHEET
2026-07-30
| JUNE | TONS | CAKE |  |  |  | JUNE | RAGS | GRIT | OTHER
| 2003 | SLUDGE | TSS |  |  |  | 2003 |  |  | (vac)
| 1st - 7th | [5 empty] | 1st - 7th
| 1 | 50 | 18.35 |  |  |  | 1
| 2 | 125 | 18.66 |  |  |  | 2 |  | 10
| 3 | 150 | 18.55 |  |  |  | 3
| 4 | 150 | 17.44 |  |  |  | 4
| 5 | 150 | 18.44 |  |  |  | 5 |  | 10
| 6 | 100 |  |  |  |  | 6 | 10
| 7 | 0 |  |  |  |  | 7
| TOTAL = | 725 | 18.288 | = AVG. |  |  | TOTAL = | 10 | 20 | 0
| 8th - 14th | [5 empty] | 8th - 14th
| 8 | 25 | 17.02 |  |  |  | 8
| 9 | 125 | 17.55 |  |  |  | 9
| 10 | 100 | 17.52 |  |  |  | 10
| 11 | 150 | 17.98 |  |  |  | 11
| 12 | 125 | 17.84 |  |  |  | 12
| 13 | 125 |  |  |  |  | 13 | 10
| 14 | 0 |  |  |  |  | 14
| TOTAL = | 650 | 17.582 | = AVG. |  |  | TOTAL = | 10 | 0 | 0
| 15th - 22nd | [5 empty] | 15th-22nd
| 15 | 25 | 17.04 |  |  |  | 15
| 16 | 150 | 16.64 |  |  |  | 16
| 17 | 150 | 16.96 |  |  |  | 17
| 18 | 150 | 17.51 |  |  |  | 18 |  |  | 4500
| 19 | 150 | 16.94 |  |  |  | 19 |  | 10
| 20 | 100 |  |  |  |  | 20 |  | 10
| 21 | 0 |  |  |  |  | 21
| 22 | 0 |  |  |  |  | 22
| TOTAL = | 725 | 17.018 | = AVG. |  |  | TOTAL = | 0 | 20 | 4500
| 23rd - 31st | [5 empty] | 23rd-31st
| 23 | 50 | 17.59 |  |  |  | 23
| 24 | 150 | 17.63 |  |  |  | 24
| 25 | 150 | 17.62 |  |  |  | 25
| 26 | 125 | 17.87 |  |  |  | 26
| 27 | 100 |  |  |  |  | 27 | 10
| 28 | 0 |  |  |  |  | 28
| 29 | 25 | 17.21 |  |  |  | 29
| 30 | 125 | 16.37 |  |  |  | 30
| TOTAL = | 725 | 17.3817 | = AVG. |  |  | TOTAL = | 10 | 0 | 0
RAGS & GRIT go to Central LandFill
Other(VAC) go to BCSR
PAGE 19

## INJECTION PAGES
|  |  |  | UNDERGROUND INJECTION CONTROL | [10 empty] | UNDERGROUND INJECTION CONTROL | [10 empty] | UNDERGROUND INJECTION CONTROL
[15 empty] | MONTHLY OPERATING REPORT | [10 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES |  |  |  |  | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES |  |  |  |  | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [10 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [10 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-1 | [7 empty] | Wet Well Description: |  |  | Effuent Wet Well for IW-1, IW-2, IW3, IW-4 and IW-5 | [7 empty] | Monitoring Well Decription: |  |  | UPPER ZONE OF MONITORING WELL MW-1
Permit #: |  | UO-06-279401 |  |  |  |  | Date of Issuance: |  | 1997-07-21 |  | Facility ID #: |  | 5006M02066 |  |  |  | Permit Number: |  |  | FLA041378 |  | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | UO-06-279512
[22 empty] | Monitoring Well ID #: |  |  | 5006A11311
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2002-07-21 | [7 empty] | Issue Date: |  |  | 1999-10-18 |  | As Identified in Permit: |  | Monitor Well MW-1 Upper Monitor Zone |  |  |  | Issue Date: |  |  | 1997-07-21
[22 empty] | Monitoring Well Interval: |  |  | 1288' to 1320'
Injection Well ID #: |  | 5006A11308 | [8 empty] | Wet Well ID #: |  | Well Facility U-001 |  |  |  | Expiration Date: |  |  | 2004-10-17 |  | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.3 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24 | Associated Injection Well(s):
Injection Interval: |  |  | 2799' to 3513' | [18 empty] | 500A11311 |  |  | INJECTION WELL IW-5
[11 empty] | Injection Well ID #: |  |  | Injection Well Description
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s): | [10 empty] | 5006A11308 |  |  | INJECTION WELL IW-1
[11 empty] | 5006A11309 |  |  | INJECTION WELL IW-2 | [7 empty] | REPORT MONTH / YEAR: |  | 2003-06-01 | DATE OF SAP / RECORDING: |  |  | 2003-06-03 | 2003-06-10 | 2003-06-17 | 2003-06-24
Monitoring Zone ID #: | [5 empty] | Description |  |  |  |  | 5006A11310 |  |  | INJECTION WELL IW-3
[11 empty] | N/A |  |  | INJECTION WELL IW-4 | [7 empty] | OPERATOR'S NAME: |  |  | BAYLER, J.
UO-06-279401 |  | UPPER ZONE OF MONITORING WELL MW-2 | [8 empty] | 5006A11311 |  |  | INJECTION WELL IW-5
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A
UO-06-279401 |  | LOWER ZONE OF MONITORING WELL MW-2
[11 empty] | THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [10 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [10 empty] | REPORT MONTH / YEAR: |  | 2003-06-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous |  |  | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2003-06-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous |  |  | OPERATOR'S NAME: |  |  | BAYLER, J.
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
OPERATOR'S NAME: |  |  | BAYLER, J. | [7 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A | [7 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4474-A | [7 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: |  |  |  | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 48.66 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 42.64 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: |  |  |  | PARAMETER |  |  |  | Sampling Frequency |  |  |  | VALUE |  | UNITS | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 47.6263 | PSIG
[11 empty] | Nitrogen, Total as N |  |  |  |  | Daily/Monthly Average |  |  | 13.8236 |  | mg/L as N | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[11 empty] | Nitrogen, Nitrate, Total as N |  |  |  |  | Daily/Monthly Average |  |  | 0.26267 |  | mg/L as N | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7531.5 | mg/l
Total monthly flow | [7 empty] | 310.02 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 3862.5 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [7 empty] | Nitrogen, Total Kjeildahl as N |  |  |  |  | Daily/Monthly Average |  |  | 13.561 |  | mg/L as N | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.83925 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 16.88 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.4775 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 74.6 |  | PSIG | pH |  |  |  |  | Daily/Monthly Average |  |  | 6.6733 |  | s.u. | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7.8575 | Std units
Monthly average of the daily flow rates | [7 empty] | 10.334 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 12037.5 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 14.7456 |  | MG | Phosphorus, Total as P |  |  |  |  | Daily/Monthly Average |  |  | 0.8209 |  | mg/L as P | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 2.509 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 73 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [10 empty] | Total Dissolved Solids (TDS) |  |  |  |  | Daily/Monthly Average |  |  | 1046.2 |  | mg/L | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.05 | mg/l
Monthly average pressure | [7 empty] | 51.2092 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 762.5 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 37 |  | PSIG | Residue, Total filterable (TSS dried at 180 C) |  |  |  |  | Daily/Monthly Average |  |  | 11.9 |  | mg/L | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 175 | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.6725 | mg/l
[11 empty] | Specific Conductance (Temperature Compensated) |  |  |  |  | Daily/Monthly Average |  |  | 2001.6667 |  | umhos/cm | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just | [6 empty] | Temperature, Water |  |  |  |  | Daily/Monthly Average |  |  | 84.7333 |  | deg C
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [9 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just |  |  | Date: |  |  |  |  | (Signature):
Date:
(Signature):
|  |  |  | UNDERGROUND INJECTION CONTROL | [21 empty] | UNDERGROUND INJECTION CONTROL
|  |  |  | MONTHLY OPERATING REPORT | [21 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES | [15 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [21 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-2 | [18 empty] | Monitoring Well Decription: |  |  | LOWER ZONE OF MONITORING WELL MW-1
Permit #: |  | UO-06-279508 |  |  |  |  | Date of Issuance: |  | 1997-07-21 | [12 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | UO-06-279512
[22 empty] | Monitoring Well ID #: |  |  | 5006A11311
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2002-07-21 | [12 empty] | As Identified in Permit: |  | Monitor Well MW-1 Lower Monitor Zone |  |  |  | Issue Date: |  |  | 1997-07-21
[22 empty] | Monitoring Well Interval: |  |  | 1449' to 1557'
Injection Well ID #: |  | 5006A11309 | [19 empty] | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.3 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24
Injection Interval: |  |  | 2798' to 3518' | [18 empty] | 500A11311 |  |  | INJECTION WELL IW-5
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s):
[22 empty] | REPORT MONTH / YEAR: |  | 2003-06-01 | DATE OF SAP / RECORDING: |  |  | 2003-06-03 | 2003-06-10 | 2003-06-17 | 2003-06-24
Monitoring Zone ID #: | [5 empty] | Description
[22 empty] | OPERATOR'S NAME: |  |  | BAYLER, J.
UO-06-279401 |  | UPPER ZONE OF MONITORING WELL MW-2
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A
UO-06-279401 |  | LOWER ZONE OF MONITORING WELL MW-2
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [21 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2003-06-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
OPERATOR'S NAME: |  |  | BAYLER, J. | [18 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4474-A | [18 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 41.52 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 25.76 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: | [14 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 35.7165 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 9478 | mg/l
Total monthly flow | [7 empty] | 295.31 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 5100 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [18 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 9.4725 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 16.73 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 11.5025 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 73.2 |  | PSIG | [11 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7.285 | Std units
Monthly average of the daily flow rates | [7 empty] | 10.1831 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 15507.5 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 14.524 |  | MG | [11 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 2.509 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 72.75 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [21 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.05 | mg/l
Monthly average pressure | [7 empty] | 51.774 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 750 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 37.4 |  | PSIG | [11 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 272.5 | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.0125 | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [21 empty] | (Signature):
Date:
|  |  |  | UNDERGROUND INJECTION CONTROL | [21 empty] | UNDERGROUND INJECTION CONTROL
|  |  |  | MONTHLY OPERATING REPORT | [21 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES | [15 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [21 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-3 | [18 empty] | Monitoring Well Decription: |  |  | UPPER ZONE OF MONITORING WELL MW-2
Permit #: |  | UO-06-279510 |  |  |  |  | Date of Issuance: |  | 1997-07-21 | [12 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | UC-06-279401 & 508
[22 empty] | Monitoring Well ID #: |  |  | 5006A11308 & 309
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2002-07-21 | [12 empty] | As Identified in Permit: |  | Monitor Well MW-2 Upper Monitor Zone |  |  |  | Issue Date: |  |  | 1997-07-21
[22 empty] | Monitoring Well Interval: |  |  | 1300' to 1344'
Injection Well ID #: |  | 5006A11310 | [19 empty] | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.3 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24
Injection Interval: |  |  | 2800' to 3977' | [18 empty] | 5006A11308 |  |  | INJECTION WELL IW-1
[22 empty] | 5006A11309 |  |  | INJECTION WELL IW-2
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s):
[22 empty] | REPORT MONTH / YEAR: |  | 2003-06-01 | DATE OF SAP / RECORDING: |  |  | 2003-06-03 | 2003-06-10 | 2003-06-17 | 2003-06-24
Monitoring Zone ID #: | [5 empty] | Description
[22 empty] | OPERATOR'S NAME: |  |  | BAYLER, J.
UO-06-279510 |  | UPPER ZONE OF MONITORING WELL MW-3
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A
UO-06-279510 |  | LOWER ZONE OF MONITORING WELL MW-3
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [21 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2003-06-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
OPERATOR'S NAME: |  |  | BAYLER, J. | [18 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4474-A | [18 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 30.9 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 0 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: | [14 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | #DIV/0! | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7293 | mg/l
Total monthly flow | [7 empty] | 278.95 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 3787.5 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [18 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.886 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 15.16 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.59 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 75.2 |  | PSIG | [11 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 8.0075 | Std units
Monthly average of the daily flow rates | [7 empty] | 9.2983 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 11807.5 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 13.2701 |  | MG | [11 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 2.509 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 71.25 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [21 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.05 | mg/l
Monthly average pressure | [7 empty] | 52.9743 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 787.5 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 37 |  | PSIG | [11 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 180 | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.735 | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [21 empty] | (Signature):
Date:
|  |  |  | UNDERGROUND INJECTION CONTROL | [21 empty] | UNDERGROUND INJECTION CONTROL
|  |  |  | MONTHLY OPERATING REPORT | [21 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES | [15 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [21 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-4 | [18 empty] | Monitoring Well Decription: |  |  | LOWER ZONE OF MONITORING WELL MW-2
Permit #: |  | UC-06-264391 |  |  |  |  | Date of Issuance: |  | N/A | [12 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | UC-06-279401 & 508
[22 empty] | Monitoring Well ID #: |  |  | 5006A11308 & 309
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2000-11-30 | [12 empty] | As Identified in Permit: |  | Monitor Well MW-2 Lower Monitor Zone |  |  |  | Issue Date: |  |  | 1997-07-21
[22 empty] | Monitoring Well Interval: |  |  | 1970' to 2025'
Injection Well ID #: |  | N/A | [19 empty] | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24
Injection Interval: |  |  | 2804' to 3977' | [18 empty] | 5006A11308 |  |  | INJECTION WELL IW-1
[22 empty] | 5006A11309 |  |  | INJECTION WELL IW-2
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s):
[22 empty] | REPORT MONTH / YEAR: |  | 2003-06-01 | DATE OF SAP / RECORDING: |  |  | 2003-06-03 | 2003-06-10 | 2003-06-17 | 2003-06-24
Monitoring Zone ID #: | [5 empty] | Description
[22 empty] | OPERATOR'S NAME: |  |  | BAYLER, J.
UO-06-279510 |  | UPPER ZONE OF MONITORING WELL MW-3
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A
UO-06-279510 |  | LOWER ZONE OF MONITORING WELL MW-3
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [21 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2003-06-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
OPERATOR'S NAME: |  |  | BAYLER, J. | [18 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4474-A | [18 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 42.33 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 29.4 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: | [14 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 40.2259 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 32015 | mg/l
Total monthly flow | [7 empty] | 19.75 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 18050 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [18 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.3225 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 13.59 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.975 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 62.5 |  | PSIG | [11 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7.315 | Std units
Monthly average of the daily flow rates | [7 empty] | 0.8587 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 47100 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 1.0081 |  | MG | [11 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 2.509 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 70.5 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [21 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.06525 | mg/l
Monthly average pressure | [7 empty] | 36.3004 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 2450 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 37.5 |  | PSIG | [11 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 837.5 | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.0425 | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [21 empty] | (Signature):
Date:
|  |  |  | UNDERGROUND INJECTION CONTROL | [21 empty] | UNDERGROUND INJECTION CONTROL
|  |  |  | MONTHLY OPERATING REPORT | [21 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES | [15 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [21 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-5 | [18 empty] | Monitoring Well Decription: |  |  | UPPER ZONE OF MONITORING WELL MW-3
Permit #: |  | UO-06-279512 |  |  |  |  | Date of Issuance: |  | 1997-07-21 | [12 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | UO-06-279510
[22 empty] | Monitoring Well ID #: |  |  | 5006A11310
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2002-07-21 | [12 empty] | As Identified in Permit: |  | Monitor Well MW-3 Upper Monitor Zone |  |  |  | Issue Date: |  |  | 1997-07-21
[22 empty] | Monitoring Well Interval: |  |  | 1300' to 1349'
Injection Well ID #: |  | 5006A11311 | [19 empty] | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.3 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24
Injection Interval: |  |  | 2818' to 3462' | [18 empty] | 5006A11310 |  |  | INJECTION WELL IW-3
[22 empty] | N/A |  |  | INJECTION WELL IW-4
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s):
[22 empty] | REPORT MONTH / YEAR: |  | 2003-06-01 | DATE OF SAP / RECORDING: |  |  | 2003-06-03 | 2003-06-10 | 2003-06-17 | 2003-06-24
Monitoring Zone ID #: | [5 empty] | Description
[22 empty] | OPERATOR'S NAME: |  |  | BAYLER, J.
UO-06-279512 |  | UPPER ZONE OF MONITORING WELL MW-1
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A
UO-06-279512 |  | LOWER ZONE OF MONITORING WELL MW-1
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [21 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2003-06-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
OPERATOR'S NAME: |  |  | BAYLER, J. | [18 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4474-A | [18 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 32.1 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 17.66 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: | [14 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 29.67 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7442 | mg/l
Total monthly flow | [7 empty] | 278.99 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 3850 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [18 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.97 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 14.77 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.485 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 74.7 |  | PSIG | [11 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 8.1675 | Std units
Monthly average of the daily flow rates | [7 empty] | 9.2997 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 11965 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 13.2793 |  | MG | [11 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 2.509 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 71.75 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [21 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.05 | mg/l
Monthly average pressure | [7 empty] | 51.5023 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 787.5 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 36.6 |  | PSIG | [11 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 182.5 | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.3575 | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [21 empty] | (Signature):
Date:
UNDERGROUND INJECTION CONTROL
MONTHLY OPERATING REPORT
[22 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
[22 empty] | Monitoring Well Decription: |  |  | LOWER ZONE OF MONITORING WELL MW-3
[22 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | UO-06-279510
[22 empty] | Monitoring Well ID #: |  |  | 5006A11310
[22 empty] | As Identified in Permit: |  | Monitor Well MW-3 Lower Monitor Zone |  |  |  | Issue Date: |  |  | 1997-07-21
[22 empty] | Monitoring Well Interval: |  |  | 1970 to 2027'
Associated Injection Well(s):
[22 empty] | Injection Well ID #: |  |  | Injection Well Description
[22 empty] | 5006A11310 |  |  | INJECTION WELL IW-3
[22 empty] | N/A |  |  | INJECTION WELL IW-4
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
[22 empty] | REPORT MONTH / YEAR: |  | 2003-06-01 | DATE OF SAP / RECORDING: |  |  | 2003-06-03 | 2003-06-10 | 2003-06-17 | 2003-06-24
[22 empty] | OPERATOR'S NAME: |  |  | BAYLER, J.
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
[22 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
[22 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
[22 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 45.45 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 34.78 | PSIG
[22 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 43.781 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
[22 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 28793 | mg/l
[22 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 16600 | mg/l
[22 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 2.3825 | mg/l
[22 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 3.2125 | mg/l
[22 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7.4125 | Std units
[22 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 43300 | umho/cm
[22 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
[22 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 70.25 | deg. F
[22 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.05 | mg/l
[22 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 2125 | mg/l
[22 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 822.5 | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.0275 | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
Date:

## DEP FORMS
Department of Environmental Protection Discharge Monitoring Report - Part A
When Completed mail this report to: Department of Environmental Protection, Wastewater Facilities Management Section, MS 3551, 2600 Blair Stone Road, Tallahassee, FL 32399-2400
PERMITEE NAME: | City of Fort Lauderdale |  |  |  |  | PERMIT NUMBER: |  | FLA041378 |  | REPORT: | Monthly
MAILING ADDRESS: | 949 NW 38th Street |  |  |  |  | LIMIT: |  | Final |  | GROUP: | Domestic
| Fort Lauderdale, FL 33309 |  |  |  |  | CLASS SIZE: |  | N/A |  | GMS TEST SITE
[6 empty] | GMS ID NO. |  | 5006M02066 |  | NO:
FACILITY: | City of Fort Lauderdale G. T. Lohmeyer WWTF |  |  |  |  | MONITORING GROUP NUMBER: |  | U-001
LOCATION: | 1765 SE 18th Street |  |  |  |  | PLANT SIZE/TREATMENT TYPE: |  | IIA
Fort Lauderdale, FL 33316
COUNTY: | Broward | [5 empty] | MONITORING PERIOD: |  |  | 2003-06-01
Parameter |  | Quantity of Loading |  | Units |  | Quality or Concentration |  | Units | No. Ex. | Frequency of Analysis | Sample Type
Flow | Sample Measurement | 14.7456 | 10.334 | [5 empty] | 0
PARM Code 50050 1 Mon.Site No. EFF-002 | Permit Requirement | 18.3 (Peak Hour.) | Report (Mo. Avg.) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
Flow | Sample Measurement | 14.524 | 10.1831 | [5 empty] | 0
PARM Code 50050 1 Mon.Site No. EFF-003 | Permit Requirement | 18.3 (Peak Hour.) | Report (Mo. Avg.) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
Flow | Sample Measurement | 13.2701 | 9.2983 | [5 empty] | 0
PARM Code 50050 1 Mon.Site No. EFF-004 | Permit Requirement | 18.3 (Peak Hour.) | Report (Mo. Avg.) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
Flow | Sample Measurement | 1.0081 | 0.8587 | [5 empty] | 0
PARM Code 50050 1 Mon.Site No. EFF-005 | Permit Requirement | 18.0 (Peak Hour.) | Report (Mo. Avg.) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
Flow | Sample Measurement | 13.2793 | 9.2997 | [5 empty] | 0
PARM Code 50050 1 Mon.Site No. EFF-006 | Permit Requirement | 18.3 (Peak Hour.) | Report (Mo. Avg.) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
I certify under penalty of law that I have personally examined and am familiar with the informantion submitted herein; and based on my inquiry of those individuals immeadiately responsible for obtaining the information, I believe the submitted
information is true, accurate and complete. I am aware that there are significant penalties for submitting false information including the possiblity of fine and imprisonment.
NAME/TITLE OF PRINCIPAL EXECUTIVE OFFICER OR AUTHORIZED AGENT |  |  |  | SIGNATURE OF PRINCIPAL EXECUTIVE OFFICER OR AUTHORIZED AGENT |  |  |  |  | TELEPHONE |  | DATE (YY/MM/DD)
954-523-1002 ext 2021
REGIONAL WASTEWATER FACILITIES MANAGER
COMMENTS AND EXPLANATION OF ANY VIOLATIONS (Reference all attachments here):
Version 8/13/99
Department of Environmental Protection Discharge Monitoring Report - Part A (Continued)
[12 empty] | PERMITEE NAME: | City of Fort Lauderdale G. T. Lohmeyer WWTF |  |  |  | PERMIT NUMBER: |  | FLA041378 | MONITORING GROUP NUMBER: U-001 |  |  | REPORT: | Monthly
[20 empty] | MONITORING PERIOD: |  |  |  | 2003-06-01
[12 empty] | Parameter |  |  | Quantity of Loading |  | Units |  | Quality or Concentration |  | Units | No. Ex. | Frequency of Analysis | Sample Type
[12 empty] | BOD, Carbonaceous 5 day, 20C |  | Sample Measurement |  |  |  | 4.3 |  |  |  | 0
[12 empty] | PARM Code 80082 Y Mon.Site No. EFF-001 |  | Permit Requirement |  |  |  | 20.0 (An.Avg.) |  |  | mg/l |  | Daily | 24-hour FPC
[12 empty] | BOD, Carbonaceous 5 day, 20C |  | Sample Measurement |  |  |  | 4.0547 | 4.1426 | 7.24 |  | 0
[12 empty] | PARM Code 80082 1 Mon.Site No. EFF-001 |  | Permit Requirement |  |  |  | 30.0 (Mo.Avg.) | 45.0 (Week.Avg.) | 60.0 (Max.) | mg/l |  | Daily | 24-hour FPC
[12 empty] | Solids, Total Suspended |  | Sample Measurement |  |  |  | 12.8 |  |  |  | 0
[12 empty] | PARM Code 00530 Y Mon.Site No. EFF-001 |  | Permit Requirement |  |  |  | 20.0 (An.Avg.) |  |  | mg/l |  | Daily | 24-hour FPC
[12 empty] | Solids, Total Suspended |  | Sample Measurement |  |  |  | 11.9 | 12.0257 | 20 |  | 0
[12 empty] | PARM Code 00530 1 Mon.Site No. EFF-001 |  | Permit Requirement |  |  |  | 30.0 (Mo.Avg.) | 45.0 (Week.Avg.) | 60.0 (Max.) | mg/l |  | Daily | 24-hour FPC
[12 empty] | pH |  | Sample Measurement |  |  |  | 6.5 |  |  |  | 0
[12 empty] | PARM Code 00400 1 Mon.Site No. EFF-001 |  | Permit Requirement |  |  |  | 6.0 (Min.) |  |  | s.u. |  | Continuous | Meter
[12 empty] | Flow |  | Sample Measurement | 39.3977 | 42.32 | [5 empty] | 0
[12 empty] | PARM Code 50050 G Mon.Site No. INF-001 |  | Permit Requirement | 43.0 (3-Mo.Avg.) | Report (Mo.Avg.) | mgd | [5 empty] | Continuous | Flow meters with 24-hour recording chart
[12 empty] | BOD, Carbonaceous 5 day, 20C |  | Sample Measurement |  |  |  | 61.9467 |  |  |  | N/A
[12 empty] | PARM Code 80082 G Mon.Site No. INF-002 |  | Permit Requirement |  |  |  | Report (Mo.Avg.) |  |  | mg/l |  | Daily | 24-hour FPC
[12 empty] | Solids, Total Suspended |  | Sample Measurement |  |  |  | 87.8667 |  |  |  | N/A
[12 empty] | PARM Code 00530 G Mon.Site No. INF-002 |  | Permit Requirement |  |  |  | Report (Mo.Avg.) |  |  | mg/l |  | Daily | 24-hour FPC
Version 8/13/99

## JULIAN CONVERT
2003-06-01 | 37773 | 1999-01-01 | 1612
FROM DATE ON "DATA INPUT" PAGE | [5 empty] | 2003-06-01
1999
MONTHYY.PAR RANGE TO COMPILE (JULIAN DAY VALUES) FOR SPLIT PROGRAM ARE | [7 empty] | 152 | THROUGH | 1643
|  | 6 | JUNE
[5 empty] | 2003-06-01 | 2003-06-01 | 6
2003-06-01 |  |  |  |  | 1 | JANUARY |  | 1995 | 1995-01-01
[5 empty] | 2 | FEBRUARY |  | 1996 | 1996-01-01
[5 empty] | 3 | MARCH |  | 1997 | 1997-01-01
JUNE |  | 0 |  | 0 | 4 | APRIL |  | 1998 | 1998-01-01
|  | 1 |  | 2 | 5 | MAY |  | 1999 | 1999-01-01
|  | 0 |  |  | 6 | JUNE |  | 2000 | 2000-01-01
|  | 0 |  |  | 7 | JULY |  | 2001 | 2001-01-01
|  | 0 |  | 0 | 8 | AUGUST |  | 2002 | 2002-01-01
|  |  |  | 2 | 9 | SEPTEMBER |  | 2003 | 2003-01-01
[5 empty] | 10 | OCTOBER |  | 2004 | 2004-01-01
[5 empty] | 11 | NOVEMBER |  | 2005 | 2005-01-01
2003 |  |  |  |  | 12 | DECEMBER |  | 2006 | 2006-01-01
37773 | [6 empty] | JUNE | 2007 | 2007-01-01
37622 | [7 empty] | 2008 | 2008-01-01
151 | 1 |  | 1 | 152 | Sunday
| 2 |  | 2 | 153 | Monday
| 3 |  | 3 | 154 | Tuesday
| 4 |  | 4 | 155 | Wednesday
| 5 |  | 5 | 156 | Thursday
| 6 |  | 6 | 157 | Friday
| 7 |  | 7 | 158 | Saturday
| 8 |  | 8 | 159 | Sunday
| 9 |  | 9 | 160 | Monday
| 10 |  | 10 | 161 | Tuesday
| 11 |  | 11 | 162 | Wednesday
| 12 |  | 12 | 163 | Thursday
| 13 |  | 13 | 164 | Friday
| 14 |  | 14 | 165 | Saturday
| 15 |  | 15 | 166 | Sunday
| 16 |  | 16 | 167 | Monday
| 17 |  | 17 | 168 | Tuesday
| 18 |  | 18 | 169 | Wednesday
| 19 |  | 19 | 170 | Thursday
| 20 |  | 20 | 171 | Friday
| 21 |  | 21 | 172 | Saturday
| 22 |  | 22 | 173 | Sunday
| 23 |  | 23 | 174 | Monday
| 24 |  | 24 | 175 | Tuesday
| 25 |  | 25 | 176 | Wednesday
| 26 |  | 26 | 177 | Thursday
| 27 |  | 27 | 178 | Friday
| 28 |  | 28 | 179 | Saturday
| 29 |  | 29 | 180 | Sunday
| 30 |  | 30 | 181 | Monday
30