## DATA INPUT
ENTER THE AVERAGE MONTHLY INFLUENT FLOW
INTO THE CORROSPONDING BOXES BELOW:
FEBRUARY | 34.03 | JANUARY | 33.434
ENTER THE PRESENT MONTH AND YEAR IN BOX BELOW (A5) | [5 empty] | MARCH
2005-03-01 | [5 empty] | 2005
IW-1 | IW-2 | IW-3 | IW-4 | IW-5
36.04 | 36.2 | 37.3 | 36.8 | 35.3 | 2005-03-22
|  | ENTER INJECTION WELL SHUT-IN PRESSURE ABOVE |  |  | ENTER DATE OF SHUT-IN READINGS
ENTER SLUDGE DISPOSAL SITE FOR EACH WEEK BELOW
| WEEK 1 | WEEK 2 | WEEK 3 | WEEK 4
1 st | Allied Waste Landfill | Allied Waste Landfill | Allied Waste Landfill | Allied Waste Landfill
2 nd | Taylor County, GA | Taylor County, GA | Taylor County, GA | Taylor County, GA
RAW DATA REPORT ENTRY CATEGORIES
GTL PLANT DAILY PROCESS SUMMARY
[6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TOTAL RAW INFLUENT FLOW (MGD) | [5 empty] | 31.911 | 31.788 | 31.874 | 34.807 | 33.806 | 32.732 | 32.855 | 32.744 | 35.23 | 39.051 | 38.19 | 36.893 | 35.545 | 34.876 | 34.082 | 34.089 | 36.113 | 40.818 | 39.012 | 37.457 | 37.161 | 36.826 | 35.766 | 35.145 | 34.698 | 34.622 | 33.989 | 34.147 | 33.456 | 33.273 | 33.381
TOTAL EFFLUENT FLOW (MGD) | [5 empty] | 31.428 | 31.261 | 31.444 | 34.772 | 32.86 | 32.122 | 32.558 | 32.497 | 35.544 | 39.27 | 37.644 | 37.071 | 35.609 | 34.992 | 33.987 | 34.274 | 36.105 | 40.87 | 38.661 | 36.5 | 36.693 | 36.794 | 36.036 | 35.217 | 34.672 | 34.055 | 33.804 | 34.406 | 33.747 | 33.277 | 33.245
MAXIMUM HOURLY RAW INFLUENT FLOW (MGD) | [5 empty] | 1.594 | 1.646 | 1.6 | 1.751 | 1.773 | 1.716 | 1.667 | 1.756 | 2.061 | 2.039 | 1.949 | 1.948 | 1.858 | 1.803 | 1.74 | 1.791 | 1.9 | 2.055 | 1.969 | 1.91 | 1.883 | 1.958 | 1.881 | 1.817 | 1.84 | 1.822 | 1.754 | 1.766 | 1.702 | 1.676 | 1.726
MAXIMUM INSTANANEOUS PEAK RAW INFUENT FLOW (MGD) | [5 empty] | 52.161 | 51.2 | 49.119 | 51.713 | 51.649 | 53.507 | 53.988 | 51.168 | 57.577 | 56.584 | 57.676 | 56.744 | 55.782 | 55.846 | 50.623 | 52.482 | 54.501 | 57.929 | 55.398 | 54.437 | 52.706 | 53.603 | 53.219 | 55.238 | 54.981 | 51.136 | 53.411 | 52.065 | 50.303 | 47.869 | 50.559
MINIMUM INSTANANEOUS PEAK RAW INFUENT FLOW (MGD) | [5 empty] | 0.896 | 0.607 | 0.832 | 13.136 | 8.746 | 4.581 | 0.864 | 0.864 | 0.96 | 0.832 | 15.219 | 12.624 | 12.432 | 0.575 | 0.319 | 11.791 | 0.928 | 20.858 | 19.031 | 15.796 | 13.681 | 12.432 | 13.809 | 12.912 | 12.688 | 13.136 | 11.31 | 12.11 | 5.126 | 6.567 | 13.329
TOTAL RETURN ACTIVATED SLUDGE FLOW (MGD) | [5 empty] | 13.744 | 13.763 | 13.691 | 14.027 | 13.259 | 12.939 | 13.246 | 13.768 | 13.451 | 13.986 | 14.349 | 14.224 | 13.995 | 13.897 | 13.612 | 13.578 | 13.904 | 14.299 | 13.262 | 12.989 | 13.338 | 13.462 | 13.497 | 13.552 | 13.96 | 13.614 | 13.546 | 13.184 | 12.99 | 13.137 | 12.328
TOTAL WASTE FLOW TO DEWATERING PROCESS (MG) | [5 empty] | 0.597 | 0.578 | 0.498 | 0.24 | 0 | 0.179 | 0.478 | 0.493 | 0.667 | 0 | 0 | 0 | 0.228 | 0.629 | 0.552 | 0.538 | 0.618 | 0.185 | 0 | 0.171 | 0.746 | 0.83 | 0.718 | 0.788 | 0.461 | 0 | 0.316 | 0.847 | 0.825 | 0.814 | 0.779
TOTAL DAILY RAINFALL | [5 empty] | 0 | 0 | 0 | 0.39 | 0 | 0 | 0 | 0.1 | 1.87 | 0.13 | 0 | 0 | 0 | 0 | 0 | 0 | 2.02 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAW INFLUENT pH | [5 empty] | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7.1 | 7 | 7 | 7 | 7 | 6.8 | 7 | 7 | 7 | 6.8 | 7 | 7 | 7.1 | 7 | 7 | 7 | 7 | 7
RAW INFLUENT HYDROGEN SULFIDE (PPM) | [5 empty] | 6 | 5 | 5 | 5 | 5 | 4 | 5 | 7 | 6 | 4 | 5 | 6 | 6 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 4 | 5 | 5 | 5 | 5 | 5 | 7 | 5 | 6 | 6 | 6
RAW INFLUENT TEMPERATURE (F ) | [5 empty] | 78 | 77 | 75 | 77 | 77 | 77 | 76.7 | 77 | 76 | 76 | 76 | 76.5 | 76 | 77 | 77 | 78 | 78 | 77 | 77 | 77 | 78 | 78 | 78 | 78.2 | 78 | 78.7 | 78.8 | 78.5 | 76.8 | 78.8 | 78.4
TOTAL DAILY KILOWATTS (FPL POWER CONSUMPTION) | [5 empty] | 32366 | 32879 | 30680 | 32380 | 32000 | 32938 | 32376 | 30955 | 30237 | 31851 | 31939 | 34621 | 34206 | 33940 | 32089 | 33008 | 29265 | 33294 | 33991 | 34052 | 33816 | 33475 | 33852 | 33159 | 33186 | 33050 | 33094 | 33354 | 32220 | 31087 | 30798
GTL PLANT DAILY PROCESS SUMMARY
(CONTINUED)
[6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
FINAL EFFLUENT FREE CHLORINE RESIDUAL (PPM) | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FINAL EFFLUENT TOTAL CHLORINE RESIDUAL (PPM) | [5 empty] | 0.7 | 0.8 | 0.9 | 0.8 | 0.8 | 0.7 | 0.7 | 0.7 | 0.8 | 0.8 | 0.4 | 0.7 | 0.9 | 0.7 | 0.8 | 0.7 | 0.5 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.7 | 0.6 | 0.2 | 1 | 0.9 | 0.7 | 0.6 | 0.6 | 0.7
FINAL EFFLUENT pH (daily average) | [5 empty] | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.7 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.7 | 6.6 | 6.6 | 6.6 | 6.5 | 6.5 | 6.5 | 6.6 | 6.6 | 6.6 | 6.6 | 6 | 6.5 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
FINAL EFFLUENT pH (daily minimum) | [5 empty] | 6.6 | 6.6 | 6.5 | 6.6 | 6.6 | 6.7 | 6.6 | 6.6 | 6.6 | 6.6 | 6.5 | 6.5 | 6.6 | 6.5 | 6.5 | 6.4 | 6.4 | 6.4 | 6.5 | 6.5 | 6.4 | 6.5 | 6.6 | 6.5 | 6.4 | 6.5 | 6.5 | 6.5 | 6.6 | 6.6 | 6.6
FINAL EFFLUENT pH (daily maximum) | [5 empty] | 6.7 | 6.6 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.6 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.7 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
FINAL EFFLUENT TEMPARTURE (F ) | [5 empty] | 80 | 79.6 | 79.3 | 79 | 79 | 79.3 | 80 | 80 | 79 | 78 | 78.4 | 78.6 | 78.9 | 79 | 80 | 80 | 80 | 77 | 80 | 80 | 80 | 80 | 80.4 | 80.6 | 81.1 | 81.4 | 81.6 | 81.5 | 81.2 | 81.4 | 82
AVERAGE CLARIFIER BLANKET DEPTH (INCHES) | [5 empty] | 40 | 42 | 35 | 42 | 54 | 55 | 64 | 55 | 43 | 54 | 71 | 65 | 57 | 50 | 42 | 39 | 36 | 49 | 62 | 57 | 49 | 38 | 32 | 24 | 24 | 37 | 37 | 28 | 23 | 19 | 23
FINAL EFFLUENT SAMPLE TEMPARTURE (C ) | [5 empty] | 3 | 2 | 2 | 4 | 3.5 | 3 | 3 | 3 | 2 | 3 | 3 | 4 | 4 | 2 | 3 | 2 | 2 | 4 | 4 | 1 | 2 | 2 | 2 | 4 | 4 | 1 | 2 | 4 | 4 | 4 | 2
TOTAL RETURN ACTIVATED SLUDGE FLOW TO REACTOR ONE (MGD) | [5 empty] | 6.559 | 6.683 | 6.638 | 6.616 | 6.793 | 6.676 | 6.631 | 6.625 | 6.445 | 6.585 | 6.805 | 6.65 | 6.532 | 6.441 | 6.55 | 6.599 | 6.37 | 6.669 | 6.83 | 6.857 | 6.672 | 6.53 | 6.482 | 6.411 | 6.491 | 6.72 | 6.519 | 6.472 | 6.592 | 6.547 | 6.633
TOTAL RETURN ACTIVATED SLUDGE FLOW TO REACTOR TWO (MGD) | [5 empty] | 7.186 | 7.08 | 7.054 | 7.411 | 6.466 | 6.263 | 6.615 | 7.143 | 7.005 | 7.4 | 7.544 | 7.574 | 7.462 | 7.456 | 7.062 | 6.979 | 7.267 | 7.63 | 6.433 | 6.132 | 6.665 | 6.931 | 7.016 | 7.14 | 7.469 | 6.894 | 7.027 | 6.712 | 6.398 | 6.59 | 5.695
GTL PLANT DAILY PROCESS SUMMARY
CONTINUED
[6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TOTAL DAILY TRUCKING LOAD OF DEWATERED SLUDGE REMOVED | [5 empty] | 6 | 5 | 5 | 3 | 0 | 1 | 6 | 4 | 6 | 1 | 0 | 0 | 2 | 6 | 6 | 5 | 6 | 2 | 0 | 1 | 8 | 7 | 7 | 7 | 5 | 0 | 2 | 9 | 6 | 6 | 4
TOTAL DAILY HYDROGEN PEROXIDE CONSUMED (LBS) | [5 empty] | 1300 | 1956 | 1966 | 1547 | 1946 | 1427 | 1537 | 1826 | 1627 | 1616 | 1558 | 1587 | 1367 | 1407 | 1606 | 1577 | 1587 | 1686 | 1437 | 1088 | 1337 | 1437 | 1447 | 1397 | 1277 | 1387 | 1307 | 1547 | 1198 | 1637 | 1806
TOTAL DAILY CHLORINE CONSUMED (LBS) | [5 empty] | 1240 | 1240 | 1320 | 1160 | 1240 | 1040 | 1480 | 1240 | 1220 | 1400 | 1240 | 1200 | 920 | 1400 | 1160 | 1160 | 1320 | 1200 | 1200 | 1440 | 1140 | 1140 | 1080 | 300 | 560 | 1040 | 1080 | 1080 | 960 | 1400 | 1280
TOTAL DAILY POLYMER CONSUMED (GALS) | [5 empty] | 105 | 87 | 87 | 0 | 15 | 15 | 57 | 56 | 87 | 0 | 0 | 6 | 53 | 52 | 87 | 85 | 107 | 4 | 3 | 16 | 92 | 132 | 135 | 107 | 38 | 0 | 57 | 71 | 41 | 153 | 102
TOTAL TONS OF LIME DELIVERED DAILY | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTAL DAILY GASIOUS OXYGEN PRODUCED (TONS) | [5 empty] | 29.8 | 32.2 | 32.4 | 34.4 | 33.8 | 34 | 29.8 | 32.1 | 33.1 | 33.7 | 33.3 | 32.1 | 35.5 | 35.8 | 31.4 | 32.8 | 31.9 | 34.4 | 33.8 | 32.2 | 33 | 33.5 | 30.9 | 27.7 | 33.3 | 36.1 | 36.9 | 36.4 | 36.3 | 27.7 | 19
AVERAGE PERCENT OXYGEN PRODUCT PURITY | [5 empty] | 99 | 98 | 98 | 98 | 98 | 98 | 97 | 98 | 96 | 92 | 99 | 98 | 92 | 96 | 95 | 98 | 96 | 92 | 98 | 98 | 93 | 96 | 96 | 97 | 96 | 97 | 96 | 92 | 97 | 100 | 96
TOTAL DAILY LIQUID OXYGEN IN STORAGE (TONS) | [5 empty] | 67.5 | 67.8 | 67.3 | 65.3 | 63.7 | 60.2 | 60.4 | 60 | 59 | 59.7 | 59.1 | 77.7 | 69.3 | 87.6 | 89.1 | 90.3 | 84.1 | 86.8 | 86.5 | 86.1 | 87.8 | 82.4 | 82.5 | 82.3 | 85.9 | 81.5 | 81.5 | 80.4 | 80 | 80.2 | 80.6
MONITORING WELL PRESSURE DATA
MONITORING WELL ONE UPPER/LOWER LEVEL
| MW-1 |  | UPPER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MINIMUM | [5 empty] | 45.82 | 48.13 | ER | 48.11 | 48.06 | ER | ER | 36.84 | 48.02 | 15.87 | 47.88 | 47.84 | 47.88 | 43.41 | 43.88 | 48.13 | 48.23 | 48.18 | 48.17 | 48.19 | 43.25 | 43.59 | 48.19 | 48.16 | 48.21 | 48.31 | 48.36 | 39.39 | 39.56 | 48.28 | 48.29
MAXIMUM | [5 empty] | 48.59 | 48.45 | ER | 48.51 | 48.4 | ER | ER | 48.57 | 48.51 | 48.46 | 48.22 | 48.13 | 48.14 | 48.14 | 48.44 | 48.31 | 48.41 | 48.47 | 48.37 | 48.4 | 48.44 | 48.61 | 48.48 | 48.45 | 48.54 | 48.6 | 48.65 | 48.66 | 48.79 | 48.58 | 48.54
AVERAGE | [5 empty] | 47.72 | 48.27 | ER | 48.31 | 48.25 | ER | ER | 48.2 | 48.28 | 47.47 | 48.01 | 47.98 | 47.99 | 45.55 | 46.42 | 48.23 | 48.4 | 48.33 | 48.3 | 48.31 | 45.62 | 46.44 | 48.36 | 48.33 | 48.42 | 48.46 | 48.48 | 43.15 | 45.88 | 48.47 | 48.47
| MW-1 |  | LOWER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MINIMUM | [5 empty] | 39.44 | 39.73 | ER | 40.71 | 41.25 | ER | ER | 11.14 | 42.49 | 13.68 | 41.5 | 41.37 | 41.41 | 35.75 | 34.51 | 41.31 | 40.53 | 40.92 | 40.86 | 41.08 | 36.18 | 35.14 | 41.31 | 41.3 | 41.94 | 41.65 | 41.85 | 34.63 | 35.24 | 39.72 | 41.51
MAXIMUM | [5 empty] | 42.91 | 43.7 | ER | 44.59 | 45.83 | ER | ER | 43.85 | 44.49 | 45.3 | 45.72 | 45.17 | 46.82 | 45.29 | 41.79 | 44.4 | 45.26 | 44.48 | 45.29 | 46.15 | 44.53 | 41.31 | 45.74 | 44.52 | 45.1 | 45.04 | 44.66 | 43.87 | 42.47 | 44.84 | 44.47
AVERAGE | [5 empty] | 40.97 | 41.23 | ER | 42.24 | 42.99 | ER | ER | 40.65 | 43.43 | 42.22 | 43.11 | 42.95 | 43.24 | 40.66 | 38.49 | 42.56 | 42.26 | 42.37 | 42.51 | 42.95 | 40.81 | 38.28 | 42.48 | 42.55 | 43.01 | 42.65 | 42.82 | 40.82 | 38.93 | 42.12 | 42.64
MONITORING WELL TWO UPPER/LOWER LEVEL
| MW-2 |  | UPPER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MINIMUM | [5 empty] | 21.02 | 24.21 | ER | 24.55 | 24.58 | ER | ER | 20.75 | 24.23 | 24.1 | 23.99 | 24.73 | 24.53 | 20.82 | 20.3 | 25.56 | 25.76 | 25.38 | 25.07 | 25.28 | 21.33 | 21.37 | 26.11 | 26.34 | 26.75 | 27.23 | 27.65 | 21.67 | 21.06 | 25.6 | 26.66
MAXIMUM | [5 empty] | 25.67 | 25.86 | ER | 25.83 | 26.78 | ER | ER | 25.54 | 24.71 | 25.68 | 26.11 | 26.23 | 26.51 | 26.18 | 26.36 | 26.9 | 27.2 | 26.71 | 26.7 | 26.87 | 26.79 | 26.86 | 27.71 | 27.36 | 28.3 | 28.55 | 28.8 | 28.75 | 27.37 | 27.57 | 27.87
AVERAGE | [5 empty] | 23.87 | 24.87 | ER | 25.11 | 25.35 | ER | ER | 23.74 | 24.43 | 24.71 | 25.01 | 25.35 | 25.56 | 23.21 | 23.73 | 26.08 | 26.12 | 26.01 | 25.78 | 26.03 | 23.97 | 24.37 | 26.66 | 26.87 | 27.47 | 27.85 | 28.16 | 25.11 | 25.05 | 26.64 | 27.14
| MW-2 |  | LOWER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MINIMUM | [5 empty] | 38.99 | 42.37 | ER | 42.5 | 42.5 | ER | ER | 35.94 | 42.28 | 42.56 | 42.55 | 42.64 | 42.67 | 37.19 | 34.46 | 42.4 | 42.65 | 42.66 | 42.68 | 42.7 | 35.99 | 34.77 | 42.43 | 42.58 | 42.65 | 42.77 | 42.88 | 35.7 | 36.9 | 42.61 | 42.75
MAXIMUM | [5 empty] | 42.46 | 42.51 | ER | 42.74 | 42.7 | ER | ER | 42.43 | 42.69 | 42.69 | 42.77 | 42.74 | 42.82 | 42.82 | 42.4 | 42.65 | 42.81 | 42.86 | 42.8 | 42.89 | 42.95 | 42.5 | 42.71 | 42.74 | 42.87 | 42.94 | 43.02 | 43.09 | 42.67 | 42.77 | 42.86
AVERAGE | [5 empty] | 41.36 | 42.47 | ER | 42.58 | 42.54 | ER | ER | 40.4 | 42.47 | 42.56 | 42.66 | 42.61 | 42.71 | 39.53 | 40.14 | 42.49 | 42.73 | 42.76 | 42.75 | 42.88 | 39.11 | 39.72 | 42.51 | 42.57 | 42.83 | 42.87 | 42.97 | 40.41 | 41.25 | 42.62 | 42.82
MONITORING WELL THREE UPPER/LOWER LEVEL
| MW-3 |  | UPPER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MINIMUM | [5 empty] | 20.84 | 32.32 | ER | 32.55 | 32.54 | ER | ER | 17.6 | 32.19 | 32.5 | 32.53 | 32.59 | 32.59 | 18.22 | 18.09 | 32.33 | 32.63 | 32.71 | 32.73 | 32.74 | 19.01 | 18.98 | 32.43 | 32.64 | 32.71 | 32.88 | 32.96 | 19.93 | 19.74 | 32.65 | 32.81
MAXIMUM | [5 empty] | 32.48 | 32.58 | ER | 32.85 | 32.83 | ER | ER | 32.42 | 32.77 | 32.77 | 32.86 | 32.81 | 32.86 | 32.86 | 32.33 | 32.66 | 32.85 | 32.92 | 32.92 | 32.97 | 32.97 | 32.54 | 32.83 | 32.89 | 33.04 | 33.14 | 33.21 | 33.21 | 32.81 | 32.93 | 32.99
AVERAGE | [5 empty] | 28.76 | 32.47 | ER | 32.69 | 32.66 | ER | ER | 27.73 | 32.47 | 32.61 | 32.74 | 32.72 | 32.72 | 24.13 | 26.44 | 32.49 | 32.72 | 32.8 | 32.81 | 32.89 | 25.02 | 26.65 | 32.62 | 32.8 | 32.87 | 32.97 | 33.01 | 25.45 | 28.71 | 32.76 | 32.95
| MW-3 |  | LOWER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MINIMUM | [5 empty] | 38.8 | 45.07 | ER | 45.24 | 45.27 | ER | ER | 35.6 | 45.03 | 45.31 | 45.32 | 45.41 | 45.45 | 37.7 | 37.64 | 45.11 | 45.38 | 45.42 | 45.45 | 45.47 | 37.97 | 37.97 | 45.18 | 45.36 | 45.42 | 45.56 | 45.68 | 37.84 | 39.58 | 45.34 | 45.48
MAXIMUM | [5 empty] | 45.14 | 45.22 | ER | 45.46 | 45.46 | ER | ER | 45.15 | 45.42 | 45.42 | 45.51 | 45.5 | 45.58 | 45.58 | 45.11 | 45.4 | 45.56 | 45.6 | 45.58 | 45.68 | 45.71 | 45.23 | 45.46 | 45.49 | 45.65 | 45.71 | 45.81 | 45.88 | 45.36 | 45.49 | 45.58
AVERAGE | [5 empty] | 43.1 | 45.05 | ER | 45.41 | 45.4 | ER | ER | 42.11 | 45.3 | 45.39 | 45.46 | 45.48 | 45.5 | 40.91 | 42.02 | 45.35 | 45.49 | 45.52 | 45.5 | 45.52 | 41.33 | 42.01 | 45.37 | 45.44 | 45.49 | 45.58 | 45.77 | 42.19 | 43.6 | 45.44 | 45.5
MONITORING WELL RMW-1 UPPER/LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
[5 empty] | JULIAN DATE | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90
| RMW-1 |  | UPPER LEVEL
MINIMUM | [5 empty] | 44.45 | 44.38 | 44.39 | 44.38 | 44.35 | 44.32 | 44.35 | 44.47 | 44.47 | 44.49 | 44.5 | 44.46 | 44.49 | 37.18 | 36.91 | 12.72 | 44.17 | 44.25 | 44.25 | 44.29 | 44.34 | 44.4 | 44.43 | 44.39 | 44.43 | 44.5 | 44.56 | 44.59 | 44.56 | 44.55 | 44.57
MAXIMUM | [5 empty] | 44.59 | 44.47 | 44.48 | 44.57 | 44.48 | 44.42 | 44.52 | 44.62 | 44.72 | 44.66 | 44.64 | 44.59 | 44.59 | 44.61 | 43.85 | 63.95 | 44.37 | 44.4 | 44.34 | 44.42 | 44.51 | 44.51 | 44.55 | 44.54 | 44.6 | 44.61 | 44.68 | 44.77 | 44.65 | 44.61 | 44.65
AVERAGE | [5 empty] | 44.51 | 44.42 | 44.45 | 44.48 | 44.41 | 44.37 | 44.44 | 44.56 | 44.58 | 44.58 | 44.56 | 44.53 | 44.55 | 40.4 | 40.98 | 43.82 | 44.27 | 44.33 | 44.3 | 44.35 | 44.45 | 44.47 | 44.49 | 44.46 | 44.51 | 44.56 | 44.62 | 44.68 | 44.61 | 44.59 | 44.6
| RMW-1 |  | LOWER LEVEL
MINIMUM | [5 empty] | 22.93 | 22.84 | 22.87 | 22.83 | 22.79 | 22.8 | 22.82 | 23 | 22.98 | 23.05 | 23.03 | 22.98 | 22.98 | 20.53 | 20.8 | 12.43 | 22.24 | 22.34 | 22.35 | 22.38 | 22.44 | 22.52 | 22.53 | 22.5 | 22.54 | 22.62 | 22.7 | 22.72 | 22.65 | 22.62 | 22.59
MAXIMUM | [5 empty] | 23.11 | 22.99 | 22.98 | 23.08 | 22.98 | 22.91 | 23.03 | 23.12 | 23.22 | 23.18 | 23.13 | 23.09 | 23.09 | 23.12 | 22.49 | 64.76 | 22.45 | 22.51 | 22.46 | 22.54 | 22.62 | 22.64 | 22.64 | 22.6 | 22.69 | 22.72 | 22.79 | 22.94 | 22.77 | 22.73 | 22.73
AVERAGE | [5 empty] | 23 | 22.91 | 22.93 | 22.96 | 22.89 | 22.85 | 22.94 | 23.07 | 23.1 | 23.1 | 23.08 | 23.03 | 23.04 | 21.83 | 21.8 | 22.33 | 22.37 | 22.43 | 22.41 | 22.46 | 22.54 | 22.57 | 22.58 | 22.55 | 22.61 | 22.66 | 22.73 | 22.77 | 22.7 | 22.67 | 22.67
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
| INJECTION WELL ONE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 11.49 | 12 | ER | 11.68 | 11.78 | ER | ER | 11.78 | 10.59 | 16.87 | 12.88 | 0 | 0 | 12.65 | 12.26 | 12.23 | 13.22 | 13.5 | 12.14 | 12.01 | 11.93 | 14.79 | 12.68 | 12.02 | 11.88 | 11.74 | 10.76 | 12.15 | 11.18 | 11.59 | 11.68
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 4.33 | 4.94 | ER | ER | 5.26 | ER | ER | 0 | ER | ER | 0 | ER | ER | 0 | 0 | 0 | 5.23 | 6.1 | ER | 5.86 | 5.32 | 0 | 0 | 0 | 5.78 | 6.08 | 0 | ER | 0 | 5.6 | 5.49
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 8.1 | 8.36 | ER | 6.7 | 8.85 | ER | ER | 7.17 | 1.88 | 6.95 | 2.96 | 0 | 0 | 2.99 | 7.12 | 7.36 | 9.79 | 10.4 | 8.39 | 9.68 | 9.57 | 2.86 | 7.52 | 7.76 | 9.1 | 8.84 | 2.05 | 7.26 | 7.41 | 8.75 | 8.62
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 56.34 | 59.05 | ER | 56.83 | 57.24 | ER | ER | 57.61 | 54.26 | 79.7 | 63.5 | 35.2 | 35.01 | 63.22 | 58.47 | 58.1 | 62.21 | 63.09 | 57.6 | 57.57 | 57.42 | 67.66 | 60.07 | 57.71 | 57.46 | 57.55 | 55.68 | 58.07 | 54.94 | 56.77 | 57.06
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 38.2 | 39.96 | ER | 34.35 | 40.22 | ER | ER | 34.26 | 34.16 | 34.12 | 34.11 | 33.58 | 33.74 | 33.63 | 33.82 | 34.03 | 40.02 | 42.21 | 34.4 | 41.4 | 40.69 | 34.85 | 34.51 | 34.28 | 41.13 | 42.19 | 35.09 | 26.35 | 34.09 | 40.96 | 41.01
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 46.66 | 47.36 | ER | 45.82 | 48.64 | ER | ER | 45.96 | 37.78 | 47.46 | 39.15 | 34.51 | 34.44 | 39.37 | 46.04 | 46.82 | 51.07 | 53.5 | 49.17 | 50.83 | 50.65 | 39.64 | 47.74 | 47.45 | 49.48 | 48.88 | 38.21 | 46.93 | 46.58 | 48.51 | 48.35
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
| INJECTION WELL TWO |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 11.66 | 12.49 | ER | 12.33 | 12.03 | ER | ER | 11.9 | 15.73 | 17 | 14.71 | 12.79 | 12.78 | 13.02 | 12.46 | 12.23 | 13.33 | 13.48 | 12.33 | 12.09 | 12.06 | 15.14 | 13.04 | 12.28 | 12.05 | 11.97 | 12.68 | 9.6 | 11.37 | 11.79 | 11.85
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 0.04 | 5.05 | ER | 7.05 | 5.4 | ER | ER | 4.17 | 4.52 | 4.13 | 4.2 | 0.04 | 6.48 | 6.08 | 5.49 | 0.05 | 0.05 | 0.04 | 0.04 | 0.04 | 5.37 | 0.05 | 0.05 | 0.05 | 0.04 | 6.13 | 4.97 | 0.04 | 0.05 | 0.04 | 5.49
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 7.22 | 8.53 | ER | 9.68 | 9.02 | ER | ER | 8.46 | 9.62 | 10.41 | 9.62 | 8.18 | 10.07 | 9.68 | 9.28 | 3.62 | 3 | 7.51 | 7.78 | 8.09 | 9.73 | 9.98 | 2.36 | 7.27 | 7.72 | 8.98 | 9.27 | 0.8 | 6.94 | 7.42 | 8.77
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 55.36 | 57.99 | ER | 56.83 | 56.49 | ER | ER | 56.64 | 70.3 | 78.4 | 64.93 | 57.69 | 57.71 | 62.95 | 57.59 | 56.18 | 61.14 | 61.84 | 56.61 | 56.52 | 56.51 | 66.59 | 60.48 | 56.76 | 56.6 | 56.68 | 58.01 | 50.08 | 53.97 | 55.78 | 56.09
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 34.69 | 39.21 | ER | 42.33 | 39.48 | ER | ER | 37.71 | 38.24 | 37.38 | 37.32 | 34.36 | 41 | 40.07 | 39.32 | 35.36 | 34.6 | 35.76 | 34.79 | 35.1 | 39.96 | 36.31 | 35.63 | 34.54 | 35.19 | 41.48 | 39.41 | 31.54 | 34.43 | 34.99 | 40.27
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 44.78 | 46.51 | ER | 49.33 | 47.81 | ER | ER | 46.67 | 49.41 | 51.67 | 49.37 | 47.55 | 49.77 | 49.13 | 48.08 | 40.27 | 40.49 | 47.68 | 47.47 | 47.59 | 49.81 | 50.8 | 38.86 | 46.11 | 46.87 | 48.12 | 48.57 | 36.96 | 45.27 | 45.96 | 47.55
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
| INJECTION WELL THREE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 11.09 | 10.73 | ER | 11.42 | 11.42 | ER | ER | 11.19 | 14.05 | 15.72 | 13.11 | 12.91 | 11.59 | 11.49 | ER | 11.3 | 12.49 | 12.57 | 12.11 | 11.5 | 11.32 | 13.62 | 12.03 | 9.15 | 11.49 | 11.3 | 11.46 | 11.28 | 9.1 | 11.23 | 11.16
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 4.57 | ER | ER | 6.98 | ER | ER | ER | 4.5 | 4.86 | 4.24 | 4.51 | 6.68 | 6.24 | ER | ER | ER | 5.32 | 6.21 | ER | ER | ER | ER | 5.93 | ER | ER | ER | 5.13 | 4.85 | ER | ER | ER
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 8.08 | 6.1 | ER | 9.31 | 6.29 | ER | ER | 8.15 | 8.92 | 9.78 | 8.95 | 9.67 | 9.27 | 6.09 | ER | 5.65 | 9.36 | 9.94 | 2.67 | 7.13 | 7.75 | 9.28 | 9.32 | 2.21 | 6.85 | 7.24 | 8.71 | 8.94 | 2.12 | 6.6 | 7.08
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 56.66 | 55.18 | ER | 58.12 | 57.54 | ER | ER | 57.84 | 71.9 | 80.2 | 66.04 | 64.75 | 58.87 | 58.96 | 37.72 | 58.24 | 62.47 | 63.24 | 61.27 | 57.69 | 57.65 | 66.55 | 61.65 | 49.49 | 57.71 | 57.7 | 58.99 | 58.2 | 49.44 | 56.99 | 57.25
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 38.37 | 34.79 | ER | 43.3 | 34.89 | ER | ER | 38.56 | 39.11 | 38.25 | 38.19 | 42.78 | 41.93 | 36.16 | 35.28 | 35.44 | 40.15 | 42.36 | 36.43 | 35.67 | 35.46 | 36.59 | 41.51 | 36.26 | 35.62 | 35.66 | 40.24 | 32.2 | 36.69 | 35.42 | 35.49
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 46.88 | 44.64 | ER | 50.44 | 45.39 | ER | ER | 47.67 | 50.49 | 52.8 | 50.4 | 52.1 | 50.8 | 45.82 | 36.65 | 45.34 | 51.21 | 53.71 | 41.48 | 47.83 | 48.7 | 51.65 | 51.06 | 39.85 | 47.05 | 47.29 | 49.51 | 50.15 | 39.63 | 46.27 | 46.83
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
FUTURE
| INJECTION WELL FOUR |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 0.03 | 0.03 | ER | 0.03 | 0.04 | ER | ER | 12.03 | 14.73 | 16.63 | 13.64 | 13.34 | 11.81 | 12.51 | 12.04 | 11.88 | 13.08 | 13.24 | 12.27 | 11.71 | 11.83 | 14.03 | 12.48 | 11.79 | 10.13 | 11.75 | 11.63 | 11.44 | 10.98 | 8.99 | 11.64
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 0.01 | 0.01 | ER | 0.01 | 0.01 | ER | ER | 4.97 | 5.35 | 4.92 | 4.92 | 6.9 | 6.53 | 6.3 | 5.63 | 6.47 | 5.7 | 6.6 | 7.26 | 0.01 | 0.02 | 0.03 | 6.06 | 5.16 | 0.03 | 0.03 | 0.03 | 4.96 | 5.99 | 0.02 | 0.03
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 0.02 | 0.02 | ER | 0.01 | 0.02 | ER | ER | 8.78 | 9.42 | 10.42 | 9.35 | 9.99 | 9.55 | 9.3 | 9.12 | 9.33 | 9.67 | 10.37 | 10.26 | 2.42 | 7.44 | 7.79 | 9.47 | 9.3 | 2.22 | 6.93 | 7.45 | 9.05 | 8.9 | 2.11 | 6.79
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 37.18 | 37.21 | ER | 37.23 | 37.43 | ER | ER | 58.25 | 72.1 | 80.5 | 66.53 | 65.24 | 59.47 | 79.7 | 59.45 | 58.77 | 62.99 | 63.81 | 61.82 | 58.41 | 58.19 | 67.04 | 62.15 | 58.6 | 53.28 | 58.33 | 59.68 | 58.79 | 55.84 | 48.92 | 57.8
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | ER | 34.75 | ER | 35.47 | 34.84 | ER | ER | 39.25 | 39.83 | 38.98 | 38.94 | 43.44 | 42.64 | 41.66 | 40.89 | 42.76 | 40.83 | 43.03 | 44.96 | 35.85 | 35.5 | 35.38 | 42.23 | 40.43 | 36.69 | 35.69 | 35.73 | 32.44 | 42.52 | 36.45 | 35.48
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | ER | 36.03 | ER | 36.41 | 36.17 | ER | ER | 48.22 | 51.04 | 53.35 | 51 | 52.67 | 51.47 | 50.8 | 49.8 | 50.63 | 51.85 | 54.3 | 53.71 | 40.33 | 48.36 | 49.84 | 51.69 | 50.73 | 39.81 | 46.93 | 48.18 | 50.78 | 49.76 | 39.53 | 46.67
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
| INJECTION WELL FIVE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 10.88 | 11.62 | ER | 11.12 | 11.23 | ER | ER | ER | 13.54 | 12.34 | 12.6 | 12.31 | 11.1 | 11.67 | 11.21 | 10.95 | 10.79 | 11.9 | 11.48 | 11.21 | 11.18 | 13.84 | 11.25 | 11.03 | 11.17 | 9.85 | 10.95 | 10.81 | 10.25 | 10.97 | 8.41
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 4.73 | ER | ER | 6.88 | 5.65 | ER | ER | ER | ER | ER | ER | 6.46 | ER | ER | 5.32 | ER | ER | ER | 6.87 | 6.03 | ER | ER | ER | 4.97 | 5.81 | ER | ER | ER | 5.74 | 5.61 | ER
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 8.02 | ER | ER | 9.14 | 8.69 | ER | ER | ER | 5.64 | 1.9 | 6.62 | 9.29 | 6.79 | 6.9 | 8.51 | 8.29 | 4.3 | 2.72 | 9.6 | 9.23 | 2.21 | 6.89 | 7.42 | 8.75 | 8.77 | 2.11 | 6.35 | 8.45 | 8.39 | 8.45 | 2.01
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 56.36 | 61.11 | ER | 57.73 | 57.06 | ER | ER | 36.47 | 71.4 | 65.04 | 65.64 | 64.56 | 58.37 | 63.14 | 58.29 | 57.79 | 57.41 | 62.95 | 61 | 57.51 | 57.3 | 67.43 | 59.79 | 57.58 | 57.22 | 52.93 | 58.63 | 57.82 | 54.86 | 56.47 | 47.16
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 38.36 | ER | ER | 43.08 | 40.24 | ER | ER | 34.29 | 34.17 | 34.28 | 34.21 | 42.61 | 34.88 | 34.91 | 39.98 | 35.59 | 34.9 | 35.23 | 44.08 | 41.34 | 35.24 | 33.99 | 35.21 | 39.46 | 41.03 | 35.53 | 34.12 | 27.01 | 41.62 | 40.94 | 35.52
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 46.68 | ER | ER | 50.12 | 48.54 | ER | ER | 35.35 | 46.05 | 38.89 | 47.3 | 51.8 | 47.4 | 47.36 | 48.79 | 48.97 | 43.16 | 41.38 | 52.73 | 50.69 | 38.86 | 48.44 | 48.62 | 49.7 | 49.26 | 38.56 | 46.28 | 49.72 | 48.74 | 48.33 | 38.33
GTL DAILY LABORATORY ANALYSIS REPORT DATA
| RAW INFLUENT DATA |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
RAW TOTAL SUSPENDED SOLIDS | [5 empty] | 104 | 120 | 174 | 44 | 122 | 124 | 80 | 2216 | 136 | 152 | 92 | 98 | 116 | 112 | 134 | 122 | 124 | 96 | 98 | 484 | 98 | 118 | 98 | 96 | 80 | 136 | 140 | 152 | 116 | 120 | 112
RAW FIXED SUSPENDED SOLIDS | [5 empty] | 0 | 8 | 36 | 4 | 14 | 6 | 18 | 406 | 8 | 24 | 16 | 8 | 16 | 12 | 10 | 26 | 20 | 24 | 16 | 68 | 12 | 26 | 15 | 40 | 24 | 4 | 16 | 32 | 28 | 24 | 24
RAW ALKILINITY | [5 empty] | 214 | 222 | 238 | 207 | 188 | 210 | 210 | 264 | 212 | 210 | 218 | 216 | 198 | 198 | 220 | 220 | 196 | 196 | 198 | 220 | 218 | 188 | 210 | 210 | 210 | 198 | 204 | 226 | 212 | 214 | 214
RAW CHLORIDES | [5 empty] | 920 | 780 | 730 | 820 | 770 | 760 | 800 | 990 | 780 | 710 | 730 | 700 | 710 | 640 | 640 | 730 | 670 | 670 | 650 | 670 | 730 | 750 | 740 | 700 | 820 | 760 | 790 | 770 | 1100 | 770 | 740
RAW COD | [5 empty] | 180 | 142 | 178 | 165 | 185 | 183 | 191 | 231 | 172 | 188 | 218 | 212 | 186 | 201 | 326 | 176 | 200 | 211 | 213 | 248 | 246 | 371 | 170 | 452 | 369 | 387 | 198 | 170 | 195 | 151 | 168
RAW CBOD | [5 empty] | 102.9 | 79.8 | 122.4 | 80.9 | 95.9 | 93.6 | 114.5 | 129 | 123.9 | 118.4 | 86.6 | 85.2 | 74.3 | 85.2 | 117.1 | 87.5 | 105.6 | 79.2 | 60.4 | 127.5 | 59.7 | 69.9 | 56.2 | 56.5 | 188 | 109.4 | 117 | 130 | 94 | 86 | 97
RAW SUFATES | [5 empty] | 165.5 | 141.3 | 125.8 | 138.8 | 137.3 | 140.5 | 140.8 | 115.8 | 142.3 | 122 | 142.8 | 138.5 | 140 | 1595 | 130.3 | 126.8 | 129 | 137.8 | 120.5 | 122.2 | 175.2 | 153.8 | 140.5 | 139 | 173 | 140.2 | 125.5 | 159.5 | 165.2 | 138.2 | 148.5
| EFFLUENT DATA |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
EFFLUENT TOTAL DISSOLVED SOLIDS | [5 empty] | 1534 | 1536 | 1592 | 1488 | 1501 | 1479 | 1454 | 1479 | 1475 | 1424 | 1469 | 1386 | 1391 | 1398 | 1408 | 1415 | 1430 | 1281 | 1288 | 1372 | 1430 | 1405 | 1425 | 1506 | 1434 | 1310 | 1520 | 1673 | 1660 | 1500 | 1715
EFFLUENT TOTAL SUSPENDED SOLIDS | [5 empty] | 8 | 10 | 10 | 4 | 18 | 16 | 21 | 12 | 17 | 15 | 41 | 21 | 20 | 10 | 10 | 18 | 20 | 19 | 15 | 20 | 22 | 14 | 20 | 18 | 19 | 18 | 15 | 24 | 22 | 29 | 44
EFFLUENT FIXED SUSPENDED SOLIDS | [5 empty] | 0 | 0 | 2 | 3 | 4 | 0 | 8 | 0 | 0 | 2 | 10 | 1 | 3 | 1 | 1 | 7 | 9 | 10 | 4 | 2 | 2 | 8 | 13 | 12 | 3 | 0 | 3 | 13 | 11 | 10 | 12
EFFLUENT ALKILINITY | [5 empty] | 190 | 184 | 184 | 182 | 188 | 186 | 188 | 188 | 190 | 190 | 192 | 190 | 194 | 188 | 198 | 192 | 184 | 180 | 180 | 196 | 196 | 180 | 198 | 196 | 194 | 186 | 196 | 172 | 194 | 196 | 196
EFFLUENT TURBIDITY | [5 empty] | 7.84 | 5.18 | 5.79 | 5.44 | 5.53 | 8.1 | 5.42 | 6.94 | 7.16 | 6.9 | 17.1 | 9.06 | 7.24 | 4.76 | 4.1 | 3.19 | 4.96 | 6.55 | 6.73 | 3.9 | 4.68 | 4.22 | 4.81 | 3.62 | 4.8 | 5.2 | 4.93 | 5.62 | 6.82 | 10.8 | 13.5
EFFLUENT CHLORIDES | [5 empty] | 870 | 830 | 860 | 810 | 780 | 770 | 790 | 790 | 790 | 750 | 720 | 710 | 710 | 720 | 710 | 730 | 720 | 660 | 660 | 710 | 730 | 700 | 700 | 710 | 710 | 690 | 780 | 620 | 770 | 750 | 740
EFFLUENT CONDUCTIVITY | [5 empty] | 3270 | 3240 | 3270 | 3200 | 3140 | 2890 | 3150 | 3100 | 3110 | 2930 | 3050 | 2900 | 2910 | 2920 | 2940 | 2940 | 2920 | 2610 | 2650 | 2800 | 2900 | 2830 | 2950 | 2890 | 2930 | 2750 | 3090 | 2530 | 3070 | 3020 | 3040
EFFLUENT TOTAL BACTERIA COUNT | [5 empty] | 80 | 350 | TNTC | TNTC | TNTC | 2600 | 6600 | 720 | 36 | 562 | 38000 | TNTC | TNTC | 45 | 27 | 71 | 152 | TNTC | 3000 | TNTC | 790 | 207 | 210 | 2800 | TNTC | 36 | 17000 | 27 | 250 | 9 | 909
EFFLUENT FECAL BACTERIA COUNT | [5 empty] | 9 | 0 | TNTC | TNTC | TNTC | 45 | 0 | 0 | 0 | 0 | 12223 | TNTC | TNTC | 0 | 0 | 0 | 0 | 310 | 0 | 9 | 0 | 0 | 0 | 18 | TNTC | 0 | 152 | 0 | 107 | 0 | 9
EFFLUENT COD | [5 empty] | 58.1 | 52.3 | 48.1 | 45.1 | 48.1 | 52.1 | 47.9 | 49.4 | 51.6 | 82.3 | 38.8 | 47.5 | 54.5 | 52.8 | 66.8 | 44.3 | 41.9 | 39.3 | 47.1 | 36.7 | 36.9 | 53.8 | 46.8 | 42.6 | 34.7 | 46.9 | 40.9 | 44.5 | 41.6 | 48.5 | 60.5
EFFLUENT CBOD | [5 empty] | 4.97 | 3.41 | 3.1 | 3.06 | 3.69 | 2.14 | 4.4 | 4.05 | 4.12 | 4.38 | 7.99 | 4.06 | 4.04 | 2.1 | 3.76 | 3.17 | 4.03 | 2.82 | 15.4 | 2.13 | 1.75 | 2.19 | 1.36 | 1.53 | 4.5 | 2.41 | 3 | 3 | 3 | 6 | 7
EFFLUENT SULFATES | [5 empty] | 129.3 | 125.5 | 127.5 | 128.3 | 126.5 | 119.5 | 118.5 | 121.3 | 115.3 | 102.5 | 107.5 | 123.8 | 116 | 117.8 | 119 | 126.8 | 135 | 134.2 | 113.2 | 110.8 | 117.2 | 113.2 | 122.2 | 145.5 | 148.8 | 129.8 | 122.8 | 108.2 | 127 | 132.5 | 137
LABORATORY NUTRIENT DATA
RAW INFLUENT | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
RAW AMMONIA (PPM) | [5 empty] | 19 | 22 | 22 | 18 | 18 | 21 | 19 | 20 | 21 | 17 | 16 | 16 | 16 | 18 | 18 | 19 | 16 | 15 | 15 | 16 | 16 | 17 | 17 | 17 | 16 | 16 | 17 | 17 | 17 | 18 | 23
RAW NITRATES (PPM) | [5 empty] | 0.05 | 0.05 | 0.057 | 0.059 | 0.05 | 0.17 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.078 | 0.12 | 0.12 | 0.61 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.13 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.11 | 0.23
RAW TOTAL KNEDJAHL NITRIGEN | [5 empty] | 22 | 27 | 29 | 21 | 19 | 27 | 20 | 25 | 22 | 27 | 26 | 21 | 22 | 24 | 23 | 30 | 27 | 19 | 21 | 19 | 20 | 20 | 21 | 21 | 20 | 29 | 27 | 27 | 26 | 28 | 27
RAW TOTAL PHOSPHORUS | [5 empty] | 3.3 | 3.1 | 3.5 | 2.9 | 3 | 3 | 2.9 | 5.7 | 3.1 | 3.7 | 2.8 | 2.9 | 2.8 | 3.1 | 3.1 | 3.7 | 3.5 | 2.2 | 3 | 3.8 | 2.9 | 2.9 | 3 | 3.3 | 3.2 | 3.1 | 3.5 | 3.1 | 2.9 | 3 | 3
EFFLUENT | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
EFFLUENT AMMONIA (PPM) | [5 empty] | 17 | 16 | 16 | 13 | 13 | 14 | 14 | 15 | 15 | 11 | 11 | 11 | 12 | 13 | 0.14 | 14 | 11 | 12 | 10 | 11 | 12 | 13 | 13 | 13 | 11 | 11 | 11 | 13 | 14 | 15 | 9.6
EFFLUENT NITRATES (PPM) | [5 empty] | 0.33 | 0.33 | 0.38 | 0.5 | 0.51 | 0.42 | 0.94 | 0.45 | 0.47 | 0.25 | 0.37 | 0.42 | 0.23 | 0.34 | 0.3 | 0.16 | 0.17 | 0.18 | 0.18 | 0.15 | 0.15 | 0.22 | 0.41 | 0.35 | 0.32 | 0.34 | 0.34 | 0.49 | 0.73 | 0.61 | 0.05
EFFLUENT TOTAL KNEDJAHL NITRIGEN | [5 empty] | 17 | 17 | 18 | 15 | 14 | 15 | 16 | 16 | 15 | 17 | 13 | 13 | 14 | 17 | 19 | 16 | 16 | 14 | 11 | 11 | 14 | 14 | 0 | 15 | 14 | 14 | 13 | 15 | 17 | 28 | 18
EFFLUENT TOTAL PHOSPHORUS | [5 empty] | 1.1 | 0.55 | 0.57 | 1.5 | 1 | 0.69 | 0.65 | 0.73 | 0.63 | 1.4 | 0.76 | 0.61 | 0.6 | 0.48 | 0.56 | 0.53 | 0.6 | 0.96 | 11 | 11 | 0.49 | 0.61 | 1 | 1.7 | 0.94 | 0.69 | 0.59 | 1.3 | 2.7 | 4.4 | 4.1
LABORATORY REACTOR PROCESSES DATA
| REACTOR ONE TRAIN A |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MIXED-LIQUIR SUSPENDED SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
AVERAGE SETTLABLE SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
MIXED LIQUIR VOLITLE SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
| REACTOR ONE TRAIN B |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MIXED-LIQUIR SUSPENDED SOLIDS | [5 empty] | 3180 | 3780 | 3050 | 3320 | 3260 | 3310 | 3500 | 3040 | 2590 | 3320 | 2950 | 2720 | 2770 | 3000 | 2880 | 2900 | 2430 | 2750 | 2800 | 2910 | 2760 | 2970 | 2600 | 2590 | 2510 | 2670 | 2810 | 3090 | 2410 | 2280 | 1980
AVERAGE SETTLABLE SOLIDS | [5 empty] | 28 | 30 | 31 | 31 | 31 | 31 | 30 | 30 | 28 | 32 | 34 | 37 | 36 | 35 | 33 | 30 | 28 | 31 | 33 | 35 | 34 | 30 | 28 | 25 | 25 | 31 | 27 | 28 | 24 | 20 | 20
MIXED LIQUIR VOLITLE SOLIDS | [5 empty] | 2660 | 3100 | 2510 | 2640 | 2690 | 2760 | 2870 | 2490 | 2140 | 2710 | 2360 | 2320 | 2330 | 2490 | 2380 | 2250 | 1950 | 2190 | 2230 | 2430 | 2320 | 2270 | 2030 | 2010 | 1920 | 2270 | 2380 | 2490 | 1920 | 1810 | 1610
LABORATORY REACTOR PROCESSES DATA
CONTINUED
| REACTOR TWO TRAIN C |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MIXED-LIQUIR SUSPENDED SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
AVERAGE SETTLABLE SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
MIXED LIQUIR VOLITLE SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
| REACTOR TWO TRAIN D |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MIXED-LIQUIR SUSPENDED SOLIDS | [5 empty] | 3050 | 3630 | 2900 | 3300 | 2920 | 2810 | 3870 | 2770 | 2630 | 3510 | 2940 | 2550 | 2800 | 3190 | 2710 | 3070 | 2390 | 2770 | 2920 | 2380 | 3160 | 2630 | 2680 | 2560 | 2660 | 2510 | 2840 | 2440 | 2450 | 2250 | 2400
AVERAGE SETTLABLE SOLIDS | [5 empty] | 28 | 30 | 31 | 31 | 31 | 30 | 31 | 29 | 25 | 32 | 35 | 35 | 35 | 32 | 32 | 30 | 29 | 32 | 34 | 32 | 31 | 29 | 29 | 26 | 25 | 30 | 27 | 28 | 24 | 23 | 27
MIXED LIQUIR VOLITLE SOLIDS | [5 empty] | 2580 | 3070 | 2390 | 2670 | 2410 | 2320 | 3140 | 2270 | 2170 | 2900 | 2380 | 2200 | 2340 | 2560 | 2240 | 2330 | 1910 | 2210 | 2330 | 2000 | 2700 | 1960 | 2110 | 2020 | 2150 | 2130 | 2320 | 1970 | 1940 | 1820 | 2010
LABORATORY RETURN ACTIVATED SLUDGE AND WASTE SLUDGE DATA
| RETURN ACTIVATED SLUDGE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
PERCENT RETURN SLUDGE TOTAL SUSPENDED SOLIDS | [5 empty] | 0.94 | 0.97 | 0.93 | 1.05 | 1 | 1.01 | 0.96 | 0.93 | 1.04 | 1.02 | 1.13 | 1 | 1 | 1.05 | 0.93 | 1 | 0.9 | 0.84 | 0.8 | 1 | 1.14 | 0.97 | 0.97 | 0.93 | 0.88 | 0.86 | 0.95 | 0.85 | 0.82 | 0.85 | 0.78
PERCENT RETURN SLUDGE FIXED SUSPENDED SOLIDS | [5 empty] | 23.91 | 24.76 | 23.94 | 25.21 | 25.71 | 24.22 | 24.53 | 25.62 | 24.4 | 24.6 | 25.2 | 25.71 | 23.26 | 22.88 | 23.5 | 22.6 | 24.09 | 24 | 23 | 24.1 | 14.9 | 24.24 | 24.11 | 26 | 24.39 | 25.58 | 27.08 | 26.77 | 27.27 | 27.17 | 25.6
|  | WASTE SLUDGE |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
PERCENT WASTE FEED TOTAL SUSPENDED SOLDS | [5 empty] | 1.3 | 1.33 | 1.38 |  |  | 1.36 | 1.38 | 1.42 | 1.23 |  |  |  | 1.27 | 1.19 | 1.43 | 1.36 | 1.33 |  |  | 1.36 | 1 | 1.44 | 1.32 | 0.97 |  |  | 1.46 | 1.24 | 1.21 | 1.01 | 1.01
PERCENT WASTE FEED FIXED SUSPENDED SOLIDS | [5 empty] | 23.85 | 23.31 | 22.46 |  |  | 22.06 | 21.74 | 21.83 | 26 |  |  |  | 22.83 | 23.53 | 21.7 | 15.4 | 23.31 |  |  | 21.3 | 27 | 23.61 | 24.24 | 29.9 |  |  | 23.29 | 28.23 | 26.45 | 27.72 | 27.72
WASTE FEED SLUDGE pH | [5 empty] | 6.61 | 6.46 | 6.43 |  |  | 6.52 | 6.6 | 6.63 | 6.64 |  |  |  | 6.63 | 6.66 | 6.38 | 6.11 | 6.14 |  |  | 6.26 | 6.46 | 6.37 | 5.9 | 6.53 |  |  | 5.95 | 6.2 | 6.15 | 6.23 | 6.11
DEWATERING FILTRATE TOTAL SUSPENDED SOLIDS | [5 empty] | 0.22 | 0.23 | 0.21 |  |  | 0.2 | 0.22 | 0.22 | 0.24 |  |  |  | 0.21 | 0.23 | 0.23 | 0.22 | 0.22 |  |  | 0.22 | 0.25 | 0.24 | 0.24 | 0.24 |  |  | 0.23 | 0.24 | 0.24 | 0.23 | 0.22
DEWATERING FILTRATE FIXED SUSPENDED SOLIDS | [5 empty] | 72.73 | 69.57 | 76.19 |  |  | 75 | 68.18 | 72.73 | 70.8 |  |  |  | 66.67 | 65.22 | 65.2 | 68.2 | 68.18 |  |  | 72.7 | 53.6 | 66.67 | 66.67 | 66.7 |  |  | 73.91 | 70.83 | 70.83 | 69.57 | 68.18
DEWATERING FILTRATE pH | [5 empty] | 7.04 | 7.05 | 7.17 |  |  | 7.05 | 7.11 | 7.16 | 7.01 |  |  |  | 6.96 | 7.1 | 7.01 | 6.72 | 6.8 |  |  | 6.78 | 6.89 | 6.89 | 6.58 | 6.92 |  |  | 6.67 | 6.75 | 6.67 | 6.75 | 6.87
| DEWATERED CAKE SLUDGE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
PERCENT TOTAL SOLIDS PRESS CAKE | [5 empty] | 17.8 | 17.99 | 17.44 |  |  | 17.82 | 17.15 | 17.45 | 17.95 |  |  |  | 17.5 | 17.18 | 17.47 | 16.88 | 17.86 |  |  | 17.47 | 17.12 | 17.5 | 16.86 | 2.96 |  |  | 17.47 | 17.47 | 18.66 | 19.37 | 19.43
PERCENT FIXED SOLIDS PRESS CAKE | [5 empty] | 14.16 | 15.73 | 16.57 |  |  | 17.12 | 13.7 | 14.15 | 16.3 |  |  |  | 13.66 | 21.77 | 17.6 | 22.2 | 16.24 |  |  | 21.9 | 14 | 24.29 | 17.56 | 15.4 |  |  | 13.97 | 30.22 | 14.26 | 16.83 | 19.66
PERCENT TOTAL SOLIDS LIME CAKE
OTHER SLUDGE REMOVAL
[6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
GRIT (CU.YDS.) | [5 empty] | 1: 10; 10: 10; 17: 10; 25: 10
RAGS (CU.YDS.) | [5 empty] | 4: 10; 11: 10; 18: 10; 25: 10
VACUUM DEBRIS (EST. GAL)
MONITORING WELLS LABORATORY DATA
| MONITOR WELL ONE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
UPPER LEVEL
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
MONITORING WELLS LABORATORY DATA
| MONITOR WELL TWO |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
UPPER LEVEL
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
MONITORING WELLS LABORATORY DATA
| MONITOR WELL THREE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
FUTURE
UPPER LEVEL
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
MONITORING WELLS LABORATORY DATA
| REGIONAL MONITOR WELL ONE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
UPPER LEVEL
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
MARCH |  | 1 |  | 3
|  | 0 |  | 0
0
0
|  | 0 |  | 0
3
[5 empty] | 1st WEEK | 1: 2nd WEEK; 2: 3rd WEEK; 3: 4th WEEK
| 1 |  | 1 |  | 1 | 1: 8; 2: 15; 3: 23
| 2 |  | 2 |  | 2 | 1: 9; 2: 16; 3: 24
| 3 |  | 3 |  | 3 | 1: 10; 2: 17; 3: 25
| 4 |  | 4 |  | 4 | 1: 11; 2: 18; 3: 26
| 5 |  | 5 |  | 5 | 1: 12; 2: 19; 3: 27
| 6 |  | 6 |  | 6 | 1: 13; 2: 20; 3: 28
| 7 |  | 7 |  | 7 | 1: 14; 2: 21; 3: 29
| 8 |  | 8 |  |  | 2: 22; 3: 30
| 9 |  | 9 |  |  | 3: 31
| 10 |  | 10
| 11 |  | 11
| 12 |  | 12
| 13 |  | 13
| 14 |  | 14
| 15 |  | 15
| 16 |  | 16
| 17 |  | 17
| 18 |  | 18
| 19 |  | 19
| 20 |  | 20
| 21 |  | 21
| 22 |  | 22
| 23 |  | 23
| 24 |  | 24
| 25 |  | 25
| 26 |  | 26
| 27 |  | 27
| 28 |  | 28
29
30
31
| APRIL | MARCH | FEBRUARY
| AUGUST | JULY | JUNE
| DECEMBER | NOVEMBER | OCTOBER
| FEBRUARY | JANUARY | DECEMBER
| JANUARY | DECEMBER | NOVEMBER
| JUNE | MAY | APRIL
| JULY | JUNE | MAY | FEBRUARY
| MARCH | FEBRUARY | JANUARY | JANUARY
| MAY | APRIL | MARCH
| NOVEMBER | OCTOBER | SEPTEMBER
| OCTOBER | SEPTEMBER | AUGUST
| SEPTEMBER | AUGUST | JULY
| HYDROGEN PEROXIDE |  | 0.1465
| CHLORINE |  | 0.295
| POLYMER |  | 0.61
| FPL |  | 0.055
[6 empty] | 1st WEEK |  |  | 2nd WEEK |  |  | 3rd WEEK |  |  | 4th WEEK
[7 empty] | G | H | I | J
[5 empty] | MW1 UP | 1: 311
312
313
314
315
316
317
318

## MONITOR DATA
UNDERGROUND INJECTION CONTROL SECTION
MONTHLY OPERATING REPORT DATA SUMMARY
FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT MONTH/YEAR |  |  |  | MARCH |  | 2005
I.D. NUMBER: 5006M02066 | [5 empty] | LEAD OPERATOR: |  |  |  |  | MIKE JUST
TELEPHONE NUMBER: (954) 523-1002
MONITORING WELL 1 DATA | [6 empty] | I.D. # 5006A11311
MW-1
PERMIT/CERTIFICATION NUMBER | [6 empty] | 0054569-142-UO
PERMIT EXPIRATION DATE |  | 2009-01-06
UPPER MONITORING INTERVAL | [6 empty] | 1,288' - 1,320' |  |  |  |  | Ft. bls.
Sample Date |  | 2005-03-01 |  | 2005-03-08 |  | 2005-03-15 |  | 2005-03-22 |  | 2005-03-29
Submittal Date |  | 2005-03-02 |  | 2005-03-09 |  | 2005-03-16 |  | 2005-03-23 |  | 2005-03-30
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [9 empty] | 48.79 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [9 empty] | 15.87 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 72 |  | 71 |  | 76 |  | 75 |  | 74 |  | degrees (F) |  | 73.6
TDS |  | 7153 |  | 7075 |  | 7475 |  | 8161 |  | 7824 |  | mg/l |  | 7537.6
CHLORIDE |  | 3750 |  | 3700 |  | 3650 |  | 3650 |  | 3650 |  | mg/l |  | 3680
AMMONIA-N |  | 0.95 |  | 0.86 |  | 0.98 |  | 0.86 |  | 1 |  | mg/l |  | 0.93
TKN |  | 1.3 |  | 1 |  | 1.1 |  | 1.2 |  | 1.3 |  | mg/l |  | 1.18
pH |  | 8.35 |  | 8.33 |  | 7.93 |  | 8.06 |  | 7.84 |  | Std units |  | 8.102
CONDUCTIVITY |  | 12150 |  | 12200 |  | 12000 |  | 12080 |  | 12110 |  | umho/cm |  | 12108
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.01 | < | 0.01 | < | 0.01 | < | 0.01 | < | 0.01 |  | mg/l |  | 0.01
SULFATE |  | 735 |  | 760 |  | 793 |  | 963 |  | 1008 |  | mg/l |  | 851.8
C.O.D. 'S | [11 empty] | mg/l |  | #DIV/0!
IRON | [11 empty] | mg/l |  | #DIV/0!
SULFIDE | [11 empty] | mg/l |  | #DIV/0!
LOWER MONITORING INTERVAL | [6 empty] | 1,449' - 1,557' |  |  |  |  | Ft. bls
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [9 empty] | 46.82 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [9 empty] | 11.14 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 70 |  | 70 |  | 73 |  | 73 |  | 73 |  | degrees (F) |  | 71.8
TDS |  | 8698 |  | 9176 |  | 9468 |  | 9662 |  | 9936 |  | mg/l |  | 9388
CHLORIDE |  | 5100 |  | 4800 |  | 5000 |  | 4800 |  | 4800 |  | mg/l |  | 4900
AMMONIA-N |  | 10 |  | 10 |  | 8.9 |  | 8.8 |  | 9.9 |  | mg/l |  | 9.52
TKN |  | 11 |  | 11 |  | 9.8 |  | 9.4 |  | 0.01 |  | mg/l |  | 8.242
pH |  | 7.34 |  | 7.3 |  | 7.2 |  | 7.46 |  | 7.27 |  | Std units |  | 7.314
CONDUCTIVITY |  | 15570 |  | 15580 |  | 15530 |  | 16510 |  | 15600 |  | umho/cm |  | 15758
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.01 |  | 0.012 |  | 0.012 | < | 0.01 |  | 0.011 |  | mg/l |  | 0.011
SULFATE |  | 620 |  | 733 |  | 670 |  | 855 |  | 948 |  | mg/l |  | 765.2
C.O.D. 'S | [11 empty] | mg/l |  | #DIV/0!
IRON | [11 empty] | mg/l |  | #DIV/0!
SULFIDE | [11 empty] | mg/l |  | #DIV/0!
PAGE 24
UNDERGROUND INJECTION CONTROL SECTION
MONTHLY OPERATING REPORT DATA SUMMARY
FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT MONTH/YEAR |  |  |  | MARCH |  | 2005
I.D. NUMBER: 5006M02066 | [5 empty] | LEAD OPERATOR: |  |  |  |  | MIKE JUST
TELEPHONE NUMBER: (954) 523-1002
MONITORING WELL 2 DATA | [6 empty] | I.D. # 5006A11308 & 309
MW-2
PERMIT/CERTIFICATION NUMBER | [6 empty] | 0054569-142-UO
PERMIT EXPIRATION DATE |  | 2009-01-06
UPPER MONITORING INTERVAL | [6 empty] | 1,300' - 1,344' |  |  |  |  | Ft. bls.
Sample Date |  | 2005-03-01 |  | 2005-03-08 |  | 2005-03-15 |  | 2005-03-22 |  | 2005-03-29
Submittal Date |  | 2005-03-02 |  | 2005-03-09 |  | 2005-03-16 |  | 2005-03-23 |  | 2005-03-30
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [9 empty] | 28.8 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [9 empty] | 20.3 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 72 |  | 70 |  | 78 |  | 70 |  | 70 |  | degrees (F) |  | 72
TDS |  | 6727 |  | 7091 |  | 7112 |  | 7437 |  | 7601 |  | mg/l |  | 7193.6
CHLORIDE |  | 3650 |  | 3500 |  | 3550 |  | 3550 |  | 3550 |  | mg/l |  | 3560
AMMONIA-N |  | 0.92 |  | 1 |  | 0.94 |  | 0.89 |  | 0.98 |  | mg/l |  | 0.946
TKN |  | 1.3 |  | 1.6 |  | 1 |  | 1.2 |  | 1.2 |  | mg/l |  | 1.26
pH |  | 7.85 |  | 7.86 |  | 7.88 |  | 8.11 |  | 7.86 |  | Std units |  | 7.912
CONDUCTIVITY |  | 11680 |  | 11700 |  | 11760 |  | 11810 |  | 1182 |  | umho/cm |  | 9626.4
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.01 |  | 0.34 | < | 0.01 | < | 0 | < | 0.01 |  | mg/l |  | 0.074
SULFATE |  | 670 |  | 768 |  | 793 |  | 940 |  | 953 |  | mg/l |  | 824.8
C.O.D. 'S | [11 empty] | mg/l |  | #DIV/0!
IRON | [11 empty] | mg/l |  | #DIV/0!
SULFIDE | [11 empty] | mg/l |  | #DIV/0!
LOWER MONITORING INTERVAL | [6 empty] | 1,970' - 2,025' |  |  |  |  | Ft. bls
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [9 empty] | 43.09 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [9 empty] | 34.46 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 70 |  | 69 |  | 78 |  | 70 |  | 69 |  | degrees (F) |  | 71.2
TDS |  | 30085 |  | 31234 |  | 31248 |  | 32366 |  | 32934 |  | mg/l |  | 31573.4
CHLORIDE |  | 18200 |  | 16200 |  | 16400 |  | 16400 |  | 16200 |  | mg/l |  | 16680
AMMONIA-N |  | 1.5 |  | 1.5 |  | 1.5 |  | 1.3 |  | 1.5 |  | mg/l |  | 1.46
TKN |  | 2.3 |  | 2.6 |  | 2.4 |  | 2 |  | 1.6 |  | mg/l |  | 2.18
pH |  | 7.52 |  | 7.49 |  | 7.47 |  | 7.53 |  | 7.4 |  | Std units |  | 7.482
CONDUCTIVITY |  | 46700 |  | 46500 |  | 46300 |  | 46500 |  | 46800 |  | umho/cm |  | 46560
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.01 |  | 0.016 | < | 0.01 | < | 0.01 | < | 0.01 |  | mg/l |  | 0.0112
SULFATE |  | 2300 |  | 2260 |  | 2350 |  | 3100 |  | 3460 |  | mg/l |  | 2694
C.O.D. 'S | [11 empty] | mg/l |  | #DIV/0!
IRON | [11 empty] | mg/l |  | #DIV/0!
SULFIDE | [11 empty] | mg/l |  | #DIV/0!
PAGE 25
UNDERGROUND INJECTION CONTROL SECTION
MONTHLY OPERATING REPORT DATA SUMMARY
FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT MONTH/YEAR |  |  |  | MARCH |  | 2005
I.D. NUMBER: 5006M02066 | [5 empty] | LEAD OPERATOR: |  |  |  |  | MIKE JUST
TELEPHONE NUMBER: (954) 523-1002
MONITORING WELL 2 DATA | [6 empty] | I.D. # 5006A11310
MW-3
PERMIT/CERTIFICATION NUMBER | [6 empty] | 0054569-142-UO
PERMIT EXPIRATION DATE |  | 2009-01-06
UPPER MONITORING INTERVAL | [6 empty] | 1,300' - 1,349' |  |  |  |  | Ft. bls.
Sample Date |  | 2005-03-01 |  | 2005-03-08 |  | 2005-03-15 |  | 2005-03-22 |  | 2005-03-29
Submittal Date |  | 2005-03-02 |  | 2005-03-09 |  | 2005-03-16 |  | 2005-03-23 |  | 2005-03-30
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [9 empty] | 33.21 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [9 empty] | 17.6 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 70 |  | 72 |  | 77 |  | 72 |  | 70 |  | degrees (F) |  | 72.2
TDS |  | 7085 |  | 7208 |  | 7543 |  | 7479 |  | 7925 |  | mg/l |  | 7448
CHLORIDE |  | 3700 |  | 3550 |  | 3550 |  | 3650 |  | 3600 |  | mg/l |  | 3610
AMMONIA-N |  | 0.97 |  | 1 |  | 2.5 |  | 0.87 |  | 0.98 |  | mg/l |  | 1.264
TKN |  | 1.4 |  | 1.1 |  | 3.3 |  | 1.1 |  | 1.3 |  | mg/l |  | 1.64
pH |  | 8.29 |  | 8.22 |  | 8.17 |  | 8.12 |  | 7.96 |  | Std units |  | 8.152
CONDUCTIVITY |  | 11880 |  | 12000 |  | 11820 |  | 12270 |  | 12120 |  | umho/cm |  | 12018
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.01 | < | 0.01 |  | 0.018 | < | 0.01 | < | 0.01 |  | mg/l |  | 0.0116
SULFATE |  | 760 |  | 790 |  | 1000 |  | 998 |  | 1028 |  | mg/l |  | 915.2
C.O.D. 'S | [11 empty] | mg/l |  | #DIV/0!
IRON | [11 empty] | mg/l |  | #DIV/0!
SULFIDE | [11 empty] | mg/l |  | #DIV/0!
LOWER MONITORING INTERVAL | [6 empty] | 1,970' - 2,027' |  |  |  |  | Ft. bls
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [9 empty] | 45.88 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [9 empty] | 35.6 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 69 |  | 70 |  | 75 |  | 69 |  | 68 |  | degrees (F) |  | 70.2
TDS |  | 26719 |  | 7387 |  | 27687 |  | 29317 |  | 29464 |  | mg/l |  | 24114.8
CHLORIDE |  | 14600 |  | 14600 |  | 14600 |  | 14800 |  | 14600 |  | mg/l |  | 14640
AMMONIA-N |  | 2.6 |  | 2.7 |  | 0.96 |  | 2.5 |  | 2.4 |  | mg/l |  | 2.232
TKN |  | 3.9 |  | 3.7 |  | 1.3 |  | 3.5 |  | 2.7 |  | mg/l |  | 3.02
pH |  | 7.43 |  | 7.43 |  | 7.37 |  | 7.51 |  | 7.32 |  | Std units |  | 7.412
CONDUCTIVITY |  | 42500 |  | 42600 |  | 42600 |  | 42600 |  | 42800 |  | umho/cm |  | 42620
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.01 |  | 0.019 | < | 0.01 | < | 0.01 |  | 0.011 |  | mg/l |  | 0.012
SULFATE |  | 2170 |  | 2170 |  | 1880 |  | 2990 |  | 3170 |  | mg/l |  | 2476
C.O.D. 'S | [11 empty] | mg/l |  | #DIV/0!
IRON | [11 empty] | mg/l |  | #DIV/0!
SULFIDE | [11 empty] | mg/l |  | #DIV/0!
PAGE 26
UNDERGROUND INJECTION CONTROL SECTION
MONTHLY OPERATING REPORT DATA SUMMARY
FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT MONTH/YEAR |  |  |  | MARCH |  | 2005
I.D. NUMBER: 5006M02066 | [5 empty] | LEAD OPERATOR: |  |  |  |  | MIKE JUST
TELEPHONE NUMBER: (954) 523-1002
REGIONAL MONITORING WELL DATA
RMW-1
PERMIT NUMBER | [6 empty] | 0054569-142-UO
PERMIT EXPIRATION DATE |  | 2009-01-06
UPPER MONITORING INTERVAL | [6 empty] | 1300' - 1339' |  |  |  |  | Ft. bls.
Sample Date | [5 empty] | 2005-03-15
Submittal Date |  | 1899-12-31 |  |  |  | 2005-03-16
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [9 empty] | 63.95 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [9 empty] | 12.72 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) | [5 empty] | 76 | [5 empty] | degrees (F) |  | 76
TDS | [5 empty] | 5417 | [5 empty] | mg/l |  | 5417
CHLORIDE | [5 empty] | 2700 | [5 empty] | mg/l |  | 2700
AMMONIA-N | [5 empty] | 0.72 | [5 empty] | mg/l |  | 0.72
TKN | [5 empty] | 0.89 | [5 empty] | mg/l |  | 0.89
pH | [5 empty] | 8 | [5 empty] | Std units |  | 8
CONDUCTIVITY | [5 empty] | 9210 | [5 empty] | umho/cm |  | 9210
FECAL COLIFORM | [5 empty] | 0 | [5 empty] | # col/100ml |  | 0
TOTAL PHOSPHOROUS | [5 empty] | 0.013 | [5 empty] | mg/l |  | 0.013
SULFATE | [5 empty] | 650 | [5 empty] | mg/l |  | 650
C.O.D. 'S | [11 empty] | mg/l |  | #DIV/0!
IRON | [11 empty] | mg/l |  | #DIV/0!
SULFIDE | [11 empty] | mg/l |  | #DIV/0!
LOWER MONITORING INTERVAL | [6 empty] | 1500' - 1600' |  |  |  |  | Ft. bls
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [9 empty] | 64.76 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [9 empty] | 12.43 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) | [5 empty] | 74 | [5 empty] | degrees (F) |  | 74
TDS | [5 empty] | 26230 | [5 empty] | mg/l |  | 26230
CHLORIDE | [5 empty] | 14200 | [5 empty] | mg/l |  | 14200
AMMONIA-N | [5 empty] | 0.37 | [5 empty] | mg/l |  | 0.37
TKN | [5 empty] | 0.91 | [5 empty] | mg/l |  | 0.91
pH | [5 empty] | 7.49 | [5 empty] | Std units |  | 7.49
CONDUCTIVITY | [5 empty] | 40500 | [5 empty] | umho/cm |  | 40500
FECAL COLIFORM | [5 empty] | 0 | [5 empty] | # col/100ml |  | 0
TOTAL PHOSPHOROUS | [5 empty] | 0.01 | [5 empty] | mg/l |  | 0.01
SULFATE | [5 empty] | 1180 | [5 empty] | mg/l |  | 1180
C.O.D. 'S | [11 empty] | mg/l |  | #DIV/0!
IRON | [11 empty] | mg/l |  | #DIV/0!
SULFIDE | [11 empty] | mg/l |  | #DIV/0!
PAGE 27
Formulas:
LEAD OPERATOR: = [LEAD OPERATOR:, row above]+1

## WELL PRN DATA
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 1 |  |  | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90
60 | 11.49 | 4.33 | 8.1 | 56.34 | 38.2 | 46.66
61 | 12 | 4.94 | 8.36 | 59.05 | 39.96 | 47.36 |  |  | FLOW
62 | ER | ER | ER | ER | ER | ER | I |  | MAX | 11.49 | 12 | ER | 11.68 | 11.78 | ER | ER | 11.78 | 10.59 | 16.87 | 12.88 | 0 | 0 | 12.65 | 12.26 | 12.23 | 13.22 | 13.5 | 12.14 | 12.01 | 11.93 | 14.79 | 12.68 | 12.02 | 11.88 | 11.74 | 10.76 | 12.15 | 11.18 | 11.59 | 11.68
63 | 11.68 | ER | 6.7 | 56.83 | 34.35 | 45.82 | N |  | MIN | 4.33 | 4.94 | ER | ER | 5.26 | ER | ER | 0 | ER | ER | 0 | ER | ER | 0 | 0 | 0 | 5.23 | 6.1 | ER | 5.86 | 5.32 | 0 | 0 | 0 | 5.78 | 6.08 | 0 | ER | 0 | 5.6 | 5.49
64 | 11.78 | 5.26 | 8.85 | 57.24 | 40.22 | 48.64 | J |  | TOT | 8.1 | 8.36 | ER | 6.7 | 8.85 | ER | ER | 7.17 | 1.88 | 6.95 | 2.96 | 0 | 0 | 2.99 | 7.12 | 7.36 | 9.79 | 10.4 | 8.39 | 9.68 | 9.57 | 2.86 | 7.52 | 7.76 | 9.1 | 8.84 | 2.05 | 7.26 | 7.41 | 8.75 | 8.62
65 | ER | ER | ER | ER | ER | ER | E | INJECTION WELL ONE
66 | ER | ER | ER | ER | ER | ER | C |  | PSI
67 | 11.78 | 0 | 7.17 | 57.61 | 34.26 | 45.96 | T |  | MAX | 56.34 | 59.05 | ER | 56.83 | 57.24 | ER | ER | 57.61 | 54.26 | 79.7 | 63.5 | 35.2 | 35.01 | 63.22 | 58.47 | 58.1 | 62.21 | 63.09 | 57.6 | 57.57 | 57.42 | 67.66 | 60.07 | 57.71 | 57.46 | 57.55 | 55.68 | 58.07 | 54.94 | 56.77 | 57.06
68 | 10.59 | ER | 1.88 | 54.26 | 34.16 | 37.78 | O |  | MIN | 38.2 | 39.96 | ER | 34.35 | 40.22 | ER | ER | 34.26 | 34.16 | 34.12 | 34.11 | 33.58 | 33.74 | 33.63 | 33.82 | 34.03 | 40.02 | 42.21 | 34.4 | 41.4 | 40.69 | 34.85 | 34.51 | 34.28 | 41.13 | 42.19 | 35.09 | 26.35 | 34.09 | 40.96 | 41.01
69 | 16.87 | ER | 6.95 | 79.7 | 34.12 | 47.46 | N |  | AVG | 46.66 | 47.36 | ER | 45.82 | 48.64 | ER | ER | 45.96 | 37.78 | 47.46 | 39.15 | 34.51 | 34.44 | 39.37 | 46.04 | 46.82 | 51.07 | 53.5 | 49.17 | 50.83 | 50.65 | 39.64 | 47.74 | 47.45 | 49.48 | 48.88 | 38.21 | 46.93 | 46.58 | 48.51 | 48.35
70 | 12.88 | 0 | 2.96 | 63.5 | 34.11 | 39.15
71 | 0 | ER | 0 | 35.2 | 33.58 | 34.51 | W
72 | 0 | ER | 0 | 35.01 | 33.74 | 34.44 | E
73 | 12.65 | 0 | 2.99 | 63.22 | 33.63 | 39.37 | L
74 | 12.26 | 0 | 7.12 | 58.47 | 33.82 | 46.04 | L
75 | 12.23 | 0 | 7.36 | 58.1 | 34.03 | 46.82 | O
76 | 13.22 | 5.23 | 9.79 | 62.21 | 40.02 | 51.07 | N
77 | 13.5 | 6.1 | 10.4 | 63.09 | 42.21 | 53.5 | E
78 | 12.14 | ER | 8.39 | 57.6 | 34.4 | 49.17
79 | 12.01 | 5.86 | 9.68 | 57.57 | 41.4 | 50.83 | D
80 | 11.93 | 5.32 | 9.57 | 57.42 | 40.69 | 50.65 | A
81 | 14.79 | 0 | 2.86 | 67.66 | 34.85 | 39.64 | T
82 | 12.68 | 0 | 7.52 | 60.07 | 34.51 | 47.74 | A
83 | 12.02 | 0 | 7.76 | 57.71 | 34.28 | 47.45
84 | 11.88 | 5.78 | 9.1 | 57.46 | 41.13 | 49.48
85 | 11.74 | 6.08 | 8.84 | 57.55 | 42.19 | 48.88
86 | 10.76 | 0 | 2.05 | 55.68 | 35.09 | 38.21
87 | 12.15 | ER | 7.26 | 58.07 | 26.35 | 46.93
88 | 11.18 | 0 | 7.41 | 54.94 | 34.09 | 46.58
89 | 11.59 | 5.6 | 8.75 | 56.77 | 40.96 | 48.51
90 | 11.68 | 5.49 | 8.62 | 57.06 | 41.01 | 48.35
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 2 |  |  | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90
60 | 11.66 | 0.04 | 7.22 | 55.36 | 34.69 | 44.78
61 | 12.49 | 5.05 | 8.53 | 57.99 | 39.21 | 46.51 |  |  | FLOW
62 | ER | ER | ER | ER | ER | ER | I |  | MAX | 11.66 | 12.49 | ER | 12.33 | 12.03 | ER | ER | 11.9 | 15.73 | 17 | 14.71 | 12.79 | 12.78 | 13.02 | 12.46 | 12.23 | 13.33 | 13.48 | 12.33 | 12.09 | 12.06 | 15.14 | 13.04 | 12.28 | 12.05 | 11.97 | 12.68 | 9.6 | 11.37 | 11.79 | 11.85
63 | 12.33 | 7.05 | 9.68 | 56.83 | 42.33 | 49.33 | N |  | MIN | 0.04 | 5.05 | ER | 7.05 | 5.4 | ER | ER | 4.17 | 4.52 | 4.13 | 4.2 | 0.04 | 6.48 | 6.08 | 5.49 | 0.05 | 0.05 | 0.04 | 0.04 | 0.04 | 5.37 | 0.05 | 0.05 | 0.05 | 0.04 | 6.13 | 4.97 | 0.04 | 0.05 | 0.04 | 5.49
64 | 12.03 | 5.4 | 9.02 | 56.49 | 39.48 | 47.81 | J |  | TOT | 7.22 | 8.53 | ER | 9.68 | 9.02 | ER | ER | 8.46 | 9.62 | 10.41 | 9.62 | 8.18 | 10.07 | 9.68 | 9.28 | 3.62 | 3 | 7.51 | 7.78 | 8.09 | 9.73 | 9.98 | 2.36 | 7.27 | 7.72 | 8.98 | 9.27 | 0.8 | 6.94 | 7.42 | 8.77
65 | ER | ER | ER | ER | ER | ER | E | INJECTION WELL TWO
66 | ER | ER | ER | ER | ER | ER | C |  | PSI
67 | 11.9 | 4.17 | 8.46 | 56.64 | 37.71 | 46.67 | T |  | MAX | 55.36 | 57.99 | ER | 56.83 | 56.49 | ER | ER | 56.64 | 70.3 | 78.4 | 64.93 | 57.69 | 57.71 | 62.95 | 57.59 | 56.18 | 61.14 | 61.84 | 56.61 | 56.52 | 56.51 | 66.59 | 60.48 | 56.76 | 56.6 | 56.68 | 58.01 | 50.08 | 53.97 | 55.78 | 56.09
68 | 15.73 | 4.52 | 9.62 | 70.3 | 38.24 | 49.41 | I |  | MIN | 34.69 | 39.21 | ER | 42.33 | 39.48 | ER | ER | 37.71 | 38.24 | 37.38 | 37.32 | 34.36 | 41 | 40.07 | 39.32 | 35.36 | 34.6 | 35.76 | 34.79 | 35.1 | 39.96 | 36.31 | 35.63 | 34.54 | 35.19 | 41.48 | 39.41 | 31.54 | 34.43 | 34.99 | 40.27
69 | 17 | 4.13 | 10.41 | 78.4 | 37.38 | 51.67 | O |  | AVG | 44.78 | 46.51 | ER | 49.33 | 47.81 | ER | ER | 46.67 | 49.41 | 51.67 | 49.37 | 47.55 | 49.77 | 49.13 | 48.08 | 40.27 | 40.49 | 47.68 | 47.47 | 47.59 | 49.81 | 50.8 | 38.86 | 46.11 | 46.87 | 48.12 | 48.57 | 36.96 | 45.27 | 45.96 | 47.55
70 | 14.71 | 4.2 | 9.62 | 64.93 | 37.32 | 49.37 | N
71 | 12.79 | 0.04 | 8.18 | 57.69 | 34.36 | 47.55
72 | 12.78 | 6.48 | 10.07 | 57.71 | 41 | 49.77 | W
73 | 13.02 | 6.08 | 9.68 | 62.17 | 40.07 | 49.13 | E
74 | 12.46 | 5.49 | 9.28 | 57.59 | 39.32 | 48.08 | L
75 | 12.23 | 0.05 | 3.62 | 56.18 | 35.36 | 40.27 | L
76 | 13.33 | 0.05 | 3 | 61.14 | 34.6 | 40.49
77 | 13.48 | 0.04 | 7.51 | 61.84 | 35.76 | 47.68 | T
78 | 12.33 | 0.04 | 7.78 | 56.61 | 34.79 | 47.47 | W
79 | 12.09 | 0.04 | 8.09 | 56.52 | 35.1 | 47.59 | O
80 | 12.06 | 5.37 | 9.73 | 56.51 | 39.96 | 49.81
81 | 15.14 | 0.05 | 9.98 | 66.59 | 36.31 | 50.8 | D
82 | 13.04 | 0.05 | 2.36 | 60.48 | 35.63 | 38.86 | A
83 | 12.28 | 0.05 | 7.27 | 56.76 | 34.54 | 46.11 | T
84 | 12.05 | 0.04 | 7.72 | 56.6 | 35.19 | 46.87 | A
85 | 11.97 | 6.13 | 8.98 | 56.68 | 41.48 | 48.12
86 | 12.68 | 4.97 | 9.27 | 58.01 | 39.41 | 48.57
87 | 9.6 | 0.04 | 0.8 | 50.08 | 31.54 | 36.96
88 | 11.37 | 0.05 | 6.94 | 53.97 | 34.43 | 45.27
89 | 11.79 | 0.04 | 7.42 | 55.78 | 34.99 | 45.96
90 | 11.85 | 5.49 | 8.77 | 56.09 | 40.27 | 47.55
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 3 |  |  | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90
60 | 11.09 | 4.57 | 8.08 | 56.66 | 38.37 | 46.88
61 | 10.73 | ER | 6.1 | 55.18 | 34.79 | 44.64 |  |  | FLOW
62 | ER | ER | ER | ER | ER | ER | I |  | MAX | 11.09 | 10.73 | ER | 11.42 | 11.42 | ER | ER | 11.19 | 14.05 | 15.72 | 13.11 | 12.91 | 11.59 | 11.49 | ER | 11.3 | 12.49 | 12.57 | 12.11 | 11.5 | 11.32 | 13.62 | 12.03 | 9.15 | 11.49 | 11.3 | 11.46 | 11.28 | 9.1 | 11.23 | 11.16
63 | 11.42 | 6.98 | 9.31 | 58.12 | 43.3 | 50.44 | N |  | MIN | 4.57 | ER | ER | 6.98 | ER | ER | ER | 4.5 | 4.86 | 4.24 | 4.51 | 6.68 | 6.24 | ER | ER | ER | 5.32 | 6.21 | ER | ER | ER | ER | 5.93 | ER | ER | ER | 5.13 | 4.85 | ER | ER | ER
64 | 11.42 | ER | 6.29 | 57.54 | 34.89 | 45.39 | J |  | TOT | 8.08 | 6.1 | ER | 9.31 | 6.29 | ER | ER | 8.15 | 8.92 | 9.78 | 8.95 | 9.67 | 9.27 | 6.09 | ER | 5.65 | 9.36 | 9.94 | 2.67 | 7.13 | 7.75 | 9.28 | 9.32 | 2.21 | 6.85 | 7.24 | 8.71 | 8.94 | 2.12 | 6.6 | 7.08
65 | ER | ER | ER | ER | ER | ER | E | INJECTION WELL THREE
66 | ER | ER | ER | ER | ER | ER | C |  | PSI
67 | 11.19 | 4.5 | 8.15 | 57.84 | 38.56 | 47.67 | T |  | MAX | 56.66 | 55.18 | ER | 58.12 | 57.54 | ER | ER | 57.84 | 71.9 | 80.2 | 66.04 | 64.75 | 58.87 | 58.96 | 37.72 | 58.24 | 62.47 | 63.24 | 61.27 | 57.69 | 57.65 | 66.55 | 61.65 | 49.49 | 57.71 | 57.7 | 58.99 | 58.2 | 49.44 | 56.99 | 57.25
68 | 14.05 | 4.86 | 8.92 | 71.9 | 39.11 | 50.49 | I |  | MIN | 38.37 | 34.79 | ER | 43.3 | 34.89 | ER | ER | 38.56 | 39.11 | 38.25 | 38.19 | 42.78 | 41.93 | 36.16 | 35.28 | 35.44 | 40.15 | 42.36 | 36.43 | 35.67 | 35.46 | 36.59 | 41.51 | 36.26 | 35.62 | 35.66 | 40.24 | 32.2 | 36.69 | 35.42 | 35.49
69 | 15.72 | 4.24 | 9.78 | 80.2 | 38.25 | 52.8 | O |  | AVG | 46.88 | 44.64 | ER | 50.44 | 45.39 | ER | ER | 47.67 | 50.49 | 52.8 | 50.4 | 52.1 | 50.8 | 45.82 | 36.65 | 45.34 | 51.21 | 53.71 | 41.48 | 47.83 | 48.7 | 51.65 | 51.06 | 39.85 | 47.05 | 47.29 | 49.51 | 50.15 | 39.63 | 46.27 | 46.83
70 | 13.11 | 4.51 | 8.95 | 66.04 | 38.19 | 50.4 | N
71 | 12.91 | 6.68 | 9.67 | 64.75 | 42.78 | 52.1
72 | 11.59 | 6.24 | 9.27 | 58.87 | 41.93 | 50.8 | W
73 | 11.49 | ER | 6.09 | 58.96 | 36.16 | 45.82 | E
74 | ER | ER | ER | 37.72 | 35.28 | 36.65 | L
75 | 11.3 | ER | 5.65 | 58.24 | 35.44 | 45.34 | L
76 | 12.49 | 5.32 | 9.36 | 62.47 | 40.15 | 51.21
77 | 12.57 | 6.21 | 9.94 | 63.24 | 42.36 | 53.71 | T
78 | 12.11 | ER | 2.67 | 61.27 | 36.43 | 41.48 | H
79 | 11.5 | ER | 7.13 | 57.69 | 35.67 | 47.83 | R
80 | 11.32 | ER | 7.75 | 57.65 | 35.46 | 48.7 | E
81 | 13.62 | ER | 9.28 | 66.55 | 36.59 | 51.65 | E
82 | 12.03 | 5.93 | 9.32 | 61.65 | 41.51 | 51.06
83 | 9.15 | ER | 2.21 | 49.49 | 36.26 | 39.85 | D
84 | 11.49 | ER | 6.85 | 57.71 | 35.62 | 47.05 | A
85 | 11.3 | ER | 7.24 | 57.7 | 35.66 | 47.29 | T
86 | 11.46 | 5.13 | 8.71 | 58.99 | 40.24 | 49.51 | A
87 | 11.28 | 4.85 | 8.94 | 58.2 | 32.2 | 50.15
88 | 9.1 | ER | 2.12 | 49.44 | 36.69 | 39.63
89 | 11.23 | ER | 6.6 | 56.99 | 35.42 | 46.27
90 | 11.16 | ER | 7.08 | 57.25 | 35.49 | 46.83
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 4 |  |  | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90
60 | 0.03 | 0.01 | 0.02 | 37.18 | ER | ER
61 | 0.03 | 0.01 | 0.02 | 37.21 | 34.75 | 36.03 |  |  | FLOW
62 | ER | ER | ER | ER | ER | ER | I |  | MAX | 0.03 | 0.03 | ER | 0.03 | 0.04 | ER | ER | 12.03 | 14.73 | 16.63 | 13.64 | 13.34 | 11.81 | 12.51 | 12.04 | 11.88 | 13.08 | 13.24 | 12.27 | 11.71 | 11.83 | 14.03 | 12.48 | 11.79 | 10.13 | 11.75 | 11.63 | 11.44 | 10.98 | 8.99 | 11.64
63 | 0.03 | 0.01 | 0.01 | 37.23 | 35.47 | 36.41 | N |  | MIN | 0.01 | 0.01 | ER | 0.01 | 0.01 | ER | ER | 4.97 | 5.35 | 4.92 | 4.92 | 6.9 | 6.53 | 6.3 | 5.63 | 6.47 | 5.7 | 6.6 | 7.26 | 0.01 | 0.02 | 0.03 | 6.06 | 5.16 | 0.03 | 0.03 | 0.03 | 4.96 | 5.99 | 0.02 | 0.03
64 | 0.04 | 0.01 | 0.02 | 37.43 | 34.84 | 36.17 | J |  | TOT | 0.02 | 0.02 | ER | 0.01 | 0.02 | ER | ER | 8.78 | 9.42 | 10.42 | 9.35 | 9.99 | 9.55 | 9.3 | 9.12 | 9.33 | 9.67 | 10.37 | 10.26 | 2.42 | 7.44 | 7.79 | 9.47 | 9.3 | 2.22 | 6.93 | 7.45 | 9.05 | 8.9 | 2.11 | 6.79
65 | ER | ER | ER | ER | ER | ER | E | INJECTION WELL FOUR
66 | ER | ER | ER | ER | ER | ER | C |  | PSI
67 | 12.03 | 4.97 | 8.78 | 58.25 | 39.25 | 48.22 | T |  | MAX | 37.18 | 37.21 | ER | 37.23 | 37.43 | ER | ER | 58.25 | 72.1 | 80.5 | 66.53 | 65.24 | 59.47 | 79.7 | 59.45 | 58.77 | 62.99 | 63.81 | 61.82 | 58.41 | 58.19 | 67.04 | 62.15 | 58.6 | 53.28 | 58.33 | 59.68 | 58.79 | 55.84 | 48.92 | 57.8
68 | 14.73 | 5.35 | 9.42 | 72.1 | 39.83 | 51.04 | I |  | MIN | ER | 34.75 | ER | 35.47 | 34.84 | ER | ER | 39.25 | 39.83 | 38.98 | 38.94 | 43.44 | 42.64 | 41.66 | 40.89 | 42.76 | 40.83 | 43.03 | 44.96 | 35.85 | 35.5 | 35.38 | 42.23 | 40.43 | 36.69 | 35.69 | 35.73 | 32.44 | 42.52 | 36.45 | 35.48
69 | 16.63 | 4.92 | 10.42 | 80.5 | 38.98 | 53.35 | O |  | AVG | ER | 36.03 | ER | 36.41 | 36.17 | ER | ER | 48.22 | 51.04 | 53.35 | 51 | 52.67 | 51.47 | 50.8 | 49.8 | 50.63 | 51.85 | 54.3 | 53.71 | 40.33 | 48.36 | 49.84 | 51.69 | 50.73 | 39.81 | 46.93 | 48.18 | 50.78 | 49.76 | 39.53 | 46.67
70 | 13.64 | 4.92 | 9.35 | 66.53 | 38.94 | 51 | N
71 | 13.34 | 6.9 | 9.99 | 65.24 | 43.44 | 52.67
72 | 11.81 | 6.53 | 9.55 | 59.47 | 42.64 | 51.47 | W
73 | 12.51 | 6.3 | 9.3 | 64.15 | 41.66 | 50.8 | E
74 | 12.04 | 5.63 | 9.12 | 59.45 | 40.89 | 49.8 | L
75 | 11.88 | 6.47 | 9.33 | 58.77 | 42.76 | 50.63 | L
76 | 13.08 | 5.7 | 9.67 | 62.99 | 40.83 | 51.85
77 | 13.24 | 6.6 | 10.37 | 63.81 | 43.03 | 54.3 | F
78 | 12.27 | 7.26 | 10.26 | 61.82 | 44.96 | 53.71 | O
79 | 11.71 | 0.01 | 2.42 | 58.41 | 35.85 | 40.33 | U
80 | 11.83 | 0.02 | 7.44 | 58.19 | 35.5 | 48.36 | R
81 | 14.03 | 0.03 | 7.79 | 67.04 | 35.38 | 49.84
82 | 12.48 | 6.06 | 9.47 | 62.15 | 42.23 | 51.69 | D
83 | 11.79 | 5.16 | 9.3 | 58.6 | 40.43 | 50.73 | A
84 | 10.13 | 0.03 | 2.22 | 53.28 | 36.69 | 39.81 | T
85 | 11.75 | 0.03 | 6.93 | 58.33 | 35.69 | 46.93 | A
86 | 11.63 | 0.03 | 7.45 | 59.68 | 35.73 | 48.18
87 | 11.44 | 4.96 | 9.05 | 58.79 | 32.44 | 50.78
88 | 10.98 | 5.99 | 8.9 | 55.84 | 42.52 | 49.76
89 | 8.99 | 0.02 | 2.11 | 48.92 | 36.45 | 39.53
90 | 11.64 | 0.03 | 6.79 | 57.8 | 35.48 | 46.67
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 5 |  |  | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90
60 | 10.88 | 4.73 | 8.02 | 56.36 | 38.36 | 46.68
61 | 11.62 | ER | ER | 61.11 | ER | ER |  |  | FLOW
62 | ER | ER | ER | ER | ER | ER | I |  | MAX | 10.88 | 11.62 | ER | 11.12 | 11.23 | ER | ER | ER | 13.54 | 12.34 | 12.6 | 12.31 | 11.1 | 11.67 | 11.21 | 10.95 | 10.79 | 11.9 | 11.48 | 11.21 | 11.18 | 13.84 | 11.25 | 11.03 | 11.17 | 9.85 | 10.95 | 10.81 | 10.25 | 10.97 | 8.41
63 | 11.12 | 6.88 | 9.14 | 57.73 | 43.08 | 50.12 | N |  | MIN | 4.73 | ER | ER | 6.88 | 5.65 | ER | ER | ER | ER | ER | ER | 6.46 | ER | ER | 5.32 | ER | ER | ER | 6.87 | 6.03 | ER | ER | ER | 4.97 | 5.81 | ER | ER | ER | 5.74 | 5.61 | ER
64 | 11.23 | 5.65 | 8.69 | 57.06 | 40.24 | 48.54 | J |  | TOT | 8.02 | ER | ER | 9.14 | 8.69 | ER | ER | ER | 5.64 | 1.9 | 6.62 | 9.29 | 6.79 | 6.9 | 8.51 | 8.29 | 4.3 | 2.72 | 9.6 | 9.23 | 2.21 | 6.89 | 7.42 | 8.75 | 8.77 | 2.11 | 6.35 | 8.45 | 8.39 | 8.45 | 2.01
65 | ER | ER | ER | ER | ER | ER | E | INJECTION WELL FIVE
66 | ER | ER | ER | ER | ER | ER | C |  | PSI
67 | ER | ER | ER | 36.47 | 34.29 | 35.35 | T |  | MAX | 56.36 | 61.11 | ER | 57.73 | 57.06 | ER | ER | 36.47 | 71.4 | 65.04 | 65.64 | 64.56 | 58.37 | 63.14 | 58.29 | 57.79 | 57.41 | 62.95 | 61 | 57.51 | 57.3 | 67.43 | 59.79 | 57.58 | 57.22 | 52.93 | 58.63 | 57.82 | 54.86 | 56.47 | 47.16
68 | 13.54 | ER | 5.64 | 71.4 | 34.17 | 46.05 | I |  | MIN | 38.36 | ER | ER | 43.08 | 40.24 | ER | ER | 34.29 | 34.17 | 34.28 | 34.21 | 42.61 | 34.88 | 34.91 | 39.98 | 35.59 | 34.9 | 35.23 | 44.08 | 41.34 | 35.24 | 33.99 | 35.21 | 39.46 | 41.03 | 35.53 | 34.12 | 27.01 | 41.62 | 40.94 | 35.52
69 | 12.34 | ER | 1.9 | 65.04 | 34.28 | 38.89 | O |  | AVG | 46.68 | ER | ER | 50.12 | 48.54 | ER | ER | 35.35 | 46.05 | 38.89 | 47.3 | 51.8 | 47.4 | 47.36 | 48.79 | 48.97 | 43.16 | 41.38 | 52.73 | 50.69 | 38.86 | 48.44 | 48.62 | 49.7 | 49.26 | 38.56 | 46.28 | 49.72 | 48.74 | 48.33 | 38.33
70 | 12.6 | ER | 6.62 | 65.64 | 34.21 | 47.3 | N
71 | 12.31 | 6.46 | 9.29 | 64.56 | 42.61 | 51.8
72 | 11.1 | ER | 6.79 | 58.37 | 34.88 | 47.4 | W
73 | 11.67 | ER | 6.9 | 63.14 | 34.91 | 47.36 | E
74 | 11.21 | 5.32 | 8.51 | 58.29 | 39.98 | 48.79 | L
75 | 10.95 | ER | 8.29 | 57.79 | 35.59 | 48.97 | L
76 | 10.79 | ER | 4.3 | 57.41 | 34.9 | 43.16
77 | 11.9 | ER | 2.72 | 62.95 | 35.23 | 41.38 | F
78 | 11.48 | 6.87 | 9.6 | 61 | 44.08 | 52.73 | I
79 | 11.21 | 6.03 | 9.23 | 57.51 | 41.34 | 50.69 | V
80 | 11.18 | ER | 2.21 | 57.3 | 35.24 | 38.86 | E
81 | 13.84 | ER | 6.89 | 67.43 | 33.99 | 48.44
82 | 11.25 | ER | 7.42 | 59.79 | 35.21 | 48.62 | D
83 | 11.03 | 4.97 | 8.75 | 57.58 | 39.46 | 49.7 | A
84 | 11.17 | 5.81 | 8.77 | 57.22 | 41.03 | 49.26 | T
85 | 9.85 | ER | 2.11 | 52.93 | 35.53 | 38.56 | A
86 | 10.95 | ER | 6.35 | 58.63 | 34.12 | 46.28
87 | 10.81 | ER | 8.45 | 57.82 | 27.01 | 49.72
88 | 10.25 | 5.74 | 8.39 | 54.86 | 41.62 | 48.74
89 | 10.97 | 5.61 | 8.45 | 56.47 | 40.94 | 48.33
90 | 8.41 | ER | 2.01 | 47.16 | 35.52 | 38.33

## RMW PRN DATA
julian | u-avg | u-min | u-max | l-avg | l-min | l-max
60 | 23 | 22.93 | 23.11 | 44.51 | 44.45 | 44.59 | R |  |  | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90
61 | 22.91 | 22.84 | 22.99 | 44.42 | 44.38 | 44.47 | E
62 | 22.93 | 22.87 | 22.98 | 44.45 | 44.39 | 44.48 | G |  | LOW
63 | 22.96 | 22.83 | 23.08 | 44.48 | 44.38 | 44.57 | I |  | MIN | 22.93 | 22.84 | 22.87 | 22.83 | 22.79 | 22.8 | 22.82 | 23 | 22.98 | 23.05 | 23.03 | 22.98 | 22.98 | 20.53 | 20.8 | 12.43 | 22.24 | 22.34 | 22.35 | 22.38 | 22.44 | 22.52 | 22.53 | 22.5 | 22.54 | 22.62 | 22.7 | 22.72 | 22.65 | 22.62 | 22.59
64 | 22.89 | 22.79 | 22.98 | 44.41 | 44.35 | 44.48 | O |  | MAX | 23.11 | 22.99 | 22.98 | 23.08 | 22.98 | 22.91 | 23.03 | 23.12 | 23.22 | 23.18 | 23.13 | 23.09 | 23.09 | 23.12 | 22.49 | 64.76 | 22.45 | 22.51 | 22.46 | 22.54 | 22.62 | 22.64 | 22.64 | 22.6 | 22.69 | 22.72 | 22.79 | 22.94 | 22.77 | 22.73 | 22.73
65 | 22.85 | 22.8 | 22.91 | 44.37 | 44.32 | 44.42 | N |  | AVG | 23 | 22.91 | 22.93 | 22.96 | 22.89 | 22.85 | 22.94 | 23.07 | 23.1 | 23.1 | 23.08 | 23.03 | 23.04 | 21.83 | 21.8 | 22.33 | 22.37 | 22.43 | 22.41 | 22.46 | 22.54 | 22.57 | 22.58 | 22.55 | 22.61 | 22.66 | 22.73 | 22.77 | 22.7 | 22.67 | 22.67
66 | 22.94 | 22.82 | 23.03 | 44.44 | 44.35 | 44.52 | A | RMW
67 | 23.07 | 23 | 23.12 | 44.56 | 44.47 | 44.62 | L |  | UP
68 | 23.1 | 22.98 | 23.22 | 44.58 | 44.47 | 44.72 |  |  | MIN | 44.45 | 44.38 | 44.39 | 44.38 | 44.35 | 44.32 | 44.35 | 44.47 | 44.47 | 44.49 | 44.5 | 44.46 | 44.49 | 37.18 | 36.91 | 12.72 | 44.17 | 44.25 | 44.25 | 44.29 | 44.34 | 44.4 | 44.43 | 44.39 | 44.43 | 44.5 | 44.56 | 44.59 | 44.56 | 44.55 | 44.57
69 | 23.1 | 23.05 | 23.18 | 44.58 | 44.49 | 44.66 | M |  | MAX | 44.59 | 44.47 | 44.48 | 44.57 | 44.48 | 44.42 | 44.52 | 44.62 | 44.72 | 44.66 | 44.64 | 44.59 | 44.59 | 44.61 | 43.85 | 63.95 | 44.37 | 44.4 | 44.34 | 44.42 | 44.51 | 44.51 | 44.55 | 44.54 | 44.6 | 44.61 | 44.68 | 44.77 | 44.65 | 44.61 | 44.65
70 | 23.08 | 23.03 | 23.13 | 44.56 | 44.5 | 44.64 | O |  | AVG | 44.51 | 44.42 | 44.45 | 44.48 | 44.41 | 44.37 | 44.44 | 44.56 | 44.58 | 44.58 | 44.56 | 44.53 | 44.55 | 40.4 | 40.98 | 43.82 | 44.27 | 44.33 | 44.3 | 44.35 | 44.45 | 44.47 | 44.49 | 44.46 | 44.51 | 44.56 | 44.62 | 44.68 | 44.61 | 44.59 | 44.6
71 | 23.03 | 22.98 | 23.09 | 44.53 | 44.46 | 44.59 | N
72 | 23.04 | 22.98 | 23.09 | 44.55 | 44.49 | 44.59 | I
73 | 21.83 | 20.53 | 23.12 | 40.4 | 37.18 | 44.61 | T
74 | 21.8 | 20.8 | 22.49 | 40.98 | 36.91 | 43.85 | O
75 | 22.33 | 12.43 | 64.76 | 43.82 | 12.72 | 63.95 | R
76 | 22.37 | 22.24 | 22.45 | 44.27 | 44.17 | 44.37
77 | 22.43 | 22.34 | 22.51 | 44.33 | 44.25 | 44.4 | W
78 | 22.41 | 22.35 | 22.46 | 44.3 | 44.25 | 44.34 | E
79 | 22.46 | 22.38 | 22.54 | 44.35 | 44.29 | 44.42 | L
80 | 22.54 | 22.44 | 22.62 | 44.45 | 44.34 | 44.51 | L
81 | 22.57 | 22.52 | 22.64 | 44.47 | 44.4 | 44.51
82 | 22.58 | 22.53 | 22.64 | 44.49 | 44.43 | 44.55
83 | 22.55 | 22.5 | 22.6 | 44.46 | 44.39 | 44.54 | R
84 | 22.61 | 22.54 | 22.69 | 44.51 | 44.43 | 44.6 | M
85 | 22.66 | 22.62 | 22.72 | 44.56 | 44.5 | 44.61 | W
86 | 22.73 | 22.7 | 22.79 | 44.62 | 44.56 | 44.68
87 | 22.77 | 22.72 | 22.94 | 44.68 | 44.59 | 44.77 | O
88 | 22.7 | 22.65 | 22.77 | 44.61 | 44.56 | 44.65 | N
89 | 22.67 | 22.62 | 22.73 | 44.59 | 44.55 | 44.61 | E
90 | 22.67 | 22.59 | 22.73 | 44.6 | 44.57 | 44.65
60 | 40.97 | 39.44 | 42.91 | 47.72 | 45.82 | 48.59 | M |  |  | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90
61 | 41.23 | 39.73 | 43.7 | 48.27 | 48.13 | 48.45 | O
62 | ER | ER | ER | ER | ER | ER | N |  | LOW
63 | 42.24 | 40.71 | 44.59 | 48.31 | 48.11 | 48.51 | I |  | MIN | 39.44 | 39.73 | ER | 40.71 | 41.25 | ER | ER | 11.14 | 42.49 | 13.68 | 41.5 | 41.37 | 41.41 | 35.75 | 34.51 | 41.31 | 40.53 | 40.92 | 40.86 | 41.08 | 36.18 | 35.14 | 41.31 | 41.3 | 41.94 | 41.65 | 41.85 | 34.63 | 35.24 | 39.72 | 41.51
64 | 42.99 | 41.25 | 45.83 | 48.25 | 48.06 | 48.4 | T |  | MAX | 42.91 | 43.7 | ER | 44.59 | 45.83 | ER | ER | 43.85 | 44.49 | 45.3 | 45.72 | 45.17 | 46.82 | 45.29 | 41.79 | 44.4 | 45.26 | 44.48 | 45.29 | 46.15 | 44.53 | 41.31 | 45.74 | 44.52 | 45.1 | 45.04 | 44.66 | 43.87 | 42.47 | 44.84 | 44.47
65 | ER | ER | ER | ER | ER | ER | O |  | AVG | 40.97 | 41.23 | ER | 42.24 | 42.99 | ER | ER | 40.65 | 43.43 | 42.22 | 43.11 | 42.95 | 43.24 | 40.66 | 38.49 | 42.56 | 42.26 | 42.37 | 42.51 | 42.95 | 40.81 | 38.28 | 42.48 | 42.55 | 43.01 | 42.65 | 42.82 | 40.82 | 38.93 | 42.12 | 42.64
66 | ER | ER | ER | ER | ER | ER | R | MW-1
67 | 40.65 | 11.14 | 43.85 | 48.2 | 36.84 | 48.57 |  |  | UP
68 | 43.43 | 42.49 | 44.49 | 48.28 | 48.02 | 48.51 | W |  | MIN | 45.82 | 48.13 | ER | 48.11 | 48.06 | ER | ER | 36.84 | 48.02 | 15.87 | 47.88 | 47.84 | 47.88 | 43.41 | 43.88 | 48.13 | 48.23 | 48.18 | 48.17 | 48.19 | 43.25 | 43.59 | 48.19 | 48.16 | 48.21 | 48.31 | 48.36 | 39.39 | 39.56 | 48.28 | 48.29
69 | 42.22 | 13.68 | 45.3 | 47.47 | 15.87 | 48.46 | E |  | MAX | 48.59 | 48.45 | ER | 48.51 | 48.4 | ER | ER | 48.57 | 48.51 | 48.46 | 48.22 | 48.13 | 48.14 | 48.14 | 48.44 | 48.31 | 48.41 | 48.47 | 48.37 | 48.4 | 48.44 | 48.61 | 48.48 | 48.45 | 48.54 | 48.6 | 48.65 | 48.66 | 48.79 | 48.58 | 48.54
70 | 43.11 | 41.5 | 45.72 | 48.01 | 47.88 | 48.22 | L |  | AVG | 47.72 | 48.27 | ER | 48.31 | 48.25 | ER | ER | 48.2 | 48.28 | 47.47 | 48.01 | 47.98 | 47.99 | 45.55 | 46.42 | 48.23 | 48.4 | 48.33 | 48.3 | 48.31 | 45.62 | 46.44 | 48.36 | 48.33 | 48.42 | 48.46 | 48.48 | 43.15 | 45.88 | 48.47 | 48.47
71 | 42.95 | 41.37 | 45.17 | 47.98 | 47.84 | 48.13 | L
72 | 43.24 | 41.41 | 46.82 | 47.99 | 47.88 | 48.14
73 | 40.66 | 35.75 | 45.29 | 45.55 | 43.41 | 48.14 | O
74 | 38.49 | 34.51 | 41.79 | 46.42 | 43.88 | 48.44 | N
75 | 42.56 | 41.31 | 44.4 | 48.23 | 48.13 | 48.31 | E
76 | 42.26 | 40.53 | 45.26 | 48.4 | 48.23 | 48.41
77 | 42.37 | 40.92 | 44.48 | 48.33 | 48.18 | 48.47 | I
78 | 42.51 | 40.86 | 45.29 | 48.3 | 48.17 | 48.37 | N
79 | 42.95 | 41.08 | 46.15 | 48.31 | 48.19 | 48.4 | J
80 | 40.81 | 36.18 | 44.53 | 45.62 | 43.25 | 48.44 | E
81 | 38.28 | 35.14 | 41.31 | 46.44 | 43.59 | 48.61 | C
82 | 42.48 | 41.31 | 45.74 | 48.36 | 48.19 | 48.48 | T
83 | 42.55 | 41.3 | 44.52 | 48.33 | 48.16 | 48.45 | I
84 | 43.01 | 41.94 | 45.1 | 48.42 | 48.21 | 48.54 | O
85 | 42.65 | 41.65 | 45.04 | 48.46 | 48.31 | 48.6 | N
86 | 42.82 | 41.85 | 44.66 | 48.48 | 48.36 | 48.65
87 | 40.82 | 34.63 | 43.87 | 43.15 | 39.39 | 48.66 | W
88 | 38.93 | 35.24 | 42.47 | 45.88 | 39.56 | 48.79 | E
89 | 42.12 | 39.72 | 44.84 | 48.47 | 48.28 | 48.58 | L
90 | 42.64 | 41.51 | 44.47 | 48.47 | 48.29 | 48.54 | L
60 | 41.36 | 38.99 | 42.46 | 23.87 | 21.02 | 25.67 | M |  |  | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90
61 | 42.47 | 42.37 | 42.51 | 24.87 | 24.21 | 25.86 | O
62 | ER | ER | ER | ER | ER | ER | N |  | LOW
63 | 42.58 | 42.5 | 42.74 | 25.11 | 24.55 | 25.83 | I |  | MIN | 38.99 | 42.37 | ER | 42.5 | 42.5 | ER | ER | 35.94 | 42.28 | 42.56 | 42.55 | 42.64 | 42.67 | 37.19 | 34.46 | 42.4 | 42.65 | 42.66 | 42.68 | 42.7 | 35.99 | 34.77 | 42.43 | 42.58 | 42.65 | 42.77 | 42.88 | 35.7 | 36.9 | 42.61 | 42.75
64 | 42.54 | 42.5 | 42.7 | 25.35 | 24.58 | 26.78 | T |  | MAX | 42.46 | 42.51 | ER | 42.74 | 42.7 | ER | ER | 42.43 | 42.69 | 42.69 | 42.77 | 42.74 | 42.82 | 42.82 | 42.4 | 42.65 | 42.81 | 42.86 | 42.8 | 42.89 | 42.95 | 42.5 | 42.71 | 42.74 | 42.87 | 42.94 | 43.02 | 43.09 | 42.67 | 42.77 | 42.86
65 | ER | ER | ER | ER | ER | ER | O |  | AVG | 41.36 | 42.47 | ER | 42.58 | 42.54 | ER | ER | 40.4 | 42.47 | 42.56 | 42.66 | 42.61 | 42.71 | 39.53 | 40.14 | 42.49 | 42.73 | 42.76 | 42.75 | 42.88 | 39.11 | 39.72 | 42.51 | 42.57 | 42.83 | 42.87 | 42.97 | 40.41 | 41.25 | 42.62 | 42.82
66 | ER | ER | ER | ER | ER | ER | R | MW-2
67 | 40.4 | 35.94 | 42.43 | 23.74 | 20.75 | 25.54 |  |  | UP
68 | 42.47 | 42.28 | 42.69 | 24.43 | 24.23 | 24.71 | W |  | MIN | 21.02 | 24.21 | ER | 24.55 | 24.58 | ER | ER | 20.75 | 24.23 | 24.1 | 23.99 | 24.73 | 24.53 | 20.82 | 20.3 | 25.56 | 25.76 | 25.38 | 25.07 | 25.28 | 21.33 | 21.37 | 26.11 | 26.34 | 26.75 | 27.23 | 27.65 | 21.67 | 21.06 | 25.6 | 26.66
69 | 42.56 | 42.56 | 42.69 | 24.71 | 24.1 | 25.68 | E |  | MAX | 25.67 | 25.86 | ER | 25.83 | 26.78 | ER | ER | 25.54 | 24.71 | 25.68 | 26.11 | 26.23 | 26.51 | 26.18 | 26.36 | 26.9 | 27.2 | 26.71 | 26.7 | 26.87 | 26.79 | 26.86 | 27.71 | 27.36 | 28.3 | 28.55 | 28.8 | 28.75 | 27.37 | 27.57 | 27.87
70 | 42.66 | 42.55 | 42.77 | 25.01 | 23.99 | 26.11 | L |  | AVG | 23.87 | 24.87 | ER | 25.11 | 25.35 | ER | ER | 23.74 | 24.43 | 24.71 | 25.01 | 25.35 | 25.56 | 23.21 | 23.73 | 26.08 | 26.12 | 26.01 | 25.78 | 26.03 | 23.97 | 24.37 | 26.66 | 26.87 | 27.47 | 27.85 | 28.16 | 25.11 | 25.05 | 26.64 | 27.14
71 | 42.61 | 42.64 | 42.74 | 25.35 | 24.73 | 26.23 | L
72 | 42.71 | 42.67 | 42.82 | 25.56 | 24.53 | 26.51
73 | 39.53 | 37.19 | 42.82 | 23.21 | 20.82 | 26.18 | T
74 | 40.14 | 34.46 | 42.4 | 23.73 | 20.3 | 26.36 | W
75 | 42.49 | 42.4 | 42.65 | 26.08 | 25.56 | 26.9 | O
76 | 42.73 | 42.65 | 42.81 | 26.12 | 25.76 | 27.2
77 | 42.76 | 42.66 | 42.86 | 26.01 | 25.38 | 26.71 | I
78 | 42.75 | 42.68 | 42.8 | 25.78 | 25.07 | 26.7 | N
79 | 42.88 | 42.7 | 42.89 | 26.03 | 25.28 | 26.87 | J
80 | 39.11 | 35.99 | 42.95 | 23.97 | 21.33 | 26.79 | E
81 | 39.72 | 34.77 | 42.5 | 24.37 | 21.37 | 26.86 | C
82 | 42.51 | 42.43 | 42.71 | 26.66 | 26.11 | 27.71 | T
83 | 42.57 | 42.58 | 42.74 | 26.87 | 26.34 | 27.36 | I
84 | 42.83 | 42.65 | 42.87 | 27.47 | 26.75 | 28.3 | O
85 | 42.87 | 42.77 | 42.94 | 27.85 | 27.23 | 28.55 | N
86 | 42.97 | 42.88 | 43.02 | 28.16 | 27.65 | 28.8
87 | 40.41 | 35.7 | 43.09 | 25.11 | 21.67 | 28.75 | W
88 | 41.25 | 36.9 | 42.67 | 25.05 | 21.06 | 27.37 | E
89 | 42.62 | 42.61 | 42.77 | 26.64 | 25.6 | 27.57 | L
90 | 42.82 | 42.75 | 42.86 | 27.14 | 26.66 | 27.87 | L
60 | 43.1 | 38.8 | 45.14 | 28.76 | 20.84 | 32.48 | M |  |  | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90
61 | 45.05 | 45.07 | 45.22 | 32.47 | 32.32 | 32.58 | O
62 | ER | ER | ER | ER | ER | ER | N |  | LOW
63 | 45.41 | 45.24 | 45.46 | 32.69 | 32.55 | 32.85 | I |  | MIN | 38.8 | 45.07 | ER | 45.24 | 45.27 | ER | ER | 35.6 | 45.03 | 45.31 | 45.32 | 45.41 | 45.45 | 37.7 | 37.64 | 45.11 | 45.38 | 45.42 | 45.45 | 45.47 | 37.97 | 37.97 | 45.18 | 45.36 | 45.42 | 45.56 | 45.68 | 37.84 | 39.58 | 45.34 | 45.48
64 | 45.4 | 45.27 | 45.46 | 32.66 | 32.54 | 32.83 | T |  | MAX | 45.14 | 45.22 | ER | 45.46 | 45.46 | ER | ER | 45.15 | 45.42 | 45.42 | 45.51 | 45.5 | 45.58 | 45.58 | 45.11 | 45.4 | 45.56 | 45.6 | 45.58 | 45.68 | 45.71 | 45.23 | 45.46 | 45.49 | 45.65 | 45.71 | 45.81 | 45.88 | 45.36 | 45.49 | 45.58
65 | ER | ER | ER | ER | ER | ER | O |  | AVG | 43.1 | 45.05 | ER | 45.41 | 45.4 | ER | ER | 42.11 | 45.3 | 45.39 | 45.46 | 45.48 | 45.5 | 40.91 | 42.02 | 45.35 | 45.49 | 45.52 | 45.5 | 45.52 | 41.33 | 42.01 | 45.37 | 45.44 | 45.49 | 45.58 | 45.77 | 42.19 | 43.6 | 45.44 | 45.5
66 | ER | ER | ER | ER | ER | ER | R | MW-3
67 | 42.11 | 35.6 | 45.15 | 27.73 | 17.6 | 32.42 |  |  | UP
68 | 45.3 | 45.03 | 45.42 | 32.47 | 32.19 | 32.77 | W |  | MIN | 20.84 | 32.32 | ER | 32.55 | 32.54 | ER | ER | 17.6 | 32.19 | 32.5 | 32.53 | 32.59 | 32.59 | 18.22 | 18.09 | 32.33 | 32.63 | 32.71 | 32.73 | 32.74 | 19.01 | 18.98 | 32.43 | 32.64 | 32.71 | 32.88 | 32.96 | 19.93 | 19.74 | 32.65 | 32.81
69 | 45.39 | 45.31 | 45.42 | 32.61 | 32.5 | 32.77 | E |  | MAX | 32.48 | 32.58 | ER | 32.85 | 32.83 | ER | ER | 32.42 | 32.77 | 32.77 | 32.86 | 32.81 | 32.86 | 32.86 | 32.33 | 32.66 | 32.85 | 32.92 | 32.92 | 32.97 | 32.97 | 32.54 | 32.83 | 32.89 | 33.04 | 33.14 | 33.21 | 33.21 | 32.81 | 32.93 | 32.99
70 | 45.46 | 45.32 | 45.51 | 32.74 | 32.53 | 32.86 | L |  | AVG | 28.76 | 32.47 | ER | 32.69 | 32.66 | ER | ER | 27.73 | 32.47 | 32.61 | 32.74 | 32.72 | 32.72 | 24.13 | 26.44 | 32.49 | 32.72 | 32.8 | 32.81 | 32.89 | 25.02 | 26.65 | 32.62 | 32.8 | 32.87 | 32.97 | 33.01 | 25.45 | 28.71 | 32.76 | 32.95
71 | 45.48 | 45.41 | 45.5 | 32.72 | 32.59 | 32.81 | L
72 | 45.5 | 45.45 | 45.58 | 32.72 | 32.59 | 32.86
73 | 40.91 | 37.7 | 45.58 | 24.13 | 18.22 | 32.86 | T
74 | 42.02 | 37.64 | 45.11 | 26.44 | 18.09 | 32.33 | H
75 | 45.35 | 45.11 | 45.4 | 32.49 | 32.33 | 32.66 | R
76 | 45.49 | 45.38 | 45.56 | 32.72 | 32.63 | 32.85 | E
77 | 45.52 | 45.42 | 45.6 | 32.8 | 32.71 | 32.92 | E
78 | 45.5 | 45.45 | 45.58 | 32.81 | 32.73 | 32.92
79 | 45.52 | 45.47 | 45.68 | 32.89 | 32.74 | 32.97 | I
80 | 41.33 | 37.97 | 45.71 | 25.02 | 19.01 | 32.97 | N
81 | 42.01 | 37.97 | 45.23 | 26.65 | 18.98 | 32.54 | J
82 | 45.37 | 45.18 | 45.46 | 32.62 | 32.43 | 32.83 | E
83 | 45.44 | 45.36 | 45.49 | 32.8 | 32.64 | 32.89 | C
84 | 45.49 | 45.42 | 45.65 | 32.87 | 32.71 | 33.04 | T
85 | 45.58 | 45.56 | 45.71 | 32.97 | 32.88 | 33.14 | I
86 | 45.77 | 45.68 | 45.81 | 33.01 | 32.96 | 33.21 | O
87 | 42.19 | 37.84 | 45.88 | 25.45 | 19.93 | 33.21 | N
88 | 43.6 | 39.58 | 45.36 | 28.71 | 19.74 | 32.81
89 | 45.44 | 45.34 | 45.49 | 32.76 | 32.65 | 32.93 | W
90 | 45.5 | 45.48 | 45.58 | 32.95 | 32.81 | 32.99 | E
L
L

## SHIFT DATA
PERSONNEL LIST
|  | SHIFT CODE |  | OPERATOR NAME |  | CERTIFICATION NUMBER |  | SOCIAL SECURITY NUMBER
CHIEF OPERATORS
HOSTNICK, N. | CO# 3207-A | 3 |  | BAYLER, J. | 3 | CO# 4474-A | "A" |  | "A" | 4474 | 3207 | 2D | J. BAROFSKY | 5096-C
McGEARY, J. | CO# 4545-A | 1 |  | HOSTNICK, N. | 1 | CO# 3207-A | "A" |  | "A" | 3207 | 4545 | 5 | S. HULL | 5613-C
BAYLER, J. | CO# 4474-A | 2 |  | McGEARY, J. | 2 | CO# 4545-A | "A" |  | "A" | 4545 | 4474 | 4 | VACANT | X
POMEROY, D. | CO# 421-B | 5 |  | POMEROY, D. | 5 | CO# 421-B | "B" |  | "B" | 421 | 421 | 3 | J. TINKER | 3291-C
[12 empty] | 1 | G. SLAYTON | 2606-B
[12 empty] | 2 | H. WALKER | 4700-A
OPERATOR II' S
JONES, K. | CO# 2466-B | 2D |  | BAROFSKY, J. | 2D | CO# 5096-C | [5 empty] | 5 | J. BENTLEY | X
THOMAS, P. | CO# 12833 C | 4 |  | BENTLEY, J. | 4 | CO# 9366-C | [5 empty] | 1D | S. CURMODE | X
HULL, S. | CO# 5613-C | 5 |  | CURMODE, S. | 5 | CO# 9379-A | [5 empty] | 4 | K. HENDERSON | 5087-B
BENTLEY, J. | CO# 9366-C | 3 |  | HULL, S. | 3 | CO# 5613-C | [5 empty] | 3D | K. JONES | 2466-C
CURMODE, S. | CO# 9379-A | 1 |  | JONES, K. | 1 | CO# 2466-B | [5 empty] | 3 | G. KLEYNHANS | 7367-C
BAROFSKY, J. | CO# 5096-C | 2 |  | THOMAS, P. | 2 | CO# 12833 C | [5 empty] | 2 | A. MORROW | 9164-C
[12 empty] | 1 | J. RAINFORTH | 2718-C
OPERATOR I' S
PEUGEOT, P. | CO# 12817-C | 1D |  | DOLES, L | 1D | CO# XXXX-X
DOLES, L | CO# XXXX-X | 3 |  | FREIDLAND, M. | 3 | CO# 13437-C
NOBERT, B. | CO# 9661-C | 4 |  | HENDERSON, K. | 4 | CO# 5087-B
FREIDLAND, M. | CO# 13437-C | 5 |  | KOKLAS, D. | 5 | CO# 13506-C
SANDERS, C. | CO# 13500-C | 2 |  | NOBERT, B. | 2 | CO# 9661-C
HENDERSON, K. | CO# 5087-B | 1 |  | PEUGEOT, P. | 1 | CO# 12817-C
KOKLAS, D. | CO# 13506-C | 3D |  | SANDERS, C. | 3D | CO# 13500-C
VERBOSH, R. | CO# 12667-C | 4A |  | VERBOSH, R. | 4A | CO# 12667-C
|  | 4 | 1 | BERNARDI, J | 4 | CO# XXXX-X
|  | 3 | 2 | FREIDLAND, M. | 3 | CO# 13437-C
|  | 5A | 3 | FUTURE, 5A | 5A | CO# XXXX-X
|  | 1 | 4 | HENDERSON, K. | 1 | CO# 5087-B
|  | 2 | 5 | KOKLAS, D. | 2 | CO# 13506-C
|  | 5 | 6 | NOBERT, B. | 5 | CO# 9661-C
|  | 4A | 7 | PEUGEOT, P. | 4A | CO# 12817-C
|  | 1D | 8 | SANDERS, C. | 1D | CO# 13500-C
|  | 3D | 9 | VERBOSH, R. | 3D | CO# 12667-C

## COVER PAGE
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
|  | MARCH |  | 2005
| OPERATOR | TITLE | CERTIFICATE # | TOTAL COST |  |  | 82502.7425
1 ST SHIFT | HOSTNICK, N. | CHIEF | CO# 3207-A | PEAK TO FLOW RATIO |  |  | 1.1648
2230-0630 | JONES, K. | OP. II | CO# 2466-B
| PEUGEOT, P. | OP. I | CO# 12817-C |  | TOTAL SUSPENDED SOLIDS
| DOLES, L | OP. I DEWAT | CO# XXXX-X |  |  |  | LBS/DAY
|  |  |  | RAW INFLUENT |  |  | 56698.381
2 ND SHIFT |  |  |  | FINAL EFFLUENT |  |  | 5373.8073
0630-1430 | McGEARY, J. | CHIEF | CO# 4545-A |  | TOTAL CBOD
| THOMAS, P. | OP. II RELIEF | CO# 12833 C |  |  |  | LBS/DAY
| BAROFSKY, J. | OP. II DEWAT | CO# 5096-C | RAW INFLUENT |  |  | 28599.9682
| NOBERT, B. | OP. I RELIEF | CO# 9661-C | FINAL EFFLUENT |  |  | 1155.4629
CHEMICALS
3 RD SHIFT | BAYLER, J. | CHIEF | CO# 4474-A |  |  | COST | POUNDS
1430-2230 | HULL, S. | OP. II | CO# 5613-C | HYDROGEN PEROXIDE |  | 6947.7625 | 47425
| FREIDLAND, M. | OP. I | CO# 13437-C | CHLORINE |  | 10584.6 | 35880
| SANDERS, C. | OP. I DEWAT | CO# 13500-C | POLYMER |  | 9411.69 | 15429
SLUDGE REMOVED
4 TH SHIFT | [6 empty] | TONS
WEEKEND | BENTLEY, J. | OP. II | CO# 9366-C | DRY TONS |  |  | 668.9255
2230-1030 | HENDERSON, K. | OP. I | CO# 5087-B |  | ENERGY
| VERBOSH, R. | OPI | CO# 12667-C |  |  | COST | KILOWATTS
5 TH SHIFT | POMEROY, D. | CHIEF | CO# 421-B | FPL CONSUMPTION |  | 55558.69 | 1010158
WEEKEND | CURMODE, S. | OP. II | CO# 9379-A
1030-2230 | KOKLAS, D. | OP. I | CO# 13506-C | POPULATION EQUIVALENCE |  |  | 168235.1071
This Monthly Operation Report prepared by: |  |  | BAYLER, J. | CO# 4474-A
State DEP Plant Classification: Class "A" Level "II"
I certify that I am familiar with the information contained in this report and that to the best of my knowledge and
belief, such information is true, complete and accurate.
Facilitiy Manager's Signature: ____________________________________ CO# __________________
Division Manager's Signature: ____________________________________ CO# __________________
Please direct all inquiries reguarding this report to the City Official Mailing Address:
Director of Public Services |  |  | Phone (954) 776-5151
City of Fort Lauderdale
P.O. Drawer 14250 |  |  | Copies mailed: Date ________________ To: DEP _____
Fort Lauderdale, Florida | [5 empty] | DNRP _____
33302
PAGE 1

## PRINT PAGES
UNDERGROUND INJECTION CONTROL SECTION
[29 empty] | MONTHLY OPERATING REPORT DATA SUMMARY | [13 empty] | DEP From # 17-801.900 (1) | [11 empty] | DEP From # 17-801.900 (1) | [19 empty] | DAILY SAMPLE RESULTS - PART B
[25 empty] | FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT DATE: |  | MARCH | 2005 | [8 empty] | Form Title:Domestic Wastewater Treatment | [11 empty] | Form Title:Domestic Wastewater Treatment
[25 empty] | I.D. NUMBER: 5006M02066 |  |  |  |  | CHIEF OPERATOR: |  |  | BAYLER, J. | CO# 4474-A | [8 empty] | Plant Monthly Operating Report | [11 empty] | Plant Monthly Operating Report | [15 empty] | Permit Number: |  | FLA041378 |  |  |  |  | Three-month Average Daily Flow: | [5 empty] | 34.169
[25 empty] | TELEPHONE NUMBER: (954) 523-1002 | [17 empty] | Effective Date: July 1, 1991 | [11 empty] | Effective Date: July 1, 1991 | [15 empty] | Monitoring Period |  | From: | 2005-03-01 | To: | 2005-03-31 |  | (TMADF):/Permitted Capacity)x100: | [5 empty] | 61.34%
[19 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [9 empty] | INJECTION WELL DATA | [13 empty] | DEP Application No. __________________ | [11 empty] | DEP Application No. __________________ | [11 empty] | Department of Natural Resource Protection
[5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [13 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [6 empty] | IW-1 | IW-2 |  | IW-3 |  | IW-4 | IW-5 | [35 empty] | Laboratory/Licensing/Enforcement |  |  |  | Flow | Flow | Flow | Flow | Flow | Flow | CBOD5 | CBOD5 | TSS | TSS | pH | pH | TDS | NH-3 | TKN | pH | cond. | temp. | TP
[5 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [13 empty] | MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING | [5 empty] | PERMIT/CERTIFICATION NUMBER: | 0054569-142-UO | 0054569-142-UO |  | 0054569-142-UO |  | 0054569-142-UO | 0054569-142-UO | [19 empty] | DOMESTIC WASTEWATER TREATMENT PLANT | [11 empty] | BROWARD COUNTY DEPARTMENT OF NATURAL RESOURCE PROTECTION | [5 empty] | 218 S. W. 1st Avenue |  |  | (MGD) | (MGD) | (MGD) | (MGD) | (MGD) | (mg/l) | (mg/l) | (mg/l) | (mg/l) | (Min) | (Max) | mg/L | mg/L | mg/L | units | umho/ | F | mg/L
[5 empty] | MONTHLY OPERATIONAL REPORT | [13 empty] | MONITORING WELL ONE |  |  |  | 1/07/04 thru 1/06/09 |  | PERMIT EXPIRATION DATE: | 2009-01-06 | 2009-01-06 |  | 2009-01-06 |  | 2009-01-06 | 2009-01-06 | [19 empty] | MONTHLY OPERATING REPORT | [11 empty] | WASTEWATER TREATMENT PLANT | [5 empty] | Fort Lauderdale, FL 33301 | [17 empty] | cm
[5 empty] | PROCESS DATA | [11 empty] | MW-1 | I.D. #: 5066A11311 |  |  | PERMIT # 0054569-142-UO |  |  |  | CASING DEPTH | 2799' | 2798' |  | 2800' |  | 2804' | 2818' | [8 empty] | DOMESTIC WASTEWATER TREATMENT PLANT |  |  |  |  | (34) | [8 empty] | MONTH: | MARCH |  | YEAR: | 2005 |  |  |  |  | MONTHLY SLUDGE REPORTS | [5 empty] | Tel. No. (954) 765-4804 | Code | 50050 | 50050 | 50050 | 50050 | 50050 | 50050 | 80082 | 80082 | 00530 | 00530 | 00400 | 00400
| RUN DATE | [14 empty] | RUN DATE | [8 empty] | TOTAL DEPTH | 3513' | 3518' |  | 3977' |  | 3305' | 3462' | [8 empty] | MONTHLY OPERATING REPORT |  |  |  |  | DAY OF | FLOW | CHLORINE | CHLORINE | CBOD5 | TSS | CBOD5 | TSS | PH |  |  | EFFLUENT NUTRIENTS (MG/L) |  |  | I. | [10 empty] | Mon. Site | INF-001 | EFF-002 | EFF-003 | EFF-004 | EFF-005 | EFF-006 | INF-002 | EFF-001 | INF-002 | EFF-001 | EFF-001 | EFF-001
| 2026-07-30 | [14 empty] | 2026-07-30 |  | UPPER MONITOR ZONE |  |  |  |  | LOWER MONITOR ZONE |  | AVERAGE DAILY FLOW: | 6.6586 | 7.8218 |  | 7.4615 |  | 6.9821 | 6.7477 | MGD | [7 empty] | Part II - General Information |  |  |  |  | THE |  | RESIDUAL | RESIDUAL | INFLUENT | INFLUENT | EFFLUENT | EFFLUENT | EFFLUENT | TKN | NH3-N | NITRATE | TOTAL | FECAL | Plant Name: | GEORGE T. LOHMEYER WASTEWATER TREATMENT FACILITY | [6 empty] | MONTH: | MARCH |  | 1 | 31.911 | 8.1 | 7.22 | 8.08 | 0.02 | 8.02 | 102.9 | 4.97 | 104 | 8 | 6.6 | 6.6 | 1534 | 17 | 17 | 6.6 | 3270 | 80 | 1.1
[17 empty] | MIN | MAX | AVG |  |  | MIN | MAX | AVG | **MAX DAILY FLOW PER MO (mg): | 10.4 | 10.41 |  | 9.94 |  | 10.42 | 9.6 | MG | [12 empty] | MONTH | (MGD) | AFTER | AFTER DE- | [8 empty] | P | COLIFORM | II. | [7 empty] | YEAR: | 2005 |  | 2 | 31.788 | 8.36 | 8.53 | 6.1 | 0.02 | ER | 79.8 | 3.41 | 120 | 10 | 6.6 | 6.6 | 1536 | 16 | 17 | 6.6 | 3240 | 79.6 | 0.55
| MARCH | INFLUENT | HOURLY | INFLUENT | INFLUENT | RAS | PERCENT | WAS | RAIN | Sufates | [5 empty] | MARCH | FT HEAD | FT HEAD | FT HEAD |  |  | FT HEAD | FT HEAD | FT HEAD | ** PEAK HR FLOW (MGD) ON MAX DAY: | 9.3775 | 10.9701 |  | 10.4291 |  | 9.6605 | 9.4757 | MGD |  | (1) Month: |  | MARCH |  | Year: | 2005 |  | Parameter | Units | STORET | Value |  |  | CONTACT | CHLORINATION | MG/L | MG/L | MG/L | MG/L | [6 empty] | A) | Sludge Treatment Provided: |  |  |  |  | B) | Sludge Dewater Processes |  |  |  | 3 | 31.874 | ER | ER | ER | ER | ER | 122.4 | 3.1 | 174 | 10 | 6.5 | 6.7 | 1592 | 16 | 18 | 6.6 | 3270 | 79.3 | 0.57
| 2005 | FLOW | MAXIMUM | MAXIMUM | MINIMUM | FLOW | RAS | FLOW | INCHES | [6 empty] | 2005 | ABOVE | ABOVE | ABOVE |  |  | ABOVE | ABOVE | ABOVE | MAX SUSTAINED INJECTION PRESSURE: | 79.7 | 78.4 |  | 80.2 |  | 80.5 | 71.4 | PSIG |  | (2) Plant's DEP Identification Number: |  |  |  |  | 5006M02066 |  |  |  | Code |  | 1 | 31.911 | 0.7 |  | 102.9 | 104 | 4.97 | 8 | 6.6 | 17 | 17 | 0.33 | 1.1 | 9 |  |  | Aerobic Digestion | [5 empty] | Thickner |  |  | 4 | 34.807 | 6.7 | 9.68 | 9.31 | 0.01 | 9.14 | 80.9 | 3.06 | 44 | 4 | 6.6 | 6.7 | 1488 | 13 | 15 | 6.6 | 3200 | 79 | 1.5
|  | MGD | MGD | MGD | MGD | MGD |  | MGD | [8 empty] | NGVD | NGVD | NGVD |  |  | NGVD | NGVD | NGVD | MONTHLY AVG. INJECTION PRESSURE: | 45.6071 | 46.7307 |  | 47.5586 |  | 47.78 | 46.2981 | PSIG |  | (3) Plant Name: |  |  |  | George T. Lohmeyer Regional Wastewater |  |  | (16) Monthly average daily flow | mgd | 050053 | 35.0431 | 2 | 31.788 | 0.8 |  | 79.8 | 120 | 3.41 | 10 | 6.6 | 17 | 16 | 0.33 | 0.55 | 0 |  |  | Anaerobic Digestion | [5 empty] | DGA___X___Filter Press |  |  | 5 | 33.806 | 8.85 | 9.02 | 6.29 | 0.02 | 8.69 | 95.9 | 3.69 | 122 | 18 | 6.6 | 6.7 | 1501 | 13 | 14 | 6.6 | 3140 | 79 | 1
| 1 | 31.911 | 1.594 | 52.161 | 0.896 | 13.744 | 43.07% | 0.597 | 0 | 165.5 |  | 1 |  |  |  | 1 | 45.82 | 48.59 | 48.45 |  |  | 39.44 | 42.91 | 40.97 | *** MAX INJECTION PRESSURE PERMITTED: | 99 | 99 |  | 99 |  | 99 | 99 | PSIG |  |  |  |  | Treatment Facility |  |  |  | (17) Permitted capacity | mgd | - | 55.7 | 3 | 31.874 | 0.9 |  | 122.4 | 174 | 3.1 | 10 | 6.6 | 18 | 16 | 0.38 | 0.57 | TNTC |  |  | Other | [5 empty] | Centrifuge Drying Beds, Bed #______ |  |  | 6 | 32.732 | ER | ER | ER | ER | ER | 93.6 | 2.14 | 124 | 16 | 6.7 | 6.7 | 1479 | 14 | 15 | 6.7 | 2890 | 79.3 | 0.69
| 2 | 31.788 | 1.646 | 51.2 | 0.607 | 13.763 | 43.3% | 0.578 | 0 | 141.3 |  | 2 |  |  |  | 2 | 48.13 | 48.45 | 47.72 |  |  | 39.73 | 43.7 | 41.23 | ***NOTE: (INJECTION PRESSURE NOT TO EXCEED 66% TESTED PRESSURE | [9 empty] | (4) Plant Address: |  |  | 1765 S.E. 18th Street at |  |  |  | (18) Three-month average daily flow | mgd | - | 34.169 | 4 | 34.807 | 0.8 |  | 80.9 | 44 | 3.06 | 4 | 6.6 | 15 | 13 | 0.5 | 1.5 | TNTC | [8 empty] | Heat Treatment____No Treatment |  |  | 7 | 32.855 | ER | ER | ER | ER | ER | 114.5 | 4.4 | 80 | 21 | 6.6 | 6.7 | 1454 | 14 | 16 | 6.6 | 3150 | 80 | 0.65
| 3 | 31.874 | 1.6 | 49.119 | 0.832 | 13.691 | 42.95% | 0.498 | 0 | 125.8 |  | 3 |  |  |  | 3 | ER | ER | ER |  |  | ER | ER | ER | TESTED CASING PRESSURE DURING MIT | 150 | 150 |  | 150 |  | 150 | 150 | PSIG |  |  |  |  | Eisenhower Boulevard |  |  |  | (19) Percent of permitted capacity | % | - | 61.34% | 5 | 33.806 | 0.8 |  | 95.9 | 122 | 3.69 | 18 | 6.6 | 14 | 13 | 0.51 | 1 | TNTC | [7 empty] | x | Other: | Press Dewatered |  | 8 | 32.744 | 7.17 | 8.46 | 8.15 | 8.78 | ER | 129 | 4.05 | 2216 | 12 | 6.6 | 6.7 | 1479 | 15 | 16 | 6.6 | 3100 | 80 | 0.73
| 4 | 34.807 | 1.751 | 51.713 | 13.136 | 14.027 | 40.3% | 0.24 | 0.39 | 138.8 |  | 4 |  |  |  | 4 | 48.11 | 48.51 | 48.31 |  |  | 40.71 | 44.59 | 42.24 | [10 empty] | (5) City: |  | Fort Lauderdale |  |  |  |  | (20) CBOD5 Effluent | mg/L | 080082 | 3.9535 | 6 | 32.732 | 0.7 |  | 93.6 | 124 | 2.14 | 16 | 6.7 | 15 | 14 | 0.42 | 0.69 | 45 | [9 empty] | To Landfill |  | 9 | 35.23 | 1.88 | 9.62 | 8.92 | 9.42 | 5.64 | 123.9 | 4.12 | 136 | 17 | 6.6 | 6.6 | 1475 | 15 | 15 | 6.6 | 3110 | 79 | 0.63
| 5 | 33.806 | 1.773 | 51.649 | 8.746 | 13.259 | 39.22% | 0 | 0 | 137.3 |  | 5 |  |  |  | 5 | 48.06 | 48.4 | 48.25 |  |  | 41.25 | 45.83 | 42.99 |  |  | MONITORING WELL DATA | [7 empty] | (6) County: |  | Broward |  |  |  |  | (21) CBOD5 Effluent | lbs/day | - | 1155.4629 | 7 | 32.855 | 0.7 |  | 114.5 | 80 | 4.4 | 21 | 6.6 | 16 | 14 | 0.94 | 0.65 | 0 | III. | Final Sludge Disposal: | [9 empty] | 10 | 39.051 | 6.95 | 10.41 | 9.78 | 10.42 | 1.9 | 118.4 | 4.38 | 152 | 15 | 6.6 | 6.7 | 1424 | 11 | 17 | 6.6 | 2930 | 78 | 1.4
| 6 | 32.732 | 1.716 | 53.507 | 4.581 | 12.939 | 39.53% | 0.179 | 0 | 140.5 |  | 6 |  |  |  | 6 | ER | ER | ER |  |  | ER | ER | ER |  | MW-1 | MW-2 |  | MW-3 |  | RMW-1 |  |  |  | (7) Phone Number: |  |  | (954) 523-1002 |  |  |  | (22) TSS Effluent | mg/L | 900201 | 18.3871 | 8 | 32.744 | 0.7 |  | 129 | 2216 | 4.05 | 12 | 6.6 | 16 | 15 | 0.45 | 0.73 | 0 | A) | Liquid Sludge Disposal: | [9 empty] | 11 | 38.19 | 2.96 | 9.62 | 8.95 | 9.35 | 6.62 | 86.6 | 7.99 | 92 | 41 | 6.5 | 6.7 | 1469 | 11 | 13 | 6.6 | 3050 | 78.4 | 0.76
| 7 | 32.855 | 1.667 | 53.988 | 0.864 | 13.246 | 40.32% | 0.478 | 0 | 140.8 |  | 7 |  |  |  | 7 | ER | ER | ER |  |  | ER | ER | ER | PERMIT NUMBER | 0054569-142-UO | 0054569-142-UO |  | 0054569-142-UO |  | 0054569-142-UO |  |  |  | (8) Permit Number: |  |  | FLA041378 |  |  |  | (23) TSS Effluent | lbs/day | - | 5373.8073 | 9 | 35.23 | 0.8 |  | 123.9 | 136 | 4.12 | 17 | 6.6 | 15 | 15 | 0.47 | 0.63 | 0 |  | WEEK OF | MARCH | GALLONS | % SOLIDS |  |  | HAULERS |  |  | DISPOSAL SITE | 12 | 36.893 | 0 | 8.18 | 9.67 | 9.99 | 9.29 | 85.2 | 4.06 | 98 | 21 | 6.5 | 6.7 | 1386 | 11 | 13 | 6.6 | 2900 | 78.6 | 0.61
| 8 | 32.744 | 1.756 | 51.168 | 0.864 | 13.768 | 42.05% | 0.493 | 0.1 | 115.8 |  | 8 |  |  |  | 8 | 36.84 | 48.57 | 48.2 |  |  | 11.14 | 43.85 | 40.65 | UPPER MONITORING INTERVAL | 1288'-1320' | 1300'-1344' |  | 1300'-1349' |  | 1300'-1339' |  | Ft. bls. |  | (9) Plant Type: |  |  | Oxygen Activated Sludge |  |  |  | (24) Minimum pH |  | - | 6.4 | 10 | 39.051 | 0.8 |  | 118.4 | 152 | 4.38 | 15 | 6.6 | 17 | 11 | 0.25 | 1.4 | 0 | [11 empty] | 13 | 35.545 | 0 | 10.07 | 9.27 | 9.55 | 6.79 | 74.3 | 4.04 | 116 | 20 | 6.6 | 6.7 | 1391 | 12 | 14 | 6.6 | 2910 | 78.9 | 0.6
| 9 | 35.23 | 2.061 | 57.577 | 0.96 | 13.451 | 38.18% | 0.667 | 1.87 | 142.3 |  | 9 |  |  |  | 9 | 48.02 | 48.51 | 48.28 |  |  | 42.49 | 44.49 | 43.43 | MONTHLY MAX DAILY PRESSURE | 48.79 | 28.8 |  | 33.21 |  | 63.95 |  | FT. HEAD |  | (10) Test Site Identification Number: |  |  |  |  | 5006X10744 |  | (25) Maximum pH |  | - | 6.7 | 11 | 38.19 | 0.4 |  | 86.6 | 92 | 7.99 | 41 | 6.6 | 13 | 11 | 0.37 | 0.76 | 12223 |  | FIRST THRU SEVENTH | [9 empty] | 14 | 34.876 | 2.99 | 9.68 | 6.09 | 9.3 | 6.9 | 85.2 | 2.1 | 112 | 10 | 6.5 | 6.7 | 1391 | 13 | 17 | 6.7 | 2920 | 79 | 0.48
| 10 | 39.051 | 2.039 | 56.584 | 0.832 | 13.986 | 35.81% | 0 | 0.13 | 122 |  | 10 |  |  |  | 10 | 15.87 | 48.46 | 47.47 |  |  | 13.68 | 45.3 | 42.22 | MONTHLY MIN DAILY PRESSURE | 15.87 | 20.3 |  | 17.6 |  | 12.72 |  | FT. HEAD |  | (11) Fecal Coliform Method | [6 empty] | (26) Total N | mg/L | 000600 | 15.39 | 12 | 36.893 | 0.7 |  | 85.2 | 98 | 4.06 | 21 | 6.6 | 13 | 11 | 0.42 | 0.61 | TNTC | [11 empty] | 15 | 34.082 | 7.12 | 9.28 | ER | 9.12 | 8.51 | 117.1 | 3.76 | 134 | 10 | 6.5 | 6.7 | 1408 | 0.14 | 19 | 6.6 | 2940 | 80 | 0.56
| 11 | 38.19 | 1.949 | 57.676 | 15.219 | 14.349 | 37.57% | 0 | 0 | 142.8 |  | 11 |  |  |  | 11 | 47.88 | 48.22 | 48.01 |  |  | 41.5 | 45.72 | 43.11 | TDS (MONTHLY AVERAGE) | 7537.6 | 7193.6 |  | 7448 |  | 5417 |  | mg/l |  |  | XX | Membrane Filter |  |  |  |  | (27) TKN | mg/L | 000625 | 15.0323 | 13 | 35.545 | 0.9 |  | 74.3 | 116 | 4.04 | 20 | 6.6 | 14 | 12 | 0.23 | 0.6 | TNTC |  | EIGHT THRU FORTEENTH | [9 empty] | 16 | 34.089 | 7.36 | 3.62 | 5.65 | 9.33 | 8.29 | 87.5 | 3.17 | 122 | 18 | 6.4 | 6.7 | 1415 | 14 | 16 | 6.6 | 2940 | 80 | 0.53
| 12 | 36.893 | 1.948 | 56.744 | 12.624 | 14.224 | 38.55% | 0 | 0 | 138.5 |  | 12 |  |  |  | 12 | 47.84 | 48.13 | 47.98 |  |  | 41.37 | 45.17 | 42.95 | CHLORIDE (MONTHLY AVERAGE) | 3680 | 3560 |  | 3610 |  | 2700 |  | mg/l |  |  |  | Most Probable Number |  |  |  |  | (28) Ammonia (NH3 - N) | mg/L | 000610 | 12.411 | 14 | 34.876 | 0.7 |  | 85.2 | 112 | 2.1 | 10 | 6.7 | 17 | 13 | 0.34 | 0.48 | 0 |  | FIFTHTEENTH THRU | [9 empty] | 17 | 36.113 | 9.79 | 3 | 9.36 | 9.67 | 4.3 | 105.6 | 4.03 | 124 | 20 | 6.4 | 6.7 | 1430 | 11 | 16 | 6.6 | 2920 | 80 | 0.6
| 13 | 35.545 | 1.858 | 55.782 | 12.432 | 13.995 | 39.37% | 0.228 | 0 | 140 |  | 13 |  |  |  | 13 | 47.88 | 48.14 | 47.99 |  |  | 41.41 | 46.82 | 43.24 | AMMONIA-N (MONTHLY AVERAGE) | 0.93 | 0.946 |  | 1.264 |  | 0.72 |  | mg/l |  | (12) Type of Effluent Disposal or Reclaimed Water Reuse | [6 empty] | (29) Nitrate | mg/L | 071850 | 0.35774 | 15 | 34.082 | 0.8 |  | 117.1 | 134 | 3.76 | 10 | 6.6 | 19 | 0.14 | 0.3 | 0.56 | 0 |  | TWENTY SECOND | [9 empty] | 18 | 40.818 | 10.4 | 7.51 | 9.94 | 10.37 | 2.72 | 79.2 | 2.82 | 96 | 19 | 6.4 | 6.6 | 1281 | 12 | 14 | 6.5 | 2610 | 77 | 0.96
| 14 | 34.876 | 1.803 | 55.846 | 0.575 | 13.897 | 39.85% | 0.629 | 0 | 1595 |  | 14 |  |  |  | 14 | 43.41 | 48.14 | 45.55 |  |  | 35.75 | 45.29 | 40.66 | TKN (MONTHLY AVERAGE) | 1.18 | 1.26 |  | 1.64 |  | 0.89 |  | mg/l |  |  |  | Deep Well Injection |  |  |  |  | (30) Total Phosphorus | mg/L | 000665 | 1.7561 | 16 | 34.089 | 0.7 |  | 87.5 | 122 | 3.17 | 18 | 6.6 | 16 | 14 | 0.16 | 0.53 | 0 |  | TWENTY THIRD THRU | [9 empty] | 19 | 39.012 | 8.39 | 7.78 | 2.67 | 10.26 | 9.6 | 60.4 | 15.4 | 98 | 15 | 6.5 | 6.6 | 1288 | 10 | 11 | 6.5 | 2650 | 80 | 11
| 15 | 34.082 | 1.74 | 50.623 | 0.319 | 13.612 | 39.94% | 0.552 | 0 | 130.3 |  | 15 |  |  |  | 15 | 43.88 | 48.44 | 46.42 |  |  | 34.51 | 41.79 | 38.49 | pH (MONTHLY AVERAGE) | 8.102 | 7.912 |  | 8.152 |  | 8 |  | Std units |  | (13) Limited Wet Wheather Discharge Activated | [6 empty] | (31) Minimum Chlorine Residual | mg/L | - | 0.2 | 17 | 36.113 | 0.5 |  | 105.6 | 124 | 4.03 | 20 | 6.6 | 16 | 11 | 0.17 | 0.6 | 0 |  | THIRTY FIRST | [9 empty] | 20 | 37.457 | 9.68 | 8.09 | 7.13 | 2.42 | 9.23 | 127.5 | 2.13 | 484 | 20 | 6.5 | 6.6 | 1372 | 11 | 11 | 6.5 | 2800 | 80 | 11
| 16 | 34.089 | 1.791 | 52.482 | 11.791 | 13.578 | 39.83% | 0.538 | 0 | 126.8 |  | 16 |  |  |  | 16 | 48.13 | 48.31 | 48.23 |  |  | 41.31 | 44.4 | 42.56 | CONDUCTIVITY (MONTHLY AVERAGE) | 12108 | 9626.4 |  | 12018 |  | 9210 |  | umho/cm |  |  |  | YES |  | XX | Not Applicable |  | (32) Maximum Chlorine Residual | mg/L | - | 1 | 18 | 40.818 | 0.7 |  | 79.2 | 96 | 2.82 | 19 | 6.5 | 14 | 12 | 0.18 | 0.96 | 310 | [11 empty] | 21 | 37.161 | 9.57 | 9.73 | 7.75 | 7.44 | 2.21 | 59.7 | 1.75 | 98 | 22 | 6.4 | 6.6 | 1430 | 12 | 14 | 6.6 | 2900 | 80 | 0.49
| 17 | 36.113 | 1.9 | 54.501 | 0.928 | 13.904 | 38.5% | 0.618 | 2.02 | 129 |  | 17 |  |  |  | 17 | 48.23 | 48.41 | 48.4 |  |  | 40.53 | 45.26 | 42.26 | FECAL COLIFORM (MONTHLY AVERAGE) | 0 | 0 |  | 0 |  | 0 |  | # col/100ml |  |  |  | NO |  |  |  |  | (33) Other Effluent Parameters |  |  |  | 19 | 39.012 | 0.7 |  | 60.4 | 98 | 15.4 | 15 | 6.5 | 11 | 10 | 0.18 | 11 | 0 | B) | Solid Sludge Hauled from Plant: | [9 empty] | 22 | 36.826 | 2.86 | 9.98 | 9.28 | 7.79 | 6.89 | 69.9 | 2.19 | 118 | 14 | 6.5 | 6.6 | 1405 | 13 | 14 | 6.6 | 2830 | 80 | 0.61
| 18 | 40.818 | 2.055 | 57.929 | 20.858 | 14.299 | 35.03% | 0.185 | 0.02 | 137.8 |  | 18 |  |  |  | 18 | 48.18 | 48.47 | 48.33 |  |  | 40.92 | 44.48 | 42.37 | TEMPERATURE (MONTHLY AVERAGE) | 73.6 | 72 |  | 72.2 |  | 76 |  | deg. F | [12 empty] | 20 | 37.457 | 0.7 |  | 127.5 | 484 | 2.13 | 20 | 6.5 | 11 | 11 | 0.15 | 11 | 9 |  | WEEK OF | MARCH | TONS |  | % SOLIDS |  | HAULERS |  |  | DISPOSAL SITE | 23 | 35.766 | 7.52 | 2.36 | 9.32 | 9.47 | 7.42 | 56.2 | 1.36 | 98 | 20 | 6.6 | 6.6 | 1425 | 13 | 0 | 6.6 | 2950 | 80.4 | 1
| 19 | 39.012 | 1.969 | 55.398 | 19.031 | 13.262 | 33.99% | 0 | 0 | 120.5 |  | 19 |  |  |  | 19 | 48.17 | 48.37 | 48.3 |  |  | 40.86 | 45.29 | 42.51 | TOTAL PHOSPHOROUS (MONTHLY AVG.) | 0.01 | 0.074 |  | 0.0116 |  | 0.013 |  | mg/l |  | (14) Cumulative Days of Wet Wheather Discharge | [10 empty] | 21 | 37.161 | 0.8 |  | 59.7 | 98 | 1.75 | 22 | 6.6 | 14 | 12 | 0.15 | 0.49 | 0 | [10 empty] | Allied Waste Landfill | 24 | 35.145 | 7.76 | 7.27 | 2.21 | 9.3 | 8.75 | 56.5 | 1.53 | 96 | 18 | 6.5 | 6.6 | 1506 | 13 | 15 | 6.6 | 2890 | 80.6 | 1.7
| 20 | 37.457 | 1.91 | 54.437 | 15.796 | 12.989 | 34.68% | 0.171 | 0 | 122.2 |  | 20 |  |  |  | 20 | 48.19 | 48.4 | 48.31 |  |  | 41.08 | 46.15 | 42.95 | SULFATE (MONTHLY AVERAGE) | 851.8 | 824.8 |  | 915.2 |  | 650 |  | mg/l |  |  |  | N/A | [8 empty] | 22 | 36.826 | 0.7 |  | 69.9 | 118 | 2.19 | 14 | 6.6 | 14 | 13 | 0.22 | 0.61 | 0 |  | FIRST THRU SEVENTH |  | 572 |  | 17.64 |  | SYNAGRO |  |  | Taylor County, GA | 25 | 34.698 | 9.1 | 7.72 | 6.85 | 2.22 | 8.77 | 188 | 4.5 | 80 | 19 | 6.4 | 6.7 | 1434 | 11 | 14 | 6 | 2930 | 81.1 | 0.94
| 21 | 37.161 | 1.883 | 52.706 | 13.681 | 13.338 | 35.89% | 0.746 | 0 | 175.2 |  | 21 |  |  |  | 21 | 43.25 | 48.44 | 45.62 |  |  | 36.18 | 44.53 | 40.81 | C.O.D. (MONTHLY AVERAGE) | #DIV/0! | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | mg/l |  | (15) Plant Staffing: | [10 empty] | 23 | 35.766 | 0.7 |  | 56.2 | 98 | 1.36 | 20 | 6.6 | 0 | 13 | 0.41 | 1 | 0 | [10 empty] | Allied Waste Landfill | 26 | 34.622 | 8.84 | 8.98 | 7.24 | 6.93 | 2.11 | 109.4 | 2.41 | 136 | 18 | 6.5 | 6.6 | 1310 | 11 | 14 | 6.5 | 2750 | 81.4 | 0.69
| 22 | 36.826 | 1.958 | 53.603 | 12.432 | 13.462 | 36.56% | 0.83 | 0 | 153.8 |  | 22 |  |  |  | 22 | 43.59 | 48.61 | 46.44 |  |  | 35.14 | 41.31 | 38.28 | IRON (MONTHLY AVERAGE) | #DIV/0! | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | mg/l | [12 empty] | 24 | 35.145 | 0.6 |  | 56.5 | 96 | 1.53 | 18 | 6.6 | 15 | 13 | 0.35 | 1.7 | 18 |  | EIGHT THRU FORTEENTH |  | 418 |  | 17.52 |  | SYNAGRO |  |  | Taylor County, GA | 27 | 33.989 | 2.05 | 9.27 | 8.71 | 7.45 | 6.35 | 117 | 3 | 140 | 15 | 6.5 | 6.6 | 1520 | 11 | 13 | 6.6 | 3090 | 81.6 | 0.59
| 23 | 35.766 | 1.881 | 53.219 | 13.809 | 13.497 | 37.74% | 0.718 | 0 | 140.5 |  | 23 |  |  |  | 23 | 48.19 | 48.48 | 48.36 |  |  | 41.31 | 45.74 | 42.48 | SULFIDE (MONTHLY AVERAGE) | #DIV/0! | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | mg/l |  |  | Day Shift Operator: |  |  | Class | "A" | Cert. No. | 4545 |  |  |  | 25 | 34.698 | 0.2 |  | 188 | 80 | 4.5 | 19 | 6 | 14 | 11 | 0.32 | 0.94 | TNTC |  | FIFTHTEENTH THRU | [8 empty] | Allied Waste Landfill | 28 | 34.147 | 7.26 | 0.8 | 8.94 | 9.05 | 8.45 | 130 | 3 | 152 | 24 | 6.5 | 6.6 | 1673 | 13 | 15 | 6.6 | 2530 | 81.5 | 1.3
| 24 | 35.145 | 1.817 | 55.238 | 12.912 | 13.552 | 38.56% | 0.788 | 0 | 139 |  | 24 |  |  |  | 24 | 48.16 | 48.45 | 48.33 |  |  | 41.3 | 44.52 | 42.55 | LOWER MONITORING INTERVAL | 1449'-1557' | 1970'-2025' |  | 1970'-2027' |  | 1500'-1600' |  | Ft. bls | [12 empty] | 26 | 34.622 | 1 |  | 109.4 | 136 | 2.41 | 18 | 6.5 | 14 | 11 | 0.34 | 0.69 | 0 |  | TWENTY SECOND |  | 773 |  | 17.52 |  | SYNAGRO |  |  | Taylor County, GA | 29 | 33.456 | 7.41 | 6.94 | 2.12 | 8.9 | 8.39 | 94 | 3 | 116 | 22 | 6.6 | 6.6 | 1660 | 14 | 17 | 6.6 | 3070 | 81.2 | 2.7
| 25 | 34.698 | 1.84 | 54.981 | 12.688 | 13.96 | 40.23% | 0.461 | 0 | 173 |  | 25 |  |  |  | 25 | 48.21 | 48.54 | 48.42 |  |  | 41.94 | 45.1 | 43.01 | MONTHLY MAX DAILY PRESSURE | 46.82 | 43.09 |  | 45.88 |  | 64.76 |  | FT. HEAD |  |  | Evening Shift Operator: |  |  | Class | "A" | Cert. No. | 4474 |  |  |  | 27 | 33.989 | 0.9 |  | 117 | 140 | 3 | 15 | 6.6 | 13 | 11 | 0.34 | 0.59 | 152 |  | TWENTY THIRD THRU | [8 empty] | Allied Waste Landfill | 30 | 33.273 | 8.75 | 7.42 | 6.6 | 2.11 | 8.45 | 86 | 6 | 120 | 29 | 6.6 | 6.6 | 1500 | 15 | 28 | 6.6 | 3020 | 81.4 | 4.4
| 26 | 34.622 | 1.822 | 51.136 | 13.136 | 13.614 | 39.32% | 0 | 0 | 140.2 |  | 26 |  |  |  | 26 | 48.31 | 48.6 | 48.46 |  |  | 41.65 | 45.04 | 42.65 | MONTHLY MIN DAILY PRESSURE | 11.14 | 34.46 |  | 35.6 |  | 12.43 |  | FT. HEAD | [12 empty] | 28 | 34.147 | 0.7 |  | 130 | 152 | 3 | 24 | 6.6 | 15 | 13 | 0.49 | 1.3 | 0 |  | THIRTY FIRST |  | 1012 |  | 16.0314 |  | SYNAGRO |  |  | Taylor County, GA | 31 | 33.381 | 8.62 | 8.77 | 7.08 | 6.79 | 2.01 | 97 | 7 | 112 | 44 | 6.6 | 6.6 | 1715 | 9.6 | 18 | 6.6 | 3040 | 82 | 4.1
| 27 | 33.989 | 1.754 | 53.411 | 11.31 | 13.546 | 39.85% | 0.316 | 0 | 125.5 |  | 27 |  |  |  | 27 | 48.36 | 48.65 | 48.48 |  |  | 41.85 | 44.66 | 42.82 | TDS (MONTHLY AVERAGE) | 9388 | 31573.4 |  | 24114.8 |  | 26230 |  | mg/l |  |  | Night Shift Operator: |  |  | Class | "A" | Cert. No. | 3207 |  |  |  | 29 | 33.456 | 0.6 |  | 94 | 116 | 3 | 22 | 6.6 | 17 | 14 | 0.73 | 2.7 | 107 | C) | Monthly quantities of solid sludge stockpiled at plant.Solid Sludge Hauled from Plant: | [9 empty] | TOT | 1086.337 | 186.44 | 219.01 | 201.46 | 195.5 | 175.44 | 3033.6 | 122.56 | 6014 | 570 | 202.5 | 206.1 | 45371 | 384.74 | 466 | 203.8 | 91940 | 2476.3 | 54.44
| 28 | 34.147 | 1.766 | 52.065 | 12.11 | 13.184 | 38.61% | 0.847 | 0 | 159.5 |  | 28 |  |  |  | 28 | 39.39 | 48.66 | 43.15 |  |  | 34.63 | 43.87 | 40.82 | CHLORIDE (MONTHLY AVERAGE) | 4900 | 16680 |  | 14640 |  | 14200 |  | mg/l | [12 empty] | 30 | 33.273 | 0.6 |  | 86 | 120 | 6 | 29 | 6.6 | 28 | 15 | 0.61 | 4.4 | 0 |  | 1) | Additions |  |  | Cubic Yards | [5 empty] | AVG | 35.0431 | 6.6586 | 7.8218 | 7.4615 | 6.9821 | 6.7477 | 97.8581 | 3.9535 | 194 | 18.3871 | 6.5323 | 6.6484 | 1463.5806 | 12.411 | 15.0323 | 6.5742 | 2965.8065 | 79.8806 | 1.7561
| 29 | 33.456 | 1.702 | 50.303 | 5.126 | 12.99 | 38.83% | 0.825 | 0 | 165.2 |  | 29 |  |  |  | 29 | 39.56 | 48.79 | 45.88 |  |  | 35.24 | 42.47 | 38.93 | AMMONIA-N (MONTHLY AVERAGE) | 9.52 | 1.46 |  | 2.232 |  | 0.37 |  | mg/l |  |  | Lead Operator:_________________________________ | [9 empty] | 31 | 33.381 | 0.7 |  | 97 | 112 | 7 | 44 | 6.6 | 18 | 9.6 | 0.05 | 4.1 | 9 | [5 empty] | Tons | [5 empty] | MAX | 40.818 | 10.4 | 10.41 | 9.94 | 10.42 | 9.6 | 188 | 15.4 | 2216 | 44 | 6.7 | 6.7 | 1715 | 17 | 28 | 6.7 | 3270 | 82 | 11
| 30 | 33.273 | 1.676 | 47.869 | 6.567 | 13.137 | 39.48% | 0.814 | 0 | 138.2 |  | 30 |  |  |  | 30 | 48.28 | 48.58 | 48.47 |  |  | 39.72 | 44.84 | 42.12 | TKN (MONTHLY AVERAGE) | 8.242 | 2.18 |  | 3.02 |  | 0.91 |  | mg/l | [5 empty] | Signature |  | Cert. No. |  |  |  |  | Lead Operator : This is to certify that I am familar with the information contained on this report and that to the best of | [14 empty] | 2) | Removals |  |  | Cubic Yards | [5 empty] | MIN | 31.788 | 0 | 0.8 | 2.12 | 0.01 | 1.9 | 56.2 | 1.36 | 44 | 4 | 6.4 | 6.6 | 1281 | 0.14 | 0 | 6 | 2530 | 77 | 0.48
| 31 | 33.381 | 1.726 | 50.559 | 13.329 | 12.328 | 36.93% | 0.779 | 0 | 148.5 |  | 31 |  |  |  | 31 | 48.29 | 48.54 | 48.47 |  |  | 41.51 | 44.47 | 42.64 | pH (MONTHLY AVERAGE) | 7.314 | 7.482 |  | 7.412 |  | 7.49 |  | Std units | [12 empty] | my knowledge and belief, this information is true, complete and accuate. | [16 empty] | X |  | Tons | [6 empty] | item #1 | 9.3775 | 10.9701 | 10.4291 | 9.6605 | 9.4757 | MAX HOURLY FLOW (MG) = |  |  |  | 2.061 | ON THE | 9 | DAY OF THIS MONTH
| TOTAL | 1086.337 | 56.351 | 1655.174 | 268.991 | 420.591 |  | 13.775 | 4.53 | 5811.6 | [5 empty] | TOTAL | 1266.23 | 1356.86 | 1334.28 |  |  | 1058.15 | 1247.59 | 1171.94 | CONDUCTIVITY (MONTHLY AVERAGE) | 15758 | 46560 |  | 42620 |  | 40500 |  | umho/cm | [33 empty] | Signature |  |  |  |  | item #2 | 45.6071 | 46.7307 | 47.5586 | 47.78 | 46.2981
| AVERAGE | 35.0431 | 1.8178 | 53.3927 | 8.6771 | 13.5675 | 38.72% | 0.551 | 0.14613 | 187.471 | [5 empty] | AVERAGE | 45.2225 | 48.4593 | 47.6529 |  |  | 37.7911 | 44.5568 | 41.855 | FECAL COLIFORM (MONTHLY AVERAGE) | 0 | 0 |  | 0 |  | 0 |  | # col/100ml | [12 empty] | Signed: ____________________________ Date: ___________________ | [20 empty] | Title |  |  |  |  | item #3 | 36.04 | 36.2 | 37.3 | 36.8 | 35.3
[16 empty] | MAXIMUM | 48.36 | 48.79 | 48.48 |  |  | 42.49 | 46.82 | 43.43 | TEMPERATURE (MONTHLY AVERAGE) | 71.8 | 71.2 |  | 70.2 |  | 74 |  | deg. F | [33 empty] | Date |  |  |  | item #1 | =monthly maximum of the daily flows (MG), with peakhour flow (MGD) on the day of the month with maximum flow = | [14 empty] | 2.061 | MG/hour multiplied by
[16 empty] | MINIMUM | 15.87 | 48.13 | 43.15 |  |  | 11.14 | 41.31 | 38.28 | TOTAL PHOSPHOROUS (MONTHLY AVG.) | 0.011 | 0.0112 |  | 0.012 |  | 0.01 |  | mg/l | [12 empty] | Name: Michael A. Just | [14 empty] | * Sludge Reports should be submitted along with the monthly operating reports to Broward County Department | [10 empty] | the % of average % of TOTAL RAW FLOW to each Injection well.
[25 empty] | SULFATE (MONTHLY AVERAGE) | 765.2 | 2694 |  | 2476 |  | 1180 |  | mg/l | [27 empty] | of Natural Resource Protection, 218 S. W. 1st Avenue, Fort Lauderdale, Florida 33301 | [9 empty] | item #2 | =monthly average injection well pressure at injection well (psig)
[25 empty] | C.O.D. (MONTHLY AVERAGE) | #DIV/0! | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | mg/l | [12 empty] | Company Name: City of Fort Lauderdale Telephone No. (954) 523-1002 | [24 empty] | item #3 | =monthly wellhead pressure with no flow (shut-in pressure,psig)
[25 empty] | IRON (MONTHLY AVERAGE) | #DIV/0! | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | mg/l | [37 empty] | PLANT STAFFING
[5 empty] | PAGE 2 | [19 empty] | SULFIDE (MONTHLY AVERAGE) | #DIV/0! | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | mg/l | [37 empty] | Day Shift Operator |  |  | Class: | "A" | Certificate No. | 4545 | Name: |  | McGEARY, J.
[71 empty] | Evening Shift Operator |  |  | Class: | "A" | Certificate No. | 4474 | Name: |  | BAYLER, J.
[20 empty] | PAGE 20 | [50 empty] | Night Shift Operator |  |  | Class: | "A" | Certificate No. | 3207 | Name: |  | HOSTNICK, N.
[71 empty] | Lead Operator |  |  | Class: | "A" | Certificate No. | 2769 | Name: |  | JUST, M.
[71 empty] | Type of Effluent Disposal or Reclaimed Water Reuse: |  |  |  |  | DEEPWELL INJECTION
[71 empty] | Permited Wet Weather Discharge Activated: |  |  |  | YES: |  | NO: |  |  | Not Applicable |  | X
[28 empty] | Page 28 | [42 empty] | If Yes, cumulative days of wet weather:
Attach additional sheets if necessary to list all certified operators. See page 1 "COVER PAGE" of supplental attachements.
DEP form 62-620.910(10), effective November 29, 1994
[19 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [47 empty] | Department of Natural Resource Protection
[5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [13 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [47 empty] | Division of Pollution Prevention and Remediation Programs
[5 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [13 empty] | MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING | [50 empty] | 218 S. W. 1st Avenue
[5 empty] | MONTHLY OPERATIONAL REPORT | [13 empty] | MONITORING WELL TWO |  |  |  | 1/07/04 thru 1/06/09 | [39 empty] | SLUDGE HAULERS MONTHLY REPORT | [6 empty] | Fort Lauderdale, FL 33301
[5 empty] | INFLUENT DATA | [11 empty] | MW-2 | I.D. #: 5066A11308 & 09 |  |  | PERMIT # 0054569-142-UO | [41 empty] | BROWARD COUNTY CODE SECTION 27-356 (d)(4)(1) | [5 empty] | Tel. No. (954) 523-1002
| RUN DATE | [14 empty] | RUN DATE | [52 empty] | *FAX (954) 519-1245
| 2026-07-30 | [14 empty] | 2026-07-30 |  | UPPER MONITOR ZONE |  |  |  |  | LOWER MONITOR ZONE
[17 empty] | MIN | MAX | AVG |  |  | MIN | MAX | AVG | [35 empty] | Plant Name: | GEORGE T. LOHMEYER WASTEWATER TREATMENT FACILITY
| MARCH | RAW | RAW TSS | RAW SS | RAW | RAW | RAW | RAW | RAW | RAW | [5 empty] | MARCH | FT HEAD | FT HEAD | FT HEAD |  |  | FT HEAD | FT HEAD | FT HEAD | [35 empty] | Address: | 1765 S.E. 18th Street at Eisenhower Boulevard | [6 empty] | MONTH: | MARCH
| 2005 | CBOD | TOTAL | FIXED | COD | pH | CL_ | ALK. | H2S | TEMP.(F) | [5 empty] | 2005 | ABOVE | ABOVE | ABOVE |  |  | ABOVE | ABOVE | ABOVE | [35 empty] | Phone: | (954) 523-1002 * FAX (954) 468-1577 | [6 empty] | YEAR: | 2005
[17 empty] | NGVD | NGVD | NGVD |  |  | NGVD | NGVD | NGVD
| 1 | 102.9 | 104 | 0 | 180 | 7 | 920 | 214 | 6 | 78 | [5 empty] | 1 | 21.02 | 25.67 | 23.87 |  |  | 38.99 | 42.46 | 41.36 | [35 empty] | a) | WEEK OF | MARCH |  | Type of Sludge |  |  | Disopsal Site |  |  | Cubic Yards
| 2 | 79.8 | 120 | 8 | 142 | 7 | 780 | 222 | 5 | 77 | [5 empty] | 2 | 24.21 | 25.86 | 24.87 |  |  | 42.37 | 42.51 | 42.47
| 3 | 122.4 | 174 | 36 | 178 | 7 | 730 | 238 | 5 | 75 | [5 empty] | 3 | ER | ER | ER |  |  | ER | ER | ER | [36 empty] | FIRST THRU SEVENTH |  |  | GRIT |  |  | Central Landfill |  |  | 10
| 4 | 80.9 | 44 | 4 | 165 | 7 | 820 | 207 | 5 | 77 | [5 empty] | 4 | 24.55 | 25.83 | 25.11 |  |  | 42.5 | 42.74 | 42.58
| 5 | 95.9 | 122 | 14 | 185 | 7 | 770 | 188 | 5 | 77 | [5 empty] | 5 | 24.58 | 26.78 | 25.35 |  |  | 42.5 | 42.7 | 42.54 | [36 empty] | EIGHT THRU FORTEENTH |  |  | GRIT |  |  | Central Landfill |  |  | 10
| 6 | 93.6 | 124 | 6 | 183 | 7 | 760 | 210 | 4 | 77 | [5 empty] | 6 | ER | ER | ER |  |  | ER | ER | ER | [36 empty] | FIFTHTEENTH THRU
| 7 | 114.5 | 80 | 18 | 191 | 7 | 800 | 210 | 5 | 76.7 | [5 empty] | 7 | ER | ER | ER |  |  | ER | ER | ER | [36 empty] | TWENTY SECOND |  |  | GRIT |  |  | Central Landfill |  |  | 10
| 8 | 129 | 2216 | 406 | 231 | 7 | 990 | 264 | 7 | 77 | [5 empty] | 8 | 20.75 | 25.54 | 23.74 |  |  | 35.94 | 42.43 | 40.4 | [36 empty] | TWENTY THIRD THRU
| 9 | 123.9 | 136 | 8 | 172 | 7 | 780 | 212 | 6 | 76 | [5 empty] | 9 | 24.23 | 24.71 | 24.43 |  |  | 42.28 | 42.69 | 42.47 | [36 empty] | THIRTY FIRST |  |  | GRIT |  |  | Central Landfill |  |  | 10
| 10 | 118.4 | 152 | 24 | 188 | 7 | 710 | 210 | 4 | 76 | [5 empty] | 10 | 24.1 | 25.68 | 24.71 |  |  | 42.56 | 42.69 | 42.56
| 11 | 86.6 | 92 | 16 | 218 | 7 | 730 | 218 | 5 | 76 | [5 empty] | 11 | 23.99 | 26.11 | 25.01 |  |  | 42.55 | 42.77 | 42.66 | [35 empty] | b) | WEEK OF | MARCH |  | Type of Sludge |  |  | Disopsal Site |  |  | Cubic Yards
| 12 | 85.2 | 98 | 8 | 212 | 7 | 700 | 216 | 6 | 76.5 | [5 empty] | 12 | 24.73 | 26.23 | 25.35 |  |  | 42.64 | 42.74 | 42.61
| 13 | 74.3 | 116 | 16 | 186 | 7 | 710 | 198 | 6 | 76 | [5 empty] | 13 | 24.53 | 26.51 | 25.56 |  |  | 42.67 | 42.82 | 42.71 | [36 empty] | FIRST THRU SEVENTH |  |  | RAGS |  |  | Central Landfill |  |  | 10
| 14 | 85.2 | 112 | 12 | 201 | 7.1 | 640 | 198 | 5 | 77 | [5 empty] | 14 | 20.82 | 26.18 | 23.21 |  |  | 37.19 | 42.82 | 39.53
| 15 | 117.1 | 134 | 10 | 326 | 7 | 640 | 220 | 5 | 77 | [5 empty] | 15 | 20.3 | 26.36 | 23.73 |  |  | 34.46 | 42.4 | 40.14 | [36 empty] | EIGHT THRU FORTEENTH |  |  | RAGS |  |  | Central Landfill |  |  | 10
| 16 | 87.5 | 122 | 26 | 176 | 7 | 730 | 220 | 5 | 78 | [5 empty] | 16 | 25.56 | 26.9 | 26.08 |  |  | 42.4 | 42.65 | 42.49 | [36 empty] | FIFTHTEENTH THRU
| 17 | 105.6 | 124 | 20 | 200 | 7 | 670 | 196 | 5 | 78 | [5 empty] | 17 | 25.76 | 27.2 | 26.12 |  |  | 42.65 | 42.81 | 42.73 | [36 empty] | TWENTY SECOND |  |  | RAGS |  |  | Central Landfill |  |  | 10
| 18 | 79.2 | 96 | 24 | 211 | 7 | 670 | 196 | 5 | 77 | [5 empty] | 18 | 25.38 | 26.71 | 26.01 |  |  | 42.66 | 42.86 | 42.76 | [36 empty] | TWENTY THIRD THRU
| 19 | 60.4 | 98 | 16 | 213 | 6.8 | 650 | 198 | 5 | 77 | [5 empty] | 19 | 25.07 | 26.7 | 25.78 |  |  | 42.68 | 42.8 | 42.75 | [36 empty] | THIRTY FIRST |  |  | RAGS |  |  | Central Landfill |  |  | 10
| 20 | 127.5 | 484 | 68 | 248 | 7 | 670 | 220 | 5 | 77 | [5 empty] | 20 | 25.28 | 26.87 | 26.03 |  |  | 42.7 | 42.89 | 42.88 | [36 empty] | BCSR = Broward County Septage Receiving
| 21 | 59.7 | 98 | 12 | 246 | 7 | 730 | 218 | 4 | 78 | [5 empty] | 21 | 21.33 | 26.79 | 23.97 |  |  | 35.99 | 42.95 | 39.11 | [35 empty] | c) | WEEK OF | MARCH |  | Type of Sludge |  |  | Disopsal Site |  |  | Gallons
| 22 | 69.9 | 118 | 26 | 371 | 7 | 750 | 188 | 5 | 78 | [5 empty] | 22 | 21.37 | 26.86 | 24.37 |  |  | 34.77 | 42.5 | 39.72
| 23 | 56.2 | 98 | 15 | 170 | 6.8 | 740 | 210 | 5 | 78 | [5 empty] | 23 | 26.11 | 27.71 | 26.66 |  |  | 42.43 | 42.71 | 42.51 | [36 empty] | FIRST THRU SEVENTH |  |  | VAC/Plastic & Rags |  |  | BCSR |  |  | 0
| 24 | 56.5 | 96 | 40 | 452 | 7 | 700 | 210 | 5 | 78.2 | [5 empty] | 24 | 26.34 | 27.36 | 26.87 |  |  | 42.58 | 42.74 | 42.57
| 25 | 188 | 80 | 24 | 369 | 7 | 820 | 210 | 5 | 78 | [5 empty] | 25 | 26.75 | 28.3 | 27.47 |  |  | 42.65 | 42.87 | 42.83 | [36 empty] | EIGHT THRU FORTEENTH |  |  | VAC/Plastic & Rags |  |  | BCSR |  |  | 0
| 26 | 109.4 | 136 | 4 | 387 | 7.1 | 760 | 198 | 5 | 78.7 | [5 empty] | 26 | 27.23 | 28.55 | 27.85 |  |  | 42.77 | 42.94 | 42.87 | [36 empty] | FIFTHTEENTH THRU
| 27 | 117 | 140 | 16 | 198 | 7 | 790 | 204 | 7 | 78.8 | [5 empty] | 27 | 27.65 | 28.8 | 28.16 |  |  | 42.88 | 43.02 | 42.97 | [36 empty] | TWENTY SECOND |  |  | VAC/Plastic & Rags |  |  | BSCR |  |  | 0
| 28 | 130 | 152 | 32 | 170 | 7 | 770 | 226 | 5 | 78.5 | [5 empty] | 28 | 21.67 | 28.75 | 25.11 |  |  | 35.7 | 43.09 | 40.41 | [36 empty] | TWENTY THIRD THRU
| 29 | 94 | 116 | 28 | 195 | 7 | 1100 | 212 | 6 | 76.8 | [5 empty] | 29 | 21.06 | 27.37 | 25.05 |  |  | 36.9 | 42.67 | 41.25 | [36 empty] | THIRTY FIRST |  |  | VAC/Plastic & Rags |  |  | BSCR |  |  | 0
| 30 | 86 | 120 | 24 | 151 | 7 | 770 | 214 | 6 | 78.8 | [5 empty] | 30 | 25.6 | 27.57 | 26.64 |  |  | 42.61 | 42.77 | 42.62 | [35 empty] | TOTALS
| 31 | 97 | 112 | 24 | 168 | 7 | 740 | 214 | 6 | 78.4 | [5 empty] | 31 | 26.66 | 27.87 | 27.14 |  |  | 42.75 | 42.86 | 42.82 | [36 empty] | a) | 40 | cu.yds |  | GRIT |  | Signature
| TOTAL | 3033.6 | 6014 | 985 | 6883 | 216.8 | 23540 | 6559 | 163 | 2396.4 | [5 empty] | TOTAL | 676.63 | 751.77 | 714.25 |  |  | 1141.77 | 1196.9 | 1175.32 | [36 empty] | b) | 40 | cu.yds |  | RAGS |  | Title
| AVERAGE | 97.8581 | 194 | 32.8333 | 222.0323 | 6.9935 | 759.3548 | 211.5806 | 5.2581 | 77.3032 | [5 empty] | AVERAGE | 24.1654 | 26.8489 | 25.5089 |  |  | 40.7775 | 42.7464 | 41.9757 | [36 empty] | c) | 0 | gal. |  | VAC/Plastic & Rags |  | Date
[16 empty] | MAXIMUM | 27.65 | 28.8 | 28.16 |  |  | 42.88 | 43.09 | 42.97
[16 empty] | MINIMUM | 20.3 | 24.71 | 23.21 |  |  | 34.46 | 42.4 | 39.11 | [36 empty] | * Sludge Reports should be submitted along with the monthly operating reports to Broward County Department
of Natural Resource Protection, 218 S. W. 1st Avenue, Fort Lauderdale, Florida 33301
PAGE 3
PAGE 21
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
[5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [13 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
[5 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [13 empty] | MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
[5 empty] | MONTHLY OPERATIONAL REPORT | [13 empty] | MONITORING WELL THREE |  |  |  | 1/07/04 thru 1/06/09
[5 empty] | EFFLUENT DATA PART 1 | [11 empty] | MW-3 | I.D. #: 5066A11310 |  |  | PERMIT # 0054569-142-UO
RUN DATE
[16 empty] | 2026-07-30 |  | UPPER MONITOR ZONE |  |  |  |  | LOWER MONITOR ZONE
| RUN DATE | [15 empty] | MIN | MAX | AVG |  |  | MIN | MAX | AVG
| 2026-07-30 | [14 empty] | MARCH | FT HEAD | FT HEAD | FT HEAD |  |  | FT HEAD | FT HEAD | FT HEAD
[14 empty] | BOD | TSS | 2005 | ABOVE | ABOVE | ABOVE |  |  | ABOVE | ABOVE | ABOVE
| MARCH | EFFLUENT | EFFL. TSS | EFFL. SS | EFFLUENT | EFFL. | EFFL. | EFFL. | EFFL. | EFFL. | TDS |  |  | MONTHLY AVG OVER 30 | MONTHLY AVG OVER 30 |  | NGVD | NGVD | NGVD |  |  | NGVD | NGVD | NGVD
| 2005 | CBOD | TOTAL | FIXED | COD | CL_ | ALK. | TURB. | COND. | TEMP.(F) |  |  |  | 0 | 0 | 1 | 20.84 | 32.48 | 28.76 |  |  | 38.8 | 45.14 | 43.1
[14 empty] | WEKKLY OVER 45 | WEKKLY OVER 45 | 2 | 32.32 | 32.58 | 32.47 |  |  | 45.07 | 45.22 | 45.05
| 1 | 4.97 | 8 | 0 | 58.1 | 870 | 190 | 7.84 | 3270 | 80 | 1534 | 1 |  | 0 | 0 | 3 | ER | ER | ER |  |  | ER | ER | ER
| 2 | 3.41 | 10 | 0 | 52.3 | 830 | 184 | 5.18 | 3240 | 79.6 | 1536 | 1 |  | SINGLE DAY OVER 60 | SINGLE DAY OVER 60 | 4 | 32.55 | 32.85 | 32.69 |  |  | 45.24 | 45.46 | 45.41
| 3 | 3.1 | 10 | 2 | 48.1 | 860 | 184 | 5.79 | 3270 | 79.3 | 1592 | 1 |  | 0 | 0 | 5 | 32.54 | 32.83 | 32.66 |  |  | 45.27 | 45.46 | 45.4
| 4 | 3.06 | 4 | 3 | 45.1 | 810 | 182 | 5.44 | 3200 | 79 | 1488 | 1 |  | 0 | 0 | 6 | ER | ER | ER |  |  | ER | ER | ER
| 5 | 3.69 | 18 | 4 | 48.1 | 780 | 188 | 5.53 | 3140 | 79 | 1501 | 1 |  |  |  | 7 | ER | ER | ER |  |  | ER | ER | ER
| 6 | 2.14 | 16 | 0 | 52.1 | 770 | 186 | 8.1 | 2890 | 79.3 | 1479 | 1 |  |  |  | 8 | 17.6 | 32.42 | 27.73 |  |  | 35.6 | 45.15 | 42.11
| 7 | 4.4 | 21 | 8 | 47.9 | 790 | 188 | 5.42 | 3150 | 80 | 1454 | 1 | 3.5386 | 3.5386 | 12.4286 | 9 | 32.19 | 32.77 | 32.47 |  |  | 45.03 | 45.42 | 45.3
| 8 | 4.05 | 12 | 0 | 49.4 | 790 | 188 | 6.94 | 3100 | 80 | 1479 | 1 |  | 3.4071 | 13 | 10 | 32.5 | 32.77 | 32.61 |  |  | 45.31 | 45.42 | 45.39
| 9 | 4.12 | 17 | 0 | 51.6 | 790 | 190 | 7.16 | 3110 | 79 | 1475 | 1 |  | 3.5086 | 14 | 11 | 32.53 | 32.86 | 32.74 |  |  | 45.32 | 45.51 | 45.46
| 10 | 4.38 | 15 | 2 | 82.3 | 750 | 190 | 6.9 | 2930 | 78 | 1424 | 1 |  | 3.6914 | 14.7143 | 12 | 32.59 | 32.81 | 32.72 |  |  | 45.41 | 45.5 | 45.48
| 11 | 7.99 | 41 | 10 | 38.8 | 720 | 192 | 17.1 | 3050 | 78.4 | 1469 | 1 |  | 4.3957 | 20 | 13 | 32.59 | 32.86 | 32.72 |  |  | 45.45 | 45.58 | 45.5
| 12 | 4.06 | 21 | 1 | 47.5 | 710 | 190 | 9.06 | 2900 | 78.6 | 1386 | 1 |  | 4.4486 | 20.4286 | 14 | 18.22 | 32.86 | 24.13 |  |  | 37.7 | 45.58 | 40.91
| 13 | 4.04 | 20 | 3 | 54.5 | 710 | 194 | 7.24 | 2910 | 78.9 | 1391 | 1 |  | 4.72 | 21 | 15 | 18.09 | 32.33 | 26.44 |  |  | 37.64 | 45.11 | 42.02
| 14 | 2.1 | 10 | 1 | 52.8 | 720 | 188 | 4.76 | 2920 | 79 | 1391 | 1 | 4.3914 | 4.3914 | 19.4286 | 16 | 32.33 | 32.66 | 32.49 |  |  | 45.11 | 45.4 | 45.35
| 15 | 3.76 | 10 | 1 | 66.8 | 710 | 198 | 4.1 | 2940 | 80 | 1408 | 1 |  | 4.35 | 19.1429 | 17 | 32.63 | 32.85 | 32.72 |  |  | 45.38 | 45.56 | 45.49
| 16 | 3.17 | 18 | 7 | 44.3 | 730 | 192 | 3.19 | 2940 | 80 | 1415 | 1 |  | 4.2143 | 19.2857 | 18 | 32.71 | 32.92 | 32.8 |  |  | 45.42 | 45.6 | 45.52
| 17 | 4.03 | 20 | 9 | 41.9 | 720 | 184 | 4.96 | 2920 | 80 | 1430 | 1 |  | 4.1643 | 20 | 19 | 32.73 | 32.92 | 32.81 |  |  | 45.45 | 45.58 | 45.5
| 18 | 2.82 | 19 | 10 | 39.3 | 660 | 180 | 6.55 | 2610 | 77 | 1281 | 1 |  | 3.4257 | 16.8571 | 20 | 32.74 | 32.97 | 32.89 |  |  | 45.47 | 45.68 | 45.52
| 19 | 15.4 | 15 | 4 | 47.1 | 660 | 180 | 6.73 | 2650 | 80 | 1288 | 1 |  | 5.0457 | 16 | 21 | 19.01 | 32.97 | 25.02 |  |  | 37.97 | 45.71 | 41.33
| 20 | 2.13 | 20 | 2 | 36.7 | 710 | 196 | 3.9 | 2800 | 80 | 1372 | 1 |  | 4.7729 | 16 | 22 | 18.98 | 32.54 | 26.65 |  |  | 37.97 | 45.23 | 42.01
| 21 | 1.75 | 22 | 2 | 36.9 | 730 | 196 | 4.68 | 2900 | 80 | 1430 | 1 | 4.7229 | 4.7229 | 17.7143 | 23 | 32.43 | 32.83 | 32.62 |  |  | 45.18 | 45.46 | 45.37
| 22 | 2.19 | 14 | 8 | 53.8 | 700 | 180 | 4.22 | 2830 | 80 | 1405 | 1 |  | 4.4986 | 18.2857 | 24 | 32.64 | 32.89 | 32.8 |  |  | 45.36 | 45.49 | 45.44
| 23 | 1.36 | 20 | 13 | 46.8 | 700 | 198 | 4.81 | 2950 | 80.4 | 1425 | 1 |  | 4.24 | 18.5714 | 25 | 32.71 | 33.04 | 32.87 |  |  | 45.42 | 45.65 | 45.49
| 24 | 1.53 | 18 | 12 | 42.6 | 710 | 196 | 3.62 | 2890 | 80.6 | 1506 | 1 |  | 3.8829 | 18.2857 | 26 | 32.88 | 33.14 | 32.97 |  |  | 45.56 | 45.71 | 45.58
| 25 | 4.5 | 19 | 3 | 34.7 | 710 | 194 | 4.8 | 2930 | 81.1 | 1434 | 1 |  | 4.1229 | 18.2857 | 27 | 32.96 | 33.21 | 33.01 |  |  | 45.68 | 45.81 | 45.77
| 26 | 2.41 | 18 | 0 | 46.9 | 690 | 186 | 5.2 | 2750 | 81.4 | 1310 | 1 |  | 2.2671 | 18.7143 | 28 | 19.93 | 33.21 | 25.45 |  |  | 37.84 | 45.88 | 42.19
| 27 | 3 | 15 | 3 | 40.9 | 780 | 196 | 4.93 | 3090 | 81.6 | 1520 | 1 |  | 2.3914 | 18 | 29 | 19.74 | 32.81 | 28.71 |  |  | 39.58 | 45.36 | 43.6
| 28 | 3 | 24 | 13 | 44.5 | 620 | 172 | 5.62 | 2530 | 81.5 | 1673 | 1 |  | 2.57 | 18.2857 | 30 | 32.65 | 32.93 | 32.76 |  |  | 45.34 | 45.49 | 45.44
| 29 | 3 | 22 | 11 | 41.6 | 770 | 194 | 6.82 | 3070 | 81.2 | 1660 | 1 |  | 2.6857 | 19.4286 | 31 | 32.81 | 32.99 | 32.95 |  |  | 45.48 | 45.58 | 45.5
| 30 | 6 | 29 | 10 | 48.5 | 750 | 196 | 10.8 | 3020 | 81.4 | 1500 | 1 |  | 3.3486 | 20.7143 | TOTAL | 804.44 | 919.3 | 867.66 |  |  | 1210.05 | 1273.74 | 1246.23
| 31 | 7 | 44 | 12 | 60.5 | 740 | 196 | 13.5 | 3040 | 82 | 1715 | 1 | 3.399 | 4.13 | 24.4286 | AVERAGE | 28.73 | 32.8321 | 30.9879 |  |  | 43.2161 | 45.4907 | 44.5082
| TOTAL | 122.56 | 570 | 154 | 1502.4 | 22990 | 5868 | 200.89 | 91940 | 2476.3 | 45371 |  |  |  |  | MAXIMUM | 32.96 | 33.21 | 33.01 |  |  | 45.68 | 45.88 | 45.77
| AVERAGE | 3.9535 | 18.3871 | 6.16 | 48.4645 | 741.6129 | 189.2903 | 6.4803 | 2965.8065 | 79.8806 | 1463.5806 |  |  | 3.8774 | 18.12 | MINIMUM | 17.6 | 32.33 | 24.13 |  |  | 35.6 | 45.11 | 40.91
| MAXIMUM | 15.4 | 44
[5 empty] | PAGE 4 | [14 empty] | PAGE 22
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
[5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [13 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
[5 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [13 empty] | MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
[5 empty] | MONTHLY OPERATIONAL REPORT | [13 empty] | REGIONAL MONITORING WELL ONE
[5 empty] | EFFLUENT DATA PART 2 | [13 empty] | RMW-1 |  |  |  | 1/07/04 thru 1/06/09
[16 empty] | RUN DATE |  |  |  |  | PERMIT # 0054569-142-UO
[16 empty] | 2026-07-30 |  | UPPER MONITOR ZONE |  |  |  |  | LOWER MONITOR ZONE
RUN DATE | [16 empty] | MIN | MAX | AVG |  |  | MIN | MAX | AVG
2026-07-30 | [15 empty] | MARCH | FT HEAD | FT HEAD | FT HEAD |  |  | FT HEAD | FT HEAD | FT HEAD
[16 empty] | 2005 | ABOVE | ABOVE | ABOVE |  |  | ABOVE | ABOVE | ABOVE
| MARCH | EFF. BACT. | EFF. BACT. | FREE | TOTAL | EFFL. | EFF PH | EFF PH | EFF. SAP | AVG. | Sufates | [5 empty] | NGVD | NGVD | NGVD |  |  | NGVD | NGVD | NGVD
| 2005 | TOTAL | FECAL | CL2 | CL2 | pH | MIN | MAX | TEMP.(C) | BLK. | [5 empty] | 1 | 44.45 | 44.59 | 44.51 |  |  | 22.93 | 23.11 | 23
[16 empty] | 2 | 44.38 | 44.47 | 44.42 |  |  | 22.84 | 22.99 | 22.91
| 1 | 80 | 9 | 0 | 0.7 | 6.6 | 6.6 | 6.6 | 3 | 40 | 129.3 |  |  |  |  | 3 | 44.39 | 44.48 | 44.45 |  |  | 22.87 | 22.98 | 22.93
| 2 | 350 | 0 | 0 | 0.8 | 6.6 | 6.6 | 6.6 | 2 | 42 | 125.5 |  |  |  |  | 4 | 44.38 | 44.57 | 44.48 |  |  | 22.83 | 23.08 | 22.96
| 3 | TNTC | TNTC | 0 | 0.9 | 6.6 | 6.5 | 6.7 | 2 | 35 | 127.5 |  |  |  |  | 5 | 44.35 | 44.48 | 44.41 |  |  | 22.79 | 22.98 | 22.89
| 4 | TNTC | TNTC | 0 | 0.8 | 6.6 | 6.6 | 6.7 | 4 | 42 | 128.3 |  |  |  |  | 6 | 44.32 | 44.42 | 44.37 |  |  | 22.8 | 22.91 | 22.85
| 5 | TNTC | TNTC | 0 | 0.8 | 6.6 | 6.6 | 6.7 | 3.5 | 54 | 126.5 |  |  |  |  | 7 | 44.35 | 44.52 | 44.44 |  |  | 22.82 | 23.03 | 22.94
| 6 | 2600 | 45 | 0 | 0.7 | 6.7 | 6.7 | 6.7 | 3 | 55 | 119.5 |  |  |  |  | 8 | 44.47 | 44.62 | 44.56 |  |  | 23 | 23.12 | 23.07
| 7 | 6600 | 0 | 0 | 0.7 | 6.6 | 6.6 | 6.7 | 3 | 64 | 118.5 |  |  |  |  | 9 | 44.47 | 44.72 | 44.58 |  |  | 22.98 | 23.22 | 23.1
| 8 | 720 | 0 | 0 | 0.7 | 6.6 | 6.6 | 6.7 | 3 | 55 | 121.3 |  |  |  |  | 10 | 44.49 | 44.66 | 44.58 |  |  | 23.05 | 23.18 | 23.1
| 9 | 36 | 0 | 0 | 0.8 | 6.6 | 6.6 | 6.6 | 2 | 43 | 115.3 |  |  |  |  | 11 | 44.5 | 44.64 | 44.56 |  |  | 23.03 | 23.13 | 23.08
| 10 | 562 | 0 | 0 | 0.8 | 6.6 | 6.6 | 6.7 | 3 | 54 | 102.5 |  |  |  |  | 12 | 44.46 | 44.59 | 44.53 |  |  | 22.98 | 23.09 | 23.03
| 11 | 38000 | 12223 | 0 | 0.4 | 6.6 | 6.5 | 6.7 | 3 | 71 | 107.5 |  |  |  |  | 13 | 44.49 | 44.59 | 44.55 |  |  | 22.98 | 23.09 | 23.04
| 12 | TNTC | TNTC | 0 | 0.7 | 6.6 | 6.5 | 6.7 | 4 | 65 | 123.8 |  |  |  |  | 14 | 37.18 | 44.61 | 40.4 |  |  | 20.53 | 23.12 | 21.83
| 13 | TNTC | TNTC | 0 | 0.9 | 6.6 | 6.6 | 6.7 | 4 | 57 | 116 |  |  |  |  | 15 | 36.91 | 43.85 | 40.98 |  |  | 20.8 | 22.49 | 21.8
| 14 | 45 | 0 | 0 | 0.7 | 6.7 | 6.5 | 6.7 | 2 | 50 | 117.8 |  |  |  |  | 16 | 12.72 | 63.95 | 43.82 |  |  | 12.43 | 64.76 | 22.33
| 15 | 27 | 0 | 0 | 0.8 | 6.6 | 6.5 | 6.7 | 3 | 42 | 119 |  |  |  |  | 17 | 44.17 | 44.37 | 44.27 |  |  | 22.24 | 22.45 | 22.37
| 16 | 71 | 0 | 0 | 0.7 | 6.6 | 6.4 | 6.7 | 2 | 39 | 126.8 |  |  |  |  | 18 | 44.25 | 44.4 | 44.33 |  |  | 22.34 | 22.51 | 22.43
| 17 | 152 | 0 | 0 | 0.5 | 6.6 | 6.4 | 6.7 | 2 | 36 | 135 |  |  |  |  | 19 | 44.25 | 44.34 | 44.3 |  |  | 22.35 | 22.46 | 22.41
| 18 | TNTC | 310 | 0 | 0.7 | 6.5 | 6.4 | 6.6 | 4 | 49 | 134.2 |  |  |  |  | 20 | 44.29 | 44.42 | 44.35 |  |  | 22.38 | 22.54 | 22.46
| 19 | 3000 | 0 | 0 | 0.7 | 6.5 | 6.5 | 6.6 | 4 | 62 | 113.2 |  |  |  |  | 21 | 44.34 | 44.51 | 44.45 |  |  | 22.44 | 22.62 | 22.54
| 20 | TNTC | 9 | 0 | 0.7 | 6.5 | 6.5 | 6.6 | 1 | 57 | 110.8 |  |  |  |  | 22 | 44.4 | 44.51 | 44.47 |  |  | 22.52 | 22.64 | 22.57
| 21 | 790 | 0 | 0 | 0.8 | 6.6 | 6.4 | 6.6 | 2 | 49 | 117.2 |  |  |  |  | 23 | 44.43 | 44.55 | 44.49 |  |  | 22.53 | 22.64 | 22.58
| 22 | 207 | 0 | 0 | 0.7 | 6.6 | 6.5 | 6.6 | 2 | 38 | 113.2 |  |  |  |  | 24 | 44.39 | 44.54 | 44.46 |  |  | 22.5 | 22.6 | 22.55
| 23 | 210 | 0 | 0 | 0.7 | 6.6 | 6.6 | 6.6 | 2 | 32 | 122.2 |  |  |  |  | 25 | 44.43 | 44.6 | 44.51 |  |  | 22.54 | 22.69 | 22.61
| 24 | 2800 | 18 | 0 | 0.6 | 6.6 | 6.5 | 6.6 | 4 | 24 | 145.5 |  |  |  |  | 26 | 44.5 | 44.61 | 44.56 |  |  | 22.62 | 22.72 | 22.66
| 25 | TNTC | TNTC | 0 | 0.2 | 6 | 6.4 | 6.7 | 4 | 24 | 148.8 |  |  |  |  | 27 | 44.56 | 44.68 | 44.62 |  |  | 22.7 | 22.79 | 22.73
| 26 | 36 | 0 | 0 | 1 | 6.5 | 6.5 | 6.6 | 1 | 37 | 129.8 |  |  |  |  | 28 | 44.59 | 44.77 | 44.68 |  |  | 22.72 | 22.94 | 22.77
| 27 | 17000 | 152 | 0 | 0.9 | 6.6 | 6.5 | 6.6 | 2 | 37 | 122.8 |  |  |  |  | 29 | 44.56 | 44.65 | 44.61 |  |  | 22.65 | 22.77 | 22.7
| 28 | 27 | 0 | 0 | 0.7 | 6.6 | 6.5 | 6.6 | 4 | 28 | 108.2 |  |  |  |  | 30 | 44.55 | 44.61 | 44.59 |  |  | 22.62 | 22.73 | 22.67
| 29 | 250 | 107 | 0 | 0.6 | 6.6 | 6.6 | 6.6 | 4 | 23 | 127 |  |  |  |  | 31 | 44.57 | 44.65 | 44.6 |  |  | 22.59 | 22.73 | 22.67
| 30 | 9 | 0 | 0 | 0.6 | 6.6 | 6.6 | 6.6 | 4 | 19 | 132.5 |  |  |  |  | TOTAL | 1330.59 | 1399.97 | 1370.93 |  |  | 689.4 | 750.11 | 703.58
| 31 | 909 | 9 | 0 | 0.7 | 6.6 | 6.6 | 6.6 | 2 | 23 | 137 |  |  |  |  | AVERAGE | 42.9223 | 45.1603 | 44.2235 |  |  | 22.2387 | 24.1971 | 22.6961
| TOTAL | 74481 | 12882 | 0 | 22 | 203.8 | 202.5 | 206.1 | 88.5 | 1346 | 3822.5 |  |  |  |  | MAXIMUM | 44.59 | 63.95 | 44.68 |  |  | 23.05 | 64.76 | 23.1
| AVERAGE | 3238.3043 | 515.28 | 0 | 0.70968 | 6.5742 | 6.5323 | 6.6484 | 2.8548 | 43.4194 | 123.3065 |  |  |  |  | MINIMUM | 12.72 | 43.85 | 40.4 |  |  | 12.43 | 22.45 | 21.8
[7 empty] | 6.4 | 6.7
[7 empty] | MIN | MAX
PAGE 5
PAGE 23
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
NUTRIENTS
RUN DATE
| 2026-07-30 |  | INFLUENT | [5 empty] | EFFLUENT
| MARCH | INFLUENT | INFLUENT | INFLUENT | INFLUENT |  | EFFL. | EFFL. | EFFL. | EFFL.
| 2005 | NH-3 | N03-N | TKN | TOT P |  | NH-3 | N03-N | TKN | TOT P
| 1 | 19 | 0.05 | 22 | 3.3 |  | 17 | 0.33 | 17 | 1.1
| 2 | 22 | 0.05 | 27 | 3.1 |  | 16 | 0.33 | 17 | 0.55
| 3 | 22 | 0.057 | 29 | 3.5 |  | 16 | 0.38 | 18 | 0.57
| 4 | 18 | 0.059 | 21 | 2.9 |  | 13 | 0.5 | 15 | 1.5
| 5 | 18 | 0.05 | 19 | 3 |  | 13 | 0.51 | 14 | 1
| 6 | 21 | 0.17 | 27 | 3 |  | 14 | 0.42 | 15 | 0.69
| 7 | 19 | 0.15 | 20 | 2.9 |  | 14 | 0.94 | 16 | 0.65
| 8 | 20 | 0.05 | 25 | 5.7 |  | 15 | 0.45 | 16 | 0.73
| 9 | 21 | 0.05 | 22 | 3.1 |  | 15 | 0.47 | 15 | 0.63
| 10 | 17 | 0.05 | 27 | 3.7 |  | 11 | 0.25 | 17 | 1.4
| 11 | 16 | 0.05 | 26 | 2.8 |  | 11 | 0.37 | 13 | 0.76
| 12 | 16 | 0.05 | 21 | 2.9 |  | 11 | 0.42 | 13 | 0.61
| 13 | 16 | 0.078 | 22 | 2.8 |  | 12 | 0.23 | 14 | 0.6
| 14 | 18 | 0.12 | 24 | 3.1 |  | 13 | 0.34 | 17 | 0.48
| 15 | 18 | 0.12 | 23 | 3.1 |  | 0.14 | 0.3 | 19 | 0.56
| 16 | 19 | 0.61 | 30 | 3.7 |  | 14 | 0.16 | 16 | 0.53
| 17 | 16 | 0.05 | 27 | 3.5 |  | 11 | 0.17 | 16 | 0.6
| 18 | 15 | 0.05 | 19 | 2.2 |  | 12 | 0.18 | 14 | 0.96
| 19 | 15 | 0.05 | 21 | 3 |  | 10 | 0.18 | 11 | 11
| 20 | 16 | 0.05 | 19 | 3.8 |  | 11 | 0.15 | 11 | 11
| 21 | 16 | 0.05 | 20 | 2.9 |  | 12 | 0.15 | 14 | 0.49
| 22 | 17 | 0.05 | 20 | 2.9 |  | 13 | 0.22 | 14 | 0.61
| 23 | 17 | 0.1 | 21 | 3 |  | 13 | 0.41 | 0 | 1
| 24 | 17 | 0.13 | 21 | 3.3 |  | 13 | 0.35 | 15 | 1.7
| 25 | 16 | 0.05 | 20 | 3.2 |  | 11 | 0.32 | 14 | 0.94
| 26 | 16 | 0.05 | 29 | 3.1 |  | 11 | 0.34 | 14 | 0.69
| 27 | 17 | 0.05 | 27 | 3.5 |  | 11 | 0.34 | 13 | 0.59
| 28 | 17 | 0.05 | 27 | 3.1 |  | 13 | 0.49 | 15 | 1.3
| 29 | 17 | 0.05 | 26 | 2.9 |  | 14 | 0.73 | 17 | 2.7
| 30 | 18 | 0.11 | 28 | 3 |  | 15 | 0.61 | 28 | 4.4
| 31 | 23 | 0.23 | 27 | 3 |  | 9.6 | 0.05 | 18 | 4.1
| TOTAL | 553 | 2.884 | 737 | 99 | TOT. | 384.74 | 11.09 | 466 | 54.44
| AVERAGE | 17.8387 | 0.093032 | 23.7742 | 3.1935 | AVG. | 12.411 | 0.35774 | 15.0323 | 1.7561
PAGE 6
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
REACTOR ONE PROCESS
RUN DATE
| 2026-07-30 |  | TRAIN "A" | [5 empty] | TRAIN "B"
| MARCH | MLSS | MLVSS | SS | SVI |  | MLSS | MLVSS | SS | SVI
| 2005 | "A" | "A" | "A" | "A" |  | "B" | "B" | "B" | "B"
| 1 | O/S | O/S | O/S |  |  | 3180 | 2660 | 28 | 88.0503
| 2 | O/S | O/S | O/S |  |  | 3780 | 3100 | 30 | 79.3651
| 3 | O/S | O/S | O/S |  |  | 3050 | 2510 | 31 | 101.6393
| 4 | O/S | O/S | O/S |  |  | 3320 | 2640 | 31 | 93.3735
| 5 | O/S | O/S | O/S |  |  | 3260 | 2690 | 31 | 95.092
| 6 | O/S | O/S | O/S |  |  | 3310 | 2760 | 31 | 93.6556
| 7 | O/S | O/S | O/S |  |  | 3500 | 2870 | 30 | 85.7143
| 8 | O/S | O/S | O/S |  |  | 3040 | 2490 | 30 | 98.6842
| 9 | O/S | O/S | O/S |  |  | 2590 | 2140 | 28 | 108.1081
| 10 | O/S | O/S | O/S |  |  | 3320 | 2710 | 32 | 96.3855
| 11 | O/S | O/S | O/S |  |  | 2950 | 2360 | 34 | 115.2542
| 12 | O/S | O/S | O/S |  |  | 2720 | 2320 | 37 | 136.0294
| 13 | O/S | O/S | O/S |  |  | 2770 | 2330 | 36 | 129.9639
| 14 | O/S | O/S | O/S |  |  | 3000 | 2490 | 35 | 116.6667
| 15 | O/S | O/S | O/S |  |  | 2880 | 2380 | 33 | 114.5833
| 16 | O/S | O/S | O/S |  |  | 2900 | 2250 | 30 | 103.4483
| 17 | O/S | O/S | O/S |  |  | 2430 | 1950 | 28 | 115.2263
| 18 | O/S | O/S | O/S |  |  | 2750 | 2190 | 31 | 112.7273
| 19 | O/S | O/S | O/S |  |  | 2800 | 2230 | 33 | 117.8571
| 20 | O/S | O/S | O/S |  |  | 2910 | 2430 | 35 | 120.2749
| 21 | O/S | O/S | O/S |  |  | 2760 | 2320 | 34 | 123.1884
| 22 | O/S | O/S | O/S |  |  | 2970 | 2270 | 30 | 101.0101
| 23 | O/S | O/S | O/S |  |  | 2600 | 2030 | 28 | 107.6923
| 24 | O/S | O/S | O/S |  |  | 2590 | 2010 | 25 | 96.5251
| 25 | O/S | O/S | O/S |  |  | 2510 | 1920 | 25 | 99.6016
| 26 | O/S | O/S | O/S |  |  | 2670 | 2270 | 31 | 116.1049
| 27 | O/S | O/S | O/S |  |  | 2810 | 2380 | 27 | 96.0854
| 28 | O/S | O/S | O/S |  |  | 3090 | 2490 | 28 | 90.6149
| 29 | O/S | O/S | O/S |  |  | 2410 | 1920 | 24 | 99.5851
| 30 | O/S | O/S | O/S |  |  | 2280 | 1810 | 20 | 87.7193
| 31 | O/S | O/S | O/S |  |  | 1980 | 1610 | 20 | 101.0101
| TOTAL | 0 | 0 | 0 |  |  | 89130 | 72530 | 926
| AVERAGE | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 2875.1613 | 2339.6774 | 29.871 | 103.8932
PAGE 7
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
REACTOR TWO PROCESS
RUN DATE
| 2026-07-30 |  | TRAIN "C" | [5 empty] | TRAIN "D"
| MARCH | MLSS | MLVSS | SS | SVI |  | MLSS | MLVSS | SS | SVI
| 2005 | "C" | "C" | "C" | "C" |  | "D" | "D" | "D" | "D"
| 1 | O/S | O/S | O/S |  |  | 3050 | 2580 | 28 | 91.8033
| 2 | O/S | O/S | O/S |  |  | 3630 | 3070 | 30 | 82.6446
| 3 | O/S | O/S | O/S |  |  | 2900 | 2390 | 31 | 106.8966
| 4 | O/S | O/S | O/S |  |  | 3300 | 2670 | 31 | 93.9394
| 5 | O/S | O/S | O/S |  |  | 2920 | 2410 | 31 | 106.1644
| 6 | O/S | O/S | O/S |  |  | 2810 | 2320 | 30 | 106.7616
| 7 | O/S | O/S | O/S |  |  | 3870 | 3140 | 31 | 80.1034
| 8 | O/S | O/S | O/S |  |  | 2770 | 2270 | 29 | 104.6931
| 9 | O/S | O/S | O/S |  |  | 2630 | 2170 | 25 | 95.057
| 10 | O/S | O/S | O/S |  |  | 3510 | 2900 | 32 | 91.1681
| 11 | O/S | O/S | O/S |  |  | 2940 | 2380 | 35 | 119.0476
| 12 | O/S | O/S | O/S |  |  | 2550 | 2200 | 35 | 137.2549
| 13 | O/S | O/S | O/S |  |  | 2800 | 2340 | 35 | 125
| 14 | O/S | O/S | O/S |  |  | 3190 | 2560 | 32 | 100.3135
| 15 | O/S | O/S | O/S |  |  | 2710 | 2240 | 32 | 118.0812
| 16 | O/S | O/S | O/S |  |  | 3070 | 2330 | 30 | 97.7199
| 17 | O/S | O/S | O/S |  |  | 2390 | 1910 | 29 | 121.3389
| 18 | O/S | O/S | O/S |  |  | 2770 | 2210 | 32 | 115.5235
| 19 | O/S | O/S | O/S |  |  | 2920 | 2330 | 34 | 116.4384
| 20 | O/S | O/S | O/S |  |  | 2380 | 2000 | 32 | 134.4538
| 21 | O/S | O/S | O/S |  |  | 3160 | 2700 | 31 | 98.1013
| 22 | O/S | O/S | O/S |  |  | 2630 | 1960 | 29 | 110.2662
| 23 | O/S | O/S | O/S |  |  | 2680 | 2110 | 29 | 108.209
| 24 | O/S | O/S | O/S |  |  | 2560 | 2020 | 26 | 101.5625
| 25 | O/S | O/S | O/S |  |  | 2660 | 2150 | 25 | 93.985
| 26 | O/S | O/S | O/S |  |  | 2510 | 2130 | 30 | 119.5219
| 27 | O/S | O/S | O/S |  |  | 2840 | 2320 | 27 | 95.0704
| 28 | O/S | O/S | O/S |  |  | 2440 | 1970 | 28 | 114.7541
| 29 | O/S | O/S | O/S |  |  | 2450 | 1940 | 24 | 97.9592
| 30 | O/S | O/S | O/S |  |  | 2250 | 1820 | 23 | 102.2222
| 31 | O/S | O/S | O/S |  |  | 2400 | 2010 | 27 | 112.5
| TOTAL | 0 | 0 | 0 |  |  | 87690 | 71550 | 923
| AVERAGE | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 2828.7097 | 2308.0645 | 29.7742 | 105.2572
PAGE 8
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
RAS SUMMARY
RUN DATE
2026-07-30
| MARCH | R-1 | R-2 | TOTAL | F/M | TOTAL | SLUDGE | % TOT | % FIX | % VOL.
| 2005 | TOT. RAS | TOT. RAS | MLVSS | RATIO | MLSS | AGE | RAS | RAS | RAS
|  | MGD | MGD
| 1 | 6.559 | 7.186 | 5240 | 0.73723 | 6230 | 1.5956 | 0.94 | 23.91 | 76.09
| 2 | 6.683 | 7.08 | 6170 | 0.48368 | 7410 | 1.6512 | 0.97 | 24.76 | 75.24
| 3 | 6.638 | 7.054 | 4900 | 0.93671 | 5950 | 0.91191 | 0.93 | 23.94 | 76.06
| 4 | 6.616 | 7.411 | 5310 | 0.62388 | 6620 | 3.6742 | 1.05 | 25.21 | 74.79
| 5 | 6.793 | 6.466 | 5100 | 0.74787 | 6180 | 1.2737 | 1 | 25.71 | 74.29
| 6 | 6.676 | 6.263 | 5080 | 0.70952 | 6120 | 1.2817 | 1.01 | 24.22 | 75.78
| 7 | 6.631 | 6.615 | 6010 | 0.7364 | 7370 | 2.3834 | 0.96 | 24.53 | 75.47
| 8 | 6.625 | 7.143 | 4760 | 1.044 | 5810 | 0.06806 | 0.93 | 25.62 | 74.38
| 9 | 6.445 | 7.005 | 4310 | 1.1915 | 5220 | 0.92606 | 1.04 | 24.4 | 75.6
| 10 | 6.585 | 7.4 | 5610 | 0.96962 | 6830 | 0.97806 | 1.02 | 24.6 | 75.4
| 11 | 6.805 | 7.544 | 4740 | 0.82086 | 5890 | 1.4249 | 1.13 | 25.2 | 74.8
| 12 | 6.65 | 7.574 | 4520 | 0.81814 | 5270 | 1.239 | 1 | 25.71 | 74.29
| 13 | 6.532 | 7.462 | 4670 | 0.66532 | 5570 | 1.1483 | 1 | 23.26 | 76.74
| 14 | 6.441 | 7.456 | 5050 | 0.69224 | 6190 | 1.347 | 1.05 | 22.88 | 77.12
| 15 | 6.55 | 7.062 | 4620 | 1.0163 | 5590 | 1.0404 | 0.93 | 23.5 | 76.5
| 16 | 6.599 | 6.979 | 4580 | 0.76619 | 5970 | 1.2202 | 1 | 22.6 | 77.4
| 17 | 6.37 | 7.267 | 3860 | 1.1623 | 4820 | 0.91491 | 0.9 | 24.09 | 75.91
| 18 | 6.669 | 7.63 | 4400 | 0.86438 | 5520 | 1.1974 | 0.84 | 24 | 76
| 19 | 6.83 | 6.433 | 4560 | 0.60793 | 5720 | 1.2717 | 0.8 | 23 | 77
| 20 | 6.857 | 6.132 | 4430 | 1.2683 | 5290 | 0.24803 | 1 | 24.1 | 75.9
| 21 | 6.672 | 6.665 | 5020 | 0.51992 | 5920 | 1.3817 | 1.14 | 14.9 | 85.1
| 22 | 6.53 | 6.931 | 4230 | 0.71593 | 5600 | 1.0954 | 0.97 | 24.24 | 75.76
| 23 | 6.482 | 7.016 | 4140 | 0.5712 | 5280 | 1.2804 | 0.97 | 24.11 | 75.89
| 24 | 6.411 | 7.14 | 4030 | 0.57968 | 5150 | 1.2975 | 0.93 | 26 | 74
| 25 | 6.491 | 7.469 | 4070 | 1.8856 | 5170 | 1.5831 | 0.88 | 24.39 | 75.61
| 26 | 6.72 | 6.894 | 4400 | 1.0127 | 5180 | 0.9351 | 0.86 | 25.58 | 74.42
| 27 | 6.519 | 7.027 | 4700 | 0.99542 | 5650 | 1.0093 | 0.95 | 27.08 | 72.92
| 28 | 6.472 | 6.712 | 4460 | 1.171 | 5530 | 0.90562 | 0.85 | 26.77 | 73.23
| 29 | 6.592 | 6.398 | 3860 | 0.95851 | 4860 | 1.0644 | 0.82 | 27.27 | 72.73
| 30 | 6.547 | 6.59 | 3630 | 0.9274 | 4530 | 0.96437 | 0.85 | 27.17 | 72.83
| 31 | 6.633 | 5.695 | 3620 | 1.0523 | 4380 | 0.99581 | 0.78 | 25.6 | 74.4
| TOTAL | 204.623 | 215.699 | 144080 |  | 176820 |  | 29.5 | 758.35 | 2341.65
| AVERAGE | 6.6007 | 6.958 | 4647.7419 | 0.86804 | 5703.871 | 0.71316 | 0.95161 | 24.4629 | 75.5371
PAGE 9
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
DEWATERING DATA
RUN DATE
| 2026-07-30 |  | FEED SLUDGE |  |  |  |  | FILTRATE RETURN
| MARCH | % TOT. | % FIX. | % VOL. | pH |  | % TOT. | % FIX. | % VOL. | pH
| 2005 | FEED | FEED | FEED |  |  | FILT. | FILT. | FILT.
| 1 | 1.3 | 23.85 | 76.15 | 6.61 |  | 0.22 | 72.73 | 27.27 | 7.04
| 2 | 1.33 | 23.31 | 76.69 | 6.46 |  | 0.23 | 69.57 | 30.43 | 7.05
| 3 | 1.38 | 22.46 | 77.54 | 6.43 |  | 0.21 | 76.19 | 23.81 | 7.17
4
5
| 6 | 1.36 | 22.06 | 77.94 | 6.52 |  | 0.2 | 75 | 25 | 7.05
| 7 | 1.38 | 21.74 | 78.26 | 6.6 |  | 0.22 | 68.18 | 31.82 | 7.11
| 8 | 1.42 | 21.83 | 78.17 | 6.63 |  | 0.22 | 72.73 | 27.27 | 7.16
| 9 | 1.23 | 26 | 74 | 6.64 |  | 0.24 | 70.8 | 29.2 | 7.01
10
11
12
| 13 | 1.27 | 22.83 | 77.17 | 6.63 |  | 0.21 | 66.67 | 33.33 | 6.96
| 14 | 1.19 | 23.53 | 76.47 | 6.66 |  | 0.23 | 65.22 | 34.78 | 7.1
| 15 | 1.43 | 21.7 | 78.3 | 6.38 |  | 0.23 | 65.2 | 34.8 | 7.01
| 16 | 1.36 | 15.4 | 84.6 | 6.11 |  | 0.22 | 68.2 | 31.8 | 6.72
| 17 | 1.33 | 23.31 | 76.69 | 6.14 |  | 0.22 | 68.18 | 31.82 | 6.8
18
19
| 20 | 1.36 | 21.3 | 78.7 | 6.26 |  | 0.22 | 72.7 | 27.3 | 6.78
| 21 | 1 | 27 | 73 | 6.46 |  | 0.25 | 53.6 | 46.4 | 6.89
| 22 | 1.44 | 23.61 | 76.39 | 6.37 |  | 0.24 | 66.67 | 33.33 | 6.89
| 23 | 1.32 | 24.24 | 75.76 | 5.9 |  | 0.24 | 66.67 | 33.33 | 6.58
| 24 | 0.97 | 29.9 | 70.1 | 6.53 |  | 0.24 | 66.7 | 33.3 | 6.92
25
26
| 27 | 1.46 | 23.29 | 76.71 | 5.95 |  | 0.23 | 73.91 | 26.09 | 6.67
| 28 | 1.24 | 28.23 | 71.77 | 6.2 |  | 0.24 | 70.83 | 29.17 | 6.75
| 29 | 1.21 | 26.45 | 73.55 | 6.15 |  | 0.24 | 70.83 | 29.17 | 6.67
| 30 | 1.01 | 27.72 | 72.28 | 6.23 |  | 0.23 | 69.57 | 30.43 | 6.75
| 31 | 1.01 | 27.72 | 72.28 | 6.11 |  | 0.22 | 68.18 | 31.82 | 6.87
| TOTAL | 28 | 527.48 | 1672.52 | 139.97 |  | 5 | 1518.33 | 681.67 | 151.95
| AVERAGE | 1.2727 | 23.9764 | 76.0236 | 6.3623 |  | 0.22727 | 69.015 | 30.985 | 6.9068
PAGE 10
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
SLUDGE VOLUME REMOVED
RUN DATE
2026-07-30
|  | MARCH | TRAILERS | TONS | DRY TONS | % LIME | % TOT. | % FIX. | % VOL.
|  | 2005 | REMOVED | SLUDGE | REMOVED | CAKE | CAKE | CAKE | CAKE
|  | 1 | 6 | 132 | 32.3634 |  | 17.8 | 14.16 | 85.84
|  | 2 | 5 | 110 | 32.0565 |  | 17.99 | 15.73 | 84.27
|  | 3 | 5 | 110 | 28.6579 |  | 17.44 | 16.57 | 83.43
|  | 4 | 3 | 66
|  | 5 | 0 | 0
|  | 6 | 1 | 22 | 10.1514 |  | 17.82 | 17.12 | 82.88
|  | 7 | 6 | 132 | 27.507 |  | 17.15 | 13.7 | 86.3
|  | 8 | 4 | 88 | 29.1925 |  | 17.45 | 14.15 | 85.85
|  | 9 | 6 | 132 | 34.2111 |  | 17.95 | 16.3 | 83.7
|  | 10 | 1 | 22
|  | 11 | 0 | 0
|  | 12 | 0 | 0
|  | 13 | 2 | 44 | 12.0747 |  | 17.5 | 13.66 | 86.34
|  | 14 | 6 | 132 | 31.2129 |  | 17.18 | 21.77 | 78.23
|  | 15 | 6 | 132 | 32.9163 |  | 17.47 | 17.6 | 82.4
|  | 16 | 5 | 110 | 30.5111 |  | 16.88 | 22.2 | 77.8
|  | 17 | 6 | 132 | 34.2749 |  | 17.86 | 16.24 | 83.76
|  | 18 | 2 | 44
|  | 19 | 0 | 0
|  | 20 | 1 | 25 | 9.6978 |  | 17.47 | 21.9 | 78.1
|  | 21 | 8 | 176 | 31.1082 |  | 17.12 | 14 | 86
|  | 22 | 7 | 154 | 49.8398 |  | 17.5 | 24.29 | 75.71
|  | 23 | 7 | 154 | 39.5216 |  | 16.86 | 17.56 | 82.44
|  | 24 | 7 | 154 | 31.8738 |  | 2.96 | 15.4 | 84.6
|  | 25 | 5 | 110
|  | 26 | 0 | 0
|  | 27 | 2 | 44 | 19.2387 |  | 17.47 | 13.97 | 86.03
|  | 28 | 9 | 198 | 43.7967 |  | 17.47 | 30.22 | 69.78
|  | 29 | 6 | 132 | 41.627 |  | 18.66 | 14.26 | 85.74
|  | 30 | 6 | 132 | 34.2832 |  | 19.37 | 16.83 | 83.17
|  | 31 | 4 | 88 | 32.8091 |  | 19.43 | 19.66 | 80.34
|  | TOTAL | 126 | 2775 | 668.9255 | 0 | 374.8 | 387.29 | 1812.71
|  | AVERAGE | 4.0645 | 89.5161 | 30.4057 | #DIV/0! | 17.0364 | 17.6041 | 82.3959
PAGE 11
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
CHEMICAL USEAGE
RUN DATE
2026-07-30
| MARCH | H2O2 | CL2 | POLYMER | POLYMER | LIME | GOX | O2 % | LOX | FPL
| 2005 | POUNDS | POUNDS | GALLONS | POUNDS | DELV. | TONS | PURITY | TONS | KW
| 1 | 1300 | 1240 | 105 | 875.7 | 0 | 29.8 | 99% | 67.5 | 32366
| 2 | 1956 | 1240 | 87 | 725.58 | 0 | 32.2 | 98% | 67.8 | 32879
| 3 | 1966 | 1320 | 87 | 725.58 | 0 | 32.4 | 98% | 67.3 | 30680
| 4 | 1547 | 1160 | 0 | 0 | 0 | 34.4 | 98% | 65.3 | 32380
| 5 | 1946 | 1240 | 15 | 125.1 | 0 | 33.8 | 98% | 63.7 | 32000
| 6 | 1427 | 1040 | 15 | 125.1 | 0 | 34 | 98% | 60.2 | 32938
| 7 | 1537 | 1480 | 57 | 475.38 | 0 | 29.8 | 97% | 60.4 | 32376
| 8 | 1826 | 1240 | 56 | 467.04 | 0 | 32.1 | 98% | 60 | 30955
| 9 | 1627 | 1220 | 87 | 725.58 | 0 | 33.1 | 96% | 59 | 30237
| 10 | 1616 | 1400 | 0 | 0 | 0 | 33.7 | 92% | 59.7 | 31851
| 11 | 1558 | 1240 | 0 | 0 | 0 | 33.3 | 99% | 59.1 | 31939
| 12 | 1587 | 1200 | 6 | 50.04 | 0 | 32.1 | 98% | 77.7 | 34621
| 13 | 1367 | 920 | 53 | 442.02 | 0 | 35.5 | 92% | 69.3 | 34206
| 14 | 1407 | 1400 | 52 | 433.68 | 0 | 35.8 | 96% | 87.6 | 33940
| 15 | 1606 | 1160 | 87 | 725.58 | 0 | 31.4 | 95% | 89.1 | 32089
| 16 | 1577 | 1160 | 85 | 708.9 | 0 | 32.8 | 98% | 90.3 | 33008
| 17 | 1587 | 1320 | 107 | 892.38 | 0 | 31.9 | 96% | 84.1 | 29265
| 18 | 1686 | 1200 | 4 | 33.36 | 0 | 34.4 | 92% | 86.8 | 33294
| 19 | 1437 | 1200 | 3 | 25.02 | 0 | 33.8 | 98% | 86.5 | 33991
| 20 | 1088 | 1440 | 16 | 133.44 | 0 | 32.2 | 98% | 86.1 | 34052
| 21 | 1337 | 1140 | 92 | 767.28 | 0 | 33 | 93% | 87.8 | 33816
| 22 | 1437 | 1140 | 132 | 1100.88 | 0 | 33.5 | 96% | 82.4 | 33475
| 23 | 1447 | 1080 | 135 | 1125.9 | 0 | 30.9 | 96% | 82.5 | 33852
| 24 | 1397 | 300 | 107 | 892.38 | 0 | 27.7 | 97% | 82.3 | 33159
| 25 | 1277 | 560 | 38 | 316.92 | 0 | 33.3 | 96% | 85.9 | 33186
| 26 | 1387 | 1040 | 0 | 0 | 0 | 36.1 | 97% | 81.5 | 33050
| 27 | 1307 | 1080 | 57 | 475.38 | 0 | 36.9 | 96% | 81.5 | 33094
| 28 | 1547 | 1080 | 71 | 592.14 | 0 | 36.4 | 92% | 80.4 | 33354
| 29 | 1198 | 960 | 41 | 341.94 | 0 | 36.3 | 97% | 80 | 32220
| 30 | 1637 | 1400 | 153 | 1276.02 | 0 | 27.7 | 100% | 80.2 | 31087
| 31 | 1806 | 1280 | 102 | 850.68 | 0 | 19 | 96% | 80.6 | 30798
| TOTAL | 47425 | 35880 | 1850 | 15429 | 0 | 1009.3 |  | 2352.6 | 1010158
| AVERAGE | 1529.8387 | 1157.4194 | 59.6774 | 497.7097 | 0 | 32.5581 | 96.45% | 75.8903 | 32585.7419
PAGE 12
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL ONE
|  | RUN DATE |  |  | PERMIT NUMBER 0054569-142-UO
|  | 2026-07-30 |  |  | 1/07/04 thru 1/06/09 |  |  | I.D. #:5006A11308
|  | MARCH | % INFL. | MAX | MIN | WELL 1 | MAX | MIN | AVG
|  | 2005 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 25.38% | 11.49 | 4.33 | 8.1 | 56.34 | 38.2 | 46.66
|  | 2 | 26.3% | 12 | 4.94 | 8.36 | 59.05 | 39.96 | 47.36
|  | 3 |  | ER | ER | ER | ER | ER | ER
|  | 4 | 19.25% | 11.68 | ER | 6.7 | 56.83 | 34.35 | 45.82
|  | 5 | 26.18% | 11.78 | 5.26 | 8.85 | 57.24 | 40.22 | 48.64
|  | 6 |  | ER | ER | ER | ER | ER | ER
|  | 7 |  | ER | ER | ER | ER | ER | ER
|  | 8 | 21.9% | 11.78 | 0 | 7.17 | 57.61 | 34.26 | 45.96
|  | 9 | 5.336% | 10.59 | ER | 1.88 | 54.26 | 34.16 | 37.78
|  | 10 | 17.8% | 16.87 | ER | 6.95 | 79.7 | 34.12 | 47.46
|  | 11 | 7.751% | 12.88 | 0 | 2.96 | 63.5 | 34.11 | 39.15
|  | 12 | 0% | 0 | ER | 0 | 35.2 | 33.58 | 34.51
|  | 13 | 0% | 0 | ER | 0 | 35.01 | 33.74 | 34.44
|  | 14 | 8.573% | 12.65 | 0 | 2.99 | 63.22 | 33.63 | 39.37
|  | 15 | 20.89% | 12.26 | 0 | 7.12 | 58.47 | 33.82 | 46.04
|  | 16 | 21.59% | 12.23 | 0 | 7.36 | 58.1 | 34.03 | 46.82
|  | 17 | 27.11% | 13.22 | 5.23 | 9.79 | 62.21 | 40.02 | 51.07
|  | 18 | 25.48% | 13.5 | 6.1 | 10.4 | 63.09 | 42.21 | 53.5
|  | 19 | 21.51% | 12.14 | ER | 8.39 | 57.6 | 34.4 | 49.17
|  | 20 | 25.84% | 12.01 | 5.86 | 9.68 | 57.57 | 41.4 | 50.83
|  | 21 | 25.75% | 11.93 | 5.32 | 9.57 | 57.42 | 40.69 | 50.65
|  | 22 | 7.766% | 14.79 | 0 | 2.86 | 67.66 | 34.85 | 39.64
|  | 23 | 21.03% | 12.68 | 0 | 7.52 | 60.07 | 34.51 | 47.74
|  | 24 | 22.08% | 12.02 | 0 | 7.76 | 57.71 | 34.28 | 47.45
|  | 25 | 26.23% | 11.88 | 5.78 | 9.1 | 57.46 | 41.13 | 49.48
|  | 26 | 25.53% | 11.74 | 6.08 | 8.84 | 57.55 | 42.19 | 48.88
|  | 27 | 6.031% | 10.76 | 0 | 2.05 | 55.68 | 35.09 | 38.21
|  | 28 | 21.26% | 12.15 | ER | 7.26 | 58.07 | 26.35 | 46.93
|  | 29 | 22.15% | 11.18 | 0 | 7.41 | 54.94 | 34.09 | 46.58
|  | 30 | 26.3% | 11.59 | 5.6 | 8.75 | 56.77 | 40.96 | 48.51
|  | 31 | 25.82% | 11.68 | 5.49 | 8.62 | 57.06 | 41.01 | 48.35
|  | TOTAL | 530.8% | 319.48 | 59.99 | 186.44 | 1615.39 | 1021.36 | 1277
|  | AVERAGE | 18.96% | 11.41 | 2.8567 | 6.6586 | 57.6925 | 36.4771 | 45.6071
|  | MAXIMUM | 27.11% | 16.87 | 6.1 | 10.4 | 79.7 | 42.21 | 53.5
|  | MINIMUM | 0% | 0 | 0 | 0 | 35.01 | 26.35 | 34.44
PAGE 13
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL TWO
|  | RUN DATE |  |  | PERMIT NUMBER 0054569-142-UO
|  | 2026-07-30 |  |  | 1/07/04 thru 1/06/09 |  |  | I.D. #:5006A11309
|  | MARCH | % INFL. | MAX | MIN | WELL 2 | MAX | MIN | AVG
|  | 2005 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 22.63% | 11.66 | 0.04 | 7.22 | 55.36 | 34.69 | 44.78
|  | 2 | 26.83% | 12.49 | 5.05 | 8.53 | 57.99 | 39.21 | 46.51
|  | 3 |  | ER | ER | ER | ER | ER | ER
|  | 4 | 27.81% | 12.33 | 7.05 | 9.68 | 56.83 | 42.33 | 49.33
|  | 5 | 26.68% | 12.03 | 5.4 | 9.02 | 56.49 | 39.48 | 47.81
|  | 6 |  | ER | ER | ER | ER | ER | ER
|  | 7 |  | ER | ER | ER | ER | ER | ER
|  | 8 | 25.84% | 11.9 | 4.17 | 8.46 | 56.64 | 37.71 | 46.67
|  | 9 | 27.31% | 15.73 | 4.52 | 9.62 | 70.3 | 38.24 | 49.41
|  | 10 | 26.66% | 17 | 4.13 | 10.41 | 78.4 | 37.38 | 51.67
|  | 11 | 25.19% | 14.71 | 4.2 | 9.62 | 64.93 | 37.32 | 49.37
|  | 12 | 22.17% | 12.79 | 0.04 | 8.18 | 57.69 | 34.36 | 47.55
|  | 13 | 28.33% | 12.78 | 6.48 | 10.07 | 57.71 | 41 | 49.77
|  | 14 | 27.76% | 13.02 | 6.08 | 9.68 | 62.95 | 40.07 | 49.13
|  | 15 | 27.23% | 12.46 | 5.49 | 9.28 | 57.59 | 39.32 | 48.08
|  | 16 | 10.62% | 12.23 | 0.05 | 3.62 | 56.18 | 35.36 | 40.27
|  | 17 | 8.307% | 13.33 | 0.05 | 3 | 61.14 | 34.6 | 40.49
|  | 18 | 18.4% | 13.48 | 0.04 | 7.51 | 61.84 | 35.76 | 47.68
|  | 19 | 19.94% | 12.33 | 0.04 | 7.78 | 56.61 | 34.79 | 47.47
|  | 20 | 21.6% | 12.09 | 0.04 | 8.09 | 56.52 | 35.1 | 47.59
|  | 21 | 26.18% | 12.06 | 5.37 | 9.73 | 56.51 | 39.96 | 49.81
|  | 22 | 27.1% | 15.14 | 0.05 | 9.98 | 66.59 | 36.31 | 50.8
|  | 23 | 6.598% | 13.04 | 0.05 | 2.36 | 60.48 | 35.63 | 38.86
|  | 24 | 20.69% | 12.28 | 0.05 | 7.27 | 56.76 | 34.54 | 46.11
|  | 25 | 22.25% | 12.05 | 0.04 | 7.72 | 56.6 | 35.19 | 46.87
|  | 26 | 25.94% | 11.97 | 6.13 | 8.98 | 56.68 | 41.48 | 48.12
|  | 27 | 27.27% | 12.68 | 4.97 | 9.27 | 58.01 | 39.41 | 48.57
|  | 28 | 2.343% | 9.6 | 0.04 | 0.8 | 50.08 | 31.54 | 36.96
|  | 29 | 20.74% | 11.37 | 0.05 | 6.94 | 53.97 | 34.43 | 45.27
|  | 30 | 22.3% | 11.79 | 0.04 | 7.42 | 55.78 | 34.99 | 45.96
|  | 31 | 26.27% | 11.85 | 5.49 | 8.77 | 56.09 | 40.27 | 47.55
|  | TOTAL | 621% | 356.19 | 75.15 | 219.01 | 1652.72 | 1040.47 | 1308.46
|  | AVERAGE | 22.18% | 12.7211 | 2.6839 | 7.8218 | 59.0257 | 37.1596 | 46.7307
|  | MAXIMUM | 28.33% | 17 | 7.05 | 10.41 | 78.4 | 42.33 | 51.67
|  | MINIMUM | 2.343% | 9.6 | 0.04 | 0.8 | 50.08 | 31.54 | 36.96
PAGE 14
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL THREE
|  | RUN DATE |  |  | PERMIT NUMBER 0054569-142-UO
|  | 2026-07-30 |  |  | 1/07/04 thru 1/06/09 |  |  | I.D. #:5006A11310
|  | MARCH | % INFL. | MAX | MIN | WELL 3 | MAX | MIN | AVG
|  | 2005 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 25.32% | 11.09 | 4.57 | 8.08 | 56.66 | 38.37 | 46.88
|  | 2 | 19.19% | 10.73 | ER | 6.1 | 55.18 | 34.79 | 44.64
|  | 3 |  | ER | ER | ER | ER | ER | ER
|  | 4 | 26.75% | 11.42 | 6.98 | 9.31 | 58.12 | 43.3 | 50.44
|  | 5 | 18.61% | 11.42 | ER | 6.29 | 57.54 | 34.89 | 45.39
|  | 6 |  | ER | ER | ER | ER | ER | ER
|  | 7 |  | ER | ER | ER | ER | ER | ER
|  | 8 | 24.89% | 11.19 | 4.5 | 8.15 | 57.84 | 38.56 | 47.67
|  | 9 | 25.32% | 14.05 | 4.86 | 8.92 | 71.9 | 39.11 | 50.49
|  | 10 | 25.04% | 15.72 | 4.24 | 9.78 | 80.2 | 38.25 | 52.8
|  | 11 | 23.44% | 13.11 | 4.51 | 8.95 | 66.04 | 38.19 | 50.4
|  | 12 | 26.21% | 12.91 | 6.68 | 9.67 | 64.75 | 42.78 | 52.1
|  | 13 | 26.08% | 11.59 | 6.24 | 9.27 | 58.87 | 41.93 | 50.8
|  | 14 | 17.46% | 11.49 | ER | 6.09 | 58.96 | 36.16 | 45.82
|  | 15 |  | ER | ER | ER | 37.72 | 35.28 | 36.65
|  | 16 | 16.57% | 11.3 | ER | 5.65 | 58.24 | 35.44 | 45.34
|  | 17 | 25.92% | 12.49 | 5.32 | 9.36 | 62.47 | 40.15 | 51.21
|  | 18 | 24.35% | 12.57 | 6.21 | 9.94 | 63.24 | 42.36 | 53.71
|  | 19 | 6.844% | 12.11 | ER | 2.67 | 61.27 | 36.43 | 41.48
|  | 20 | 19.04% | 11.5 | ER | 7.13 | 57.69 | 35.67 | 47.83
|  | 21 | 20.86% | 11.32 | ER | 7.75 | 57.65 | 35.46 | 48.7
|  | 22 | 25.2% | 13.62 | ER | 9.28 | 66.55 | 36.59 | 51.65
|  | 23 | 26.06% | 12.03 | 5.93 | 9.32 | 61.65 | 41.51 | 51.06
|  | 24 | 6.288% | 9.15 | ER | 2.21 | 49.49 | 36.26 | 39.85
|  | 25 | 19.74% | 11.49 | ER | 6.85 | 57.71 | 35.62 | 47.05
|  | 26 | 20.91% | 11.3 | ER | 7.24 | 57.7 | 35.66 | 47.29
|  | 27 | 25.63% | 11.46 | 5.13 | 8.71 | 58.99 | 40.24 | 49.51
|  | 28 | 26.18% | 11.28 | 4.85 | 8.94 | 58.2 | 32.2 | 50.15
|  | 29 | 6.337% | 9.1 | ER | 2.12 | 49.44 | 36.69 | 39.63
|  | 30 | 19.84% | 11.23 | ER | 6.6 | 56.99 | 35.42 | 46.27
|  | 31 | 21.21% | 11.16 | ER | 7.08 | 57.25 | 35.49 | 46.83
|  | TOTAL | 569.3% | 317.83 | 70.02 | 201.46 | 1658.31 | 1052.8 | 1331.64
|  | AVERAGE | 21.08% | 11.7715 | 5.3862 | 7.4615 | 59.2254 | 37.6 | 47.5586
|  | MAXIMUM | 26.75% | 15.72 | 6.98 | 9.94 | 80.2 | 43.3 | 53.71
|  | MINIMUM | 6.288% | 9.1 | 4.24 | 2.12 | 37.72 | 32.2 | 36.65
PAGE 15
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL FOUR
|  | RUN DATE |  |  | PERMIT NUMBER 0054569-142-UO
|  | 2026-07-30 |  |  | 1/07/04 thru 1/06/09
|  | MARCH | % INFL. | MAX | MIN | WELL 4 | MAX | MIN | AVG
|  | 2005 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 0.06267% | 0.03 | 0.01 | 0.02 | 37.18 | ER | ER
|  | 2 | 0.06292% | 0.03 | 0.01 | 0.02 | 37.21 | 34.75 | 36.03
|  | 3 |  | ER | ER | ER | ER | ER | ER
|  | 4 | 0.02873% | 0.03 | 0.01 | 0.01 | 37.23 | 35.47 | 36.41
|  | 5 | 0.05916% | 0.04 | 0.01 | 0.02 | 37.43 | 34.84 | 36.17
|  | 6 |  | ER | ER | ER | ER | ER | ER
|  | 7 |  | ER | ER | ER | ER | ER | ER
|  | 8 | 26.81% | 12.03 | 4.97 | 8.78 | 58.25 | 39.25 | 48.22
|  | 9 | 26.74% | 14.73 | 5.35 | 9.42 | 72.1 | 39.83 | 51.04
|  | 10 | 26.68% | 16.63 | 4.92 | 10.42 | 80.5 | 38.98 | 53.35
|  | 11 | 24.48% | 13.64 | 4.92 | 9.35 | 66.53 | 38.94 | 51
|  | 12 | 27.08% | 13.34 | 6.9 | 9.99 | 65.24 | 43.44 | 52.67
|  | 13 | 26.87% | 11.81 | 6.53 | 9.55 | 59.47 | 42.64 | 51.47
|  | 14 | 26.67% | 12.51 | 6.3 | 9.3 | 79.7 | 41.66 | 50.8
|  | 15 | 26.76% | 12.04 | 5.63 | 9.12 | 59.45 | 40.89 | 49.8
|  | 16 | 27.37% | 11.88 | 6.47 | 9.33 | 58.77 | 42.76 | 50.63
|  | 17 | 26.78% | 13.08 | 5.7 | 9.67 | 62.99 | 40.83 | 51.85
|  | 18 | 25.41% | 13.24 | 6.6 | 10.37 | 63.81 | 43.03 | 54.3
|  | 19 | 26.3% | 12.27 | 7.26 | 10.26 | 61.82 | 44.96 | 53.71
|  | 20 | 6.461% | 11.71 | 0.01 | 2.42 | 58.41 | 35.85 | 40.33
|  | 21 | 20.02% | 11.83 | 0.02 | 7.44 | 58.19 | 35.5 | 48.36
|  | 22 | 21.15% | 14.03 | 0.03 | 7.79 | 67.04 | 35.38 | 49.84
|  | 23 | 26.48% | 12.48 | 6.06 | 9.47 | 62.15 | 42.23 | 51.69
|  | 24 | 26.46% | 11.79 | 5.16 | 9.3 | 58.6 | 40.43 | 50.73
|  | 25 | 6.398% | 10.13 | 0.03 | 2.22 | 53.28 | 36.69 | 39.81
|  | 26 | 20.02% | 11.75 | 0.03 | 6.93 | 58.33 | 35.69 | 46.93
|  | 27 | 21.92% | 11.63 | 0.03 | 7.45 | 59.68 | 35.73 | 48.18
|  | 28 | 26.5% | 11.44 | 4.96 | 9.05 | 58.79 | 32.44 | 50.78
|  | 29 | 26.6% | 10.98 | 5.99 | 8.9 | 55.84 | 42.52 | 49.76
|  | 30 | 6.341% | 8.99 | 0.02 | 2.11 | 48.92 | 36.45 | 39.53
|  | 31 | 20.34% | 11.64 | 0.03 | 6.79 | 57.8 | 35.48 | 46.67
|  | TOTAL | 546.8% | 295.73 | 93.96 | 195.5 | 1634.71 | 1046.66 | 1290.06
|  | AVERAGE | 19.53% | 10.5618 | 3.3557 | 6.9821 | 58.3825 | 38.7652 | 47.78
|  | MAXIMUM | 27.37% | 16.63 | 7.26 | 10.42 | 80.5 | 44.96 | 54.3
|  | MINIMUM | 0.02873% | 0.03 | 0.01 | 0.01 | 37.18 | 32.44 | 36.03
PAGE 16
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL FIVE
|  | RUN DATE |  |  | PERMIT NUMBER 0054569-142-UO
|  | 2026-07-30 |  |  | 1/07/04 thru 1/06/09 |  |  | I.D. #:5006A11311
|  | MARCH | % INFL. | MAX | MIN | WELL 5 | MAX | MIN | AVG
|  | 2005 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 25.13% | 10.88 | 4.73 | 8.02 | 56.36 | 38.36 | 46.68
|  | 2 |  | 11.62 | ER | ER | 61.11 | ER | ER
|  | 3 |  | ER | ER | ER | ER | ER | ER
|  | 4 | 26.26% | 11.12 | 6.88 | 9.14 | 57.73 | 43.08 | 50.12
|  | 5 | 25.71% | 11.23 | 5.65 | 8.69 | 57.06 | 40.24 | 48.54
|  | 6 |  | ER | ER | ER | ER | ER | ER
|  | 7 |  | ER | ER | ER | ER | ER | ER
|  | 8 |  | ER | ER | ER | 36.47 | 34.29 | 35.35
|  | 9 | 16.01% | 13.54 | ER | 5.64 | 71.4 | 34.17 | 46.05
|  | 10 | 4.865% | 12.34 | ER | 1.9 | 65.04 | 34.28 | 38.89
|  | 11 | 17.33% | 12.6 | ER | 6.62 | 65.64 | 34.21 | 47.3
|  | 12 | 25.18% | 12.31 | 6.46 | 9.29 | 64.56 | 42.61 | 51.8
|  | 13 | 19.1% | 11.1 | ER | 6.79 | 58.37 | 34.88 | 47.4
|  | 14 | 19.78% | 11.67 | ER | 6.9 | 63.14 | 34.91 | 47.36
|  | 15 | 24.97% | 11.21 | 5.32 | 8.51 | 58.29 | 39.98 | 48.79
|  | 16 | 24.32% | 10.95 | ER | 8.29 | 57.79 | 35.59 | 48.97
|  | 17 | 11.91% | 10.79 | ER | 4.3 | 57.41 | 34.9 | 43.16
|  | 18 | 6.664% | 11.9 | ER | 2.72 | 62.95 | 35.23 | 41.38
|  | 19 | 24.61% | 11.48 | 6.87 | 9.6 | 61 | 44.08 | 52.73
|  | 20 | 24.64% | 11.21 | 6.03 | 9.23 | 57.51 | 41.34 | 50.69
|  | 21 | 5.947% | 11.18 | ER | 2.21 | 57.3 | 35.24 | 38.86
|  | 22 | 18.71% | 13.84 | ER | 6.89 | 67.43 | 33.99 | 48.44
|  | 23 | 20.75% | 11.25 | ER | 7.42 | 59.79 | 35.21 | 48.62
|  | 24 | 24.9% | 11.03 | 4.97 | 8.75 | 57.58 | 39.46 | 49.7
|  | 25 | 25.28% | 11.17 | 5.81 | 8.77 | 57.22 | 41.03 | 49.26
|  | 26 | 6.094% | 9.85 | ER | 2.11 | 52.93 | 35.53 | 38.56
|  | 27 | 18.68% | 10.95 | ER | 6.35 | 58.63 | 34.12 | 46.28
|  | 28 | 24.75% | 10.81 | ER | 8.45 | 57.82 | 27.01 | 49.72
|  | 29 | 25.08% | 10.25 | 5.74 | 8.39 | 54.86 | 41.62 | 48.74
|  | 30 | 25.4% | 10.97 | 5.61 | 8.45 | 56.47 | 40.94 | 48.33
|  | 31 | 6.021% | 8.41 | ER | 2.01 | 47.16 | 35.52 | 38.33
|  | TOTAL | 498.1% | 305.66 | 64.07 | 175.44 | 1639.02 | 1001.82 | 1250.05
|  | AVERAGE | 19.16% | 11.3207 | 5.8245 | 6.7477 | 58.5364 | 37.1044 | 46.2981
|  | MAXIMUM | 26.26% | 13.84 | 6.88 | 9.6 | 71.4 | 44.08 | 52.73
|  | MINIMUM | 4.865% | 8.41 | 4.73 | 1.9 | 36.47 | 27.01 | 35.35
PAGE 17
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
INJECTION WELL SUMMARY
RUN DATE
2026-07-30
| MARCH | INFLUENT | EFFLUENT | EFFLUENT | IW-1 | IW-2 | IW-3 | IW-4 | IW-5 | TOTAL
| 2005 | FLOW | FLOW | SS | LBS SS | LBS SS | LBS SS | LBS SS | LBS SS | LBS SS
|  | MGD | MGD
| 1 | 31.911 | 31.428 | 8 | 540.432 | 481.7184 | 539.0976 | 1.3344 | 535.0944 | 2096.3424
| 2 | 31.788 | 31.261 | 10 | 697.224 | 711.402 | 508.74 | 1.668
| 3 | 31.874 | 31.444 | 10
| 4 | 34.807 | 34.772 | 4 | 223.512 | 322.9248 | 310.5816 | 0.3336 | 304.9104 | 1161.9288
| 5 | 33.806 | 32.86 | 18 | 1328.562 | 1354.0824 | 944.2548 | 3.0024 | 1304.5428 | 4931.442
| 6 | 32.732 | 32.122 | 16
| 7 | 32.855 | 32.558 | 21
| 8 | 32.744 | 32.497 | 12 | 717.5736 | 846.6768 | 815.652 | 878.7024
| 9 | 35.23 | 35.544 | 17 | 266.5464 | 1363.9236 | 1264.6776 | 1335.5676 | 799.6392 | 3694.7868
| 10 | 39.051 | 39.27 | 15 | 869.445 | 1302.291 | 1223.478 | 1303.542 | 237.69 | 3632.904
| 11 | 38.19 | 37.644 | 41 | 1012.1424 | 3289.4628 | 3060.363 | 3197.139 | 2263.6428 | 9625.611
| 12 | 36.893 | 37.071 | 21 | 0 | 1432.6452 | 1693.6038 | 1749.6486 | 1627.0506 | 4753.2996
| 13 | 35.545 | 35.609 | 20 | 0 | 1679.676 | 1546.236 | 1592.94 | 1132.572 | 4358.484
| 14 | 34.876 | 34.992 | 10 | 249.366 | 807.312 | 507.906 | 775.62 | 575.46 | 2140.044
| 15 | 34.082 | 33.987 | 10 | 593.808 | 773.952 |  | 760.608 | 709.734
| 16 | 34.089 | 34.274 | 18 | 1104.8832 | 543.4344 | 848.178 | 1400.6196 | 1244.4948 | 3740.9904
| 17 | 36.113 | 36.105 | 20 | 1632.972 | 500.4 | 1561.248 | 1612.956 | 717.24 | 4411.86
| 18 | 40.818 | 40.87 | 19 | 1647.984 | 1190.0346 | 1575.0924 | 1643.2302 | 431.0112 | 4844.1222
| 19 | 39.012 | 38.661 | 15 | 1049.589 | 973.278 | 334.017 | 1283.526 | 1200.96 | 3557.844
| 20 | 37.457 | 36.5 | 20 | 1614.624 | 1349.412 | 1189.284 | 403.656 | 1539.564 | 5692.884
| 21 | 37.161 | 36.693 | 22 | 1755.9036 | 1785.2604 | 1421.97 | 1365.0912 | 405.4908 | 5368.6248
| 22 | 36.826 | 36.794 | 14 | 333.9336 | 1165.2648 | 1083.5328 | 909.5604 | 804.4764 | 3387.2076
| 23 | 35.766 | 36.036 | 20 | 1254.336 | 393.648 | 1554.576 | 1579.596 | 1237.656 | 4440.216
| 24 | 35.145 | 35.217 | 18 | 1164.9312 | 1091.3724 | 331.7652 | 1396.116 | 1313.55 | 3901.6188
| 25 | 34.698 | 34.672 | 19 | 1441.986 | 1223.3112 | 1085.451 | 351.7812 | 1389.6942 | 5140.4424
| 26 | 34.622 | 34.055 | 18 | 1327.0608 | 1348.0776 | 1086.8688 | 1040.3316 | 316.7532 | 4078.7604
| 27 | 33.989 | 33.804 | 15 | 256.455 | 1159.677 | 1089.621 | 931.995 | 794.385 | 3300.138
| 28 | 34.147 | 34.406 | 24 | 1453.1616 | 160.128 | 1789.4304 | 1811.448 | 1691.352 | 5094.072
| 29 | 33.456 | 33.747 | 22 | 1359.5868 | 1273.3512 | 388.9776 | 1632.972 | 1539.3972 | 4561.3128
| 30 | 33.273 | 33.277 | 29 | 2116.275 | 1794.6012 | 1596.276 | 510.3246 | 2043.717 | 7550.8692
| 31 | 33.381 | 33.245 | 44 | 3163.1952 | 3218.2392 | 2598.0768 | 2491.6584 | 737.5896 | 9717.1008
| TOTAL | 1086.337 | 1081.415 | 570 | 29175.4884 | 33535.557 | 31948.9554 | 31964.9682 | 26897.6676 | 115182.906
| AVERAGE | 35.0431 | 34.8844 | 18.3871 | 1041.9817 | 1197.6985 | 1183.2946 | 1141.606 | 1034.5257 | 4607.3162
PAGE 18
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
| RUN DATE |  |  |  | SOLIDS REMOVAL INVENTORY DATA SHEET
2026-07-30
| MARCH | TONS | CAKE |  |  |  | MARCH | RAGS | GRIT | OTHER
| 2005 | SLUDGE | TSS |  |  |  | 2005 |  |  | (vac)
| 1st - 7th | [5 empty] | 1st - 7th
| 1 | 132 | 17.8 |  |  |  | 1 |  | 10
| 2 | 110 | 17.99 |  |  |  | 2
| 3 | 110 | 17.44 |  |  |  | 3
| 4 | 66 |  |  |  |  | 4 | 10
| 5 | 0 |  |  |  |  | 5
| 6 | 22 | 17.82 |  |  |  | 6
| 7 | 132 | 17.15 |  |  |  | 7
| TOTAL = | 572 | 17.64 | = AVG. |  |  | TOTAL = | 10 | 10 | 0
| 8th - 14th | [5 empty] | 8th - 14th
| 8 | 88 | 17.45 |  |  |  | 8
| 9 | 132 | 17.95 |  |  |  | 9
| 10 | 22 |  |  |  |  | 10 |  | 10
| 11 | 0 |  |  |  |  | 11 | 10
| 12 | 0 |  |  |  |  | 12
| 13 | 44 | 17.5 |  |  |  | 13
| 14 | 132 | 17.18 |  |  |  | 14
| TOTAL = | 418 | 17.52 | = AVG. |  |  | TOTAL = | 10 | 10 | 0
| 15th - 22nd | [5 empty] | 15th-22nd
| 15 | 132 | 17.47 |  |  |  | 15
| 16 | 110 | 16.88 |  |  |  | 16
| 17 | 132 | 17.86 |  |  |  | 17 |  | 10
| 18 | 44 |  |  |  |  | 18 | 10
| 19 | 0 |  |  |  |  | 19
| 20 | 25 | 17.47 |  |  |  | 20
| 21 | 176 | 17.12 |  |  |  | 21
| 22 | 154 | 17.5 |  |  |  | 22
| TOTAL = | 773 | 17.3833 | = AVG. |  |  | TOTAL = | 10 | 10 | 0
| 23rd - 31st | [5 empty] | 23rd-31st
| 23 | 154 | 16.86 |  |  |  | 23
| 24 | 154 | 2.96 |  |  |  | 24
| 25 | 110 |  |  |  |  | 25 | 10 | 10
| 26 | 0 |  |  |  |  | 26
| 27 | 44 | 17.47 |  |  |  | 27
| 28 | 198 | 17.47 |  |  |  | 28
| 29 | 132 | 18.66 |  |  |  | 29
| 30 | 132 | 19.37 |  |  |  | 30
| 31 | 88 | 19.43 |  |  |  | 31
| TOTAL = | 1012 | 16.0314 | = AVG. |  |  | TOTAL = | 10 | 10 | 0
RAGS & GRIT go to Central LandFill
Other(VAC) go to BCSR
PAGE 19

## INJECTION PAGES
|  |  |  | UNDERGROUND INJECTION CONTROL | [10 empty] | UNDERGROUND INJECTION CONTROL | [10 empty] | UNDERGROUND INJECTION CONTROL
[15 empty] | MONTHLY OPERATING REPORT | [10 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES |  |  |  |  | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES |  |  |  |  | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [10 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [10 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-1 | [7 empty] | Wet Well Description: |  |  | Effuent Wet Well for IW-1, IW-2, IW3, IW-4 and IW-5 | [7 empty] | Monitoring Well Decription: |  |  | UPPER ZONE OF MONITORING WELL MW-1
Permit #: |  | 0054569-142-UO |  |  |  |  | Date of Issuance: |  | 2004-01-07 |  | Facility ID #: |  | 5006M02066 |  |  |  | Permit Number: |  |  | FLA041378 |  | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | 0054569-142-UO
[22 empty] | Monitoring Well ID #: |  |  | 5006A11311
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2009-01-06 | [7 empty] | Issue Date: |  |  | 1999-10-18 |  | As Identified in Permit: |  | Monitor Well MW-1 Upper Monitor Zone |  |  |  | Issue Date: |  |  | 2004-01-07
[22 empty] | Monitoring Well Interval: |  |  | 1288' to 1320'
Injection Well ID #: |  | 5006A11308 | [8 empty] | Wet Well ID #: |  | Well Facility U-001 |  |  |  | Expiration Date: |  |  | 2004-10-17 |  | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.7 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24 | Associated Injection Well(s):
Injection Interval: |  |  | 2799' to 3513' | [18 empty] | 500A11311 |  |  | INJECTION WELL IW-5
[11 empty] | Injection Well ID #: |  |  | Injection Well Description
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s): | [10 empty] | 5006A11308 |  |  | INJECTION WELL IW-1
[11 empty] | 5006A11309 |  |  | INJECTION WELL IW-2 | [7 empty] | REPORT MONTH / YEAR: |  | 2005-03-01 | DATE OF SAP / RECORDING: |  |  | 2005-03-01 | 2005-03-08 | 2005-03-15 | 2005-03-22 | 2005-03-29
Monitoring Zone ID #: | [5 empty] | Description |  |  |  |  | 5006A11310 |  |  | INJECTION WELL IW-3
[11 empty] | N/A |  |  | INJECTION WELL IW-4 | [7 empty] | OPERATOR'S NAME: |  |  | BAYLER, J.
UO-06-279401 |  | UPPER ZONE OF MONITORING WELL MW-2 | [8 empty] | 5006A11311 |  |  | INJECTION WELL IW-5
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A
UO-06-279401 |  | LOWER ZONE OF MONITORING WELL MW-2
[11 empty] | THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [10 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [10 empty] | REPORT MONTH / YEAR: |  | 2005-03-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous |  |  | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2005-03-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous |  |  | OPERATOR'S NAME: |  |  | BAYLER, J.
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
OPERATOR'S NAME: |  |  | BAYLER, J. | [7 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A | [7 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4474-A | [7 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: |  |  |  | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 48.79 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 15.87 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: |  |  |  | PARAMETER |  |  |  | Sampling Frequency |  |  |  | VALUE |  | UNITS | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 47.6529 | PSIG
[11 empty] | Nitrogen, Total as N |  |  |  |  | Daily/Monthly Average |  |  | 15.39 |  | mg/L as N | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[11 empty] | Nitrogen, Nitrate, Total as N |  |  |  |  | Daily/Monthly Average |  |  | 0.35774 |  | mg/L as N | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7537.6 | mg/l
Total monthly flow | [7 empty] | 186.44 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 3680 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [7 empty] | Nitrogen, Total Kjeildahl as N |  |  |  |  | Daily/Monthly Average |  |  | 15.0323 |  | mg/L as N | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.93 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 16.87 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.18 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 79.7 |  | PSIG | pH |  |  |  |  | Daily/Monthly Average |  |  | 6.5742 |  | s.u. | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 8.102 | Std units
Monthly average of the daily flow rates | [7 empty] | 6.6586 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 12108 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 9.3775 |  | MG | Phosphorus, Total as P |  |  |  |  | Daily/Monthly Average |  |  | 1.7561 |  | mg/L as P | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 2.061 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 73.6 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [10 empty] | Total Dissolved Solids (TDS) |  |  |  |  | Daily/Monthly Average |  |  | 1463.5806 |  | mg/L | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.01 | mg/l
Monthly average pressure | [7 empty] | 45.6071 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 851.8 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 36.04 |  | PSIG | Residue, Total filterable (TSS dried at 180 C) |  |  |  |  | Daily/Monthly Average |  |  | 18.3871 |  | mg/L | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[11 empty] | Specific Conductance (Temperature Compensated) |  |  |  |  | Daily/Monthly Average |  |  | 2965.8065 |  | umhos/cm | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just | [6 empty] | Temperature, Water |  |  |  |  | Daily/Monthly Average |  |  | 79.8806 |  | deg C
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [9 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just |  |  | Date: |  |  |  |  | (Signature):
[12 empty] | (Signature): | [10 empty] | Date:
|  |  |  | UNDERGROUND INJECTION CONTROL | [21 empty] | UNDERGROUND INJECTION CONTROL
|  |  |  | MONTHLY OPERATING REPORT | [21 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES | [15 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [21 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-2 | [18 empty] | Monitoring Well Decription: |  |  | LOWER ZONE OF MONITORING WELL MW-1
Permit #: |  | 0054569-142-UO |  |  |  |  | Date of Issuance: |  | 2004-01-07 | [12 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | 0054569-142-UO
[22 empty] | Monitoring Well ID #: |  |  | 5006A11311
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2009-01-06 | [12 empty] | As Identified in Permit: |  | Monitor Well MW-1 Lower Monitor Zone |  |  |  | Issue Date: |  |  | 2004-01-07
[22 empty] | Monitoring Well Interval: |  |  | 1449' to 1557'
Injection Well ID #: |  | 5006A11309 | [19 empty] | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.7 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24
Injection Interval: |  |  | 2798' to 3518' | [18 empty] | 500A11311 |  |  | INJECTION WELL IW-5
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s):
[22 empty] | REPORT MONTH / YEAR: |  | 2005-03-01 | DATE OF SAP / RECORDING: |  |  | 2005-03-01 | 2005-03-08 | 2005-03-15 | 2005-03-22 | 2005-03-29
Monitoring Zone ID #: | [5 empty] | Description
[22 empty] | OPERATOR'S NAME: |  |  | BAYLER, J.
UO-06-279401 |  | UPPER ZONE OF MONITORING WELL MW-2
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A
UO-06-279401 |  | LOWER ZONE OF MONITORING WELL MW-2
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [21 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2005-03-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
OPERATOR'S NAME: |  |  | BAYLER, J. | [18 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4474-A | [18 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 46.82 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 11.14 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: | [14 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 41.855 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 9388 | mg/l
Total monthly flow | [7 empty] | 219.01 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 4900 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [18 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 9.52 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 17 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 8.242 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 78.4 |  | PSIG | [11 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7.314 | Std units
Monthly average of the daily flow rates | [7 empty] | 7.8218 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 15758 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 10.9701 |  | MG | [11 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 2.061 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 71.8 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [21 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.011 | mg/l
Monthly average pressure | [7 empty] | 46.7307 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 765.2 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 36.2 |  | PSIG | [11 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [21 empty] | (Signature):
Date:
|  |  |  | UNDERGROUND INJECTION CONTROL | [21 empty] | UNDERGROUND INJECTION CONTROL
|  |  |  | MONTHLY OPERATING REPORT | [21 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES | [15 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [21 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-3 | [18 empty] | Monitoring Well Decription: |  |  | UPPER ZONE OF MONITORING WELL MW-2
Permit #: |  | 0054569-142-UO |  |  |  |  | Date of Issuance: |  | 2004-01-07 | [12 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | 0054569-142-UO
[22 empty] | Monitoring Well ID #: |  |  | 5006A11308 & 309
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2009-01-06 | [12 empty] | As Identified in Permit: |  | Monitor Well MW-2 Upper Monitor Zone |  |  |  | Issue Date: |  |  | 2004-01-07
[22 empty] | Monitoring Well Interval: |  |  | 1300' to 1344'
Injection Well ID #: |  | 5006A11310 | [19 empty] | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.7 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24
Injection Interval: |  |  | 2800' to 3977' | [18 empty] | 5006A11308 |  |  | INJECTION WELL IW-1
[22 empty] | 5006A11309 |  |  | INJECTION WELL IW-2
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s):
[22 empty] | REPORT MONTH / YEAR: |  | 2005-03-01 | DATE OF SAP / RECORDING: |  |  | 2005-03-01 | 2005-03-08 | 2005-03-15 | 2005-03-22 | 2005-03-29
Monitoring Zone ID #: | [5 empty] | Description
[22 empty] | OPERATOR'S NAME: |  |  | BAYLER, J.
UO-06-279510 |  | UPPER ZONE OF MONITORING WELL MW-3
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A
UO-06-279510 |  | LOWER ZONE OF MONITORING WELL MW-3
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [21 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2005-03-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
OPERATOR'S NAME: |  |  | BAYLER, J. | [18 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4474-A | [18 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 28.8 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 20.3 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: | [14 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 25.5089 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7193.6 | mg/l
Total monthly flow | [7 empty] | 201.46 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 3560 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [18 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.946 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 15.72 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.26 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 80.2 |  | PSIG | [11 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7.912 | Std units
Monthly average of the daily flow rates | [7 empty] | 7.4615 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 9626.4 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 10.4291 |  | MG | [11 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 2.061 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 72 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [21 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.074 | mg/l
Monthly average pressure | [7 empty] | 47.5586 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 824.8 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 37.3 |  | PSIG | [11 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [21 empty] | (Signature):
Date:
|  |  |  | UNDERGROUND INJECTION CONTROL | [21 empty] | UNDERGROUND INJECTION CONTROL
|  |  |  | MONTHLY OPERATING REPORT | [21 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES | [15 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [21 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-4 | [18 empty] | Monitoring Well Decription: |  |  | LOWER ZONE OF MONITORING WELL MW-2
Permit #: |  | 0054569-142-UO |  |  |  |  | Date of Issuance: |  | 2004-01-07 | [12 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | 0054569-142-UO
[22 empty] | Monitoring Well ID #: |  |  | 5006A11308 & 309
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2009-01-06 | [12 empty] | As Identified in Permit: |  | Monitor Well MW-2 Lower Monitor Zone |  |  |  | Issue Date: |  |  | 2004-01-07
[22 empty] | Monitoring Well Interval: |  |  | 1970' to 2025'
Injection Well ID #: |  | N/A | [19 empty] | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.7 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24
Injection Interval: |  |  | 2804' to 3977' | [18 empty] | 5006A11308 |  |  | INJECTION WELL IW-1
[22 empty] | 5006A11309 |  |  | INJECTION WELL IW-2
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s):
[22 empty] | REPORT MONTH / YEAR: |  | 2005-03-01 | DATE OF SAP / RECORDING: |  |  | 2005-03-01 | 2005-03-08 | 2005-03-15 | 2005-03-22 | 2005-03-29
Monitoring Zone ID #: | [5 empty] | Description
[22 empty] | OPERATOR'S NAME: |  |  | BAYLER, J.
UO-06-279510 |  | UPPER ZONE OF MONITORING WELL MW-3
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A
UO-06-279510 |  | LOWER ZONE OF MONITORING WELL MW-3
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [21 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2005-03-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
OPERATOR'S NAME: |  |  | BAYLER, J. | [18 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4474-A | [18 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 43.09 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 34.46 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: | [14 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 41.9757 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 31573.4 | mg/l
Total monthly flow | [7 empty] | 195.5 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 16680 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [18 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.46 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 16.63 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 2.18 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 80.5 |  | PSIG | [11 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7.482 | Std units
Monthly average of the daily flow rates | [7 empty] | 6.9821 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 46560 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 9.6605 |  | MG | [11 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 2.061 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 71.2 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [21 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.0112 | mg/l
Monthly average pressure | [7 empty] | 47.78 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 2694 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 36.8 |  | PSIG | [11 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [21 empty] | (Signature):
Date:
|  |  |  | UNDERGROUND INJECTION CONTROL | [21 empty] | UNDERGROUND INJECTION CONTROL
|  |  |  | MONTHLY OPERATING REPORT | [21 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES | [15 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [21 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-5 | [18 empty] | Monitoring Well Decription: |  |  | UPPER ZONE OF MONITORING WELL MW-3
Permit #: |  | 0054569-142-UO |  |  |  |  | Date of Issuance: |  | 2004-01-07 | [12 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | 0054569-142-UO
[22 empty] | Monitoring Well ID #: |  |  | 5006A11310
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2009-01-06 | [12 empty] | As Identified in Permit: |  | Monitor Well MW-3 Upper Monitor Zone |  |  |  | Issue Date: |  |  | 2004-01-07
[22 empty] | Monitoring Well Interval: |  |  | 1300' to 1349'
Injection Well ID #: |  | 5006A11311 | [19 empty] | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.7 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24
Injection Interval: |  |  | 2818' to 3462' | [18 empty] | 5006A11310 |  |  | INJECTION WELL IW-3
[22 empty] | N/A |  |  | INJECTION WELL IW-4
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s):
[22 empty] | REPORT MONTH / YEAR: |  | 2005-03-01 | DATE OF SAP / RECORDING: |  |  | 2005-03-01 | 2005-03-08 | 2005-03-15 | 2005-03-22 | 2005-03-29
Monitoring Zone ID #: | [5 empty] | Description
[22 empty] | OPERATOR'S NAME: |  |  | BAYLER, J.
UO-06-279512 |  | UPPER ZONE OF MONITORING WELL MW-1
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A
UO-06-279512 |  | LOWER ZONE OF MONITORING WELL MW-1
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [21 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2005-03-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
OPERATOR'S NAME: |  |  | BAYLER, J. | [18 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4474-A | [18 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 33.21 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 17.6 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: | [14 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 30.9879 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7448 | mg/l
Total monthly flow | [7 empty] | 175.44 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 3610 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [18 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.264 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 13.84 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.64 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 71.4 |  | PSIG | [11 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 8.152 | Std units
Monthly average of the daily flow rates | [7 empty] | 6.7477 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 12018 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 9.4757 |  | MG | [11 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 2.061 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 72.2 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [21 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.0116 | mg/l
Monthly average pressure | [7 empty] | 46.2981 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 915.2 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 35.3 |  | PSIG | [11 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [21 empty] | (Signature):
Date:
UNDERGROUND INJECTION CONTROL
MONTHLY OPERATING REPORT
[22 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
[22 empty] | Monitoring Well Decription: |  |  | LOWER ZONE OF MONITORING WELL MW-3
[22 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | 0054569-142-UO
[22 empty] | Monitoring Well ID #: |  |  | 5006A11310
[22 empty] | As Identified in Permit: |  | Monitor Well MW-3 Lower Monitor Zone |  |  |  | Issue Date: |  |  | 2004-01-07
[22 empty] | Monitoring Well Interval: |  |  | 1970 to 2027'
Associated Injection Well(s):
[22 empty] | Injection Well ID #: |  |  | Injection Well Description
[22 empty] | 5006A11310 |  |  | INJECTION WELL IW-3
[22 empty] | N/A |  |  | INJECTION WELL IW-4
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
[22 empty] | REPORT MONTH / YEAR: |  | 2005-03-01 | DATE OF SAP / RECORDING: |  |  | 2005-03-01 | 2005-03-08 | 2005-03-15 | 2005-03-22 | 2005-03-29
[22 empty] | OPERATOR'S NAME: |  |  | BAYLER, J.
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
[22 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
[22 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
[22 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 45.88 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 35.6 | PSIG
[22 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 44.5082 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
[22 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 24114.8 | mg/l
[22 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 14640 | mg/l
[22 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 2.232 | mg/l
[22 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 3.02 | mg/l
[22 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7.412 | Std units
[22 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 42620 | umho/cm
[22 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
[22 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 70.2 | deg. F
[22 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.012 | mg/l
[22 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 2476 | mg/l
[22 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
Date:

## DEP FORMS
Department of Environmental Protection Discharge Monitoring Report - Part A
When Completed mail this report to: Department of Environmental Protection, Wastewater Facilities Management Section, MS 3551, 2600 Blair Stone Road, Tallahassee, FL 32399-2400
PERMITEE NAME: | City of Fort Lauderdale |  |  |  |  | PERMIT NUMBER: |  | FLA041378 |  | REPORT: | Monthly
MAILING ADDRESS: | 949 NW 38th Street |  |  |  |  | LIMIT: |  | Final |  | GROUP: | Domestic
| Fort Lauderdale, FL 33309 |  |  |  |  | CLASS SIZE: |  | N/A |  | GMS TEST SITE
[6 empty] | GMS ID NO. |  | 5006M02066 |  | NO:
FACILITY: | City of Fort Lauderdale G. T. Lohmeyer WWTF |  |  |  |  | MONITORING GROUP NUMBER: |  | U-001
LOCATION: | 1765 SE 18th Street |  |  |  |  | PLANT SIZE/TREATMENT TYPE: |  | IIA
Fort Lauderdale, FL 33316
COUNTY: | Broward | [5 empty] | MONITORING PERIOD: |  |  | 2005-03-01
Parameter |  | Quantity of Loading |  | Units |  | Quality or Concentration |  | Units | No. Ex. | Frequency of Analysis | Sample Type
Flow | Sample Measurement | 9.3775 | 6.6586 | [5 empty] | 0
PARM Code 50050 1 Mon.Site No. EFF-002 | Permit Requirement | 18.3 (Peak Hour.) | Report (Mo. Avg.) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
Flow | Sample Measurement | 10.9701 | 7.8218 | [5 empty] | 0
PARM Code 50050 1 Mon.Site No. EFF-003 | Permit Requirement | 18.3 (Peak Hour.) | Report (Mo. Avg.) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
Flow | Sample Measurement | 10.4291 | 7.4615 | [5 empty] | 0
PARM Code 50050 1 Mon.Site No. EFF-004 | Permit Requirement | 18.3 (Peak Hour.) | Report (Mo. Avg.) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
Flow | Sample Measurement | 9.6605 | 6.9821 | [5 empty] | 0
PARM Code 50050 1 Mon.Site No. EFF-005 | Permit Requirement | 18.0 (Peak Hour.) | Report (Mo. Avg.) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
Flow | Sample Measurement | 9.4757 | 6.7477 | [5 empty] | 0
PARM Code 50050 1 Mon.Site No. EFF-006 | Permit Requirement | 18.3 (Peak Hour.) | Report (Mo. Avg.) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
I certify under penalty of law that I have personally examined and am familiar with the informantion submitted herein; and based on my inquiry of those individuals immeadiately responsible for obtaining the information, I believe the submitted
information is true, accurate and complete. I am aware that there are significant penalties for submitting false information including the possiblity of fine and imprisonment.
NAME/TITLE OF PRINCIPAL EXECUTIVE OFFICER OR AUTHORIZED AGENT |  |  |  | SIGNATURE OF PRINCIPAL EXECUTIVE OFFICER OR AUTHORIZED AGENT |  |  |  |  | TELEPHONE |  | DATE (YY/MM/DD)
954-523-1002 ext 2021
REGIONAL WASTEWATER FACILITIES MANAGER
COMMENTS AND EXPLANATION OF ANY VIOLATIONS (Reference all attachments here):
Version 8/13/99
Department of Environmental Protection Discharge Monitoring Report - Part A (Continued)
[12 empty] | PERMITEE NAME: | City of Fort Lauderdale G. T. Lohmeyer WWTF |  |  |  | PERMIT NUMBER: |  | FLA041378 | MONITORING GROUP NUMBER: U-001 |  |  | REPORT: | Monthly
[20 empty] | MONITORING PERIOD: |  |  |  | 2005-03-01
[12 empty] | Parameter |  |  | Quantity of Loading |  | Units |  | Quality or Concentration |  | Units | No. Ex. | Frequency of Analysis | Sample Type
[12 empty] | BOD, Carbonaceous 5 day, 20C |  | Sample Measurement |  |  |  | 4.9 |  |  |  | 0
[12 empty] | PARM Code 80082 Y Mon.Site No. EFF-001 |  | Permit Requirement |  |  |  | 20.0 (An.Avg.) |  |  | mg/l |  | Daily | 24-hour FPC
[12 empty] | BOD, Carbonaceous 5 day, 20C |  | Sample Measurement |  |  |  | 3.9535 | 3.8774 | 15.4 |  | 0
[12 empty] | PARM Code 80082 1 Mon.Site No. EFF-001 |  | Permit Requirement |  |  |  | 30.0 (Mo.Avg.) | 45.0 (Week.Avg.) | 60.0 (Max.) | mg/l |  | Daily | 24-hour FPC
[12 empty] | Solids, Total Suspended |  | Sample Measurement |  |  |  | 17.2 |  |  |  | 0
[12 empty] | PARM Code 00530 Y Mon.Site No. EFF-001 |  | Permit Requirement |  |  |  | 20.0 (An.Avg.) |  |  | mg/l |  | Daily | 24-hour FPC
[12 empty] | Solids, Total Suspended |  | Sample Measurement |  |  |  | 18.3871 | 18.12 | 44 |  | 0
[12 empty] | PARM Code 00530 1 Mon.Site No. EFF-001 |  | Permit Requirement |  |  |  | 30.0 (Mo.Avg.) | 45.0 (Week.Avg.) | 60.0 (Max.) | mg/l |  | Daily | 24-hour FPC
[12 empty] | pH |  | Sample Measurement |  |  |  | 6.4 |  |  |  | 0
[12 empty] | PARM Code 00400 1 Mon.Site No. EFF-001 |  | Permit Requirement |  |  |  | 6.0 (Min.) |  |  | s.u. |  | Continuous | Meter
[12 empty] | Flow |  | Sample Measurement | 34.169 | 35.0431 | [5 empty] | 0
[12 empty] | PARM Code 50050 G Mon.Site No. INF-001 |  | Permit Requirement | 55.7 (3-Mo.Avg.) | Report (Mo.Avg.) | mgd | [5 empty] | Continuous | Flow meters with 24-hour recording chart
[12 empty] | BOD, Carbonaceous 5 day, 20C |  | Sample Measurement |  |  |  | 97.8581 |  |  |  | N/A
[12 empty] | PARM Code 80082 G Mon.Site No. INF-002 |  | Permit Requirement |  |  |  | Report (Mo.Avg.) |  |  | mg/l |  | Daily | 24-hour FPC
[12 empty] | Solids, Total Suspended |  | Sample Measurement |  |  |  | 194 |  |  |  | N/A
[12 empty] | PARM Code 00530 G Mon.Site No. INF-002 |  | Permit Requirement |  |  |  | Report (Mo.Avg.) |  |  | mg/l |  | Daily | 24-hour FPC
Version 8/13/99

## JULIAN CONVERT
2005-03-01 | 38412 | 1999-01-01 | 2251
FROM DATE ON "DATA INPUT" PAGE | [5 empty] | 2005-03-01
2004
MONTHYY.PAR RANGE TO COMPILE (JULIAN DAY VALUES) FOR SPLIT PROGRAM ARE | [7 empty] | 60 | THROUGH | 2283
|  | 3 | MARCH
[5 empty] | 2005-03-01 | 2005-03-01 | 3
2005-03-01 |  |  |  |  | 1 | JANUARY |  | 1995 | 1995-01-01
[5 empty] | 2 | FEBRUARY |  | 1996 | 1996-01-01
[5 empty] | 3 | MARCH |  | 1997 | 1997-01-01
MARCH |  | 1 |  | 3 | 4 | APRIL |  | 1998 | 1998-01-01
|  | 0 |  | 0 | 5 | MAY |  | 1999 | 1999-01-01
|  | 1 |  |  | 6 | JUNE |  | 2000 | 2000-01-01
|  | 0 |  |  | 7 | JULY |  | 2001 | 2001-01-01
|  | 1 |  | 0 | 8 | AUGUST |  | 2002 | 2002-01-01
|  |  |  | 3 | 9 | SEPTEMBER |  | 2003 | 2003-01-01
[5 empty] | 10 | OCTOBER |  | 2004 | 2004-01-01
[5 empty] | 11 | NOVEMBER |  | 2005 | 2005-01-01
2005 |  |  |  |  | 12 | DECEMBER |  | 2006 | 2006-01-01
38412 | [6 empty] | MARCH | 2007 | 2007-01-01
38353 | [7 empty] | 2008 | 2008-01-01
59 | 1 |  | 1 | 60 | Tuesday
| 2 |  | 2 | 61 | Wednesday
| 3 |  | 3 | 62 | Thursday
| 4 |  | 4 | 63 | Friday
| 5 |  | 5 | 64 | Saturday
| 6 |  | 6 | 65 | Sunday
| 7 |  | 7 | 66 | Monday
| 8 |  | 8 | 67 | Tuesday
| 9 |  | 9 | 68 | Wednesday
| 10 |  | 10 | 69 | Thursday
| 11 |  | 11 | 70 | Friday
| 12 |  | 12 | 71 | Saturday
| 13 |  | 13 | 72 | Sunday
| 14 |  | 14 | 73 | Monday
| 15 |  | 15 | 74 | Tuesday
| 16 |  | 16 | 75 | Wednesday
| 17 |  | 17 | 76 | Thursday
| 18 |  | 18 | 77 | Friday
| 19 |  | 19 | 78 | Saturday
| 20 |  | 20 | 79 | Sunday
| 21 |  | 21 | 80 | Monday
| 22 |  | 22 | 81 | Tuesday
| 23 |  | 23 | 82 | Wednesday
| 24 |  | 24 | 83 | Thursday
| 25 |  | 25 | 84 | Friday
| 26 |  | 26 | 85 | Saturday
| 27 |  | 27 | 86 | Sunday
| 28 |  | 28 | 87 | Monday
| 29 |  | 29 | 88 | Tuesday
| 30 |  | 30 | 89 | Wednesday
| 31 |  | 31 | 90 | Thursday
31