## DATA INPUT
ENTER THE AVERAGE MONTHLY INFLUENT FLOW
INTO THE CORROSPONDING BOXES BELOW:
AUGUST | 35.748 | JULY | 31.602
ENTER THE PRESENT MONTH AND YEAR IN BOX BELOW (A5) | [5 empty] | SEPTEMBER
2003-09-01 | [5 empty] | 2003
IW-1 | IW-2 | IW-3 | IW-4 | IW-5
37.5 | 38.1 | 38.2 | 38.4 | 38.2 | 2003-09-05
|  | ENTER INJECTION WELL SHUT-IN PRESSURE ABOVE |  |  | ENTER DATE OF SHUT-IN READINGS
ENTER SLUDGE DISPOSAL SITE FOR EACH WEEK BELOW
| WEEK 1 | WEEK 2 | WEEK 3 | WEEK 4
1 st | Nutri-Cylcle Inc. | Nutri-Cylcle Inc. | Nutri-Cylcle Inc. | Nutri-Cylcle Inc.
2 nd | Arcadia, FL | Arcadia, FL | Arcadia, FL | Arcadia, FL
RAW DATA REPORT ENTRY CATEGORIES
GTL PLANT DAILY PROCESS SUMMARY
[6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
TOTAL RAW INFLUENT FLOW (MGD) | [5 empty] | 36.561 | 38.615 | 37.609 | 38.719 | 39.657 | 42.344 | 41.953 | 41.6 | 39.883 | 38.584 | 37.261 | 38.224 | 38.145 | 37.595 | 37.957 | 37.419 | 37.225 | 27.052 | 36.748 | 35.658 | 35.028 | 35.516 | 34.752 | 34.451 | 35.781 | 36.305 | 39.731 | 47.244 | 47.07 | 50.791
TOTAL EFFLUENT FLOW (MGD) | [5 empty] | 36.065 | 37.775 | 36.979 | 38.033 | 39.5 | 41.574 | 40.927 | 40.838 | 39.198 | 36.851 | 37.245 | 38.155 | 37.658 | 37.285 | 37.702 | 37.297 | 37.08 | 36.952 | 37.254 | 35.3 | 34.992 | 35.45 | 34.879 | 34.516 | 35.846 | 36.642 | 39.307 | 46.399 | 46.498 | 49.933
MAXIMUM HOURLY RAW INFLUENT FLOW (MGD) | [5 empty] | 1.812 | 1.818 | 1.755 | 1.867 | 2.058 | 2.057 | 1.95 | 1.97 | 1.913 | 1.862 | 1.785 | 1.839 | 1.876 | 1.881 | 1.768 | 1.747 | 1.78 | 1.788 | 1.784 | 1.767 | 1.759 | 1.776 | 1.778 | 1.768 | 1.779 | 1.777 | 2.258 | 2.233 | 2.202 | 2.498
MAXIMUM INSTANANEOUS PEAK RAW INFUENT FLOW (MGD) | [5 empty] | 52.45 | 54.02 | 50.559 | 53.668 | 56.616 | 56.231 | 56.808 | 56.103 | 53.764 | 52.29 | 52.097 | 51.841 | 53.764 | 53.86 | 52.802 | 50.976 | 51.008 | 49.696 | 50.014 | 50.111 | 50.367 | 51.521 | 51.456 | 51.232 | 50.976 | 50.816 | 61.422 | 61.198 | 58.891 | 63.986
MINIMUM INSTANANEOUS PEAK RAW INFUENT FLOW (MGD) | [5 empty] | 17.14 | 18.198 | 19.8 | 21.723 | 16.085 | 20.858 | 21.819 | 22.428 | 21.018 | 19.095 | 18.839 | 17.173 | 18.39 | 18.899 | 19.672 | 21.082 | 19.416 | 19.287 | 19.928 | 18.454 | 17.429 | 15.988 | 15.668 | 15.924 | 14.835 | 16.661 | 17.301 | 30.631 | 29.445 | 33.898
TOTAL RETURN ACTIVATED SLUDGE FLOW (MGD) | [5 empty] | 10.052 | 11.761 | 10.882 | 11.978 | 12.488 | 12.496 | 11.925 | 11.006 | 11.897 | 11.41 | 12.294 | 12.444 | 11.377 | 11.446 | 11.648 | 12.136 | 12.214 | 12.259 | 11.944 | 11.428 | 11.897 | 11.394 | 11.419 | 11.04 | 11.866 | 12.597 | 12.055 | 12.885 | 12.97 | 12.808
TOTAL WASTE FLOW TO DEWATERING PROCESS (MG) | [5 empty] | 0.368 | 0.54 | 0.612 | 0.52 | 0.174 | 0 | 0.202 | 0.496 | 0.532 | 0.552 | 0.495 | 0.223 | 0 | 0.184 | 0.56 | 0.568 | 0.564 | 0.569 | 0.294 | 0 | 0.203 | 0.553 | 0.52 | 0.499 | 0.659 | 0.327 | 0 | 0.236 | 0.588 | 0.626
TOTAL DAILY RAINFALL | [5 empty] | 0.33 | 0.5 | 0.03 | 0.4 | 1.34 | 0.71 | 0.2 | 0 | 0.47 | 0 | 0 | 0 | 0 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0 | 0 | 0 | 0.05 | 0.43 | 0.03 | 1.64 | 0 | 1.01 | 1.6
RAW INFLUENT pH | [5 empty] | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.3 | 7.3 | 7.2 | 7.3 | 7.2 | 7.3 | 7.2 | 7.2 | 7.1 | 7.2 | 7.1 | 7.1 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7.1 | 7 | 7.1 | 7 | 7 | 7.1
RAW INFLUENT HYDROGEN SULFIDE (PPM) | [5 empty] | 5 | 3 | 3 | 3 | 5 | 3 | 4 | 4 | 4 | 5 | 5 | 6 | 5 | 5 | 6 | 6 | 7 | 6 | 6 | 4 | 6 | 6 | 6 | 7 | 7 | 7 | 5 | 3 | 5 | 4
RAW INFLUENT TEMPERATURE (F ) | [5 empty] | 81 | 80 | 81 | 81 | 81 | 81 | 82 | 82 | 81 | 82 | 81 | 82 | 82 | 82 | 81 | 81 | 82 | 82 | 82 | 81 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82
TOTAL DAILY KILOWATTS (FPL POWER CONSUMPTION) | [5 empty] | 31016 | 31045 | 30967 | 30974 | 31100 | 31110 | 31050 | 30931 | 31004 | 31082 | ER | 31097 | 30959 | 30962 | 30902 | 31011 | 31087 | 31098 | 31200 | 31255 | 30887 | 30653 | 31105 | 31055 | 29771 | 28326 | 20546 | 19649 | 19734 | 19568
GTL PLANT DAILY PROCESS SUMMARY
(CONTINUED)
[6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
FINAL EFFLUENT FREE CHLORINE RESIDUAL (PPM) | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FINAL EFFLUENT TOTAL CHLORINE RESIDUAL (PPM) | [5 empty] | 1 | 1 | 9 | 1.2 | 1.3 | 1 | 1 | 1.1 | 0.6 | 1 | 1.1 | 1.1 | 0.9 | 1.1 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 1 | 1 | 0.8 | 0.7 | 0.8 | 0.9 | 1.1 | 0.5 | 0.2 | 0.4 | 0.7
FINAL EFFLUENT pH (daily average) | [5 empty] | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.5 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.7 | 6.7
FINAL EFFLUENT pH (daily minimum) | [5 empty] | 6.5 | 6.5 | 6.5 | 6.5 | 6.6 | 6.6 | 6.5 | 6.5 | 6.5 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.4 | 6.5 | 6.6 | 6.6 | 6.6 | 6.6 | 6.5 | 6.6 | 6.6
FINAL EFFLUENT pH (daily maximum) | [5 empty] | 6.7 | 6.7 | 6.7 | 6.6 | 6.6 | 6.6 | 6.7 | 6.7 | 6.7 | 6.8 | 6.7 | 6.7 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.7 | 6.7 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.7 | 6.7 | 6.7 | 6.8 | 6.8
FINAL EFFLUENT TEMPARTURE (F ) | [5 empty] | 85 | 85 | 84 | 84 | 84 | 84 | 84 | 85 | 84 | 84 | 87 | 84 | 85 | 85 | 84 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 84 | 84
AVERAGE CLARIFIER BLANKET DEPTH (INCHES) | [5 empty] | 28 | 35 | 27 | 26 | 24 | 31 | 33 | 31 | 28 | 25 | 22 | 23 | 29 | 23 | 26 | 23 | 17 | 18 | 17 | 17 | 20 | 22 | 22 | 21 | 16 | 16 | 23 | 22 | 22 | 21
FINAL EFFLUENT SAMPLE TEMPARTURE (C ) | [5 empty] | 6 | 6 | 7 | 0 | 8 | 8 | 5 | 5 | 5 | 5 | 7 | 7 | 6 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 4 | 5 | 5 | 5 | 5
TOTAL RETURN ACTIVATED SLUDGE FLOW TO REACTOR ONE (MGD) | [5 empty] | 3.953 | 5.606 | 4.637 | 5.172 | 5.339 | 5.333 | 4.618 | 4.258 | 5.396 | 5.184 | 5.05 | 5.364 | 4.526 | 4.447 | 4.608 | 5.066 | 4.913 | 4.779 | 4.192 | 3.92 | 3.969 | 4.135 | 4.15 | 4.232 | 4.804 | 5.317 | 5.038 | 5.365 | 6.35 | 5.817
TOTAL RETURN ACTIVATED SLUDGE FLOW TO REACTOR TWO (MGD) | [5 empty] | 6.099 | 6.155 | 6.245 | 6.806 | 7.149 | 7.164 | 7.307 | 6.749 | 6.501 | 6.226 | 7.244 | 7.08 | 6.851 | 6.999 | 7.04 | 7.07 | 7.301 | 7.48 | 7.752 | 7.508 | 7.928 | 7.258 | 7.269 | 6.808 | 7.062 | 7.28 | 7.017 | 7.52 | 6.62 | 6.991
GTL PLANT DAILY PROCESS SUMMARY
CONTINUED
[6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
TOTAL DAILY TRUCKING LOAD OF DEWATERED SLUDGE REMOVED | [5 empty] | 3 | 5 | 7 | 6 | 4 | 0 | 1 | 6 | 6 | 6 | 4 | 4 | 0 | 1 | 6 | 6 | 6 | 6 | 4 | 0 | 1 | 6 | 6 | 4 | 6 | 4 | 0 | 1 | 6 | 6
TOTAL DAILY HYDROGEN PEROXIDE CONSUMED (LBS) | [5 empty] | 2475 | 2215 | 2216 | 3254 | 2774 | 2624 | 2604 | 2355 | 2056 | 1298 | 1581 | 1188 | 1297 | 1398 | 1208 | 1178 | 958 | 1258 | 1187 | 2607 | 1070 | 1378 | 1108 | 1547 | 1936 | 1796 | 5782 | 1857 | 1287 | 2056
TOTAL DAILY CHLORINE CONSUMED (LBS) | [5 empty] | 1280 | 1280 | 1180 | 1580 | 1540 | 1280 | 1360 | 1220 | 880 | 1060 | 1120 | 1040 | 1200 | 1200 | 1140 | 1220 | 960 | 940 | 1140 | 1160 | 1100 | 1060 | 980 | 1300 | 1140 | 1040 | 880 | 680 | 840 | 1180
TOTAL DAILY POLYMER CONSUMED (GALS) | [5 empty] | 15 | 79 | 83 | 69 | 0 | 0 | 17 | 70 | 6 | 62 | 77 | 0 | 0 | 16 | 56 | 34 | 45 | 34 | 0 | 42 | 0 | 64 | 33 | 49 | 53 | 47 | 6 | 19 | 36 | 49
TOTAL TONS OF LIME DELIVERED DAILY | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTAL DAILY GASIOUS OXYGEN PRODUCED (TONS) | [5 empty] | 21 | 20.3 | 19.3 | 18.3 | 18.9 | 22.2 | 23 | 18.9 | 19.3 | 23.9 | 23.4 | 24.5 | 24.6 | 25.6 | 26.1 | 24.5 | 24 | 23.4 | 24 | 23.8 | 24.2 | 24.1 | 24.4 | 24.9 | 29.5 | 27 | 27.5 | 28 | 29.4 | 24.6
AVERAGE PERCENT OXYGEN PRODUCT PURITY | [5 empty] | 99 | 100 | 100 | 100 | 99 | 100 | 100 | 100 | 100 | 99 | 100 | 100 | 100 | 100 | 100 | 99 | 99 | 100 | 100 | 100 | 100 | 100 | 100 | 97 | 99 | 95 | 95 | 91 | 93 | 96
TOTAL DAILY LIQUID OXYGEN IN STORAGE (TONS) | [5 empty] | 143 | 144 | 144 | 145 | 144 | 143 | 143 | 144 | 145 | 145 | 146 | 146 | 144 | 144 | 145 | 146 | 146 | 147 | 147 | 146 | 146 | 147 | 148 | 148 | 148 | 141 | 131 | 120 | 108 | 103
MONITORING WELL PRESSURE DATA
MONITORING WELL ONE UPPER/LOWER LEVEL
| MW-1 |  | UPPER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
MINIMUM | [5 empty] | 45.79 | 46.3 | 48.4 | 48.51 | 48.6 | 48.64 | 48.71 | 47.44 | 47.78 | 48.52 | 48.61 | 48.7 | 48.68 | 48.64 | 47.61 | 47.87 | 48.72 | 48.71 | 48.63 | 48.55 | 48.51 | 45.35 | 45.79 | 48.55 | 48.61 | 48.63 | 48.68 | 48.72 | 46.97 | 47.3
MAXIMUM | [5 empty] | 48.76 | 48.6 | 48.74 | 48.89 | 48.97 | 49.02 | 49.08 | 49 | 48.77 | 48.87 | 48.96 | 48.93 | 48.89 | 48.91 | 48.91 | 48.88 | 48.94 | 48.94 | 48.87 | 48.84 | 48.83 | 48.78 | 49.08 | 48.92 | 48.94 | 48.99 | 49.02 | 49.03 | 48.97 | 48.93
AVERAGE | [5 empty] | 47.02 | 47.91 | 48.52 | 48.69 | 48.84 | 48.88 | 48.9 | 48.09 | 48.37 | 48.7 | 48.76 | 48.86 | 48.81 | 48.81 | 48.2 | 48.66 | 48.9 | 48.91 | 48.79 | 48.69 | 48.67 | 46.63 | 47.9 | 48.73 | 48.77 | 48.85 | 48.92 | 48.93 | 47.79 | 48.4
| MW-1 |  | LOWER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
MINIMUM | [5 empty] | 28.92 | 28.96 | 41.84 | 41.99 | 42.12 | 42.22 | 42.13 | 30.7 | 30.76 | 42.18 | 42.37 | 42.47 | 42.54 | 42.52 | 37.79 | 37.71 | 42.5 | 42.56 | 42.53 | 42.43 | 42.47 | 28.11 | 28.13 | 41.85 | 41.82 | 42 | 42.01 | 42.2 | 37.98 | 37.81
MAXIMUM | [5 empty] | 42.01 | 41.92 | 42.22 | 42.3 | 42.39 | 42.5 | 42.47 | 42.39 | 42.22 | 42.42 | 42.56 | 42.66 | 42.68 | 42.71 | 42.71 | 42.55 | 42.77 | 42.75 | 42.69 | 42.63 | 42.63 | 42.56 | 42.05 | 42.19 | 42.14 | 42.24 | 42.35 | 42.45 | 42.24 | 42.27
AVERAGE | [5 empty] | 32.82 | 38.2 | 41.97 | 42.11 | 42.33 | 42.39 | 42.42 | 34.07 | 38.76 | 42.36 | 42.47 | 42.52 | 42.56 | 42.58 | 39.69 | 41.19 | 42.54 | 42.59 | 42.55 | 42.53 | 42.52 | 32.31 | 37.99 | 42.03 | 42 | 42.07 | 42.2 | 42.35 | 39.21 | 40.83
MONITORING WELL TWO UPPER/LOWER LEVEL
| MW-2 |  | UPPER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
MINIMUM | bar: 1 to 30
MAXIMUM | bar: 1 to 30
AVERAGE | bar: 1 to 30
| MW-2 |  | LOWER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
MINIMUM | [5 empty] | 30.56 | 30.48 | 42.09 | 42.28 | 42.42 | 42.5 | 42.6 | 30.23 | 30.23 | 42.32 | 42.54 | 42.71 | 42.77 | 42.79 | 38.77 | 38 | 42.67 | 42.74 | 42.73 | 42.7 | 42.68 | 30.51 | 30.08 | 30.48 | 30.48 | 30.58 | 30.65 | 30.64 | 30.2 | 30.09
MAXIMUM | [5 empty] | 42.53 | 42.12 | 42.33 | 42.52 | 42.64 | 42.71 | 42.81 | 42.78 | 42.37 | 42.61 | 42.79 | 42.84 | 42.86 | 42.93 | 42.93 | 42.68 | 42.83 | 42.91 | 42.89 | 42.86 | 42.86 | 42.84 | 30.61 | 30.62 | 30.66 | 30.75 | 30.78 | 30.87 | 30.84 | 42.17
AVERAGE | [5 empty] | 34.19 | 38.75 | 42.29 | 42.4 | 42.5 | 42.53 | 42.69 | 33.82 | 38.67 | 42.47 | 42.71 | 42.85 | 42.86 | 42.9 | 40.48 | 41.4 | 42.84 | 42.87 | 42.88 | 42.85 | 42.83 | 34.32 | 30.5 | 30.53 | 30.53 | 30.69 | 30.7 | 30.78 | 30.44 | 38.59
MONITORING WELL THREE UPPER/LOWER LEVEL
| MW-3 |  | UPPER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
MINIMUM | [5 empty] | 22.16 | 22.01 | 31.34 | 31.56 | 31.71 | 31.77 | 31.88 | 21.1 | 21.04 | 31.51 | 31.7 | 31.81 | 31.82 | 31.79 | 17.43 | 17.32 | 31.4 | 31.52 | 31.53 | 31.49 | 31.5 | 21.75 | 21.74 | 31.49 | 31.65 | 31.75 | 31.83 | 31.92 | 21.66 | 21.48
MAXIMUM | [5 empty] | 31.48 | 31.41 | 31.69 | 31.9 | 31.99 | 32.09 | 32.17 | 32.07 | 31.62 | 31.85 | 31.99 | 31.99 | 32 | 32.02 | 32.02 | 31.48 | 31.72 | 31.8 | 31.78 | 31.75 | 31.78 | 31.71 | 31.6 | 31.84 | 31.94 | 32.05 | 32.1 | 32.18 | 32.13 | 31.82
AVERAGE | [5 empty] | 25 | 28.62 | 31.5 | 31.71 | 31.88 | 31.93 | 32 | 24.28 | 28.32 | 31.75 | 31.85 | 31.95 | 31.95 | 31.94 | 22.83 | 27.44 | 31.54 | 31.61 | 31.61 | 31.6 | 31.61 | 24.87 | 28.51 | 31.69 | 31.8 | 31.93 | 31.96 | 32.04 | 24.6 | 28.57
| MW-3 |  | LOWER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
MINIMUM | [5 empty] | 37.93 | 37.87 | 45.23 | 45.42 | 45.58 | 45.65 | 45.74 | 38.31 | 38.31 | 45.47 | 45.7 | 45.87 | 45.93 | 45.96 | 39.37 | 39.32 | 45.74 | 45.84 | 45.85 | 45.84 | 45.82 | 37.45 | 37.45 | 44.93 | 45.07 | 45.17 | 45.27 | 45.31 | 38.94 | 38.85
MAXIMUM | [5 empty] | 45.64 | 45.23 | 45.46 | 45.66 | 45.76 | 45.85 | 45.95 | 45.92 | 45.5 | 45.75 | 45.92 | 45.99 | 46.01 | 46.09 | 46.09 | 45.74 | 45.93 | 46.03 | 46.02 | 45.99 | 46 | 45.97 | 44.99 | 45.18 | 45.25 | 45.36 | 45.4 | 45.45 | 45.39 | 45.38
AVERAGE | [5 empty] | 40.3 | 42.96 | 45.37 | 45.5 | 45.6 | 45.81 | 45.89 | 40.56 | 43.3 | 45.5 | 45.86 | 45.97 | 45.99 | 46 | 41.93 | 43.81 | 45.87 | 45.93 | 45.94 | 45.95 | 45.94 | 40.08 | 42.71 | 45 | 45.11 | 45.36 | 45.4 | 45.44 | 40.78 | 43.38
MONITORING WELL RMW-1 UPPER/LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
[5 empty] | JULIAN DATE | 244 | 245 | 246 | 247 | 248 | 249 | 250 | 251 | 252 | 253 | 254 | 255 | 256 | 257 | 258 | 259 | 260 | 261 | 262 | 263 | 264 | 265 | 266 | 267 | 268 | 269 | 270 | 271 | 272 | 273
| RMW-1 |  | UPPER LEVEL
MINIMUM | [5 empty] | 33.1 | 32.31 | 43.57 | 43.82 | 44 | 44.16 | 44.24 | 44.33 | 44.38 | 44.46 | 44.54 | 44.64 | 44.64 | 44.65 | 44.71 | 44.78 | 44.82 | 44.77 | 44.63 | 44.54 | 44.46 | 44.43 | 44.43 | 44.39 | 44.39 | 44.44 | 44.45 | 44.43 | 44.39 | 44.36
MAXIMUM | [5 empty] | 44.32 | 43.59 | 43.84 | 44.02 | 44.19 | 44.29 | 44.39 | 44.48 | 44.52 | 44.62 | 44.7 | 44.73 | 44.73 | 44.75 | 44.83 | 44.88 | 44.9 | 44.88 | 44.79 | 44.7 | 44.59 | 44.55 | 44.52 | 44.52 | 44.56 | 44.58 | 44.55 | 44.56 | 44.5 | 44.43
AVERAGE | [5 empty] | 36.23 | 40.45 | 43.71 | 43.91 | 44.08 | 44.23 | 44.31 | 44.4 | 44.46 | 44.53 | 44.63 | 44.68 | 44.69 | 44.71 | 44.78 | 44.83 | 44.86 | 44.83 | 44.71 | 44.61 | 44.52 | 44.49 | 44.47 | 44.46 | 44.46 | 44.51 | 44.51 | 44.5 | 44.44 | 44.4
| RMW-1 |  | LOWER LEVEL
MINIMUM | [5 empty] | 20.31 | 20.38 | 21.65 | 21.89 | 22.09 | 22.21 | 22.29 | 22.38 | 22.4 | 22.45 | 22.5 | 22.5 | 22.52 | 22.5 | 22.54 | 22.59 | 22.62 | 22.57 | 22.46 | 22.38 | 22.33 | 22.34 | 22.39 | 22.39 | 22.33 | 22.47 | 22.49 | 22.48 | 22.45 | 22.41
MAXIMUM | [5 empty] | 22.37 | 21.65 | 21.93 | 22.13 | 22.31 | 22.38 | 22.43 | 22.5 | 22.49 | 22.52 | 22.6 | 22.6 | 22.58 | 22.6 | 22.67 | 22.72 | 22.74 | 22.71 | 22.61 | 22.54 | 22.48 | 22.51 | 22.5 | 22.5 | 22.52 | 22.55 | 22.56 | 22.59 | 22.55 | 22.55
AVERAGE | [5 empty] | 21.13 | 21.21 | 21.79 | 22.02 | 22.19 | 22.3 | 22.36 | 22.43 | 22.45 | 22.48 | 22.55 | 22.57 | 22.55 | 22.55 | 22.6 | 22.66 | 22.68 | 22.64 | 22.53 | 22.46 | 22.42 | 22.42 | 22.45 | 22.46 | 22.46 | 22.52 | 22.52 | 22.54 | 22.5 | 22.48
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
| INJECTION WELL ONE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 12.98 | 12.57 | 13.53 | 15.18 | 15.27 | 13.5 | 13.71 | 13.25 | 12.84 | 13.99 | 11.88 | 14.73 | 12.64 | 12.65 | 13.12 | 13.79 | 12.16 | 16.73 | 13.42 | 11.55 | 12.71 | 12.07 | 12.48 | 13.42 | 13.69 | 12 | 15.78 | 14.76 | 14.58 | 17.79
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 5.55 | 6.3 | 6.01 | 4.03 | 4.45 | 6.58 | 6.79 | 6.63 | 6.51 | 6.29 | 6.29 | 5.88 | 6.35 | 5.96 | 5.75 | 6.54 | 6.15 | 0.01 | 5.39 | 5.76 | 5.68 | 5.17 | 4.96 | 4.67 | 5.16 | 4.74 | 5.68 | 8.69 | 8.87 | 9.38
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 9.47 | 9.9 | 9.68 | 10 | 10.46 | 10.93 | 10.77 | 10.71 | 10.31 | 10 | 9.76 | 10.01 | 9.75 | 9.67 | 9.8 | 9.66 | 9.65 | 9.63 | 9.66 | 9.11 | 9.04 | 9.18 | 9.02 | 8.93 | 9.32 | 9.5 | 10.28 | 12.09 | 12.17 | 13.13
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 60.85 | 59.29 | 66.5 | 69.93 | 68.76 | 61.95 | 64.01 | 65.98 | 61.74 | 64.41 | 58.01 | 67.76 | 59.07 | 59.7 | 61.25 | 63.69 | 58.68 | 74.6 | 62.88 | 55.96 | 59.79 | 57.69 | 59.53 | 62.59 | 63.82 | 57.92 | 72.3 | 68.17 | 68.08 | 81.4
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 41.85 | 43.47 | 43.79 | 41.21 | 43.64 | 44.51 | 44.99 | 44.78 | 44.17 | 43.27 | 43.38 | 42.69 | 43.52 | 42.76 | 42.49 | 43.95 | 42.9 | 36.82 | 41.78 | 42.43 | 42.13 | 41.16 | 41.06 | 40.27 | 41.21 | 40.42 | 41.74 | 49.22 | 48.94 | 50.12
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 50.75 | 51.89 | 51.93 | 52.65 | 53.63 | 55 | 54.77 | 54.74 | 53.06 | 52.46 | 51.93 | 52.33 | 51.4 | 51.27 | 51.62 | 51.44 | 51.51 | 51.65 | 51.53 | 49.76 | 49.7 | 50.13 | 49.67 | 49.65 | 50.58 | 51.04 | 53.36 | 58.95 | 58.81 | 62.28
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
| INJECTION WELL TWO |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 13.09 | 12.71 | 13.63 | 15.45 | 14.68 | 13.58 | 14.02 | 13.46 | 12.97 | 13.4 | 12.49 | 15.54 | 13.25 | 13.33 | 13.77 | 14.47 | 12.76 | 17.54 | 14.07 | 12.13 | 13.35 | 12.57 | 13.16 | 14.08 | 14.36 | 12.7 | 16.56 | 15.46 | 15.38 | 18.57
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 5.47 | 6.25 | 6.01 | 3.83 | 0.14 | 6.73 | 6.79 | 6.63 | 6.53 | ER | 6.75 | ER | 6.74 | 6.29 | 6.14 | 6.98 | 6.54 | 0.13 | 5.79 | 6.08 | 6 | 5.44 | 5.11 | 4.87 | 5.34 | 4.9 | 6.15 | 9.34 | 9.42 | 9.97
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 9.61 | 10.09 | 9.84 | 10.15 | 10.59 | 11.13 | 10.95 | 10.89 | 10.48 | ER | 10.31 | 10.25 | 10.32 | 10.25 | 10.34 | 10.23 | 10.15 | 10.04 | 10.23 | 9.67 | 9.63 | 9.75 | 9.58 | 9.47 | 9.88 | 10.08 | 10.9 | 12.73 | 12.78 | 13.75
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 59.68 | 58.15 | 65.29 | 68.62 | 64.63 | 60.78 | 62.86 | 64.77 | 60.57 | 62.01 | 56.91 | 66.46 | 57.98 | 73.1 | 60.11 | 62.45 | 57.53 | 73.1 | 61.68 | 54.96 | 58.69 | 56.6 | 58.41 | 61.42 | 62.59 | 56.81 | 70.9 | 66.93 | 66.83 | 79.8
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 41.09 | 42.66 | 43 | 40.44 | 38.42 | 43.68 | 44.16 | 43.96 | 43.36 | 37.73 | 42.57 | 41.88 | 42.7 | 41.96 | 41.71 | 43.11 | 42.09 | 37.53 | 41.02 | 41.65 | 41.37 | 40.42 | 40.3 | 39.52 | 40.44 | 39.67 | 40.94 | 48.28 | 48.01 | 49.18
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 49.82 | 50.92 | 51.01 | 51.66 | 52.57 | 53.98 | 53.79 | 53.74 | 52.09 | 51.27 | 50.97 | 51.34 | 50.44 | 50.29 | 50.63 | 50.47 | 50.53 | 50.46 | 50.58 | 48.83 | 48.78 | 49.2 | 48.74 | 48.73 | 49.62 | 50.07 | 52.35 | 57.86 | 57.72 | 61.08
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
| INJECTION WELL THREE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 11.48 | 11.19 | 11.95 | 13.7 | 13.59 | 11.99 | 12.34 | 11.88 | 11.42 | 12.51 | 10.69 | 13.35 | 11.3 | 11.35 | 11.79 | 12.36 | 10.83 | 14.73 | 12.08 | 10.34 | 11.31 | 10.69 | 11.19 | 12.04 | 12.24 | 10.77 | 14.16 | 13.28 | 13.16 | 15.96
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 4.77 | 5.48 | 5.33 | 3.37 | 2.78 | 5.82 | 6.02 | 5.88 | 5.76 | 5.56 | 5.54 | 5.13 | 5.57 | 5.18 | 5.02 | 5.79 | 5.37 | ER | 4.68 | 5.03 | 4.9 | 4.39 | 4.21 | 3.9 | 4.34 | 3.96 | 4.95 | 7.89 | 7.99 | 8.45
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 8.44 | 8.84 | 8.63 | 8.96 | 9.41 | 9.8 | 9.65 | 9.6 | 9.23 | 8.96 | 8.74 | 8.97 | 8.72 | 8.64 | 8.75 | 8.62 | 8.6 | 8.62 | 8.64 | 8.15 | 8.07 | 8.19 | 8.04 | 7.96 | 8.33 | 8.49 | 9.22 | 10.89 | 10.92 | 11.75
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 61.17 | 59.67 | 66.9 | 70.3 | 69.08 | 62.31 | 64.45 | 66.34 | 62.15 | 64.69 | 58.34 | 68.21 | 59.45 | 59.98 | 61.62 | 64.09 | 58.96 | 73.6 | 63.2 | 56.26 | 60.15 | 57.97 | 59.85 | 62.98 | 64.16 | 58.22 | 72.7 | 68.56 | 68.49 | 81.9
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 41.96 | 43.63 | 43.95 | 41.33 | 43.09 | 44.67 | 45.16 | 44.96 | 44.33 | 43.41 | 43.51 | 42.81 | 43.65 | 42.88 | 42.61 | 44.1 | 43.05 | 36.76 | 41.91 | 42.56 | 42.27 | 41.29 | 41.18 | 40.38 | 41.31 | 40.53 | 41.88 | 49.42 | 49.13 | 50.33
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 51 | 52.12 | 52.17 | 52.87 | 54.01 | 55.28 | 55.07 | 54.99 | 53.35 | 52.7 | 52.15 | 52.57 | 51.61 | 51.46 | 51.87 | 51.65 | 51.74 | 51.85 | 51.73 | 49.94 | 49.92 | 50.34 | 49.88 | 49.87 | 50.78 | 51.23 | 53.58 | 59.27 | 59.13 | 62.59
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
FUTURE
| INJECTION WELL FOUR |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | ER | ER | ER | ER | ER | ER | ER | ER | ER | 11.86 | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER
INSTANTANEOUS MINIMUM FLOW (MGD) | bar: 1 to 30
TOTAL DAILY WELL FLOW (MGD) | bar: 1 to 30
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 38.55 | 38.35 | 39.01 | 39.16 | 38.89 | 38.77 | 38.95 | 38.7 | 38.59 | 38.61 | 38.15 | 38.78 | 38.15 | 64.41 | 38.2 | 38.08 | 37.78 | 38.41 | 37.87 | 37.36 | 37.57 | 37.54 | 37.72 | 38.11 | 38.16 | 37.75 | 38.89 | 38.71 | 38.61 | 39.81
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 36.63 | 36.83 | 36.99 | 36.66 | 37.13 | 37.32 | 37.39 | 37.14 | 36.95 | 36.75 | 36.69 | 36.48 | 36.51 | 36.33 | 36.26 | 36.34 | 36.21 | 35.95 | 36.21 | 36.1 | 36.01 | 35.95 | 35.99 | 35.91 | 35.93 | 35.75 | 35.99 | 36.73 | 36.74 | 36.92
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 37.64 | 37.74 | 37.83 | 37.92 | 38.01 | 38.18 | 38.17 | 38.04 | 37.8 | 37.66 | 37.54 | 37.5 | 37.38 | 37.27 | 37.25 | 37.2 | 37.16 | 37.11 | 37.07 | 36.84 | 36.78 | 36.88 | 36.9 | 36.92 | 36.97 | 37.02 | 37.24 | 37.8 | 37.77 | 38.04
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
| INJECTION WELL FIVE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 11.41 | 11.04 | 11.92 | 13.4 | 13.15 | 11.71 | 12.05 | 11.62 | 11.24 | 12.18 | 10.54 | 13.03 | 11.1 | 11.18 | 11.58 | 12.14 | 10.74 | 14.73 | 11.93 | 10.25 | 11.22 | 10.57 | 11.08 | 11.84 | 12.11 | 10.67 | 13.94 | 13.02 | 12.93 | 15.58
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 5.11 | 5.8 | 5.58 | 3.53 | ER | 6.16 | 6.26 | 6.11 | 6 | 5.87 | 5.89 | 5.41 | 5.83 | 5.47 | 5.32 | 6.01 | 5.67 | ER | 5.13 | 5.3 | 5.23 | 4.81 | 4.55 | 4.32 | 4.7 | 2.79 | 5.29 | 7.9 | 8 | 8.41
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 8.51 | 8.89 | 8.68 | 8.94 | 9.16 | 9.71 | 9.57 | 9.51 | 9.2 | 8.97 | 8.77 | 8.95 | 8.73 | 8.66 | 8.77 | 8.65 | 8.64 | 8.63 | 8.7 | 8.21 | 8.16 | 8.26 | 8.13 | 8.05 | 8.38 | 8.53 | 9.19 | 10.71 | 10.75 | 11.55
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 61.18 | 59.06 | 57.9 | 64.46 | 61.28 | 60.57 | 61.25 | 68.87 | 59.76 | 60.21 | 58.23 | 62 | 60.43 | 61.55 | 61.05 | 59.03 | 60.95 | 73.1 | 58.18 | 56.71 | 58.49 | 57.88 | 58.35 | 61.57 | 59.64 | 61.12 | 65.68 | 68.26 | 65.49 | 81.2
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 32.51 | 30.87 | 33.53 | 29.29 | 29.41 | 31.57 | 25.37 | 35.17 | 36.08 | 38.82 | 39.77 | 32.36 | 28.64 | 31.93 | 38.64 | 33.86 | 36.69 | 36.61 | 29.05 | 25.54 | 37.2 | 34.8 | 26.85 | 20.75 | 23.63 | 28.6 | 23.01 | 44.96 | 40.55 | 33.63
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 48.37 | 49.73 | 49.12 | 50.11 | 51.18 | 52.73 | 52.54 | 51.66 | 50.71 | 50.01 | 49.13 | 50.01 | 48.99 | 48.77 | 49.19 | 48.27 | 48.59 | 48.67 | 48.31 | 47.27 | 47.31 | 47.24 | 47.16 | 47.11 | 47.85 | 48.09 | 49.83 | 55.18 | 56.51 | 60.77
GTL DAILY LABORATORY ANALYSIS REPORT DATA
| RAW INFLUENT DATA |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
RAW TOTAL SUSPENDED SOLIDS | [5 empty] | 72 | 76 | 100 | 100 | 114 | 108 | 78 | 120 | 88 | 84 | 94 | 84 | 88 | 152 | 152 | 98 | 84 | 78 | 98 | 100 | 66 | 44 | 94 | 100 | 82 | 96 | 78 | 84 | 80 | 60
RAW FIXED SUSPENDED SOLIDS | [5 empty] | 10 | 12 | 20 | 20 | 12 | 22 | 12 | 14 | 12 | 12 | 10 | 10 | 14 | 14 | 14 | 8 | 14 | 8 | 2 | 14 | 12 | 10 | 16 | 4 | 6 | 4 | 6 | 12 | 16 | 12
RAW ALKILINITY | [5 empty] | 194 | 196 | 216 | 206 | 224 | 214 | 212 | 196 | 198 | 196 | 182 | 164 | 196 | 296 | 296 | 178 | 220 | 218 | 208 | 212 | 210 | 208 | 206 | 198 | 196 | 196 | 198 | 208 | 202 | 200
RAW CHLORIDES | [5 empty] | 620 | 600 | 580 | 570 | 570 | 520 | 500 | 540 | 630 | 670 | 590 | 630 | 610 | 640 | 660 | 640 | 620 | 780 | 740 | 750 | 720 | 730 | 730 | 700 | 720 | 680 | 700 | 730 | 720 | 730
RAW COD | [7 empty] | 242 | 216 | 224 | 223 | 270 |  |  | 293 | 264 | 247 | 229 | 293 |  |  | 294 | 265 | 255 | 213 | 302 |  |  | 280 | 325 | 187 | 193 | 196
RAW CBOD | [5 empty] | 66 | 84 | 65 | 93 | 73.1 | 62.2 | 60.6 | 55 | 59.1 | 69.8 | 60 | 115 | 54 | 83 | 83 | 53.9 | 79.8 | 78 | 60.8 | 58.5 | 68.9 | 57.3 | 61 | 85 | 58 | 57 | 47 | 50 | 35 | 28
| EFFLUENT DATA |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
EFFLUENT TOTAL DISSOLVED SOLIDS | [5 empty] | 1190 | 1240 | 1096 | 1050 | 1052 | 1115 | 1029 | 1062 | 1010 | 1189 | 1244 | 1210 | 1270 | 1294 | 1294 | 1335 | 1315 | 1298 | 1308 | 1385 | 1346 | 1393 | 1432 | 1403 | 1650 | 1410 | 1186 | 1240 | 1261 | 1125
EFFLUENT TOTAL SUSPENDED SOLIDS | [5 empty] | 18 | 8 | 24 | 13 | 23 | 12 | 11 | 10 | 8 | 24 | 13 | 9 | 10 | 12 | 12 | 7 | 17 | 13 | 11 | 11 | 17 | 8 | 11 | 12 | 12 | 10 | 10 | 18 | 16 | 10
EFFLUENT FIXED SUSPENDED SOLIDS | [5 empty] | 6 | 1 | 6 | 2 | 4 | 2 | 3 | 2 | 1 | 5 | 1 | 1 | 2 | 4 | 4 | 1 | 4 | 1 | 1 | 2 | 4 | 1 | 2 | 1 | 2 | 1 | 1 | 4 | 4 | 2
EFFLUENT ALKILINITY | [5 empty] | 186 | 188 | 190 | 188 | 180 | 184 | 190 | 192 | 192 | 190 | 196 | 200 | 188 | 192 | 192 | 196 | 196 | 198 | 182 | 188 | 190 | 188 | 188 | 184 | 182 | 180 | 184 | 192 | 190 | 192
EFFLUENT TURBIDITY | [5 empty] | 4.96 | 4.88 | 8.81 | 4.64 | 5.71 | 5.54 | 4.5 | 4.69 | 5.22 | 4.55 | 4.96 | 3.32 | 4.66 | 4.58 | 4.58 | 4.62 | 5.39 | 5.56 | 6.23 | 5.34 | 5.91 | 5.03 | 4.66 | 5.28 | 5.35 | 5.47 | 5.4 | 9.8 | 8.4 | 9.57
EFFLUENT CHLORIDES | [5 empty] | 600 | 620 | 580 | 580 | 580 | 560 | 500 | 510 | 600 | 580 | 570 | 640 | 610 | 650 | 650 | 630 | 650 | 700 | 730 | 730 | 720 | 710 | 730 | 680 | 690 | 690 | 680 | 690 | 710 | 720
EFFLUENT CONDUCTIVITY | [5 empty] | 2390 | 2280 | 2160 | 2210 | 2180 | 2200 | 1983 | 2030 | 2120 | 2220 | 2290 | 2500 | 2210 | 2640 | 2640 | 2650 | 2630 | 2660 | 2680 | 2610 | 2680 | 2750 | 2820 | 2840 | 2860 | 2800 | 2810 | 2420 | 2460 | 2280
EFFLUENT TOTAL BACTERIA COUNT | [5 empty] | 36 | 0 | 3600 | 1083 | 0 | 616 | 9 | 9 | 200 | 62 | 22500 | 3900 | 9 | TNTC | 71 | 71 | 3500 | TNTC | 46500 | 18 | 3900 | 440 | 22000 | 98 | 6300 | TNTC | 223 | TNTC | TNTC | TNTC
EFFLUENT FECAL BACTERIA COUNT | [5 empty] | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 9 | 40 | 54 | 0 | TNTC | 9 | 9 | 0 | 464 | 71 | 9 | 27 | 0 | 9 | 0 | 0 | 0 | 0 | 18 | 72500 | TNTC
EFFLUENT COD | [7 empty] | 242 | 216 | 216 | 223 | 270 |  |  | 48.5 | 42.4 | 42.6 | 58 | 43.3 |  |  | 54 | 45.4 | 52.2 | 21.2 | 58.8 |  |  | 56.8 | 52.6 | 52.6 | 62.4 | 58
EFFLUENT CBOD | [5 empty] | 3.2 | 4.4 | 3.4 | 3 | 4.63 | 2.3 | 2.7 | 2.7 | 3.08 | 3.3 | 5 | 3 | 3.05 | 3.1 | 3.1 | 6.14 | 3.71 | 5 | 4.53 | 3.4 | 3.27 | 3.77 | 3.5 | 4.2 | 4 | 4 | 3 | 4 | 5 | 4
LABORATORY NUTRIENT DATA
RAW INFLUENT | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
RAW AMMONIA (PPM) | [7 empty] | 13 | 13 | 13 | 11 | 11 |  |  | 14 | 14 | 14.19 | 12.88 | 13.63 |  |  | 15 | 13.94 | 14.53 | 13.62 | 14.19 |  |  | 13.82 | 14.59 | 14.81 | 13.39 | 10.88
RAW NITRATES (PPM) | [7 empty] | 0.076 | 0.02 | 0.02 | 0.02 | 0.02 |  |  | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 |  |  | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 |  |  | 0.217 | 0.242 | 0.303 | 0.264 | 0.268
RAW TOTAL KNEDJAHL NITRIGEN | [7 empty] | 19 | 18 | 18 | 16 | 15 |  |  | 18 | 18 | 21.14 | 19.56 | 20.36 |  |  | 20.38 | 18.68 | 20.99 | 19.52 | 20.21 |  |  | 20.55 | 21.61 | 19.53 | 19.27 | 17.5
RAW TOTAL PHOSPHORUS | [7 empty] | 2.5 | 2.4 | 2.4 | 2.1 | 2.2 |  |  | 2.5 | 2.4 | 2.69 | 2.72 | 2.82 |  |  | 2.64 | 2.37 | 2.68 | 1.53 | 1.82 |  |  | 2.72 | 2.66 | 2.2 | 2.07 | 2.03
EFFLUENT | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
EFFLUENT AMMONIA (PPM) | [7 empty] | 11 | 10 | 10 | 8.3 | 7.9 |  |  | 10 | 10 | 10.74 | 9.41 | 9.79 |  |  | 11.37 | 11.81 | 11.58 | 11.11 | 11.03 |  |  | 10.5 | 11.67 | 11.57 | 10.15 | 8.04
EFFLUENT NITRATES (PPM) | [7 empty] | 0.65 | 0.67 | 0.67 | 0.42 | 0.6 |  |  | 0.54 | 0.55 | 0.356 | 0.366 | 0.443 |  |  | 0.444 | 0.467 | 0.411 | 0.382 | 0.439 |  |  | 0.38 | 0.482 | 0.371 | 0.193 | 0.477
EFFLUENT TOTAL KNEDJAHL NITRIGEN | [7 empty] | 12 | 11 | 11 | 9.2 | 8.3 |  |  | 11 | 12 | 14.57 | 13.14 | 13.58 |  |  | 15.16 | 15.44 | 15.45 | 14.76 | 14.84 |  |  | 14.94 | 15.91 | 15.72 | 14.57 | 12.36
EFFLUENT TOTAL PHOSPHORUS | [7 empty] | 1.1 | 0.83 | 0.83 | 0.85 | 0.71 |  |  | 0.86 | 1.6 | 0.735 | 1.05 | 1.04 |  |  | 1.06 | 1.02 | 0.772 | 0.72 | 0.72 |  |  | 1.03 | 1.19 | 1.24 | 1.34 | 1.25
LABORATORY REACTOR PROCESSES DATA
| REACTOR ONE TRAIN A |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
MIXED-LIQUIR SUSPENDED SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
AVERAGE SETTLABLE SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
MIXED LIQUIR VOLITLE SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
| REACTOR ONE TRAIN B |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
MIXED-LIQUIR SUSPENDED SOLIDS | [5 empty] | 1890 | 2380 | 2240 | 2270 | 1530 | 2250 | 2120 | 2480 | 1800 | 2200 | 2600 | 2100 | 2410 | 1970 | 1970 | 2230 | 1910 | 1770 | 2010 | 2110 | 2490 | 2460 | 1960 | 2280 | 1810 | 1910 | 1870 | 1620 | 1470 | 1350
AVERAGE SETTLABLE SOLIDS | [5 empty] | 18 | 19 | 19 | 19 | 21 | 24 | 21 | 17 | 19 | 17 | 17 | 19 | 23 | 23 | 23 | 18 | 17 | 15 | 19 | 19 | 22 | 20 | 18 | 17 | 13 | 14 | 14 | 16 | 13 | 13
MIXED LIQUIR VOLITLE SOLIDS | [5 empty] | 1550 | 1980 | 1860 | 1880 | 1320 | 1870 | 1760 | 2060 | 1500 | 1830 | 2170 | 1770 | 2000 | 1590 | 1590 | 1900 | 1580 | 1490 | 1720 | 1750 | 2070 | 2080 | 1630 | 1900 | 1450 | 1530 | 1510 | 1340 | 1220 | 1120
LABORATORY REACTOR PROCESSES DATA
CONTINUED
| REACTOR TWO TRAIN C |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
MIXED-LIQUIR SUSPENDED SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
AVERAGE SETTLABLE SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
MIXED LIQUIR VOLITLE SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
| REACTOR TWO TRAIN D |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
MIXED-LIQUIR SUSPENDED SOLIDS | [5 empty] | 2060 | 2720 | 2420 | 2260 | 1900 | 2190 | 2620 | 2730 | 2420 | 2970 | 1000 | 1470 | 2240 | 2280 | 2280 | 2150 | 1710 | 1870 | 1930 | 2190 | 2670 | 2490 | 2880 | 2070 | 1900 | 1910 | 1810 | 1620 | 1460 | 1500
AVERAGE SETTLABLE SOLIDS | [5 empty] | 20 | 19 | 19 | 19 | 21 | 23 | 21 | 19 | 19 | 17 | 19 | 20 | 21 | 23 | 23 | 20 | 18 | 15 | 20 | 20 | 22 | 20 | 20 | 18 | 14 | 14 | 15 | 16 | 13 | 13
MIXED LIQUIR VOLITLE SOLIDS | [5 empty] | 1730 | 2260 | 2010 | 1880 | 1650 | 1820 | 2170 | 2290 | 1980 | 2430 | 940 | 1260 | 1860 | 1890 | 1890 | 1880 | 1390 | 1570 | 1620 | 1820 | 2240 | 2120 | 2390 | 1650 | 1500 | 1520 | 1470 | 1360 | 1210 | 1240
LABORATORY RETURN ACTIVATED SLUDGE AND WASTE SLUDGE DATA
| RETURN ACTIVATED SLUDGE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
PERCENT RETURN SLUDGE TOTAL SUSPENDED SOLIDS | [5 empty] | 0.52 | 0.98 | 0.92 | 0.92 | 0.92 | 0.92 | 0.87 | 0.87 | 0.8 | 0.78 | 0.41 | 0.94 | 0.94 | 0.93 | 0.93 | 0.93 | 0.74 | 0.7 | 0.88 | 0.85 | 0.72 | 0.55 | 0.7 | 0.76 | 0.64 | 0.8 | 0.64 | 0.82 | 0.76 | 0.76
PERCENT RETURN SLUDGE FIXED SUSPENDED SOLIDS | [5 empty] | 25 | 22.4 | 22.1 | 20.6 | 23.5 | 23.9 | 22.3 | 22.1 | 28.6 | 28.1 | 25.3 | 24.5 | 25.5 | 22.7 | 22.7 | 22.9 | 24.5 | 27 | 24.7 | 26.3 | 27.3 | 28.9 | 27.1 | 29.4 | 29.3 | 27.1 | 24.6 | 24.1 | 25 | 24.8
|  | WASTE SLUDGE |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
PERCENT WASTE FEED TOTAL SUSPENDED SOLDS | [5 empty] | 1.08 | 0.9 | 1.23 | 1.53 |  |  | 0.9 | 1.42 | 1.49 | 1.43 | 1.56 |  |  | 1.5 | 1.5 | 1.44 | 0.97 |  |  |  | 1.5 | 0.78 | 1.21 | 1.42 | 1.04 |  |  | 1.19 | 0.62 | 1.51
PERCENT WASTE FEED FIXED SUSPENDED SOLIDS | [5 empty] | 25.9 | 25.6 | 21.1 | 19 |  |  | 24.4 | 19.7 | 20.8 | 21 | 19.2 |  |  | 20.7 | 20.7 | 20.8 | 24.7 |  |  |  | 21.3 | 29.5 | 24 | 23.2 | 38.5 |  |  | 22.7 | 30.6 | 25.2
WASTE FEED SLUDGE pH | [5 empty] | 6.9 | 6.84 | 6.81 | 6.78 |  |  | 6.79 | 6.78 | 6.79 | 6.64 | 6.68 |  |  | 6.47 | 6.47 | 6.49 | 6.53 |  |  |  | 6.36 | 6.33 | 6.79 | 6.51 | 6.5 |  |  | 6.74 | 6.78 | 6.78
DEWATERING FILTRATE TOTAL SUSPENDED SOLIDS | [5 empty] | 0.45 | 0.41 | 0.53 | 0.43 |  |  | 0.31 | 0.26 | 0.23 | 0.3 | 0.36 |  |  | 0.27 | 0.27 | 0.28 | 0.29 |  |  |  | 0.23 | 0.27 | 0.32 | 0.35 | 0.37 |  |  | 0.3 | 0.3 | 0.31
DEWATERING FILTRATE FIXED SUSPENDED SOLIDS | [5 empty] | 33.3 | 34.1 | 28.3 | 30.2 |  |  | 35.5 | 42.3 | 56.5 | 43.3 | 36.1 |  |  | 51.8 | 51.9 | 46.4 | 48.3 |  |  |  | 60.9 | 48.1 | 34.4 | 42.9 | 43.2 |  |  | 43.3 | 46.7 | 48.4
DEWATERING FILTRATE pH | [5 empty] | 7.34 | 7.24 | 7.18 | 7.2 |  |  | 7.19 | 7.47 | 7.24 | 7.37 | 7.33 |  |  | 7.28 | 7.28 | 7.14 | 7.14 |  |  |  | 7.34 | 7.26 | 7.21 | 7.19 | 7.19 |  |  | 7.21 | 7.24 | 7.2
| DEWATERED CAKE SLUDGE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
PERCENT TOTAL SOLIDS PRESS CAKE | [5 empty] | 17.32 | 8.43 | 18.4 | 17.69 |  |  | 17.57 | 17.57 | 18.07 | 17.99 | 17.86 |  |  | 17.4 | 17.4 | 18.65 | 17.78 |  |  |  | 16.44 | 17.08 | 18.45 | 18.01 | 18.99 |  |  | 18.14 | 17.68 | 18.98
PERCENT FIXED SOLIDS PRESS CAKE | [5 empty] | 16.2 | 14.5 | 17.7 | 14.1 |  |  | 14.7 | 17.6 | 14.9 | 14.5 | 14.22 |  |  | 14.7 | 17.4 | 16.2 | 16.5 |  |  |  | 16.1 | 14.3 | 15.8 | 17.8 | 18.3 |  |  | 14.3 | 15.7 | 15.8
PERCENT TOTAL SOLIDS LIME CAKE
OTHER SLUDGE REMOVAL
[6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
GRIT (CU.YDS.) | [5 empty] | 19: 10; 22: 10; 25: 10; 30: 10
RAGS (CU.YDS.) | [5 empty] | 5: 10; 15: 10; 19: 10; 26: 10
VACUUM DEBRIS (EST. GAL) | [5 empty] | 18: 4500
MONITORING WELLS LABORATORY DATA
| MONITOR WELL ONE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
UPPER LEVEL
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
MONITORING WELLS LABORATORY DATA
| MONITOR WELL TWO |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
UPPER LEVEL
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
MONITORING WELLS LABORATORY DATA
| MONITOR WELL THREE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
FUTURE
UPPER LEVEL
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
MONITORING WELLS LABORATORY DATA
| REGIONAL MONITOR WELL ONE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
UPPER LEVEL
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
SEPTEMBER |  | 0 |  | 0
|  | 1 |  | 2
0
0
|  | 0 |  | 0
2
[5 empty] | 1st WEEK | 1: 2nd WEEK; 2: 3rd WEEK; 3: 4th WEEK
| 1 |  | 1 |  | 1 | 1: 8; 2: 15; 3: 23
| 2 |  | 2 |  | 2 | 1: 9; 2: 16; 3: 24
| 3 |  | 3 |  | 3 | 1: 10; 2: 17; 3: 25
| 4 |  | 4 |  | 4 | 1: 11; 2: 18; 3: 26
| 5 |  | 5 |  | 5 | 1: 12; 2: 19; 3: 27
| 6 |  | 6 |  | 6 | 1: 13; 2: 20; 3: 28
| 7 |  | 7 |  | 7 | 1: 14; 2: 21; 3: 29
| 8 |  | 8 |  |  | 2: 22; 3: 30
| 9 |  | 9
| 10 |  | 10
| 11 |  | 11
| 12 |  | 12
| 13 |  | 13
| 14 |  | 14
| 15 |  | 15
| 16 |  | 16
| 17 |  | 17
| 18 |  | 18
| 19 |  | 19
| 20 |  | 20
| 21 |  | 21
| 22 |  | 22
| 23 |  | 23
| 24 |  | 24
| 25 |  | 25
| 26 |  | 26
| 27 |  | 27
| 28 |  | 28
29
30
| APRIL | MARCH | FEBRUARY
| AUGUST | JULY | JUNE
| DECEMBER | NOVEMBER | OCTOBER
| FEBRUARY | JANUARY | DECEMBER
| JANUARY | DECEMBER | NOVEMBER
| JUNE | MAY | APRIL
| JULY | JUNE | MAY | AUGUST
| MARCH | FEBRUARY | JANUARY | JULY
| MAY | APRIL | MARCH
| NOVEMBER | OCTOBER | SEPTEMBER
| OCTOBER | SEPTEMBER | AUGUST
| SEPTEMBER | AUGUST | JULY
| HYDROGEN PEROXIDE |  | 0.1395
| CHLORINE |  | 0.1475
| POLYMER |  | 0.61
| FPL |  | 0.055
[6 empty] | 1st WEEK |  |  | 2nd WEEK |  |  | 3rd WEEK |  |  | 4th WEEK
[7 empty] | G | H | I | J
[5 empty] | MW1 UP | 1: 311
312
313
314
315
316
317
318

## MONITOR DATA
UNDERGROUND INJECTION CONTROL SECTION
MONTHLY OPERATING REPORT DATA SUMMARY
FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT MONTH/YEAR |  |  |  | SEPTEMBER |  | 2003
I.D. NUMBER: 5006M02066 | [5 empty] | LEAD OPERATOR: |  |  |  |  | MIKE JUST
TELEPHONE NUMBER: (954) 523-1002
MONITORING WELL 1 DATA | [6 empty] | I.D. # 5006A11311
MW-1
PERMIT/CERTIFICATION NUMBER | [6 empty] | UO-06-279512
PERMIT EXPIRATION DATE |  | 2002-07-21
UPPER MONITORING INTERVAL | [6 empty] | 1,288' - 1,320' |  |  |  |  | Ft. bls.
Sample Date |  | 2003-09-02 |  | 2003-09-09 |  | 2003-09-16 |  | 2003-09-23 |  | 2003-09-30
Submittal Date |  | 2003-09-03 |  | 2003-09-10 |  | 2003-09-17 |  | 2003-09-24 |  | 2003-10-01
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [9 empty] | 49.08 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [9 empty] | 45.35 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 73 |  | 72 |  | 74 |  | 72 |  | 74 |  | degrees (F) |  | 73
TDS |  | 7545 |  | 7420 |  | 7180 |  | 7180 |  | 7300 |  | mg/l |  | 7325
CHLORIDE |  | 3800 |  | 3850 |  | 3800 |  | 3800 |  | 3850 |  | mg/l |  | 3820
AMMONIA-N |  | 0.886 |  | 0.92 |  | 0.779 |  | 0.779 |  | 0.916 |  | mg/l |  | 0.856
TKN |  | 1.33 |  | 0.9 |  | 1.37 |  | 1.37 |  | 1.93 |  | mg/l |  | 1.38
pH |  | 7.97 |  | 7.87 |  | 7.78 |  | 7.78 |  | 7.74 |  | Std units |  | 7.828
CONDUCTIVITY |  | 12060 |  | 12090 |  | 12080 |  | 12080 |  | 12080 |  | umho/cm |  | 12078
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.05 | < | 0.01 | < | 0.05 | < | 0.05 | < | 0.05 |  | mg/l |  | 0.042
SULFATE |  | 850 |  | 800 |  | 850 |  | 850 |  | 900 |  | mg/l |  | 850
C.O.D. 'S |  | 200 |  | 170 |  | 180 |  | 180 |  | 190 |  | mg/l |  | 184
IRON |  | 0.25 |  | 0.4 |  | 0.45 |  | 0.45 |  | 0.61 |  | mg/l |  | 0.432
SULFIDE | [11 empty] | mg/l |  | #DIV/0!
LOWER MONITORING INTERVAL | [6 empty] | 1,449' - 1,557' |  |  |  |  | Ft. bls
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [9 empty] | 42.77 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [9 empty] | 28.11 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 73 |  | 71 |  | 73 |  | 73 |  | 73 |  | degrees (F) |  | 72.6
TDS |  | 9106 |  | 9703 |  | 9060 |  | 9060 |  | 9375 |  | mg/l |  | 9260.8
CHLORIDE |  | 5200 |  | 5100 |  | 5300 |  | 5300 |  | 5100 |  | mg/l |  | 5200
AMMONIA-N |  | 9.67 |  | 9.3 |  | 9.6 |  | 9.6 |  | 9.74 |  | mg/l |  | 9.582
TKN |  | 11.2 |  | 10 |  | 11.55 |  | 11.55 |  | 12.24 |  | mg/l |  | 11.308
pH |  | 7.32 |  | 7.25 |  | 7.19 |  | 7.19 |  | 7.24 |  | Std units |  | 7.238
CONDUCTIVITY |  | 19990 |  | 15740 |  | 16000 |  | 16000 |  | 15900 |  | umho/cm |  | 16726
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.05 | < | 0.01 | < | 0.05 | < | 0.05 | < | 0.05 |  | mg/l |  | 0.042
SULFATE |  | 800 |  | 850 |  | 750 |  | 750 |  | 800 |  | mg/l |  | 790
C.O.D. 'S |  | 270 |  | 290 |  | 260 |  | 260 |  | 280 |  | mg/l |  | 272
IRON |  | 0.01 |  | 0.01 |  | 0.02 |  | 0.02 |  | 0.02 |  | mg/l |  | 0.016
SULFIDE | [11 empty] | mg/l |  | #DIV/0!
PAGE 24
UNDERGROUND INJECTION CONTROL SECTION
MONTHLY OPERATING REPORT DATA SUMMARY
FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT MONTH/YEAR |  |  |  | SEPTEMBER |  | 2003
I.D. NUMBER: 5006M02066 | [5 empty] | LEAD OPERATOR: |  |  |  |  | MIKE JUST
TELEPHONE NUMBER: (954) 523-1002
MONITORING WELL 2 DATA | [6 empty] | I.D. # 5006A11308 & 309
MW-2
PERMIT/CERTIFICATION NUMBER | [6 empty] | UO-06-279401 & 508
PERMIT EXPIRATION DATE |  | 2002-07-21
UPPER MONITORING INTERVAL | [6 empty] | 1,300' - 1,344' |  |  |  |  | Ft. bls.
Sample Date |  | 2003-09-02 |  | 2003-09-09 |  | 2003-09-16 |  | 2003-09-23 |  | 2003-09-30
Submittal Date |  | 2003-09-03 |  | 2003-09-10 |  | 2003-09-17 |  | 2003-09-24 |  | 2003-10-01
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [9 empty] | 0 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [9 empty] | 0 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 72 |  | 71 |  | 73 |  | 71 |  | 70 |  | degrees (F) |  | 71.4
TDS |  | 7537 |  | 7400 |  | 6960 |  | 6960 |  | 7222 |  | mg/l |  | 7215.8
CHLORIDE |  | 3800 |  | 3600 |  | 3750 |  | 3750 |  | 3800 |  | mg/l |  | 3740
AMMONIA-N |  | 0.889 |  | 0.89 |  | 1.07 |  | 1.07 |  | 0.893 |  | mg/l |  | 0.9624
TKN |  | 1.5 |  | 1.4 |  | 1.63 |  | 1.63 |  | 1.63 |  | mg/l |  | 1.558
pH |  | 8 |  | 8 |  | 7.87 |  | 7.87 |  | 7.97 |  | Std units |  | 7.942
CONDUCTIVITY |  | 11800 |  | 11820 |  | 11800 |  | 11800 |  | 11800 |  | umho/cm |  | 11804
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.05 | < | 0.01 | < | 0.05 | < | 0.05 | < | 0.05 |  | mg/l |  | 0.042
SULFATE |  | 850 |  | 800 |  | 850 |  | 850 |  | 850 |  | mg/l |  | 840
C.O.D. 'S |  | 200 |  | 180 |  | 170 |  | 170 |  | 180 |  | mg/l |  | 180
IRON |  | 0.99 |  | 0.96 |  | 0.97 |  | 0.97 |  | 0.89 |  | mg/l |  | 0.956
SULFIDE | [11 empty] | mg/l |  | #DIV/0!
LOWER MONITORING INTERVAL | [6 empty] | 1,970' - 2,025' |  |  |  |  | Ft. bls
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [9 empty] | 42.93 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [9 empty] | 30.08 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 70 |  | 70 |  | 71 |  | 70 |  | 70 |  | degrees (F) |  | 70.2
TDS |  | 31165 |  | 32324 |  | 30830 |  | 30830 |  | 31530 |  | mg/l |  | 31335.8
CHLORIDE |  | 18000 |  | 17800 |  | 18000 |  | 18000 |  | 17600 |  | mg/l |  | 17880
AMMONIA-N |  | 1.51 |  | 1.2 |  | 1.42 |  | 1.42 |  | 1.27 |  | mg/l |  | 1.364
TKN |  | 1.62 |  | 1.4 |  | 1.71 |  | 1.71 |  | 2.31 |  | mg/l |  | 1.75
pH |  | 7.3 |  | 7.3 |  | 7.22 |  | 7.22 |  | 7.31 |  | Std units |  | 7.27
CONDUCTIVITY |  | 47100 |  | 47200 |  | 46800 |  | 46800 |  | 47000 |  | umho/cm |  | 46980
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.05 | < | 0.01 | < | 0.05 | < | 0.05 | < | 0.05 |  | mg/l |  | 0.042
SULFATE |  | 2300 |  | 2200 |  | 2600 |  | 2600 |  | 2500 |  | mg/l |  | 2440
C.O.D. 'S |  | 850 |  | 890 |  | 820 |  | 820 |  | 860 |  | mg/l |  | 848
IRON |  | 0.02 |  | 0.03 |  | 0.04 |  | 0.04 |  | 0.05 |  | mg/l |  | 0.036
SULFIDE | [11 empty] | mg/l |  | #DIV/0!
PAGE 25
UNDERGROUND INJECTION CONTROL SECTION
MONTHLY OPERATING REPORT DATA SUMMARY
FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT MONTH/YEAR |  |  |  | SEPTEMBER |  | 2003
I.D. NUMBER: 5006M02066 | [5 empty] | LEAD OPERATOR: |  |  |  |  | MIKE JUST
TELEPHONE NUMBER: (954) 523-1002
MONITORING WELL 2 DATA | [6 empty] | I.D. # 5006A11310
MW-3
PERMIT/CERTIFICATION NUMBER | [6 empty] | UO-06-279510
PERMIT EXPIRATION DATE |  | 2002-07-21
UPPER MONITORING INTERVAL | [6 empty] | 1,300' - 1,349' |  |  |  |  | Ft. bls.
Sample Date |  | 2003-09-02 |  | 2003-09-09 |  | 2003-09-16 |  | 2003-09-23 |  | 2003-09-30
Submittal Date |  | 2003-09-03 |  | 2003-09-10 |  | 2003-09-17 |  | 2003-09-24 |  | 2003-10-01
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [9 empty] | 32.18 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [9 empty] | 17.32 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 70 |  | 70 |  | 70 |  | 70 |  | 70 |  | degrees (F) |  | 70
TDS |  | 7280 |  | 7438 |  | 7270 |  | 7270 |  | 7242 |  | mg/l |  | 7300
CHLORIDE |  | 3800 |  | 3750 |  | 3800 |  | 3800 |  | 3850 |  | mg/l |  | 3800
AMMONIA-N |  | 1.14 |  | 0.88 |  | 1.06 |  | 1.06 |  | 0.879 |  | mg/l |  | 1.0038
TKN |  | 1.26 |  | 0.98 |  | 1.34 |  | 1.34 |  | 1.79 |  | mg/l |  | 1.342
pH |  | 8.12 |  | 8.13 |  | 8.04 |  | 8.04 |  | 8.01 |  | Std units |  | 8.068
CONDUCTIVITY |  | 11900 |  | 11950 |  | 12160 |  | 12160 |  | 12090 |  | umho/cm |  | 12052
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.05 | < | 0.01 | < | 0.05 | < | 0.05 | < | 0.05 |  | mg/l |  | 0.042
SULFATE |  | 900 |  | 850 |  | 800 |  | 800 |  | 850 |  | mg/l |  | 840
C.O.D. 'S |  | 200 |  | 170 |  | 180 |  | 180 |  | 180 |  | mg/l |  | 182
IRON |  | 0.93 |  | 0.89 |  | 0.64 |  | 0.64 |  | 0.88 |  | mg/l |  | 0.796
SULFIDE | [11 empty] | mg/l |  | #DIV/0!
LOWER MONITORING INTERVAL | [6 empty] | 1,970' - 2,027' |  |  |  |  | Ft. bls
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [9 empty] | 46.09 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [9 empty] | 37.45 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 69 |  | 69 |  | 69 |  | 69 |  | 69 |  | degrees (F) |  | 69
TDS |  | 29120 |  | 29485 |  | 28835 |  | 28835 |  |  |  | mg/l |  | 29068.75
CHLORIDE |  | 15400 |  | 16400 |  | 16600 |  | 16600 |  |  |  | mg/l |  | 16250
AMMONIA-N |  | 2.55 |  | 2.3 |  | 2.48 |  | 2.48 |  |  |  | mg/l |  | 2.4525
TKN |  | 2.95 |  | 2.5 |  | 2.94 |  | 2.94 |  |  |  | mg/l |  | 2.8325
pH |  | 7.33 |  | 7.39 |  | 7.37 |  | 7.37 |  |  |  | Std units |  | 7.365
CONDUCTIVITY |  | 43800 |  | 43500 |  | 43600 |  | 43600 |  |  |  | umho/cm |  | 43625
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.05 | < | 0.015 | < | 0.05 | < | 0.05 |  |  |  | mg/l |  | 0.04125
SULFATE |  | 2300 |  | 2300 |  | 2400 |  | 2400 |  |  |  | mg/l |  | 2350
C.O.D. 'S |  | 750 |  | 780 |  | 800 |  | 800 |  |  |  | mg/l |  | 782.5
IRON |  | 0.04 |  | 0.03 |  | 0.03 |  | 0.03 |  |  |  | mg/l |  | 0.0325
SULFIDE | [11 empty] | mg/l |  | #DIV/0!
PAGE 26
UNDERGROUND INJECTION CONTROL SECTION
MONTHLY OPERATING REPORT DATA SUMMARY
FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT MONTH/YEAR |  |  |  | SEPTEMBER |  | 2003
I.D. NUMBER: 5006M02066 | [5 empty] | LEAD OPERATOR: |  |  |  |  | MIKE JUST
TELEPHONE NUMBER: (954) 523-1002
REGIONAL MONITORING WELL DATA
RMW-1
PERMIT NUMBER | [6 empty] | UC06-249353
PERMIT EXPIRATION DATE |  | 1997-04-27
UPPER MONITORING INTERVAL | [6 empty] | 1300' - 1339' |  |  |  |  | Ft. bls.
Sample Date |  | 2003-09-02
Submittal Date |  | 2003-09-03
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [9 empty] | 44.9 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [9 empty] | 32.31 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 70 | [9 empty] | degrees (F) |  | 70
TDS |  | 5550 | [9 empty] | mg/l |  | 5550
CHLORIDE |  | 2750 | [9 empty] | mg/l |  | 2750
AMMONIA-N |  | 0.911 | [9 empty] | mg/l |  | 0.911
TKN |  | 1.1 | [9 empty] | mg/l |  | 1.1
pH |  | 8.35 | [9 empty] | Std units |  | 8.35
CONDUCTIVITY |  | 9100 | [9 empty] | umho/cm |  | 9100
FECAL COLIFORM |  | 0 | [9 empty] | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.05 | [9 empty] | mg/l |  | 0.05
SULFATE |  | 750 | [9 empty] | mg/l |  | 750
C.O.D. 'S |  | 160 | [9 empty] | mg/l |  | 160
IRON |  | 0.16 | [9 empty] | mg/l |  | 0.16
SULFIDE | [11 empty] | mg/l |  | #DIV/0!
LOWER MONITORING INTERVAL | [6 empty] | 1500' - 1600' |  |  |  |  | Ft. bls
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [9 empty] | 22.74 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [9 empty] | 20.31 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 68 | [9 empty] | degrees (F) |  | 68
TDS |  | 27092 | [9 empty] | mg/l |  | 27092
CHLORIDE |  | 15000 | [9 empty] | mg/l |  | 15000
AMMONIA-N |  | 0.524 | [9 empty] | mg/l |  | 0.524
TKN |  | 0.5 | [9 empty] | mg/l |  | 0.5
pH |  | 7.6 | [9 empty] | Std units |  | 7.6
CONDUCTIVITY |  | 4200 | [9 empty] | umho/cm |  | 4200
FECAL COLIFORM |  | 0 | [9 empty] | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.05 | [9 empty] | mg/l |  | 0.05
SULFATE |  | 1500 | [9 empty] | mg/l |  | 1500
C.O.D. 'S |  | 570 | [9 empty] | mg/l |  | 570
IRON |  | 0.07 | [9 empty] | mg/l |  | 0.07
SULFIDE | [11 empty] | mg/l |  | #DIV/0!
PAGE 27
Formulas:
LEAD OPERATOR: = [LEAD OPERATOR:, row above]+1

## WELL PRN DATA
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 1 |  |  | 244 | 245 | 246 | 247 | 248 | 249 | 250 | 251 | 252 | 253 | 254 | 255 | 256 | 257 | 258 | 259 | 260 | 261 | 262 | 263 | 264 | 265 | 266 | 267 | 268 | 269 | 270 | 271 | 272 | 273
244 | 12.98 | 5.55 | 9.47 | 60.85 | 41.85 | 50.75
245 | 12.57 | 6.3 | 9.9 | 59.29 | 43.47 | 51.89 |  |  | FLOW
246 | 13.53 | 6.01 | 9.68 | 66.5 | 43.79 | 51.93 | I |  | MAX | 12.98 | 12.57 | 13.53 | 15.18 | 15.27 | 13.5 | 13.71 | 13.25 | 12.84 | 13.99 | 11.88 | 14.73 | 12.64 | 12.65 | 13.12 | 13.79 | 12.16 | 16.73 | 13.42 | 11.55 | 12.71 | 12.07 | 12.48 | 13.42 | 13.69 | 12 | 15.78 | 14.76 | 14.58 | 17.79
247 | 15.18 | 4.03 | 10 | 69.93 | 41.21 | 52.65 | N |  | MIN | 5.55 | 6.3 | 6.01 | 4.03 | 4.45 | 6.58 | 6.79 | 6.63 | 6.51 | 6.29 | 6.29 | 5.88 | 6.35 | 5.96 | 5.75 | 6.54 | 6.15 | 0.01 | 5.39 | 5.76 | 5.68 | 5.17 | 4.96 | 4.67 | 5.16 | 4.74 | 5.68 | 8.69 | 8.87 | 9.38
248 | 15.27 | 4.45 | 10.46 | 68.76 | 43.64 | 53.63 | J |  | TOT | 9.47 | 9.9 | 9.68 | 10 | 10.46 | 10.93 | 10.77 | 10.71 | 10.31 | 10 | 9.76 | 10.01 | 9.75 | 9.67 | 9.8 | 9.66 | 9.65 | 9.63 | 9.66 | 9.11 | 9.04 | 9.18 | 9.02 | 8.93 | 9.32 | 9.5 | 10.28 | 12.09 | 12.17 | 13.13
249 | 13.5 | 6.58 | 10.93 | 61.95 | 44.51 | 55 | E | INJECTION WELL ONE
250 | 13.71 | 6.79 | 10.77 | 64.01 | 44.99 | 54.77 | C |  | PSI
251 | 13.25 | 6.63 | 10.71 | 65.98 | 44.78 | 54.74 | T |  | MAX | 60.85 | 59.29 | 66.5 | 69.93 | 68.76 | 61.95 | 64.01 | 65.98 | 61.74 | 64.41 | 58.01 | 67.76 | 59.07 | 59.7 | 61.25 | 63.69 | 58.68 | 74.6 | 62.88 | 55.96 | 59.79 | 57.69 | 59.53 | 62.59 | 63.82 | 57.92 | 72.3 | 68.17 | 68.08 | 81.4
252 | 12.84 | 6.51 | 10.31 | 61.74 | 44.17 | 53.06 | O |  | MIN | 41.85 | 43.47 | 43.79 | 41.21 | 43.64 | 44.51 | 44.99 | 44.78 | 44.17 | 43.27 | 43.38 | 42.69 | 43.52 | 42.76 | 42.49 | 43.95 | 42.9 | 36.82 | 41.78 | 42.43 | 42.13 | 41.16 | 41.06 | 40.27 | 41.21 | 40.42 | 41.74 | 49.22 | 48.94 | 50.12
253 | 13.99 | 6.29 | 10 | 64.41 | 43.27 | 52.46 | N |  | AVG | 50.75 | 51.89 | 51.93 | 52.65 | 53.63 | 55 | 54.77 | 54.74 | 53.06 | 52.46 | 51.93 | 52.33 | 51.4 | 51.27 | 51.62 | 51.44 | 51.51 | 51.65 | 51.53 | 49.76 | 49.7 | 50.13 | 49.67 | 49.65 | 50.58 | 51.04 | 53.36 | 58.95 | 58.81 | 62.28
254 | 11.88 | 6.29 | 9.76 | 58.01 | 43.38 | 51.93
255 | 14.73 | 5.88 | 10.01 | 67.76 | 42.69 | 52.33 | W
256 | 12.64 | 6.35 | 9.75 | 59.07 | 43.52 | 51.4 | E
257 | 12.65 | 5.96 | 9.67 | 59.7 | 42.76 | 51.27 | L
258 | 13.12 | 5.75 | 9.8 | 61.25 | 42.49 | 51.62 | L
259 | 13.79 | 6.54 | 9.66 | 63.69 | 43.95 | 51.44 | O
260 | 12.16 | 6.15 | 9.65 | 58.68 | 42.9 | 51.51 | N
261 | 16.73 | 0.01 | 9.63 | 74.6 | 36.82 | 51.65 | E
262 | 13.42 | 5.39 | 9.66 | 62.88 | 41.78 | 51.53
263 | 11.55 | 5.76 | 9.11 | 55.96 | 42.43 | 49.76 | D
264 | 12.71 | 5.68 | 9.04 | 59.79 | 42.13 | 49.7 | A
265 | 12.07 | 5.17 | 9.18 | 57.69 | 41.16 | 50.13 | T
266 | 12.48 | 4.96 | 9.02 | 59.53 | 41.06 | 49.67 | A
267 | 13.42 | 4.67 | 8.93 | 62.59 | 40.27 | 49.65
268 | 13.69 | 5.16 | 9.32 | 63.82 | 41.21 | 50.58
269 | 12 | 4.74 | 9.5 | 57.92 | 40.42 | 51.04
270 | 15.78 | 5.68 | 10.28 | 72.3 | 41.74 | 53.36
271 | 14.76 | 8.69 | 12.09 | 68.17 | 49.22 | 58.95
272 | 14.58 | 8.87 | 12.17 | 68.08 | 48.94 | 58.81
273 | 17.79 | 9.38 | 13.13 | 81.4 | 50.12 | 62.28
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 2 |  |  | 244 | 245 | 246 | 247 | 248 | 249 | 250 | 251 | 252 | 253 | 254 | 255 | 256 | 257 | 258 | 259 | 260 | 261 | 262 | 263 | 264 | 265 | 266 | 267 | 268 | 269 | 270 | 271 | 272 | 273
244 | 13.09 | 5.47 | 9.61 | 59.68 | 41.09 | 49.82
245 | 12.71 | 6.25 | 10.09 | 58.15 | 42.66 | 50.92 |  |  | FLOW
246 | 13.63 | 6.01 | 9.84 | 65.29 | 43 | 51.01 | I |  | MAX | 13.09 | 12.71 | 13.63 | 15.45 | 14.68 | 13.58 | 14.02 | 13.46 | 12.97 | 13.4 | 12.49 | 15.54 | 13.25 | 13.33 | 13.77 | 14.47 | 12.76 | 17.54 | 14.07 | 12.13 | 13.35 | 12.57 | 13.16 | 14.08 | 14.36 | 12.7 | 16.56 | 15.46 | 15.38 | 18.57
247 | 15.45 | 3.83 | 10.15 | 68.62 | 40.44 | 51.66 | N |  | MIN | 5.47 | 6.25 | 6.01 | 3.83 | 0.14 | 6.73 | 6.79 | 6.63 | 6.53 | ER | 6.75 | ER | 6.74 | 6.29 | 6.14 | 6.98 | 6.54 | 0.13 | 5.79 | 6.08 | 6 | 5.44 | 5.11 | 4.87 | 5.34 | 4.9 | 6.15 | 9.34 | 9.42 | 9.97
248 | 14.68 | 0.14 | 10.59 | 64.63 | 38.42 | 52.57 | J |  | TOT | 9.61 | 10.09 | 9.84 | 10.15 | 10.59 | 11.13 | 10.95 | 10.89 | 10.48 | ER | 10.31 | 10.25 | 10.32 | 10.25 | 10.34 | 10.23 | 10.15 | 10.04 | 10.23 | 9.67 | 9.63 | 9.75 | 9.58 | 9.47 | 9.88 | 10.08 | 10.9 | 12.73 | 12.78 | 13.75
249 | 13.58 | 6.73 | 11.13 | 60.78 | 43.68 | 53.98 | E | INJECTION WELL TWO
250 | 14.02 | 6.79 | 10.95 | 62.86 | 44.16 | 53.79 | C |  | PSI
251 | 13.46 | 6.63 | 10.89 | 64.77 | 43.96 | 53.74 | T |  | MAX | 59.68 | 58.15 | 65.29 | 68.62 | 64.63 | 60.78 | 62.86 | 64.77 | 60.57 | 62.01 | 56.91 | 66.46 | 57.98 | 73.1 | 60.11 | 62.45 | 57.53 | 73.1 | 61.68 | 54.96 | 58.69 | 56.6 | 58.41 | 61.42 | 62.59 | 56.81 | 70.9 | 66.93 | 66.83 | 79.8
252 | 12.97 | 6.53 | 10.48 | 60.57 | 43.36 | 52.09 | I |  | MIN | 41.09 | 42.66 | 43 | 40.44 | 38.42 | 43.68 | 44.16 | 43.96 | 43.36 | 37.73 | 42.57 | 41.88 | 42.7 | 41.96 | 41.71 | 43.11 | 42.09 | 37.53 | 41.02 | 41.65 | 41.37 | 40.42 | 40.3 | 39.52 | 40.44 | 39.67 | 40.94 | 48.28 | 48.01 | 49.18
253 | 13.4 | ER | ER | 62.01 | 37.73 | 51.27 | O |  | AVG | 49.82 | 50.92 | 51.01 | 51.66 | 52.57 | 53.98 | 53.79 | 53.74 | 52.09 | 51.27 | 50.97 | 51.34 | 50.44 | 50.29 | 50.63 | 50.47 | 50.53 | 50.46 | 50.58 | 48.83 | 48.78 | 49.2 | 48.74 | 48.73 | 49.62 | 50.07 | 52.35 | 57.86 | 57.72 | 61.08
254 | 12.49 | 6.75 | 10.31 | 56.91 | 42.57 | 50.97 | N
255 | 15.54 | ER | 10.25 | 66.46 | 41.88 | 51.34
256 | 13.25 | 6.74 | 10.32 | 57.98 | 42.7 | 50.44 | W
257 | 13.33 | 6.29 | 10.25 | 58.57 | 41.96 | 50.29 | E
258 | 13.77 | 6.14 | 10.34 | 60.11 | 41.71 | 50.63 | L
259 | 14.47 | 6.98 | 10.23 | 62.45 | 43.11 | 50.47 | L
260 | 12.76 | 6.54 | 10.15 | 57.53 | 42.09 | 50.53
261 | 17.54 | 0.13 | 10.04 | 73.1 | 37.53 | 50.46 | T
262 | 14.07 | 5.79 | 10.23 | 61.68 | 41.02 | 50.58 | W
263 | 12.13 | 6.08 | 9.67 | 54.96 | 41.65 | 48.83 | O
264 | 13.35 | 6 | 9.63 | 58.69 | 41.37 | 48.78
265 | 12.57 | 5.44 | 9.75 | 56.6 | 40.42 | 49.2 | D
266 | 13.16 | 5.11 | 9.58 | 58.41 | 40.3 | 48.74 | A
267 | 14.08 | 4.87 | 9.47 | 61.42 | 39.52 | 48.73 | T
268 | 14.36 | 5.34 | 9.88 | 62.59 | 40.44 | 49.62 | A
269 | 12.7 | 4.9 | 10.08 | 56.81 | 39.67 | 50.07
270 | 16.56 | 6.15 | 10.9 | 70.9 | 40.94 | 52.35
271 | 15.46 | 9.34 | 12.73 | 66.93 | 48.28 | 57.86
272 | 15.38 | 9.42 | 12.78 | 66.83 | 48.01 | 57.72
273 | 18.57 | 9.97 | 13.75 | 79.8 | 49.18 | 61.08
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 3 |  |  | 244 | 245 | 246 | 247 | 248 | 249 | 250 | 251 | 252 | 253 | 254 | 255 | 256 | 257 | 258 | 259 | 260 | 261 | 262 | 263 | 264 | 265 | 266 | 267 | 268 | 269 | 270 | 271 | 272 | 273
244 | 11.48 | 4.77 | 8.44 | 61.17 | 41.96 | 51
245 | 11.19 | 5.48 | 8.84 | 59.67 | 43.63 | 52.12 |  |  | FLOW
246 | 11.95 | 5.33 | 8.63 | 66.9 | 43.95 | 52.17 | I |  | MAX | 11.48 | 11.19 | 11.95 | 13.7 | 13.59 | 11.99 | 12.34 | 11.88 | 11.42 | 12.51 | 10.69 | 13.35 | 11.3 | 11.35 | 11.79 | 12.36 | 10.83 | 14.73 | 12.08 | 10.34 | 11.31 | 10.69 | 11.19 | 12.04 | 12.24 | 10.77 | 14.16 | 13.28 | 13.16 | 15.96
247 | 13.7 | 3.37 | 8.96 | 70.3 | 41.33 | 52.87 | N |  | MIN | 4.77 | 5.48 | 5.33 | 3.37 | 2.78 | 5.82 | 6.02 | 5.88 | 5.76 | 5.56 | 5.54 | 5.13 | 5.57 | 5.18 | 5.02 | 5.79 | 5.37 | ER | 4.68 | 5.03 | 4.9 | 4.39 | 4.21 | 3.9 | 4.34 | 3.96 | 4.95 | 7.89 | 7.99 | 8.45
248 | 13.59 | 2.78 | 9.41 | 69.08 | 43.09 | 54.01 | J |  | TOT | 8.44 | 8.84 | 8.63 | 8.96 | 9.41 | 9.8 | 9.65 | 9.6 | 9.23 | 8.96 | 8.74 | 8.97 | 8.72 | 8.64 | 8.75 | 8.62 | 8.6 | 8.62 | 8.64 | 8.15 | 8.07 | 8.19 | 8.04 | 7.96 | 8.33 | 8.49 | 9.22 | 10.89 | 10.92 | 11.75
249 | 11.99 | 5.82 | 9.8 | 62.31 | 44.67 | 55.28 | E | INJECTION WELL THREE
250 | 12.34 | 6.02 | 9.65 | 64.45 | 45.16 | 55.07 | C |  | PSI
251 | 11.88 | 5.88 | 9.6 | 66.34 | 44.96 | 54.99 | T |  | MAX | 61.17 | 59.67 | 66.9 | 70.3 | 69.08 | 62.31 | 64.45 | 66.34 | 62.15 | 64.69 | 58.34 | 68.21 | 59.45 | 59.98 | 61.62 | 64.09 | 58.96 | 73.6 | 63.2 | 56.26 | 60.15 | 57.97 | 59.85 | 62.98 | 64.16 | 58.22 | 72.7 | 68.56 | 68.49 | 81.9
252 | 11.42 | 5.76 | 9.23 | 62.15 | 44.33 | 53.35 | I |  | MIN | 41.96 | 43.63 | 43.95 | 41.33 | 43.09 | 44.67 | 45.16 | 44.96 | 44.33 | 43.41 | 43.51 | 42.81 | 43.65 | 42.88 | 42.61 | 44.1 | 43.05 | 36.76 | 41.91 | 42.56 | 42.27 | 41.29 | 41.18 | 40.38 | 41.31 | 40.53 | 41.88 | 49.42 | 49.13 | 50.33
253 | 12.51 | 5.56 | 8.96 | 64.69 | 43.41 | 52.7 | O |  | AVG | 51 | 52.12 | 52.17 | 52.87 | 54.01 | 55.28 | 55.07 | 54.99 | 53.35 | 52.7 | 52.15 | 52.57 | 51.61 | 51.46 | 51.87 | 51.65 | 51.74 | 51.85 | 51.73 | 49.94 | 49.92 | 50.34 | 49.88 | 49.87 | 50.78 | 51.23 | 53.58 | 59.27 | 59.13 | 62.59
254 | 10.69 | 5.54 | 8.74 | 58.34 | 43.51 | 52.15 | N
255 | 13.35 | 5.13 | 8.97 | 68.21 | 42.81 | 52.57
256 | 11.3 | 5.57 | 8.72 | 59.45 | 43.65 | 51.61 | W
257 | 11.35 | 5.18 | 8.64 | 59.98 | 42.88 | 51.46 | E
258 | 11.79 | 5.02 | 8.75 | 61.62 | 42.61 | 51.87 | L
259 | 12.36 | 5.79 | 8.62 | 64.09 | 44.1 | 51.65 | L
260 | 10.83 | 5.37 | 8.6 | 58.96 | 43.05 | 51.74
261 | 14.73 | ER | 8.62 | 73.6 | 36.76 | 51.85 | T
262 | 12.08 | 4.68 | 8.64 | 63.2 | 41.91 | 51.73 | H
263 | 10.34 | 5.03 | 8.15 | 56.26 | 42.56 | 49.94 | R
264 | 11.31 | 4.9 | 8.07 | 60.15 | 42.27 | 49.92 | E
265 | 10.69 | 4.39 | 8.19 | 57.97 | 41.29 | 50.34 | E
266 | 11.19 | 4.21 | 8.04 | 59.85 | 41.18 | 49.88
267 | 12.04 | 3.9 | 7.96 | 62.98 | 40.38 | 49.87 | D
268 | 12.24 | 4.34 | 8.33 | 64.16 | 41.31 | 50.78 | A
269 | 10.77 | 3.96 | 8.49 | 58.22 | 40.53 | 51.23 | T
270 | 14.16 | 4.95 | 9.22 | 72.7 | 41.88 | 53.58 | A
271 | 13.28 | 7.89 | 10.89 | 68.56 | 49.42 | 59.27
272 | 13.16 | 7.99 | 10.92 | 68.49 | 49.13 | 59.13
273 | 15.96 | 8.45 | 11.75 | 81.9 | 50.33 | 62.59
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 4 |  |  | 244 | 245 | 246 | 247 | 248 | 249 | 250 | 251 | 252 | 253 | 254 | 255 | 256 | 257 | 258 | 259 | 260 | 261 | 262 | 263 | 264 | 265 | 266 | 267 | 268 | 269 | 270 | 271 | 272 | 273
244 | ER | ER | ER | 38.55 | 36.63 | 37.64
245 | ER | ER | ER | 38.35 | 36.83 | 37.74 |  |  | FLOW
246 | ER | ER | ER | 39.01 | 36.99 | 37.83 | I |  | MAX | ER | ER | ER | ER | ER | ER | ER | ER | ER | 11.86 | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER
247 | ER | ER | ER | 39.16 | 36.66 | 37.92 | N |  | MIN | bar: 244 to 273
248 | ER | ER | ER | 38.89 | 37.13 | 38.01 | J |  | TOT | bar: 244 to 273
249 | ER | ER | ER | 38.77 | 37.32 | 38.18 | E | INJECTION WELL FOUR
250 | ER | ER | ER | 38.95 | 37.39 | 38.17 | C |  | PSI
251 | ER | ER | ER | 38.7 | 37.14 | 38.04 | T |  | MAX | 38.55 | 38.35 | 39.01 | 39.16 | 38.89 | 38.77 | 38.95 | 38.7 | 38.59 | 38.61 | 38.15 | 38.78 | 38.15 | 64.41 | 38.2 | 38.08 | 37.78 | 38.41 | 37.87 | 37.36 | 37.57 | 37.54 | 37.72 | 38.11 | 38.16 | 37.75 | 38.89 | 38.71 | 38.61 | 39.81
252 | ER | ER | ER | 38.59 | 36.95 | 37.8 | I |  | MIN | 36.63 | 36.83 | 36.99 | 36.66 | 37.13 | 37.32 | 37.39 | 37.14 | 36.95 | 36.75 | 36.69 | 36.48 | 36.51 | 36.33 | 36.26 | 36.34 | 36.21 | 35.95 | 36.21 | 36.1 | 36.01 | 35.95 | 35.99 | 35.91 | 35.93 | 35.75 | 35.99 | 36.73 | 36.74 | 36.92
253 | 11.86 | ER | ER | 38.61 | 36.75 | 37.66 | O |  | AVG | 37.64 | 37.74 | 37.83 | 37.92 | 38.01 | 38.18 | 38.17 | 38.04 | 37.8 | 37.66 | 37.54 | 37.5 | 37.38 | 37.27 | 37.25 | 37.2 | 37.16 | 37.11 | 37.07 | 36.84 | 36.78 | 36.88 | 36.9 | 36.92 | 36.97 | 37.02 | 37.24 | 37.8 | 37.77 | 38.04
254 | ER | ER | ER | 38.15 | 36.69 | 37.54 | N
255 | ER | ER | ER | 38.78 | 36.48 | 37.5
256 | ER | ER | ER | 38.15 | 36.51 | 37.38 | W
257 | ER | ER | ER | 38.1 | 36.33 | 37.27 | E
258 | ER | ER | ER | 38.2 | 36.26 | 37.25 | L
259 | ER | ER | ER | 38.08 | 36.34 | 37.2 | L
260 | ER | ER | ER | 37.78 | 36.21 | 37.16
261 | ER | ER | ER | 38.41 | 35.95 | 37.11 | F
262 | ER | ER | ER | 37.87 | 36.21 | 37.07 | O
263 | ER | ER | ER | 37.36 | 36.1 | 36.84 | U
264 | ER | ER | ER | 37.57 | 36.01 | 36.78 | R
265 | ER | ER | ER | 37.54 | 35.95 | 36.88
266 | ER | ER | ER | 37.72 | 35.99 | 36.9 | D
267 | ER | ER | ER | 38.11 | 35.91 | 36.92 | A
268 | ER | ER | ER | 38.16 | 35.93 | 36.97 | T
269 | ER | ER | ER | 37.75 | 35.75 | 37.02 | A
270 | ER | ER | ER | 38.89 | 35.99 | 37.24
271 | ER | ER | ER | 38.71 | 36.73 | 37.8
272 | ER | ER | ER | 38.61 | 36.74 | 37.77
273 | ER | ER | ER | 39.81 | 36.92 | 38.04
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 5 |  |  | 244 | 245 | 246 | 247 | 248 | 249 | 250 | 251 | 252 | 253 | 254 | 255 | 256 | 257 | 258 | 259 | 260 | 261 | 262 | 263 | 264 | 265 | 266 | 267 | 268 | 269 | 270 | 271 | 272 | 273
244 | 11.41 | 5.11 | 8.51 | 61.18 | 32.51 | 48.37
245 | 11.04 | 5.8 | 8.89 | 59.06 | 30.87 | 49.73 |  |  | FLOW
246 | 11.92 | 5.58 | 8.68 | 57.9 | 33.53 | 49.12 | I |  | MAX | 11.41 | 11.04 | 11.92 | 13.4 | 13.15 | 11.71 | 12.05 | 11.62 | 11.24 | 12.18 | 10.54 | 13.03 | 11.1 | 11.18 | 11.58 | 12.14 | 10.74 | 14.73 | 11.93 | 10.25 | 11.22 | 10.57 | 11.08 | 11.84 | 12.11 | 10.67 | 13.94 | 13.02 | 12.93 | 15.58
247 | 13.4 | 3.53 | 8.94 | 64.46 | 29.29 | 50.11 | N |  | MIN | 5.11 | 5.8 | 5.58 | 3.53 | ER | 6.16 | 6.26 | 6.11 | 6 | 5.87 | 5.89 | 5.41 | 5.83 | 5.47 | 5.32 | 6.01 | 5.67 | ER | 5.13 | 5.3 | 5.23 | 4.81 | 4.55 | 4.32 | 4.7 | 2.79 | 5.29 | 7.9 | 8 | 8.41
248 | 13.15 | ER | 9.16 | 61.28 | 29.41 | 51.18 | J |  | TOT | 8.51 | 8.89 | 8.68 | 8.94 | 9.16 | 9.71 | 9.57 | 9.51 | 9.2 | 8.97 | 8.77 | 8.95 | 8.73 | 8.66 | 8.77 | 8.65 | 8.64 | 8.63 | 8.7 | 8.21 | 8.16 | 8.26 | 8.13 | 8.05 | 8.38 | 8.53 | 9.19 | 10.71 | 10.75 | 11.55
249 | 11.71 | 6.16 | 9.71 | 60.57 | 31.57 | 52.73 | E | INJECTION WELL FIVE
250 | 12.05 | 6.26 | 9.57 | 61.25 | 25.37 | 52.54 | C |  | PSI
251 | 11.62 | 6.11 | 9.51 | 68.87 | 35.17 | 51.66 | T |  | MAX | 61.18 | 59.06 | 57.9 | 64.46 | 61.28 | 60.57 | 61.25 | 68.87 | 59.76 | 60.21 | 58.23 | 62 | 60.43 | 61.55 | 61.05 | 59.03 | 60.95 | 73.1 | 58.18 | 56.71 | 58.49 | 57.88 | 58.35 | 61.57 | 59.64 | 61.12 | 65.68 | 68.26 | 65.49 | 81.2
252 | 11.24 | 6 | 9.2 | 59.76 | 36.08 | 50.71 | I |  | MIN | 32.51 | 30.87 | 33.53 | 29.29 | 29.41 | 31.57 | 25.37 | 35.17 | 36.08 | 38.82 | 39.77 | 32.36 | 28.64 | 31.93 | 38.64 | 33.86 | 36.69 | 36.61 | 29.05 | 25.54 | 37.2 | 34.8 | 26.85 | 20.75 | 23.63 | 28.6 | 23.01 | 44.96 | 40.55 | 33.63
253 | 12.18 | 5.87 | 8.97 | 60.21 | 38.82 | 50.01 | O |  | AVG | 48.37 | 49.73 | 49.12 | 50.11 | 51.18 | 52.73 | 52.54 | 51.66 | 50.71 | 50.01 | 49.13 | 50.01 | 48.99 | 48.77 | 49.19 | 48.27 | 48.59 | 48.67 | 48.31 | 47.27 | 47.31 | 47.24 | 47.16 | 47.11 | 47.85 | 48.09 | 49.83 | 55.18 | 56.51 | 60.77
254 | 10.54 | 5.89 | 8.77 | 58.23 | 39.77 | 49.13 | N
255 | 13.03 | 5.41 | 8.95 | 62 | 32.36 | 50.01
256 | 11.1 | 5.83 | 8.73 | 60.43 | 28.64 | 48.99 | W
257 | 11.18 | 5.47 | 8.66 | 61.55 | 31.93 | 48.77 | E
258 | 11.58 | 5.32 | 8.77 | 61.05 | 38.64 | 49.19 | L
259 | 12.14 | 6.01 | 8.65 | 59.03 | 33.86 | 48.27 | L
260 | 10.74 | 5.67 | 8.64 | 60.95 | 36.69 | 48.59
261 | 14.73 | ER | 8.63 | 73.1 | 36.61 | 48.67 | F
262 | 11.93 | 5.13 | 8.7 | 58.18 | 29.05 | 48.31 | I
263 | 10.25 | 5.3 | 8.21 | 56.71 | 25.54 | 47.27 | V
264 | 11.22 | 5.23 | 8.16 | 58.49 | 37.2 | 47.31 | E
265 | 10.57 | 4.81 | 8.26 | 57.88 | 34.8 | 47.24
266 | 11.08 | 4.55 | 8.13 | 58.35 | 26.85 | 47.16 | D
267 | 11.84 | 4.32 | 8.05 | 61.57 | 20.75 | 47.11 | A
268 | 12.11 | 4.7 | 8.38 | 59.64 | 23.63 | 47.85 | T
269 | 10.67 | 2.79 | 8.53 | 61.12 | 28.6 | 48.09 | A
270 | 13.94 | 5.29 | 9.19 | 65.68 | 23.01 | 49.83
271 | 13.02 | 7.9 | 10.71 | 68.26 | 44.96 | 55.18
272 | 12.93 | 8 | 10.75 | 65.49 | 40.55 | 56.51
273 | 15.58 | 8.41 | 11.55 | 81.2 | 33.63 | 60.77

## RMW PRN DATA
julian | u-avg | u-min | u-max | l-avg | l-min | l-max
244 | 21.13 | 20.31 | 22.37 | 36.23 | 33.1 | 44.32 | R |  |  | 244 | 245 | 246 | 247 | 248 | 249 | 250 | 251 | 252 | 253 | 254 | 255 | 256 | 257 | 258 | 259 | 260 | 261 | 262 | 263 | 264 | 265 | 266 | 267 | 268 | 269 | 270 | 271 | 272 | 273
245 | 21.21 | 20.38 | 21.65 | 40.45 | 32.31 | 43.59 | E
246 | 21.79 | 21.65 | 21.93 | 43.71 | 43.57 | 43.84 | G |  | LOW
247 | 22.02 | 21.89 | 22.13 | 43.91 | 43.82 | 44.02 | I |  | MIN | 20.31 | 20.38 | 21.65 | 21.89 | 22.09 | 22.21 | 22.29 | 22.38 | 22.4 | 22.45 | 22.5 | 22.5 | 22.52 | 22.5 | 22.54 | 22.59 | 22.62 | 22.57 | 22.46 | 22.38 | 22.33 | 22.34 | 22.39 | 22.39 | 22.33 | 22.47 | 22.49 | 22.48 | 22.45 | 22.41
248 | 22.19 | 22.09 | 22.31 | 44.08 | 44 | 44.19 | O |  | MAX | 22.37 | 21.65 | 21.93 | 22.13 | 22.31 | 22.38 | 22.43 | 22.5 | 22.49 | 22.52 | 22.6 | 22.6 | 22.58 | 22.6 | 22.67 | 22.72 | 22.74 | 22.71 | 22.61 | 22.54 | 22.48 | 22.51 | 22.5 | 22.5 | 22.52 | 22.55 | 22.56 | 22.59 | 22.55 | 22.55
249 | 22.3 | 22.21 | 22.38 | 44.23 | 44.16 | 44.29 | N |  | AVG | 21.13 | 21.21 | 21.79 | 22.02 | 22.19 | 22.3 | 22.36 | 22.43 | 22.45 | 22.48 | 22.55 | 22.57 | 22.55 | 22.55 | 22.6 | 22.66 | 22.68 | 22.64 | 22.53 | 22.46 | 22.42 | 22.42 | 22.45 | 22.46 | 22.46 | 22.52 | 22.52 | 22.54 | 22.5 | 22.48
250 | 22.36 | 22.29 | 22.43 | 44.31 | 44.24 | 44.39 | A | RMW
251 | 22.43 | 22.38 | 22.5 | 44.4 | 44.33 | 44.48 | L |  | UP
252 | 22.45 | 22.4 | 22.49 | 44.46 | 44.38 | 44.52 |  |  | MIN | 33.1 | 32.31 | 43.57 | 43.82 | 44 | 44.16 | 44.24 | 44.33 | 44.38 | 44.46 | 44.54 | 44.64 | 44.64 | 44.65 | 44.71 | 44.78 | 44.82 | 44.77 | 44.63 | 44.54 | 44.46 | 44.43 | 44.43 | 44.39 | 44.39 | 44.44 | 44.45 | 44.43 | 44.39 | 44.36
253 | 22.48 | 22.45 | 22.52 | 44.53 | 44.46 | 44.62 | M |  | MAX | 44.32 | 43.59 | 43.84 | 44.02 | 44.19 | 44.29 | 44.39 | 44.48 | 44.52 | 44.62 | 44.7 | 44.73 | 44.73 | 44.75 | 44.83 | 44.88 | 44.9 | 44.88 | 44.79 | 44.7 | 44.59 | 44.55 | 44.52 | 44.52 | 44.56 | 44.58 | 44.55 | 44.56 | 44.5 | 44.43
254 | 22.55 | 22.5 | 22.6 | 44.63 | 44.54 | 44.7 | O |  | AVG | 36.23 | 40.45 | 43.71 | 43.91 | 44.08 | 44.23 | 44.31 | 44.4 | 44.46 | 44.53 | 44.63 | 44.68 | 44.69 | 44.71 | 44.78 | 44.83 | 44.86 | 44.83 | 44.71 | 44.61 | 44.52 | 44.49 | 44.47 | 44.46 | 44.46 | 44.51 | 44.51 | 44.5 | 44.44 | 44.4
255 | 22.57 | 22.5 | 22.6 | 44.68 | 44.64 | 44.73 | N
256 | 22.55 | 22.52 | 22.58 | 44.69 | 44.64 | 44.73 | I
257 | 22.55 | 22.5 | 22.6 | 44.71 | 44.65 | 44.75 | T
258 | 22.6 | 22.54 | 22.67 | 44.78 | 44.71 | 44.83 | O
259 | 22.66 | 22.59 | 22.72 | 44.83 | 44.78 | 44.88 | R
260 | 22.68 | 22.62 | 22.74 | 44.86 | 44.82 | 44.9
261 | 22.64 | 22.57 | 22.71 | 44.83 | 44.77 | 44.88 | W
262 | 22.53 | 22.46 | 22.61 | 44.71 | 44.63 | 44.79 | E
263 | 22.46 | 22.38 | 22.54 | 44.61 | 44.54 | 44.7 | L
264 | 22.42 | 22.33 | 22.48 | 44.52 | 44.46 | 44.59 | L
265 | 22.42 | 22.34 | 22.51 | 44.49 | 44.43 | 44.55
266 | 22.45 | 22.39 | 22.5 | 44.47 | 44.43 | 44.52
267 | 22.46 | 22.39 | 22.5 | 44.46 | 44.39 | 44.52 | R
268 | 22.46 | 22.33 | 22.52 | 44.46 | 44.39 | 44.56 | M
269 | 22.52 | 22.47 | 22.55 | 44.51 | 44.44 | 44.58 | W
270 | 22.52 | 22.49 | 22.56 | 44.51 | 44.45 | 44.55
271 | 22.54 | 22.48 | 22.59 | 44.5 | 44.43 | 44.56 | O
272 | 22.5 | 22.45 | 22.55 | 44.44 | 44.39 | 44.5 | N
273 | 22.48 | 22.41 | 22.55 | 44.4 | 44.36 | 44.43 | E
244 | 32.82 | 28.92 | 42.01 | 47.02 | 45.79 | 48.76 | M |  |  | 244 | 245 | 246 | 247 | 248 | 249 | 250 | 251 | 252 | 253 | 254 | 255 | 256 | 257 | 258 | 259 | 260 | 261 | 262 | 263 | 264 | 265 | 266 | 267 | 268 | 269 | 270 | 271 | 272 | 273
245 | 38.2 | 28.96 | 41.92 | 47.91 | 46.3 | 48.6 | O
246 | 41.97 | 41.84 | 42.22 | 48.52 | 48.4 | 48.74 | N |  | LOW
247 | 42.11 | 41.99 | 42.3 | 48.69 | 48.51 | 48.89 | I |  | MIN | 28.92 | 28.96 | 41.84 | 41.99 | 42.12 | 42.22 | 42.13 | 30.7 | 30.76 | 42.18 | 42.37 | 42.47 | 42.54 | 42.52 | 37.79 | 37.71 | 42.5 | 42.56 | 42.53 | 42.43 | 42.47 | 28.11 | 28.13 | 41.85 | 41.82 | 42 | 42.01 | 42.2 | 37.98 | 37.81
248 | 42.33 | 42.12 | 42.39 | 48.84 | 48.6 | 48.97 | T |  | MAX | 42.01 | 41.92 | 42.22 | 42.3 | 42.39 | 42.5 | 42.47 | 42.39 | 42.22 | 42.42 | 42.56 | 42.66 | 42.68 | 42.71 | 42.71 | 42.55 | 42.77 | 42.75 | 42.69 | 42.63 | 42.63 | 42.56 | 42.05 | 42.19 | 42.14 | 42.24 | 42.35 | 42.45 | 42.24 | 42.27
249 | 42.39 | 42.22 | 42.5 | 48.88 | 48.64 | 49.02 | O |  | AVG | 32.82 | 38.2 | 41.97 | 42.11 | 42.33 | 42.39 | 42.42 | 34.07 | 38.76 | 42.36 | 42.47 | 42.52 | 42.56 | 42.58 | 39.69 | 41.19 | 42.54 | 42.59 | 42.55 | 42.53 | 42.52 | 32.31 | 37.99 | 42.03 | 42 | 42.07 | 42.2 | 42.35 | 39.21 | 40.83
250 | 42.42 | 42.13 | 42.47 | 48.9 | 48.71 | 49.08 | R | MW-1
251 | 34.07 | 30.7 | 42.39 | 48.09 | 47.44 | 49 |  |  | UP
252 | 38.76 | 30.76 | 42.22 | 48.37 | 47.78 | 48.77 | W |  | MIN | 45.79 | 46.3 | 48.4 | 48.51 | 48.6 | 48.64 | 48.71 | 47.44 | 47.78 | 48.52 | 48.61 | 48.7 | 48.68 | 48.64 | 47.61 | 47.87 | 48.72 | 48.71 | 48.63 | 48.55 | 48.51 | 45.35 | 45.79 | 48.55 | 48.61 | 48.63 | 48.68 | 48.72 | 46.97 | 47.3
253 | 42.36 | 42.18 | 42.42 | 48.7 | 48.52 | 48.87 | E |  | MAX | 48.76 | 48.6 | 48.74 | 48.89 | 48.97 | 49.02 | 49.08 | 49 | 48.77 | 48.87 | 48.96 | 48.93 | 48.89 | 48.91 | 48.91 | 48.88 | 48.94 | 48.94 | 48.87 | 48.84 | 48.83 | 48.78 | 49.08 | 48.92 | 48.94 | 48.99 | 49.02 | 49.03 | 48.97 | 48.93
254 | 42.47 | 42.37 | 42.56 | 48.76 | 48.61 | 48.96 | L |  | AVG | 47.02 | 47.91 | 48.52 | 48.69 | 48.84 | 48.88 | 48.9 | 48.09 | 48.37 | 48.7 | 48.76 | 48.86 | 48.81 | 48.81 | 48.2 | 48.66 | 48.9 | 48.91 | 48.79 | 48.69 | 48.67 | 46.63 | 47.9 | 48.73 | 48.77 | 48.85 | 48.92 | 48.93 | 47.79 | 48.4
255 | 42.52 | 42.47 | 42.66 | 48.86 | 48.7 | 48.93 | L
256 | 42.56 | 42.54 | 42.68 | 48.81 | 48.68 | 48.89
257 | 42.58 | 42.52 | 42.71 | 48.81 | 48.64 | 48.91 | O
258 | 39.69 | 37.79 | 42.71 | 48.2 | 47.61 | 48.91 | N
259 | 41.19 | 37.71 | 42.55 | 48.66 | 47.87 | 48.88 | E
260 | 42.54 | 42.5 | 42.77 | 48.9 | 48.72 | 48.94
261 | 42.59 | 42.56 | 42.75 | 48.91 | 48.71 | 48.94 | I
262 | 42.55 | 42.53 | 42.69 | 48.79 | 48.63 | 48.87 | N
263 | 42.53 | 42.43 | 42.63 | 48.69 | 48.55 | 48.84 | J
264 | 42.52 | 42.47 | 42.63 | 48.67 | 48.51 | 48.83 | E
265 | 32.31 | 28.11 | 42.56 | 46.63 | 45.35 | 48.78 | C
266 | 37.99 | 28.13 | 42.05 | 47.9 | 45.79 | 49.08 | T
267 | 42.03 | 41.85 | 42.19 | 48.73 | 48.55 | 48.92 | I
268 | 42 | 41.82 | 42.14 | 48.77 | 48.61 | 48.94 | O
269 | 42.07 | 42 | 42.24 | 48.85 | 48.63 | 48.99 | N
270 | 42.2 | 42.01 | 42.35 | 48.92 | 48.68 | 49.02
271 | 42.35 | 42.2 | 42.45 | 48.93 | 48.72 | 49.03 | W
272 | 39.21 | 37.98 | 42.24 | 47.79 | 46.97 | 48.97 | E
273 | 40.83 | 37.81 | 42.27 | 48.4 | 47.3 | 48.93 | L
L
244 | 34.19 | 30.56 | 42.53 | ER | ER | ER | M |  |  | 244 | 245 | 246 | 247 | 248 | 249 | 250 | 251 | 252 | 253 | 254 | 255 | 256 | 257 | 258 | 259 | 260 | 261 | 262 | 263 | 264 | 265 | 266 | 267 | 268 | 269 | 270 | 271 | 272 | 273
245 | 38.75 | 30.48 | 42.12 | ER | ER | ER | O
246 | 42.29 | 42.09 | 42.33 | ER | ER | ER | N |  | LOW
247 | 42.4 | 42.28 | 42.52 | ER | ER | ER | I |  | MIN | 30.56 | 30.48 | 42.09 | 42.28 | 42.42 | 42.5 | 42.6 | 30.23 | 30.23 | 42.32 | 42.54 | 42.71 | 42.77 | 42.79 | 38.77 | 38 | 42.67 | 42.74 | 42.73 | 42.7 | 42.68 | 30.51 | 30.08 | 30.48 | 30.48 | 30.58 | 30.65 | 30.64 | 30.2 | 30.09
248 | 42.5 | 42.42 | 42.64 | ER | ER | ER | T |  | MAX | 42.53 | 42.12 | 42.33 | 42.52 | 42.64 | 42.71 | 42.81 | 42.78 | 42.37 | 42.61 | 42.79 | 42.84 | 42.86 | 42.93 | 42.93 | 42.68 | 42.83 | 42.91 | 42.89 | 42.86 | 42.86 | 42.84 | 30.61 | 30.62 | 30.66 | 30.75 | 30.78 | 30.87 | 30.84 | 42.17
249 | 42.53 | 42.5 | 42.71 | ER | ER | ER | O |  | AVG | 34.19 | 38.75 | 42.29 | 42.4 | 42.5 | 42.53 | 42.69 | 33.82 | 38.67 | 42.47 | 42.71 | 42.85 | 42.86 | 42.9 | 40.48 | 41.4 | 42.84 | 42.87 | 42.88 | 42.85 | 42.83 | 34.32 | 30.5 | 30.53 | 30.53 | 30.69 | 30.7 | 30.78 | 30.44 | 38.59
250 | 42.69 | 42.6 | 42.81 | ER | ER | ER | R | MW-2
251 | 33.82 | 30.23 | 42.78 | ER | ER | ER |  |  | UP
252 | 38.67 | 30.23 | 42.37 | ER | ER | ER | W |  | MIN | bar: 244 to 273
253 | 42.47 | 42.32 | 42.61 | ER | ER | ER | E |  | MAX | bar: 244 to 273
254 | 42.71 | 42.54 | 42.79 | ER | ER | ER | L |  | AVG | bar: 244 to 273
255 | 42.85 | 42.71 | 42.84 | ER | ER | ER | L
256 | 42.86 | 42.77 | 42.86 | ER | ER | ER
257 | 42.9 | 42.79 | 42.93 | ER | ER | ER | T
258 | 40.48 | 38.77 | 42.93 | ER | ER | ER | W
259 | 41.4 | 38 | 42.68 | ER | ER | ER | O
260 | 42.84 | 42.67 | 42.83 | ER | ER | ER
261 | 42.87 | 42.74 | 42.91 | ER | ER | ER | I
262 | 42.88 | 42.73 | 42.89 | ER | ER | ER | N
263 | 42.85 | 42.7 | 42.86 | ER | ER | ER | J
264 | 42.83 | 42.68 | 42.86 | ER | ER | ER | E
265 | 34.32 | 30.51 | 42.84 | ER | ER | ER | C
266 | 30.5 | 30.08 | 30.61 | ER | ER | ER | T
267 | 30.53 | 30.48 | 30.62 | ER | ER | ER | I
268 | 30.53 | 30.48 | 30.66 | ER | ER | ER | O
269 | 30.69 | 30.58 | 30.75 | ER | ER | ER | N
270 | 30.7 | 30.65 | 30.78 | ER | ER | ER
271 | 30.78 | 30.64 | 30.87 | ER | ER | ER | W
272 | 30.44 | 30.2 | 30.84 | ER | ER | ER | E
273 | 38.59 | 30.09 | 42.17 | ER | ER | ER | L
L
244 | 40.3 | 37.93 | 45.64 | 25 | 22.16 | 31.48 | M |  |  | 244 | 245 | 246 | 247 | 248 | 249 | 250 | 251 | 252 | 253 | 254 | 255 | 256 | 257 | 258 | 259 | 260 | 261 | 262 | 263 | 264 | 265 | 266 | 267 | 268 | 269 | 270 | 271 | 272 | 273
245 | 42.96 | 37.87 | 45.23 | 28.62 | 22.01 | 31.41 | O
246 | 45.37 | 45.23 | 45.46 | 31.5 | 31.34 | 31.69 | N |  | LOW
247 | 45.5 | 45.42 | 45.66 | 31.71 | 31.56 | 31.9 | I |  | MIN | 37.93 | 37.87 | 45.23 | 45.42 | 45.58 | 45.65 | 45.74 | 38.31 | 38.31 | 45.47 | 45.7 | 45.87 | 45.93 | 45.96 | 39.37 | 39.32 | 45.74 | 45.84 | 45.85 | 45.84 | 45.82 | 37.45 | 37.45 | 44.93 | 45.07 | 45.17 | 45.27 | 45.31 | 38.94 | 38.85
248 | 45.6 | 45.58 | 45.76 | 31.88 | 31.71 | 31.99 | T |  | MAX | 45.64 | 45.23 | 45.46 | 45.66 | 45.76 | 45.85 | 45.95 | 45.92 | 45.5 | 45.75 | 45.92 | 45.99 | 46.01 | 46.09 | 46.09 | 45.74 | 45.93 | 46.03 | 46.02 | 45.99 | 46 | 45.97 | 44.99 | 45.18 | 45.25 | 45.36 | 45.4 | 45.45 | 45.39 | 45.38
249 | 45.81 | 45.65 | 45.85 | 31.93 | 31.77 | 32.09 | O |  | AVG | 40.3 | 42.96 | 45.37 | 45.5 | 45.6 | 45.81 | 45.89 | 40.56 | 43.3 | 45.5 | 45.86 | 45.97 | 45.99 | 46 | 41.93 | 43.81 | 45.87 | 45.93 | 45.94 | 45.95 | 45.94 | 40.08 | 42.71 | 45 | 45.11 | 45.36 | 45.4 | 45.44 | 40.78 | 43.38
250 | 45.89 | 45.74 | 45.95 | 32 | 31.88 | 32.17 | R | MW-3
251 | 40.56 | 38.31 | 45.92 | 24.28 | 21.1 | 32.07 |  |  | UP
252 | 43.3 | 38.31 | 45.5 | 28.32 | 21.04 | 31.62 | W |  | MIN | 22.16 | 22.01 | 31.34 | 31.56 | 31.71 | 31.77 | 31.88 | 21.1 | 21.04 | 31.51 | 31.7 | 31.81 | 31.82 | 31.79 | 17.43 | 17.32 | 31.4 | 31.52 | 31.53 | 31.49 | 31.5 | 21.75 | 21.74 | 31.49 | 31.65 | 31.75 | 31.83 | 31.92 | 21.66 | 21.48
253 | 45.5 | 45.47 | 45.75 | 31.75 | 31.51 | 31.85 | E |  | MAX | 31.48 | 31.41 | 31.69 | 31.9 | 31.99 | 32.09 | 32.17 | 32.07 | 31.62 | 31.85 | 31.99 | 31.99 | 32 | 32.02 | 32.02 | 31.48 | 31.72 | 31.8 | 31.78 | 31.75 | 31.78 | 31.71 | 31.6 | 31.84 | 31.94 | 32.05 | 32.1 | 32.18 | 32.13 | 31.82
254 | 45.86 | 45.7 | 45.92 | 31.85 | 31.7 | 31.99 | L |  | AVG | 25 | 28.62 | 31.5 | 31.71 | 31.88 | 31.93 | 32 | 24.28 | 28.32 | 31.75 | 31.85 | 31.95 | 31.95 | 31.94 | 22.83 | 27.44 | 31.54 | 31.61 | 31.61 | 31.6 | 31.61 | 24.87 | 28.51 | 31.69 | 31.8 | 31.93 | 31.96 | 32.04 | 24.6 | 28.57
255 | 45.97 | 45.87 | 45.99 | 31.95 | 31.81 | 31.99 | L
256 | 45.99 | 45.93 | 46.01 | 31.95 | 31.82 | 32
257 | 46 | 45.96 | 46.09 | 31.94 | 31.79 | 32.02 | T
258 | 41.93 | 39.37 | 46.09 | 22.83 | 17.43 | 32.02 | H
259 | 43.81 | 39.32 | 45.74 | 27.44 | 17.32 | 31.48 | R
260 | 45.87 | 45.74 | 45.93 | 31.54 | 31.4 | 31.72 | E
261 | 45.93 | 45.84 | 46.03 | 31.61 | 31.52 | 31.8 | E
262 | 45.94 | 45.85 | 46.02 | 31.61 | 31.53 | 31.78
263 | 45.95 | 45.84 | 45.99 | 31.6 | 31.49 | 31.75 | I
264 | 45.94 | 45.82 | 46 | 31.61 | 31.5 | 31.78 | N
265 | 40.08 | 37.45 | 45.97 | 24.87 | 21.75 | 31.71 | J
266 | 42.71 | 37.45 | 44.99 | 28.51 | 21.74 | 31.6 | E
267 | 45 | 44.93 | 45.18 | 31.69 | 31.49 | 31.84 | C
268 | 45.11 | 45.07 | 45.25 | 31.8 | 31.65 | 31.94 | T
269 | 45.36 | 45.17 | 45.36 | 31.93 | 31.75 | 32.05 | I
270 | 45.4 | 45.27 | 45.4 | 31.96 | 31.83 | 32.1 | O
271 | 45.44 | 45.31 | 45.45 | 32.04 | 31.92 | 32.18 | N
272 | 40.78 | 38.94 | 45.39 | 24.6 | 21.66 | 32.13
273 | 43.38 | 38.85 | 45.38 | 28.57 | 21.48 | 31.82 | W
E
L
L

## SHIFT DATA
PERSONNEL LIST
|  | SHIFT CODE |  | OPERATOR NAME |  | CERTIFICATION NUMBER |  | SOCIAL SECURITY NUMBER
CHIEF OPERATORS
HOSTNICK, N. | CO# 3207-A | 3 |  | BAYLER, J. | 3 | CO# 4474-A | "A" |  | "A" | 4474 | 3207 | 2D | J. BAROFSKY | 5096-C
McGEARY, J. | CO# 4545-A | 1 |  | HOSTNICK, N. | 1 | CO# 3207-A | "A" |  | "A" | 3207 | 4545 | 5 | S. HULL | 5613-C
BAYLER, J. | CO# 4474-A | 2 |  | McGEARY, J. | 2 | CO# 4545-A | "A" |  | "A" | 4545 | 4474 | 4 | VACANT | X
POMEROY, D. | CO# 421-B | 5 |  | POMEROY, D. | 5 | CO# 421-B | "B" |  | "B" | 421 | 421 | 3 | J. TINKER | 3291-C
[12 empty] | 1 | G. SLAYTON | 2606-B
[12 empty] | 2 | H. WALKER | 4700-A
OPERATOR II' S
BENTLEY, J. | CO# 9366-C | 4 |  | BAROFSKY, J. | 4 | CO# 5096-C | [5 empty] | 5 | J. BENTLEY | X
CURMODE, S. | CO# 9379-A | 1 |  | BENTLEY, J. | 1 | CO# 9366-C | [5 empty] | 1D | S. CURMODE | X
JONES, K. | CO# 2466-B | 2 |  | CURMODE, S. | 2 | CO# 9379-A | [5 empty] | 4 | K. HENDERSON | 5087-B
BAROFSKY, J. | CO# 5096-C | 2D |  | HULL, S. | 2D | CO# 5613-C | [5 empty] | 3D | K. JONES | 2466-C
THOMAS, P. | CO# 12833 C | 3 |  | JONES, K. | 3 | CO# 2466-B | [5 empty] | 3 | G. KLEYNHANS | 7367-C
HULL, S. | CO# 5613-C | 5 |  | THOMAS, P. | 5 | CO# 12833 C | [5 empty] | 2 | A. MORROW | 9164-C
[12 empty] | 1 | J. RAINFORTH | 2718-C
OPERATOR I' S
HENDERSON, K. | CO# 5087-B | 3 |  | FREIDLAND, M. | 3 | CO# XXXX-X
SANDERS, C. | CO# XXXX-X | 1 |  | HENDERSON, K. | 1 | CO# 5087-B
KOKLAS, D. | CO# XXXX-X | 2 |  | KOKLAS, D. | 2 | CO# XXXX-X
FREIDLAND, M. | CO# XXXX-X | 5 |  | NOBERT, B. | 5 | CO# 9661-C
VERBOSH, R. | CO# 12667-C | 4 |  | PEUGEOT, P. | 4 | CO# 12817-C
PEUGEOT, P. | CO# 12817-C | 1D |  | SANDERS, C. | 1D | CO# XXXX-X
NOBERT, B. | CO# 9661-C | 3D |  | VERBOSH, R. | 3D | CO# 12667-C
|  | 4 | 1 | BERNARDI, J | 4 | CO# XXXX-X
|  | 3 | 2 | FREIDLAND, M. | 3 | CO# XXXX-X
|  | 5A | 3 | FUTURE, 5A | 5A | CO# XXXX-X
|  | 1 | 4 | HENDERSON, K. | 1 | CO# 5087-B
|  | 2 | 5 | KOKLAS, D. | 2 | CO# XXXX-X
|  | 5 | 6 | NOBERT, B. | 5 | CO# 9661-C
|  | 4A | 7 | PEUGEOT, P. | 4A | CO# 12817-C
|  | 1D | 8 | SANDERS, C. | 1D | CO# XXXX-X
|  | 3D | 9 | VERBOSH, R. | 3D | CO# 12667-C

## COVER PAGE
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
|  | SEPTEMBER |  | 2003
| OPERATOR | TITLE | CERTIFICATE # | TOTAL COST |  |  | 65250.6474
1 ST SHIFT | HOSTNICK, N. | CHIEF | CO# 3207-A | PEAK TO FLOW RATIO |  |  | 1.3187
2230-0630 | BENTLEY, J. | OP. II | CO# 9366-C
| HENDERSON, K. | OP. I | CO# 5087-B |  | TOTAL SUSPENDED SOLIDS
| SANDERS, C. | OP. I DEWAT | CO# XXXX-X |  |  |  | LBS/DAY
|  |  |  | RAW INFLUENT |  |  | 29466.8459
2 ND SHIFT |  |  |  | FINAL EFFLUENT |  |  | 4175.8975
0630-1430 | McGEARY, J. | CHIEF | CO# 4545-A |  | TOTAL CBOD
| CURMODE, S. | OP. II RELIEF | CO# 9379-A |  |  |  | LBS/DAY
| HULL, S. | OP. II DEWAT | CO# 5613-C | RAW INFLUENT |  |  | 20997.2692
| KOKLAS, D. | OP. I RELIEF | CO# XXXX-X | FINAL EFFLUENT |  |  | 1193.6642
CHEMICALS
3 RD SHIFT | BAYLER, J. | CHIEF | CO# 4474-A |  |  | COST | POUNDS
1430-2230 | JONES, K. | OP. II | CO# 2466-B | HYDROGEN PEROXIDE |  | 8027.946 | 57548
| FREIDLAND, M. | OP. I | CO# XXXX-X | CHLORINE |  | 5012.05 | 33980
| VERBOSH, R. | OP. I DEWAT | CO# 12667-C | POLYMER |  | 5397.7314 | 8848.74
SLUDGE REMOVED
4 TH SHIFT | [6 empty] | TONS
WEEKEND | BAROFSKY, J. | OP. II | CO# 5096-C | DRY TONS |  |  | 521.3668
2230-1030 | PEUGEOT, P. | OP. I | CO# 12817-C |  | ENERGY
| BERNARDI, J. | OP. I | CO# XXXX-X |  |  | COST | KILOWATTS
5 TH SHIFT | POMEROY, D. | CHIEF | 0 | FPL CONSUMPTION |  | 46812.92 | 851144
WEEKEND | THOMAS, P. | OP. II | CO# 12833 C
1030-2230 | NOBERT, B. | OP. I | CO# 9661-C | POPULATION EQUIVALENCE |  |  | 123513.3481
This Monthly Operation Report prepared by: |  |  | BAYLER, J. | CO# 4474-A
State DEP Plant Classification: Class "A" Level "II"
I certify that I am familiar with the information contained in this report and that to the best of my knowledge and
belief, such information is true, complete and accurate.
Facilitiy Manager's Signature: ____________________________________ CO# __________________
Division Manager's Signature: ____________________________________ CO# __________________
Please direct all inquiries reguarding this report to the City Official Mailing Address:
Director of Public Services |  |  | Phone (954) 776-5151
City of Fort Lauderdale
P.O. Drawer 14250 |  |  | Copies mailed: Date ________________ To: DEP _____
Fort Lauderdale, Florida | [5 empty] | DNRP _____
33302
PAGE 1

## PRINT PAGES
UNDERGROUND INJECTION CONTROL SECTION
[28 empty] | MONTHLY OPERATING REPORT DATA SUMMARY | [13 empty] | DEP From # 17-801.900 (1) | [11 empty] | DEP From # 17-801.900 (1) | [19 empty] | DAILY SAMPLE RESULTS - PART B
[25 empty] | FACILITY: GEORGE T. LOHMEYER WWTP |  |  |  |  | REPORT DATE: |  | SEPTEMBER | 2003 | [8 empty] | Form Title:Domestic Wastewater Treatment | [11 empty] | Form Title:Domestic Wastewater Treatment
[25 empty] | I.D. NUMBER: 5006M02066 |  |  |  | CHIEF OPERATOR: |  |  | BAYLER, J. | CO# 4474-A | [8 empty] | Plant Monthly Operating Report | [11 empty] | Plant Monthly Operating Report | [15 empty] | Permit Number: |  | FLA041378 |  |  |  |  | Three-month Average Daily Flow: | [5 empty] | 35.2886
[25 empty] | TELEPHONE NUMBER: (954) 523-1002 | [16 empty] | Effective Date: July 1, 1991 | [11 empty] | Effective Date: July 1, 1991 | [15 empty] | Monitoring Period |  | From: | 2003-09-01 | To: | 2003-10-01 |  | (TMADF):/Permitted Capacity)x100: | [5 empty] | 82.07%
[19 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [8 empty] | INJECTION WELL DATA | [13 empty] | DEP Application No. __________________ | [11 empty] | DEP Application No. __________________ | [11 empty] | Department of Natural Resource Protection
[5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [13 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [6 empty] | IW-1 | IW-2 | IW-3 |  | IW-4 | IW-5 | [35 empty] | Laboratory/Licensing/Enforcement |  |  |  | Flow | Flow | Flow | Flow | Flow | Flow | CBOD5 | CBOD5 | TSS | TSS | pH | pH | TDS | NH-3 | TKN | pH | cond. | temp. | TP
[5 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [13 empty] | MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING | [5 empty] | PERMIT/CERTIFICATION NUMBER: | UO-06-279401 | UO-06-279508 | UO-06-279510 |  | UC 06-264391 | UO-06-2795112 | [19 empty] | DOMESTIC WASTEWATER TREATMENT PLANT | [11 empty] | BROWARD COUNTY DEPARTMENT OF NATURAL RESOURCE PROTECTION | [5 empty] | 218 S. W. 1st Avenue |  |  | (MGD) | (MGD) | (MGD) | (MGD) | (MGD) | (mg/l) | (mg/l) | (mg/l) | (mg/l) | (Min) | (Max) | mg/L | mg/L | mg/L | units | umho/ | F | mg/L
[5 empty] | MONTHLY OPERATIONAL REPORT | [13 empty] | MONITORING WELL ONE |  |  |  | 7/21/97 thru 7/21/02 |  | PERMIT EXPIRATION DATE: | 2002-07-27 | 2002-07-27 | 2002-07-27 |  | 2000-11-30 | 2002-07-27 | [19 empty] | MONTHLY OPERATING REPORT | [11 empty] | WASTEWATER TREATMENT PLANT | [5 empty] | Fort Lauderdale, FL 33301 | [17 empty] | cm
[5 empty] | PROCESS DATA | [11 empty] | MW-1 | I.D. #: 5066A11311 |  |  | PERMIT/CERT. #: UO-06-279512 |  |  |  | CASING DEPTH | 2799' | 2798' | 2800' |  | 2804' | 2818' | [8 empty] | DOMESTIC WASTEWATER TREATMENT PLANT |  |  |  |  | (34) | [8 empty] | MONTH: | SEPTEMBER |  | YEAR: | 2003 |  |  |  |  | MONTHLY SLUDGE REPORTS | [5 empty] | Tel. No. (954) 765-4804 | Code | 50050 | 50050 | 50050 | 50050 | 50050 | 50050 | 80082 | 80082 | 00530 | 00530 | 00400 | 00400
| RUN DATE | [14 empty] | RUN DATE | [8 empty] | TOTAL DEPTH | 3513' | 3518' | 3977' |  | 3305' | 3462' | [8 empty] | MONTHLY OPERATING REPORT |  |  |  |  | DAY OF | FLOW | CHLORINE | CHLORINE | CBOD5 | TSS | CBOD5 | TSS | PH |  |  | EFFLUENT NUTRIENTS (MG/L) |  |  | I. | [10 empty] | Mon. Site | INF-001 | EFF-002 | EFF-003 | EFF-004 | EFF-005 | EFF-006 | INF-002 | EFF-001 | INF-002 | EFF-001 | EFF-001 | EFF-001
| 2026-07-30 | [14 empty] | 2026-07-30 |  | UPPER MONITOR ZONE |  |  |  |  | LOWER MONITOR ZONE |  | AVERAGE DAILY FLOW: | 10.053 | 10.4852 | 8.9943 |  | #DIV/0! | 8.9853 | MGD | [7 empty] | Part II - General Information |  |  |  |  | THE |  | RESIDUAL | RESIDUAL | INFLUENT | INFLUENT | EFFLUENT | EFFLUENT | EFFLUENT | TKN | NH3-N | NITRATE | TOTAL | FECAL | Plant Name: | GEORGE T. LOHMEYER WASTEWATER TREATMENT FACILITY | [6 empty] | MONTH: | SEPTEMBER |  | 1 | 36.561 | 9.47 | 9.61 | 8.44 | ER | 8.51 | 66 | 3.2 | 72 | 18 | 6.6 | 6.6 | 1190 |  |  | 6.6 | 2390 | 85
[17 empty] | MIN | MAX | AVG |  |  | MIN | MAX | AVG | **MAX DAILY FLOW PER MO (mg): | 13.13 | 13.75 | 11.75 |  | 0 | 11.55 | MG | [12 empty] | MONTH | (MGD) | AFTER | AFTER DE- | [8 empty] | P | COLIFORM | II. | [7 empty] | YEAR: | 2003 |  | 2 | 38.615 | 9.9 | 10.09 | 8.84 | ER | 8.89 | 84 | 4.4 | 76 | 8 | 6.5 | 6.5 | 1240 |  |  | 6.6 | 2280 | 85
| SEPTEMBER | INFLUENT | HOURLY | INFLUENT | INFLUENT | RAS | PERCENT | WAS | RAIN | SPARE | [5 empty] | SEPTEMBER | FT HEAD | FT HEAD | FT HEAD |  |  | FT HEAD | FT HEAD | FT HEAD | ** PEAK HR FLOW (MGD) ON MAX DAY: | 15.7084 | 16.3946 | 14.052 |  | #DIV/0! | 14.0487 | MGD |  | (1) Month: |  | SEPTEMBER |  | Year: | 2003 |  | Parameter | Units | STORET | Value |  |  | CONTACT | CHLORINATION | MG/L | MG/L | MG/L | MG/L | [6 empty] | A) | Sludge Treatment Provided: |  |  |  |  | B) | Sludge Dewater Processes |  |  |  | 3 | 37.609 | 9.68 | 9.84 | 8.63 | ER | 8.68 | 65 | 3.4 | 100 | 24 | 6.5 | 6.7 | 1096 | 11 | 12 | 6.6 | 2160 | 84 | 1.1
| 2003 | FLOW | MAXIMUM | MAXIMUM | MINIMUM | FLOW | RAS | FLOW | INCHES | [6 empty] | 2003 | ABOVE | ABOVE | ABOVE |  |  | ABOVE | ABOVE | ABOVE | MAX SUSTAINED INJECTION PRESSURE: | 81.4 | 79.8 | 81.9 |  | 64.41 | 81.2 | PSIG |  | (2) Plant's DEP Identification Number: |  |  |  |  | 5006M02066 |  |  |  | Code |  | 1 | 36.561 | 1 |  | 66 | 72 | 3.2 | 18 | 6.6 |  |  |  |  | 0 |  |  | Aerobic Digestion | [5 empty] | Thickner |  |  | 4 | 38.719 | 10 | 10.15 | 8.96 | ER | 8.94 | 93 | 3 | 100 | 13 | 6.5 | 6.6 | 1050 | 10 | 11 | 6.6 | 2210 | 84 | 0.83
|  | MGD | MGD | MGD | MGD | MGD |  | MGD | [8 empty] | NGVD | NGVD | NGVD |  |  | NGVD | NGVD | NGVD | MONTHLY AVG. INJECTION PRESSURE: | 52.6497 | 51.6513 | 52.8907 |  | 37.4543 | 50.0137 | PSIG |  | (3) Plant Name: |  |  |  | George T. Lohmeyer Regional Wastewater |  |  | (16) Monthly average daily flow | mgd | 050053 | 38.5159 | 2 | 38.615 | 1 |  | 84 | 76 | 4.4 | 8 | 6.6 |  |  |  |  | 0 |  |  | Anaerobic Digestion | [5 empty] | DGA___X___Filter Press |  |  | 5 | 39.657 | 10.46 | 10.59 | 9.41 | ER | 9.16 | 73.1 | 4.63 | 114 | 23 | 6.6 | 6.6 | 1052 | 10 | 11 | 6.6 | 2180 | 84 | 0.83
| 1 | 36.561 | 1.812 | 52.45 | 17.14 | 10.052 | 27.49% | 0.368 | 0.33 |  |  | 1 |  |  |  | 1 | 45.79 | 48.76 | 48.6 |  |  | 28.92 | 42.01 | 32.82 | *** MAX INJECTION PRESSURE PERMITTED: | 99 | 99 | 99 |  | 99 | 99 | PSIG |  |  |  |  | Treatment Facility |  |  |  | (17) Permitted capacity | mgd | - | 43 | 3 | 37.609 | 9 |  | 65 | 100 | 3.4 | 24 | 6.6 | 12 | 11 | 0.65 | 1.1 | 0 |  |  | Other | [5 empty] | Centrifuge Drying Beds, Bed #______ |  |  | 6 | 42.344 | 10.93 | 11.13 | 9.8 | ER | 9.71 | 62.2 | 2.3 | 108 | 12 | 6.6 | 6.6 | 1115 | 8.3 | 9.2 | 6.6 | 2200 | 84 | 0.85
| 2 | 38.615 | 1.818 | 54.02 | 18.198 | 11.761 | 30.46% | 0.54 | 0.5 |  |  | 2 |  |  |  | 2 | 46.3 | 48.6 | 47.02 |  |  | 28.96 | 41.92 | 38.2 | ***NOTE: (INJECTION PRESSURE NOT TO EXCEED 66% TESTED PRESSURE | [8 empty] | (4) Plant Address: |  |  | 1765 S.E. 18th Street at |  |  |  | (18) Three-month average daily flow | mgd | - | 35.2886 | 4 | 38.719 | 1.2 |  | 93 | 100 | 3 | 13 | 6.6 | 11 | 10 | 0.67 | 0.83 | 9 | [8 empty] | Heat Treatment____No Treatment |  |  | 7 | 41.953 | 10.77 | 10.95 | 9.65 | ER | 9.57 | 60.6 | 2.7 | 78 | 11 | 6.5 | 6.7 | 1029 | 7.9 | 8.3 | 6.6 | 1983 | 84 | 0.71
| 3 | 37.609 | 1.755 | 50.559 | 19.8 | 10.882 | 28.93% | 0.612 | 0.03 |  |  | 3 |  |  |  | 3 | 48.4 | 48.74 | 48.52 |  |  | 41.84 | 42.22 | 41.97 | TESTED CASING PRESSURE DURING MIT | 150 | 150 | 150 |  | 150 | 150 | PSIG |  |  |  |  | Eisenhower Boulevard |  |  |  | (19) Percent of permitted capacity | % | - | 82.07% | 5 | 39.657 | 1.3 |  | 73.1 | 114 | 4.63 | 23 | 6.6 | 11 | 10 | 0.67 | 0.83 | 0 | [7 empty] | x | Other: | LIME STABILIZATION |  | 8 | 41.6 | 10.71 | 10.89 | 9.6 | ER | 9.51 | 55 | 2.7 | 120 | 10 | 6.5 | 6.7 | 1062 |  |  | 6.6 | 2030 | 85
| 4 | 38.719 | 1.867 | 53.668 | 21.723 | 11.978 | 30.94% | 0.52 | 0.4 |  |  | 4 |  |  |  | 4 | 48.51 | 48.89 | 48.69 |  |  | 41.99 | 42.3 | 42.11 | [9 empty] | (5) City: |  | Fort Lauderdale |  |  |  |  | (20) CBOD5 Effluent | mg/L | 080082 | 3.716 | 6 | 42.344 | 1 |  | 62.2 | 108 | 2.3 | 12 | 6.6 | 9.2 | 8.3 | 0.42 | 0.85 | 0 | [9 empty] | CLASS "AA" |  | 9 | 39.883 | 10.31 | 10.48 | 9.23 | ER | 9.2 | 59.1 | 3.08 | 88 | 8 | 6.5 | 6.7 | 1010 |  |  | 6.6 | 2120 | 84
| 5 | 39.657 | 2.058 | 56.616 | 16.085 | 12.488 | 31.49% | 0.174 | 1.34 |  |  | 5 |  |  |  | 5 | 48.6 | 48.97 | 48.84 |  |  | 42.12 | 42.39 | 42.33 |  |  | MONITORING WELL DATA | [6 empty] | (6) County: |  | Broward |  |  |  |  | (21) CBOD5 Effluent | lbs/day | - | 1193.6642 | 7 | 41.953 | 1 |  | 60.6 | 78 | 2.7 | 11 | 6.6 | 8.3 | 7.9 | 0.6 | 0.71 | 0 | III. | Final Sludge Disposal: | [7 empty] | RMF-Azurix (Nutri-Cycle) |  | 10 | 38.584 | 10 | ER | 8.96 | ER | 8.97 | 69.8 | 3.3 | 84 | 24 | 6.6 | 6.8 | 1189 | 10 | 11 | 6.6 | 2220 | 84 | 0.86
| 6 | 42.344 | 2.057 | 56.231 | 20.858 | 12.496 | 29.51% | 0 | 0.71 |  |  | 6 |  |  |  | 6 | 48.64 | 49.02 | 48.88 |  |  | 42.22 | 42.5 | 42.39 |  | MW-1 | MW-2 | MW-3 |  | RMW-1 |  |  |  | (7) Phone Number: |  |  | (954) 523-1002 |  |  |  | (22) TSS Effluent | mg/L | 900201 | 13 | 8 | 41.6 | 1.1 |  | 55 | 120 | 2.7 | 10 | 6.6 |  |  |  |  | 0 | A) | Liquid Sludge Disposal: | [9 empty] | 11 | 37.261 | 9.76 | 10.31 | 8.74 | ER | 8.77 | 60 | 5 | 94 | 13 | 6.6 | 6.7 | 1244 | 10 | 12 | 6.6 | 2290 | 87 | 1.6
| 7 | 41.953 | 1.95 | 56.808 | 21.819 | 11.925 | 28.42% | 0.202 | 0.2 |  |  | 7 |  |  |  | 7 | 48.71 | 49.08 | 48.9 |  |  | 42.13 | 42.47 | 42.42 | PERMIT NUMBER | UO-06-279512 | UO-06-279401 | UO-06-279510 |  | UC06-249353 |  |  |  | (8) Permit Number: |  |  | FLA041378 |  |  |  | (23) TSS Effluent | lbs/day | - | 4175.8975 | 9 | 39.883 | 0.6 |  | 59.1 | 88 | 3.08 | 8 | 6.6 |  |  |  |  | 0 |  | WEEK OF | SEPTEMBER | GALLONS | % SOLIDS |  |  | HAULERS |  |  | DISPOSAL SITE | 12 | 38.224 | 10.01 | 10.25 | 8.97 | ER | 8.95 | 115 | 3 | 84 | 9 | 6.6 | 6.7 | 1210 | 10.74 | 14.57 | 6.6 | 2500 | 84 | 0.735
| 8 | 41.6 | 1.97 | 56.103 | 22.428 | 11.006 | 26.46% | 0.496 | 0 |  |  | 8 |  |  |  | 8 | 47.44 | 49 | 48.09 |  |  | 30.7 | 42.39 | 34.07 | UPPER MONITORING INTERVAL | 1288'-1320' | 1300'-1344' | 1300'-1349' |  | 1300'-1339' |  | Ft. bls. |  | (9) Plant Type: |  |  | Oxygen Activated Sludge |  |  |  | (24) Minimum pH |  | - | 6.4 | 10 | 38.584 | 1 |  | 69.8 | 84 | 3.3 | 24 | 6.6 | 11 | 10 | 0.54 | 0.86 | 9 | [11 empty] | 13 | 38.145 | 9.75 | 10.32 | 8.72 | ER | 8.73 | 54 | 3.05 | 88 | 10 | 6.6 | 6.6 | 1270 | 9.41 | 13.14 | 6.6 | 2210 | 85 | 1.05
| 9 | 39.883 | 1.913 | 53.764 | 21.018 | 11.897 | 29.83% | 0.532 | 0.47 |  |  | 9 |  |  |  | 9 | 47.78 | 48.77 | 48.37 |  |  | 30.76 | 42.22 | 38.76 | MONTHLY MAX DAILY PRESSURE | 49.08 | 0 | 32.18 |  | 44.9 |  | FT. HEAD |  | (10) Test Site Identification Number: |  |  |  |  | 5006X10744 |  | (25) Maximum pH |  | - | 6.8 | 11 | 37.261 | 1.1 |  | 60 | 94 | 5 | 13 | 6.6 | 12 | 10 | 0.55 | 1.6 | 40 |  | FIRST THRU SEVENTH | [9 empty] | 14 | 37.595 | 9.67 | 10.25 | 8.64 | ER | 8.66 | 83 | 3.1 | 152 | 12 | 6.6 | 6.6 | 1270 | 9.79 | 13.58 | 6.6 | 2640 | 85 | 1.04
| 10 | 38.584 | 1.862 | 52.29 | 19.095 | 11.41 | 29.57% | 0.552 | 0 |  |  | 10 |  |  |  | 10 | 48.52 | 48.87 | 48.7 |  |  | 42.18 | 42.42 | 42.36 | MONTHLY MIN DAILY PRESSURE | 45.35 | 0 | 17.32 |  | 32.31 |  | FT. HEAD |  | (11) Fecal Coliform Method | [6 empty] | (26) Total N | mg/L | 000600 | 13.7126 | 12 | 38.224 | 1.1 |  | 115 | 84 | 3 | 9 | 6.6 | 14.57 | 10.74 | 0.356 | 0.735 | 54 | [11 empty] | 15 | 37.957 | 9.8 | 10.34 | 8.75 | ER | 8.77 | 83 | 3.1 | 152 | 12 | 6.5 | 6.6 | 1294 |  |  | 6.6 | 2640 | 84
| 11 | 37.261 | 1.785 | 52.097 | 18.839 | 12.294 | 32.99% | 0.495 | 0 |  |  | 11 |  |  |  | 11 | 48.61 | 48.96 | 48.76 |  |  | 42.37 | 42.56 | 42.47 | TDS (MONTHLY AVERAGE) | 7325 | 7215.8 | 7300 |  | 5550 |  | mg/l |  |  | XX | Membrane Filter |  |  |  |  | (27) TKN | mg/L | 000625 | 13.247 | 13 | 38.145 | 0.9 |  | 54 | 88 | 3.05 | 10 | 6.6 | 13.14 | 9.41 | 0.366 | 1.05 | 0 |  | EIGHT THRU FORTEENTH | [9 empty] | 16 | 37.419 | 9.66 | 10.23 | 8.62 | ER | 8.65 | 53.9 | 6.14 | 98 | 7 | 6.5 | 6.6 | 1335 |  |  | 6.6 | 2650 | 85
| 12 | 38.224 | 1.839 | 51.841 | 17.173 | 12.444 | 32.56% | 0.223 | 0 |  |  | 12 |  |  |  | 12 | 48.7 | 48.93 | 48.86 |  |  | 42.47 | 42.66 | 42.52 | CHLORIDE (MONTHLY AVERAGE) | 3820 | 3740 | 3800 |  | 2750 |  | mg/l |  |  |  | Most Probable Number |  |  |  |  | (28) Ammonia (NH3 - N) | mg/L | 000610 | 10.2985 | 14 | 37.595 | 1.1 |  | 83 | 152 | 3.1 | 12 | 6.6 | 13.58 | 9.79 | 0.443 | 1.04 | TNTC |  | FIFTHTEENTH THRU | [9 empty] | 17 | 37.225 | 9.65 | 10.15 | 8.6 | ER | 8.64 | 79.8 | 3.71 | 84 | 17 | 6.5 | 6.6 | 1315 | 11.37 | 15.16 | 6.6 | 2630 | 85 | 1.06
| 13 | 38.145 | 1.876 | 53.764 | 18.39 | 11.377 | 29.83% | 0 | 0 |  |  | 13 |  |  |  | 13 | 48.68 | 48.89 | 48.81 |  |  | 42.54 | 42.68 | 42.56 | AMMONIA-N (MONTHLY AVERAGE) | 0.856 | 0.9624 | 1.0038 |  | 0.911 |  | mg/l |  | (12) Type of Effluent Disposal or Reclaimed Water Reuse | [6 empty] | (29) Nitrate | mg/L | 071850 | 0.46555 | 15 | 37.957 | 0.9 |  | 83 | 152 | 3.1 | 12 | 6.6 |  |  |  |  | 9 |  | TWENTY SECOND | [9 empty] | 18 | 27.052 | 9.63 | 10.04 | 8.62 | ER | 8.63 | 78 | 5 | 78 | 13 | 6.5 | 6.7 | 1298 | 11.81 | 15.44 | 6.6 | 2660 | 85 | 1.02
| 14 | 37.595 | 1.881 | 53.86 | 18.899 | 11.446 | 30.45% | 0.184 | 0.02 |  |  | 14 |  |  |  | 14 | 48.64 | 48.91 | 48.81 |  |  | 42.52 | 42.71 | 42.58 | TKN (MONTHLY AVERAGE) | 1.38 | 1.558 | 1.342 |  | 1.1 |  | mg/l |  |  |  | Deep Well Injection |  |  |  |  | (30) Total Phosphorus | mg/L | 000665 | 0.99735 | 16 | 37.419 | 0.9 |  | 53.9 | 98 | 6.14 | 7 | 6.6 |  |  |  |  | 9 |  | TWENTY THIRD THRU | [9 empty] | 19 | 36.748 | 9.66 | 10.23 | 8.64 | ER | 8.7 | 60.8 | 4.53 | 98 | 11 | 6.5 | 6.7 | 1308 | 11.58 | 15.45 | 6.6 | 2680 | 85 | 0.772
| 15 | 37.957 | 1.768 | 52.802 | 19.672 | 11.648 | 30.69% | 0.56 | 0 |  |  | 15 |  |  |  | 15 | 47.61 | 48.91 | 48.2 |  |  | 37.79 | 42.71 | 39.69 | pH (MONTHLY AVERAGE) | 7.828 | 7.942 | 8.068 |  | 8.35 |  | Std units |  | (13) Limited Wet Wheather Discharge Activated | [6 empty] | (31) Minimum Chlorine Residual | mg/L | - | 0.2 | 17 | 37.225 | 0.9 |  | 79.8 | 84 | 3.71 | 17 | 6.6 | 15.16 | 11.37 | 0.444 | 1.06 | 0 |  | THIRTY FIRST | [9 empty] | 20 | 35.658 | 9.11 | 9.67 | 8.15 | ER | 8.21 | 58.5 | 3.4 | 100 | 11 | 6.5 | 6.6 | 1385 | 11.11 | 14.76 | 6.5 | 2610 | 85 | 0.72
| 16 | 37.419 | 1.747 | 50.976 | 21.082 | 12.136 | 32.43% | 0.568 | 0 |  |  | 16 |  |  |  | 16 | 47.87 | 48.88 | 48.66 |  |  | 37.71 | 42.55 | 41.19 | CONDUCTIVITY (MONTHLY AVERAGE) | 12078 | 11804 | 12052 |  | 9100 |  | umho/cm |  |  |  | YES |  | XX | Not Applicable |  | (32) Maximum Chlorine Residual | mg/L | - | 9 | 18 | 27.052 | 0.8 |  | 78 | 78 | 5 | 13 | 6.6 | 15.44 | 11.81 | 0.467 | 1.02 | 464 | [11 empty] | 21 | 35.028 | 9.04 | 9.63 | 8.07 | ER | 8.16 | 68.9 | 3.27 | 66 | 17 | 6.5 | 6.6 | 1346 | 11.03 | 14.84 | 6.6 | 2680 | 85 | 0.72
| 17 | 37.225 | 1.78 | 51.008 | 19.416 | 12.214 | 32.81% | 0.564 | 0 |  |  | 17 |  |  |  | 17 | 48.72 | 48.94 | 48.9 |  |  | 42.5 | 42.77 | 42.54 | FECAL COLIFORM (MONTHLY AVERAGE) | 0 | 0 | 0 |  | 0 |  | # col/100ml |  |  |  | NO |  |  |  |  | (33) Other Effluent Parameters |  |  |  | 19 | 36.748 | 0.9 |  | 60.8 | 98 | 4.53 | 11 | 6.6 | 15.45 | 11.58 | 0.411 | 0.772 | 71 | B) | Solid Sludge Hauled from Plant: | [9 empty] | 22 | 35.516 | 9.18 | 9.75 | 8.19 | ER | 8.26 | 57.3 | 3.77 | 44 | 8 | 6.4 | 6.6 | 1393 |  |  | 6.6 | 2750 | 85
| 18 | 27.052 | 1.788 | 49.696 | 19.287 | 12.259 | 45.32% | 0.569 | 0 |  |  | 18 |  |  |  | 18 | 48.71 | 48.94 | 48.91 |  |  | 42.56 | 42.75 | 42.59 | TEMPERATURE (MONTHLY AVERAGE) | 73 | 71.4 | 70 |  | 70 |  | deg. F | [12 empty] | 20 | 35.658 | 1 |  | 58.5 | 100 | 3.4 | 11 | 6.5 | 14.76 | 11.11 | 0.382 | 0.72 | 9 |  | WEEK OF | SEPTEMBER | TONS |  | % SOLIDS |  | HAULERS |  |  | DISPOSAL SITE | 23 | 34.752 | 9.02 | 9.58 | 8.04 | ER | 8.13 | 61 | 3.5 | 94 | 11 | 6.5 | 6.6 | 1432 |  |  | 6.6 | 2820 | 85
| 19 | 36.748 | 1.784 | 50.014 | 19.928 | 11.944 | 32.5% | 0.294 | 0 |  |  | 19 |  |  |  | 19 | 48.63 | 48.87 | 48.79 |  |  | 42.53 | 42.69 | 42.55 | TOTAL PHOSPHOROUS (MONTHLY AVG.) | 0.042 | 0.042 | 0.042 |  | 0.05 |  | mg/l |  | (14) Cumulative Days of Wet Wheather Discharge | [10 empty] | 21 | 35.028 | 1 |  | 68.9 | 66 | 3.27 | 17 | 6.6 | 14.84 | 11.03 | 0.439 | 0.72 | 27 | [10 empty] | Nutri-Cylcle Inc. | 24 | 34.451 | 8.93 | 9.47 | 7.96 | ER | 8.05 | 85 | 4.2 | 100 | 12 | 6.6 | 6.6 | 1403 | 10.5 | 14.94 | 6.6 | 2840 | 85 | 1.03
| 20 | 35.658 | 1.767 | 50.111 | 18.454 | 11.428 | 32.05% | 0 | 0.09 |  |  | 20 |  |  |  | 20 | 48.55 | 48.84 | 48.69 |  |  | 42.43 | 42.63 | 42.53 | SULFATE (MONTHLY AVERAGE) | 850 | 840 | 840 |  | 750 |  | mg/l |  |  |  | N/A | [8 empty] | 22 | 35.516 | 0.8 |  | 57.3 | 44 | 3.77 | 8 | 6.6 |  |  |  |  | 0 |  | FIRST THRU SEVENTH |  | 650 |  | 15.882 |  | AZURIX |  |  | Arcadia, FL | 25 | 35.781 | 9.32 | 9.88 | 8.33 | ER | 8.38 | 58 | 4 | 82 | 12 | 6.6 | 6.6 | 1650 | 11.67 | 15.91 | 6.6 | 2860 | 85 | 1.19
| 21 | 35.028 | 1.759 | 50.367 | 17.429 | 11.897 | 33.96% | 0.203 | 0 |  |  | 21 |  |  |  | 21 | 48.51 | 48.83 | 48.67 |  |  | 42.47 | 42.63 | 42.52 | C.O.D. (MONTHLY AVERAGE) | 184 | 180 | 182 |  | 160 |  | mg/l |  | (15) Plant Staffing: | [10 empty] | 23 | 34.752 | 0.7 |  | 61 | 94 | 3.5 | 11 | 6.6 |  |  |  |  | 9 | [10 empty] | Nutri-Cylcle Inc. | 26 | 36.305 | 9.5 | 10.08 | 8.49 | ER | 8.53 | 57 | 4 | 96 | 10 | 6.6 | 6.7 | 1410 | 11.57 | 15.72 | 6.6 | 2800 | 85 | 1.24
| 22 | 35.516 | 1.776 | 51.521 | 15.988 | 11.394 | 32.08% | 0.553 | 0 |  |  | 22 |  |  |  | 22 | 45.35 | 48.78 | 46.63 |  |  | 28.11 | 42.56 | 32.31 | IRON (MONTHLY AVERAGE) | 0.432 | 0.956 | 0.796 |  | 0.16 |  | mg/l | [12 empty] | 24 | 34.451 | 0.8 |  | 85 | 100 | 4.2 | 12 | 6.6 | 14.94 | 10.5 | 0.38 | 1.03 | 0 |  | EIGHT THRU FORTEENTH |  | 675 |  | 17.778 |  | AZURIX |  |  | Arcadia, FL | 27 | 39.731 | 10.28 | 10.9 | 9.22 | ER | 9.19 | 47 | 3 | 78 | 10 | 6.6 | 6.7 | 1186 | 10.15 | 14.57 | 6.6 | 2810 | 85 | 1.34
| 23 | 34.752 | 1.778 | 51.456 | 15.668 | 11.419 | 32.86% | 0.52 | 0 |  |  | 23 |  |  |  | 23 | 45.79 | 49.08 | 47.9 |  |  | 28.13 | 42.05 | 37.99 | SULFIDE (MONTHLY AVERAGE) | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! |  | mg/l |  |  | Day Shift Operator: |  |  | Class | "A" | Cert. No. | 4545 |  |  |  | 25 | 35.781 | 0.9 |  | 58 | 82 | 4 | 12 | 6.6 | 15.91 | 11.67 | 0.482 | 1.19 | 0 |  | FIFTHTEENTH THRU | [8 empty] | Nutri-Cylcle Inc. | 28 | 47.244 | 12.09 | 12.73 | 10.89 | ER | 10.71 | 50 | 4 | 84 | 18 | 6.5 | 6.7 | 1240 | 8.04 | 12.36 | 6.6 | 2420 | 85 | 1.25
| 24 | 34.451 | 1.768 | 51.232 | 15.924 | 11.04 | 32.05% | 0.499 | 0.05 |  |  | 24 |  |  |  | 24 | 48.55 | 48.92 | 48.73 |  |  | 41.85 | 42.19 | 42.03 | LOWER MONITORING INTERVAL | 1449'-1557' | 1970'-2025' | 1970'-2027' |  | 1500'-1600' |  | Ft. bls | [12 empty] | 26 | 36.305 | 1.1 |  | 57 | 96 | 4 | 10 | 6.6 | 15.72 | 11.57 | 0.371 | 1.24 | 0 |  | TWENTY SECOND |  | 875 |  | 17.778 |  | AZURIX |  |  | Arcadia, FL | 29 | 47.07 | 12.17 | 12.78 | 10.92 | ER | 10.75 | 35 | 5 | 80 | 16 | 6.6 | 6.8 | 1261 |  |  | 6.7 | 2460 | 84
| 25 | 35.781 | 1.779 | 50.976 | 14.835 | 11.866 | 33.16% | 0.659 | 0.43 |  |  | 25 |  |  |  | 25 | 48.61 | 48.94 | 48.77 |  |  | 41.82 | 42.14 | 42 | MONTHLY MAX DAILY PRESSURE | 42.77 | 42.93 | 46.09 |  | 22.74 |  | FT. HEAD |  |  | Evening Shift Operator: |  |  | Class | "A" | Cert. No. | 4474 |  |  |  | 27 | 39.731 | 0.5 |  | 47 | 78 | 3 | 10 | 6.6 | 14.57 | 10.15 | 0.193 | 1.34 | 0 |  | TWENTY THIRD THRU | [8 empty] | Nutri-Cylcle Inc. | 30 | 50.791 | 13.13 | 13.75 | 11.75 | ER | 11.55 | 28 | 4 | 60 | 10 | 6.6 | 6.8 | 1125 |  |  | 6.7 | 2280 | 84
| 26 | 36.305 | 1.777 | 50.816 | 16.661 | 12.597 | 34.7% | 0.327 | 0.03 |  |  | 26 |  |  |  | 26 | 48.63 | 48.99 | 48.85 |  |  | 42 | 42.24 | 42.07 | MONTHLY MIN DAILY PRESSURE | 28.11 | 30.08 | 37.45 |  | 20.31 |  | FT. HEAD | [12 empty] | 28 | 47.244 | 0.2 |  | 50 | 84 | 4 | 18 | 6.6 | 12.36 | 8.04 | 0.477 | 1.25 | 18 |  | THIRTY FIRST |  | 825 |  | 18.375 |  | AZURIX |  |  | Arcadia, FL | 31
| 27 | 39.731 | 2.258 | 61.422 | 17.301 | 12.055 | 30.34% | 0 | 1.64 |  |  | 27 |  |  |  | 27 | 48.68 | 49.02 | 48.92 |  |  | 42.01 | 42.35 | 42.2 | TDS (MONTHLY AVERAGE) | 9260.8 | 31335.8 | 29068.75 |  | 27092 |  | mg/l |  |  | Night Shift Operator: |  |  | Class | "A" | Cert. No. | 3207 |  |  |  | 29 | 47.07 | 0.4 |  | 35 | 80 | 5 | 16 | 6.7 |  |  |  |  | 72500 | C) | Monthly quantities of solid sludge stockpiled at plant.Solid Sludge Hauled from Plant: | [9 empty] | TOT | 1155.478 | 301.59 | 304.07 | 269.83 | 0 | 269.56 | 1961 | 111.48 | 2752 | 390 | 196.3 | 199.6 | 37408 | 205.97 | 264.94 | 198.1 | 74003 | 2541 | 19.947
| 28 | 47.244 | 2.233 | 61.198 | 30.631 | 12.885 | 27.27% | 0.236 | 0 |  |  | 28 |  |  |  | 28 | 48.72 | 49.03 | 48.93 |  |  | 42.2 | 42.45 | 42.35 | CHLORIDE (MONTHLY AVERAGE) | 5200 | 17880 | 16250 |  | 15000 |  | mg/l | [12 empty] | 30 | 50.791 | 0.7 |  | 28 | 60 | 4 | 10 | 6.7 |  |  |  |  | TNTC |  | 1) | Additions |  |  | Cubic Yards | [5 empty] | AVG | 38.5159 | 10.053 | 10.4852 | 8.9943 | #DIV/0! | 8.9853 | 65.3667 | 3.716 | 91.7333 | 13 | 6.5433 | 6.6533 | 1246.9333 | 10.2985 | 13.247 | 6.6033 | 2466.7667 | 84.7 | 0.99735
| 29 | 47.07 | 2.202 | 58.891 | 29.445 | 12.97 | 27.55% | 0.588 | 1.01 |  |  | 29 |  |  |  | 29 | 46.97 | 48.97 | 47.79 |  |  | 37.98 | 42.24 | 39.21 | AMMONIA-N (MONTHLY AVERAGE) | 9.582 | 1.364 | 2.4525 |  | 0.524 |  | mg/l |  |  | Lead Operator:_________________________________ | [28 empty] | Tons | [5 empty] | MAX | 50.791 | 13.13 | 13.75 | 11.75 | 0 | 11.55 | 115 | 6.14 | 152 | 24 | 6.6 | 6.8 | 1650 | 11.81 | 15.91 | 6.7 | 2860 | 87 | 1.6
| 30 | 50.791 | 2.498 | 63.986 | 33.898 | 12.808 | 25.22% | 0.626 | 1.6 |  |  | 30 |  |  |  | 30 | 47.3 | 48.93 | 48.4 |  |  | 37.81 | 42.27 | 40.83 | TKN (MONTHLY AVERAGE) | 11.308 | 1.75 | 2.8325 |  | 0.5 |  | mg/l | [5 empty] | Signature |  | Cert. No. |  |  |  |  | Lead Operator : This is to certify that I am familar with the information contained on this report and that to the best of | [14 empty] | 2) | Removals |  |  | Cubic Yards | [5 empty] | MIN | 27.052 | 8.93 | 9.47 | 7.96 | 0 | 8.05 | 28 | 2.3 | 44 | 7 | 6.4 | 6.5 | 1010 | 7.9 | 8.3 | 6.5 | 1983 | 84 | 0.71
[25 empty] | pH (MONTHLY AVERAGE) | 7.238 | 7.27 | 7.365 |  | 7.6 |  | Std units | [12 empty] | my knowledge and belief, this information is true, complete and accuate. | [16 empty] | X |  | Tons | [6 empty] | item #1 | 15.7084 | 16.3946 | 14.052 | #DIV/0! | 14.0487 | MAX HOURLY FLOW (MG) = |  |  |  | 2.498 | ON THE | 30 | DAY OF THIS MONTH
| TOTAL | 1155.478 | 56.905 | 1610.543 | 597.084 | 356.016 |  | 11.664 | 8.85 | [6 empty] | TOTAL | 1440.52 | 1467.26 | 1455.59 |  |  | 1171.62 | 1272.67 | 1222.16 | CONDUCTIVITY (MONTHLY AVERAGE) | 16726 | 46980 | 43625 |  | 4200 |  | umho/cm | [33 empty] | Signature |  |  |  |  | item #2 | 52.6497 | 51.6513 | 52.8907 | 37.4543 | 50.0137
| AVERAGE | 38.5159 | 1.8968 | 53.6848 | 19.9028 | 11.8672 | 30.81% | 0.44862 | 0.295 | [6 empty] | AVERAGE | 48.0173 | 48.9087 | 48.5197 |  |  | 39.054 | 42.4223 | 40.7387 | FECAL COLIFORM (MONTHLY AVERAGE) | 0 | 0 | 0 |  | 0 |  | # col/100ml | [12 empty] | Signed: ____________________________ Date: ___________________ | [20 empty] | Title |  |  |  |  | item #3 | 37.5 | 38.1 | 38.2 | 38.4 | 38.2
[16 empty] | MAXIMUM | 48.72 | 49.08 | 48.93 |  |  | 42.56 | 42.77 | 42.59 | TEMPERATURE (MONTHLY AVERAGE) | 72.6 | 70.2 | 69 |  | 68 |  | deg. F | [33 empty] | Date |  |  |  | item #1 | =monthly maximum of the daily flows (MG), with peakhour flow (MGD) on the day of the month with maximum flow = | [14 empty] | 2.498 | MG/hour multiplied by
[16 empty] | MINIMUM | 45.35 | 48.6 | 46.63 |  |  | 28.11 | 41.92 | 32.31 | TOTAL PHOSPHOROUS (MONTHLY AVG.) | 0.042 | 0.042 | 0.04125 |  | 0.05 |  | mg/l | [12 empty] | Name: Michael A. Just | [14 empty] | * Sludge Reports should be submitted along with the monthly operating reports to Broward County Department | [10 empty] | the % of average % of TOTAL RAW FLOW to each Injection well.
[25 empty] | SULFATE (MONTHLY AVERAGE) | 790 | 2440 | 2350 |  | 1500 |  | mg/l | [27 empty] | of Natural Resource Protection, 218 S. W. 1st Avenue, Fort Lauderdale, Florida 33301 | [9 empty] | item #2 | =monthly average injection well pressure at injection well (psig)
[25 empty] | C.O.D. (MONTHLY AVERAGE) | 272 | 848 | 782.5 |  | 570 |  | mg/l | [12 empty] | Company Name: City of Fort Lauderdale Telephone No. (954) 523-1002 | [24 empty] | item #3 | =monthly wellhead pressure with no flow (shut-in pressure,psig)
[25 empty] | IRON (MONTHLY AVERAGE) | 0.016 | 0.036 | 0.0325 |  | 0.07 |  | mg/l | [37 empty] | PLANT STAFFING
[5 empty] | PAGE 2 | [19 empty] | SULFIDE (MONTHLY AVERAGE) | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! |  | mg/l | [37 empty] | Day Shift Operator |  |  | Class: | "A" | Certificate No. | 4545 | Name: |  | McGEARY, J.
[70 empty] | Evening Shift Operator |  |  | Class: | "A" | Certificate No. | 4474 | Name: |  | BAYLER, J.
[20 empty] | PAGE 20 | [49 empty] | Night Shift Operator |  |  | Class: | "A" | Certificate No. | 3207 | Name: |  | HOSTNICK, N.
[70 empty] | Lead Operator |  |  | Class: | "A" | Certificate No. | 2769 | Name: |  | JUST, M.
[70 empty] | Type of Effluent Disposal or Reclaimed Water Reuse: |  |  |  |  | DEEPWELL INJECTION
[70 empty] | Permited Wet Weather Discharge Activated: |  |  |  | YES: |  | NO: |  |  | Not Applicable |  | X
If Yes, cumulative days of wet weather:
Attach additional sheets if necessary to list all certified operators. See page 1 "COVER PAGE" of supplental attachements.
DEP form 62-620.910(10), effective November 29, 1994
[19 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [46 empty] | Department of Natural Resource Protection
[5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [13 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [46 empty] | Division of Pollution Prevention and Remediation Programs
[5 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [13 empty] | MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING | [49 empty] | 218 S. W. 1st Avenue
[5 empty] | MONTHLY OPERATIONAL REPORT | [13 empty] | MONITORING WELL TWO |  |  |  | 7/21/97 thru 7/21/02 | [38 empty] | SLUDGE HAULERS MONTHLY REPORT | [6 empty] | Fort Lauderdale, FL 33301
[5 empty] | INFLUENT DATA | [11 empty] | MW-2 | I.D. #: 5066A11308 & 09 |  |  | PERMIT/CERT. #: UO-06-279401 & 508 | [40 empty] | BROWARD COUNTY CODE SECTION 27-356 (d)(4)(1) | [5 empty] | Tel. No. (954) 523-1002
| RUN DATE | [14 empty] | RUN DATE | [51 empty] | *FAX (954) 519-1245
| 2026-07-30 | [14 empty] | 2026-07-30 |  | UPPER MONITOR ZONE |  |  |  |  | LOWER MONITOR ZONE
[17 empty] | MIN | MAX | AVG |  |  | MIN | MAX | AVG | [34 empty] | Plant Name: | GEORGE T. LOHMEYER WASTEWATER TREATMENT FACILITY
| SEPTEMBER | RAW | RAW TSS | RAW SS | RAW | RAW | RAW | RAW | RAW | RAW | [5 empty] | SEPTEMBER | FT HEAD | FT HEAD | FT HEAD |  |  | FT HEAD | FT HEAD | FT HEAD | [34 empty] | Address: | 1765 S.E. 18th Street at Eisenhower Boulevard | [6 empty] | MONTH: | SEPTEMBER
| 2003 | CBOD | TOTAL | FIXED | COD | pH | CL_ | ALK. | H2S | TEMP.(F) | [5 empty] | 2003 | ABOVE | ABOVE | ABOVE |  |  | ABOVE | ABOVE | ABOVE | [34 empty] | Phone: | (954) 523-1002 * FAX (954) 468-1577 | [6 empty] | YEAR: | 2003
[17 empty] | NGVD | NGVD | NGVD |  |  | NGVD | NGVD | NGVD
| 1 | 66 | 72 | 10 |  | 7.2 | 620 | 194 | 5 | 81 | [5 empty] | 1 | ER | ER | ER |  |  | 30.56 | 42.53 | 34.19 | [34 empty] | a) | WEEK OF | SEPTEMBER |  | Type of Sludge |  |  | Disopsal Site |  |  | Cubic Yards
| 2 | 84 | 76 | 12 |  | 7.2 | 600 | 196 | 3 | 80 | [5 empty] | 2 | ER | ER | ER |  |  | 30.48 | 42.12 | 38.75
| 3 | 65 | 100 | 20 | 242 | 7.2 | 580 | 216 | 3 | 81 | [5 empty] | 3 | ER | ER | ER |  |  | 42.09 | 42.33 | 42.29 | [35 empty] | FIRST THRU SEVENTH |  |  | GRIT |  |  | Central Landfill |  |  | 0
| 4 | 93 | 100 | 20 | 216 | 7.2 | 570 | 206 | 3 | 81 | [5 empty] | 4 | ER | ER | ER |  |  | 42.28 | 42.52 | 42.4
| 5 | 73.1 | 114 | 12 | 224 | 7.2 | 570 | 224 | 5 | 81 | [5 empty] | 5 | ER | ER | ER |  |  | 42.42 | 42.64 | 42.5 | [35 empty] | EIGHT THRU FORTEENTH |  |  | GRIT |  |  | Central Landfill |  |  | 0
| 6 | 62.2 | 108 | 22 | 223 | 7.3 | 520 | 214 | 3 | 81 | [5 empty] | 6 | ER | ER | ER |  |  | 42.5 | 42.71 | 42.53 | [35 empty] | FIFTHTEENTH THRU
| 7 | 60.6 | 78 | 12 | 270 | 7.3 | 500 | 212 | 4 | 82 | [5 empty] | 7 | ER | ER | ER |  |  | 42.6 | 42.81 | 42.69 | [35 empty] | TWENTY SECOND |  |  | GRIT |  |  | Central Landfill |  |  | 20
| 8 | 55 | 120 | 14 |  | 7.2 | 540 | 196 | 4 | 82 | [5 empty] | 8 | ER | ER | ER |  |  | 30.23 | 42.78 | 33.82 | [35 empty] | TWENTY THIRD THRU
| 9 | 59.1 | 88 | 12 |  | 7.3 | 630 | 198 | 4 | 81 | [5 empty] | 9 | ER | ER | ER |  |  | 30.23 | 42.37 | 38.67 | [35 empty] | THIRTY FIRST |  |  | GRIT |  |  | Central Landfill |  |  | 20
| 10 | 69.8 | 84 | 12 | 293 | 7.2 | 670 | 196 | 5 | 82 | [5 empty] | 10 | ER | ER | ER |  |  | 42.32 | 42.61 | 42.47
| 11 | 60 | 94 | 10 | 264 | 7.3 | 590 | 182 | 5 | 81 | [5 empty] | 11 | ER | ER | ER |  |  | 42.54 | 42.79 | 42.71 | [34 empty] | b) | WEEK OF | SEPTEMBER |  | Type of Sludge |  |  | Disopsal Site |  |  | Cubic Yards
| 12 | 115 | 84 | 10 | 247 | 7.2 | 630 | 164 | 6 | 82 | [5 empty] | 12 | ER | ER | ER |  |  | 42.71 | 42.84 | 42.85
| 13 | 54 | 88 | 14 | 229 | 7.2 | 610 | 196 | 5 | 82 | [5 empty] | 13 | ER | ER | ER |  |  | 42.77 | 42.86 | 42.86 | [35 empty] | FIRST THRU SEVENTH |  |  | RAGS |  |  | Central Landfill |  |  | 10
| 14 | 83 | 152 | 14 | 293 | 7.1 | 640 | 296 | 5 | 82 | [5 empty] | 14 | ER | ER | ER |  |  | 42.79 | 42.93 | 42.9
| 15 | 83 | 152 | 14 |  | 7.2 | 660 | 296 | 6 | 81 | [5 empty] | 15 | ER | ER | ER |  |  | 38.77 | 42.93 | 40.48 | [35 empty] | EIGHT THRU FORTEENTH |  |  | RAGS |  |  | Central Landfill |  |  | 0
| 16 | 53.9 | 98 | 8 |  | 7.1 | 640 | 178 | 6 | 81 | [5 empty] | 16 | ER | ER | ER |  |  | 38 | 42.68 | 41.4 | [35 empty] | FIFTHTEENTH THRU
| 17 | 79.8 | 84 | 14 | 294 | 7.1 | 620 | 220 | 7 | 82 | [5 empty] | 17 | ER | ER | ER |  |  | 42.67 | 42.83 | 42.84 | [35 empty] | TWENTY SECOND |  |  | RAGS |  |  | Central Landfill |  |  | 20
| 18 | 78 | 78 | 8 | 265 | 7 | 780 | 218 | 6 | 82 | [5 empty] | 18 | ER | ER | ER |  |  | 42.74 | 42.91 | 42.87 | [35 empty] | TWENTY THIRD THRU
| 19 | 60.8 | 98 | 2 | 255 | 7 | 740 | 208 | 6 | 82 | [5 empty] | 19 | ER | ER | ER |  |  | 42.73 | 42.89 | 42.88 | [35 empty] | THIRTY FIRST |  |  | RAGS |  |  | Central Landfill |  |  | 10
| 20 | 58.5 | 100 | 14 | 213 | 7 | 750 | 212 | 4 | 81 | [5 empty] | 20 | ER | ER | ER |  |  | 42.7 | 42.86 | 42.85 | [35 empty] | BCSR = Broward County Septage Receiving
| 21 | 68.9 | 66 | 12 | 302 | 7 | 720 | 210 | 6 | 82 | [5 empty] | 21 | ER | ER | ER |  |  | 42.68 | 42.86 | 42.83 | [34 empty] | c) | WEEK OF | SEPTEMBER |  | Type of Sludge |  |  | Disopsal Site |  |  | Gallons
| 22 | 57.3 | 44 | 10 |  | 7 | 730 | 208 | 6 | 82 | [5 empty] | 22 | ER | ER | ER |  |  | 30.51 | 42.84 | 34.32
| 23 | 61 | 94 | 16 |  | 7 | 730 | 206 | 6 | 82 | [5 empty] | 23 | ER | ER | ER |  |  | 30.08 | 30.61 | 30.5 | [35 empty] | FIRST THRU SEVENTH |  |  | VAC/Plastic & Rags |  |  | BCSR |  |  | 0
| 24 | 85 | 100 | 4 | 280 | 7 | 700 | 198 | 7 | 82 | [5 empty] | 24 | ER | ER | ER |  |  | 30.48 | 30.62 | 30.53
| 25 | 58 | 82 | 6 | 325 | 7.1 | 720 | 196 | 7 | 82 | [5 empty] | 25 | ER | ER | ER |  |  | 30.48 | 30.66 | 30.53 | [35 empty] | EIGHT THRU FORTEENTH |  |  | VAC/Plastic & Rags |  |  | BCSR |  |  | 0
| 26 | 57 | 96 | 4 | 187 | 7 | 680 | 196 | 7 | 82 | [5 empty] | 26 | ER | ER | ER |  |  | 30.58 | 30.75 | 30.69 | [35 empty] | FIFTHTEENTH THRU
| 27 | 47 | 78 | 6 | 193 | 7.1 | 700 | 198 | 5 | 82 | [5 empty] | 27 | ER | ER | ER |  |  | 30.65 | 30.78 | 30.7 | [35 empty] | TWENTY SECOND |  |  | VAC/Plastic & Rags |  |  | BSCR |  |  | 4500
| 28 | 50 | 84 | 12 | 196 | 7 | 730 | 208 | 3 | 82 | [5 empty] | 28 | ER | ER | ER |  |  | 30.64 | 30.87 | 30.78 | [35 empty] | TWENTY THIRD THRU
| 29 | 35 | 80 | 16 |  | 7 | 720 | 202 | 5 | 82 | [5 empty] | 29 | ER | ER | ER |  |  | 30.2 | 30.84 | 30.44 | [35 empty] | THIRTY FIRST |  |  | VAC/Plastic & Rags |  |  | BSCR |  |  | 0
| 30 | 28 | 60 | 12 |  | 7.1 | 730 | 200 | 4 | 82 | [5 empty] | 30 | ER | ER | ER |  |  | 30.09 | 42.17 | 38.59 | [34 empty] | TOTALS
[60 empty] | a) | 40 | cu.yds |  | GRIT |  | Signature
| TOTAL | 1961 | 2752 | 352 | 5011 | 213.8 | 19620 | 6244 | 151 | 2448 | [5 empty] | TOTAL | 0 | 0 | 0 |  |  | 1110.52 | 1196.94 | 1154.86 | [35 empty] | b) | 40 | cu.yds |  | RAGS |  | Title
| AVERAGE | 65.3667 | 91.7333 | 11.7333 | 250.55 | 7.1267 | 654 | 208.1333 | 5.0333 | 81.6 | [5 empty] | AVERAGE | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 37.0173 | 39.898 | 38.4953 | [35 empty] | c) | 4500 | gal. |  | VAC/Plastic & Rags |  | Date
[16 empty] | MAXIMUM | 0 | 0 | 0 |  |  | 42.79 | 42.93 | 42.9
[16 empty] | MINIMUM | 0 | 0 | 0 |  |  | 30.08 | 30.61 | 30.44 | [35 empty] | * Sludge Reports should be submitted along with the monthly operating reports to Broward County Department
of Natural Resource Protection, 218 S. W. 1st Avenue, Fort Lauderdale, Florida 33301
PAGE 3
PAGE 21
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
[5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [13 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
[5 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [13 empty] | MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
[5 empty] | MONTHLY OPERATIONAL REPORT | [13 empty] | MONITORING WELL THREE |  |  |  | 7/21/97 thru 7/21/02
[5 empty] | EFFLUENT DATA PART 1 | [11 empty] | MW-3 | I.D. #: 5066A11310 |  |  | PERMIT/CERT. #: UO-06-279510
RUN DATE
[16 empty] | 2026-07-30 |  | UPPER MONITOR ZONE |  |  |  |  | LOWER MONITOR ZONE
| RUN DATE | [15 empty] | MIN | MAX | AVG |  |  | MIN | MAX | AVG
| 2026-07-30 | [14 empty] | SEPTEMBER | FT HEAD | FT HEAD | FT HEAD |  |  | FT HEAD | FT HEAD | FT HEAD
[14 empty] | BOD | TSS | 2003 | ABOVE | ABOVE | ABOVE |  |  | ABOVE | ABOVE | ABOVE
| SEPTEMBER | EFFLUENT | EFFL. TSS | EFFL. SS | EFFLUENT | EFFL. | EFFL. | EFFL. | EFFL. | EFFL. | TDS |  |  | MONTHLY AVG OVER 30 | MONTHLY AVG OVER 30 |  | NGVD | NGVD | NGVD |  |  | NGVD | NGVD | NGVD
| 2003 | CBOD | TOTAL | FIXED | COD | CL_ | ALK. | TURB. | COND. | TEMP.(F) |  |  |  | 0 | 0 | 1 | 22.16 | 31.48 | 25 |  |  | 37.93 | 45.64 | 40.3
[14 empty] | WEKKLY OVER 45 | WEKKLY OVER 45 | 2 | 22.01 | 31.41 | 28.62 |  |  | 37.87 | 45.23 | 42.96
| 1 | 3.2 | 18 | 6 |  | 600 | 186 | 4.96 | 2390 | 85 | 1190 | 1 |  | 0 | 0 | 3 | 31.34 | 31.69 | 31.5 |  |  | 45.23 | 45.46 | 45.37
| 2 | 4.4 | 8 | 1 |  | 620 | 188 | 4.88 | 2280 | 85 | 1240 | 1 |  | SINGLE DAY OVER 60 | SINGLE DAY OVER 60 | 4 | 31.56 | 31.9 | 31.71 |  |  | 45.42 | 45.66 | 45.5
| 3 | 3.4 | 24 | 6 | 242 | 580 | 190 | 8.81 | 2160 | 84 | 1096 | 1 |  | 0 | 0 | 5 | 31.71 | 31.99 | 31.88 |  |  | 45.58 | 45.76 | 45.6
| 4 | 3 | 13 | 2 | 216 | 580 | 188 | 4.64 | 2210 | 84 | 1050 | 1 |  | 0 | 0 | 6 | 31.77 | 32.09 | 31.93 |  |  | 45.65 | 45.85 | 45.81
| 5 | 4.63 | 23 | 4 | 216 | 580 | 180 | 5.71 | 2180 | 84 | 1052 | 1 |  |  |  | 7 | 31.88 | 32.17 | 32 |  |  | 45.74 | 45.95 | 45.89
| 6 | 2.3 | 12 | 2 | 223 | 560 | 184 | 5.54 | 2200 | 84 | 1115 | 1 |  |  |  | 8 | 21.1 | 32.07 | 24.28 |  |  | 38.31 | 45.92 | 40.56
| 7 | 2.7 | 11 | 3 | 270 | 500 | 190 | 4.5 | 1983 | 84 | 1029 | 1 | 3.3757 | 3.3757 | 15.5714 | 9 | 21.04 | 31.62 | 28.32 |  |  | 38.31 | 45.5 | 43.3
| 8 | 2.7 | 10 | 2 |  | 510 | 192 | 4.69 | 2030 | 85 | 1062 | 1 |  | 3.3043 | 14.4286 | 10 | 31.51 | 31.85 | 31.75 |  |  | 45.47 | 45.75 | 45.5
| 9 | 3.08 | 8 | 1 |  | 600 | 192 | 5.22 | 2120 | 84 | 1010 | 1 |  | 3.1157 | 14.4286 | 11 | 31.7 | 31.99 | 31.85 |  |  | 45.7 | 45.92 | 45.86
| 10 | 3.3 | 24 | 5 | 48.5 | 580 | 190 | 4.55 | 2220 | 84 | 1189 | 1 |  | 3.1014 | 14.4286 | 12 | 31.81 | 31.99 | 31.95 |  |  | 45.87 | 45.99 | 45.97
| 11 | 5 | 13 | 1 | 42.4 | 570 | 196 | 4.96 | 2290 | 87 | 1244 | 1 |  | 3.3871 | 14.4286 | 13 | 31.82 | 32 | 31.95 |  |  | 45.93 | 46.01 | 45.99
| 12 | 3 | 9 | 1 | 42.6 | 640 | 200 | 3.32 | 2500 | 84 | 1210 | 1 |  | 3.1543 | 12.4286 | 14 | 31.79 | 32.02 | 31.94 |  |  | 45.96 | 46.09 | 46
| 13 | 3.05 | 10 | 2 | 58 | 610 | 188 | 4.66 | 2210 | 85 | 1270 | 1 |  | 3.2614 | 12.1429 | 15 | 17.43 | 32.02 | 22.83 |  |  | 39.37 | 46.09 | 41.93
| 14 | 3.1 | 12 | 4 | 43.3 | 650 | 192 | 4.58 | 2640 | 85 | 1270 | 1 | 3.3186 | 3.3186 | 12.2857 | 16 | 17.32 | 31.48 | 27.44 |  |  | 39.32 | 45.74 | 43.81
| 15 | 3.1 | 12 | 4 |  | 650 | 192 | 4.58 | 2640 | 84 | 1294 | 1 |  | 3.3757 | 12.5714 | 17 | 31.4 | 31.72 | 31.54 |  |  | 45.74 | 45.93 | 45.87
| 16 | 6.14 | 7 | 1 |  | 630 | 196 | 4.62 | 2650 | 85 | 1335 | 1 |  | 3.8129 | 12.4286 | 18 | 31.52 | 31.8 | 31.61 |  |  | 45.84 | 46.03 | 45.93
| 17 | 3.71 | 17 | 4 | 54 | 650 | 196 | 5.39 | 2630 | 85 | 1315 | 1 |  | 3.8714 | 11.4286 | 19 | 31.53 | 31.78 | 31.61 |  |  | 45.85 | 46.02 | 45.94
| 18 | 5 | 13 | 1 | 45.4 | 700 | 198 | 5.56 | 2660 | 85 | 1298 | 1 |  | 3.8714 | 11.4286 | 20 | 31.49 | 31.75 | 31.6 |  |  | 45.84 | 45.99 | 45.95
| 19 | 4.53 | 11 | 1 | 52.2 | 730 | 182 | 6.23 | 2680 | 85 | 1308 | 1 |  | 4.09 | 11.7143 | 21 | 31.5 | 31.78 | 31.61 |  |  | 45.82 | 46 | 45.94
| 20 | 3.4 | 11 | 2 | 21.2 | 730 | 188 | 5.34 | 2610 | 85 | 1385 | 1 |  | 4.14 | 11.8571 | 22 | 21.75 | 31.71 | 24.87 |  |  | 37.45 | 45.97 | 40.08
| 21 | 3.27 | 17 | 4 | 58.8 | 720 | 190 | 5.91 | 2680 | 85 | 1346 | 1 | 4.1643 | 4.1643 | 12.5714 | 23 | 21.74 | 31.6 | 28.51 |  |  | 37.45 | 44.99 | 42.71
| 22 | 3.77 | 8 | 1 |  | 710 | 188 | 5.03 | 2750 | 85 | 1393 | 1 |  | 4.26 | 12 | 24 | 31.49 | 31.84 | 31.69 |  |  | 44.93 | 45.18 | 45
| 23 | 3.5 | 11 | 2 |  | 730 | 188 | 4.66 | 2820 | 85 | 1432 | 1 |  | 3.8829 | 12.5714 | 25 | 31.65 | 31.94 | 31.8 |  |  | 45.07 | 45.25 | 45.11
| 24 | 4.2 | 12 | 1 | 56.8 | 680 | 184 | 5.28 | 2840 | 85 | 1403 | 1 |  | 3.9529 | 11.8571 | 26 | 31.75 | 32.05 | 31.93 |  |  | 45.17 | 45.36 | 45.36
| 25 | 4 | 12 | 2 | 52.6 | 690 | 182 | 5.35 | 2860 | 85 | 1650 | 1 |  | 3.81 | 11.7143 | 27 | 31.83 | 32.1 | 31.96 |  |  | 45.27 | 45.4 | 45.4
| 26 | 4 | 10 | 1 | 52.6 | 690 | 180 | 5.47 | 2800 | 85 | 1410 | 1 |  | 3.7343 | 11.5714 | 28 | 31.92 | 32.18 | 32.04 |  |  | 45.31 | 45.45 | 45.44
| 27 | 3 | 10 | 1 | 62.4 | 680 | 184 | 5.4 | 2810 | 85 | 1186 | 1 |  | 3.6771 | 11.4286 | 29 | 21.66 | 32.13 | 24.6 |  |  | 38.94 | 45.39 | 40.78
| 28 | 4 | 18 | 4 | 58 | 690 | 192 | 9.8 | 2420 | 85 | 1240 | 1 |  | 3.7814 | 11.5714 | 30 | 21.48 | 31.82 | 28.57 |  |  | 38.85 | 45.38 | 43.38
| 29 | 5 | 16 | 4 |  | 710 | 190 | 8.4 | 2460 | 84 | 1261 | 1 |  | 3.9571 | 12.7143
| 30 | 4 | 10 | 2 |  | 720 | 192 | 9.57 | 2280 | 84 | 1125 | 1 |  | 4.0286 | 12.5714 | TOTAL | 840.66 | 955.97 | 898.89 |  |  | 1295.19 | 1370.9 | 1333.24
[12 empty] | 0 | 3.9411 | 4 | 12.6667 | AVERAGE | 28.022 | 31.8657 | 29.963 |  |  | 43.173 | 45.6967 | 44.4413
| TOTAL | 111.48 | 390 | 75 | 1915.8 | 19290 | 5678 | 167.61 | 74003 | 2541 | 37408 |  |  |  |  | MAXIMUM | 31.92 | 32.18 | 32.04 |  |  | 45.96 | 46.09 | 46
| AVERAGE | 3.716 | 13 | 2.5 | 95.79 | 643 | 189.2667 | 5.587 | 2466.7667 | 84.7 | 1246.9333 |  |  | 3.6971 | 12.5924 | MINIMUM | 17.32 | 31.41 | 22.83 |  |  | 37.45 | 44.99 | 40.08
| MAXIMUM | 6.14 | 24
[5 empty] | PAGE 4 | [14 empty] | PAGE 22
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
[5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [13 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
[5 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [13 empty] | MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
[5 empty] | MONTHLY OPERATIONAL REPORT | [13 empty] | REGIONAL MONITORING WELL ONE
[5 empty] | EFFLUENT DATA PART 2 | [13 empty] | RMW-1
[16 empty] | RUN DATE |  |  | UC06-249353
[16 empty] | 2026-07-30 |  | UPPER MONITOR ZONE |  |  |  |  | LOWER MONITOR ZONE
RUN DATE | [16 empty] | MIN | MAX | AVG |  |  | MIN | MAX | AVG
2026-07-30 | [15 empty] | SEPTEMBER | FT HEAD | FT HEAD | FT HEAD |  |  | FT HEAD | FT HEAD | FT HEAD
[16 empty] | 2003 | ABOVE | ABOVE | ABOVE |  |  | ABOVE | ABOVE | ABOVE
| SEPTEMBER | EFF. BACT. | EFF. BACT. | FREE | TOTAL | EFFL. | EFF PH | EFF PH | EFF. SAP | AVG. | [6 empty] | NGVD | NGVD | NGVD |  |  | NGVD | NGVD | NGVD
| 2003 | TOTAL | FECAL | CL2 | CL2 | pH | MIN | MAX | TEMP.(C) | BLK. | [5 empty] | 1 | 33.1 | 44.32 | 36.23 |  |  | 20.31 | 22.37 | 21.13
[16 empty] | 2 | 32.31 | 43.59 | 40.45 |  |  | 20.38 | 21.65 | 21.21
| 1 | 36 | 0 | 0 | 1 | 6.6 | 6.6 | 6.6 | 6 | 28 | [5 empty] | 3 | 43.57 | 43.84 | 43.71 |  |  | 21.65 | 21.93 | 21.79
| 2 | 0 | 0 | 0 | 1 | 6.6 | 6.5 | 6.5 | 6 | 35 | [5 empty] | 4 | 43.82 | 44.02 | 43.91 |  |  | 21.89 | 22.13 | 22.02
| 3 | 3600 | 0 | 0 | 9 | 6.6 | 6.5 | 6.7 | 7 | 27 | [5 empty] | 5 | 44 | 44.19 | 44.08 |  |  | 22.09 | 22.31 | 22.19
| 4 | 1083 | 9 | 0 | 1.2 | 6.6 | 6.5 | 6.6 | 0 | 26 | [5 empty] | 6 | 44.16 | 44.29 | 44.23 |  |  | 22.21 | 22.38 | 22.3
| 5 | 0 | 0 | 0 | 1.3 | 6.6 | 6.6 | 6.6 | 8 | 24 | [5 empty] | 7 | 44.24 | 44.39 | 44.31 |  |  | 22.29 | 22.43 | 22.36
| 6 | 616 | 0 | 0 | 1 | 6.6 | 6.6 | 6.6 | 8 | 31 | [5 empty] | 8 | 44.33 | 44.48 | 44.4 |  |  | 22.38 | 22.5 | 22.43
| 7 | 9 | 0 | 0 | 1 | 6.6 | 6.5 | 6.7 | 5 | 33 | [5 empty] | 9 | 44.38 | 44.52 | 44.46 |  |  | 22.4 | 22.49 | 22.45
| 8 | 9 | 0 | 0 | 1.1 | 6.6 | 6.5 | 6.7 | 5 | 31 | [5 empty] | 10 | 44.46 | 44.62 | 44.53 |  |  | 22.45 | 22.52 | 22.48
| 9 | 200 | 0 | 0 | 0.6 | 6.6 | 6.5 | 6.7 | 5 | 28 | [5 empty] | 11 | 44.54 | 44.7 | 44.63 |  |  | 22.5 | 22.6 | 22.55
| 10 | 62 | 9 | 0 | 1 | 6.6 | 6.6 | 6.8 | 5 | 25 | [5 empty] | 12 | 44.64 | 44.73 | 44.68 |  |  | 22.5 | 22.6 | 22.57
| 11 | 22500 | 40 | 0 | 1.1 | 6.6 | 6.6 | 6.7 | 7 | 22 | [5 empty] | 13 | 44.64 | 44.73 | 44.69 |  |  | 22.52 | 22.58 | 22.55
| 12 | 3900 | 54 | 0 | 1.1 | 6.6 | 6.6 | 6.7 | 7 | 23 | [5 empty] | 14 | 44.65 | 44.75 | 44.71 |  |  | 22.5 | 22.6 | 22.55
| 13 | 9 | 0 | 0 | 0.9 | 6.6 | 6.6 | 6.6 | 6 | 29 | [5 empty] | 15 | 44.71 | 44.83 | 44.78 |  |  | 22.54 | 22.67 | 22.6
| 14 | TNTC | TNTC | 0 | 1.1 | 6.6 | 6.6 | 6.6 | 5 | 23 | [5 empty] | 16 | 44.78 | 44.88 | 44.83 |  |  | 22.59 | 22.72 | 22.66
| 15 | 71 | 9 | 0 | 0.9 | 6.6 | 6.5 | 6.6 | 5 | 26 | [5 empty] | 17 | 44.82 | 44.9 | 44.86 |  |  | 22.62 | 22.74 | 22.68
| 16 | 71 | 9 | 0 | 0.9 | 6.6 | 6.5 | 6.6 | 5 | 23 | [5 empty] | 18 | 44.77 | 44.88 | 44.83 |  |  | 22.57 | 22.71 | 22.64
| 17 | 3500 | 0 | 0 | 0.9 | 6.6 | 6.5 | 6.6 | 5 | 17 | [5 empty] | 19 | 44.63 | 44.79 | 44.71 |  |  | 22.46 | 22.61 | 22.53
| 18 | TNTC | 464 | 0 | 0.8 | 6.6 | 6.5 | 6.7 | 5 | 18 | [5 empty] | 20 | 44.54 | 44.7 | 44.61 |  |  | 22.38 | 22.54 | 22.46
| 19 | 46500 | 71 | 0 | 0.9 | 6.6 | 6.5 | 6.7 | 5 | 17 | [5 empty] | 21 | 44.46 | 44.59 | 44.52 |  |  | 22.33 | 22.48 | 22.42
| 20 | 18 | 9 | 0 | 1 | 6.5 | 6.5 | 6.6 | 5 | 17 | [5 empty] | 22 | 44.43 | 44.55 | 44.49 |  |  | 22.34 | 22.51 | 22.42
| 21 | 3900 | 27 | 0 | 1 | 6.6 | 6.5 | 6.6 | 5 | 20 | [5 empty] | 23 | 44.43 | 44.52 | 44.47 |  |  | 22.39 | 22.5 | 22.45
| 22 | 440 | 0 | 0 | 0.8 | 6.6 | 6.4 | 6.6 | 5 | 22 | [5 empty] | 24 | 44.39 | 44.52 | 44.46 |  |  | 22.39 | 22.5 | 22.46
| 23 | 22000 | 9 | 0 | 0.7 | 6.6 | 6.5 | 6.6 | 5 | 22 | [5 empty] | 25 | 44.39 | 44.56 | 44.46 |  |  | 22.33 | 22.52 | 22.46
| 24 | 98 | 0 | 0 | 0.8 | 6.6 | 6.6 | 6.6 | 5 | 21 | [5 empty] | 26 | 44.44 | 44.58 | 44.51 |  |  | 22.47 | 22.55 | 22.52
| 25 | 6300 | 0 | 0 | 0.9 | 6.6 | 6.6 | 6.6 | 5 | 16 | [5 empty] | 27 | 44.45 | 44.55 | 44.51 |  |  | 22.49 | 22.56 | 22.52
| 26 | TNTC | 0 | 0 | 1.1 | 6.6 | 6.6 | 6.7 | 4 | 16 | [5 empty] | 28 | 44.43 | 44.56 | 44.5 |  |  | 22.48 | 22.59 | 22.54
| 27 | 223 | 0 | 0 | 0.5 | 6.6 | 6.6 | 6.7 | 5 | 23 | [5 empty] | 29 | 44.39 | 44.5 | 44.44 |  |  | 22.45 | 22.55 | 22.5
| 28 | TNTC | 18 | 0 | 0.2 | 6.6 | 6.5 | 6.7 | 5 | 22 | [5 empty] | 30 | 44.36 | 44.43 | 44.4 |  |  | 22.41 | 22.55 | 22.48
| 29 | TNTC | 72500 | 0 | 0.4 | 6.7 | 6.6 | 6.8 | 5 | 22
| 30 | TNTC | TNTC | 0 | 0.7 | 6.7 | 6.6 | 6.8 | 5 | 21 | [5 empty] | TOTAL | 1309.26 | 1335.51 | 1322.4 |  |  | 667.31 | 674.39 | 670.92
[16 empty] | AVERAGE | 43.642 | 44.517 | 44.08 |  |  | 22.2437 | 22.4797 | 22.364
| TOTAL | 115145 | 73228 | 0 | 34.9 | 198.1 | 196.3 | 199.6 | 159 | 708 | [5 empty] | MAXIMUM | 44.82 | 44.9 | 44.86 |  |  | 22.62 | 22.74 | 22.68
| AVERAGE | 4797.7083 | 2615.2857 | 0 | 1.1633 | 6.6033 | 6.5433 | 6.6533 | 5.129 | 23.6 | [5 empty] | MINIMUM | 32.31 | 43.59 | 36.23 |  |  | 20.31 | 21.65 | 21.13
[7 empty] | 6.4 | 6.8
[7 empty] | MIN | MAX
PAGE 5
PAGE 23
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
NUTRIENTS
RUN DATE
| 2026-07-30 |  | INFLUENT | [5 empty] | EFFLUENT
| SEPTEMBER | INFLUENT | INFLUENT | INFLUENT | INFLUENT |  | EFFL. | EFFL. | EFFL. | EFFL.
| 2003 | NH-3 | N03-N | TKN | TOT P |  | NH-3 | N03-N | TKN | TOT P
1
2
| 3 | 13 | 0.076 | 19 | 2.5 |  | 11 | 0.65 | 12 | 1.1
| 4 | 13 | 0.02 | 18 | 2.4 |  | 10 | 0.67 | 11 | 0.83
| 5 | 13 | 0.02 | 18 | 2.4 |  | 10 | 0.67 | 11 | 0.83
| 6 | 11 | 0.02 | 16 | 2.1 |  | 8.3 | 0.42 | 9.2 | 0.85
| 7 | 11 | 0.02 | 15 | 2.2 |  | 7.9 | 0.6 | 8.3 | 0.71
8
9
| 10 | 14 | 0.02 | 18 | 2.5 |  | 10 | 0.54 | 11 | 0.86
| 11 | 14 | 0.02 | 18 | 2.4 |  | 10 | 0.55 | 12 | 1.6
| 12 | 14.19 | 0.02 | 21.14 | 2.69 |  | 10.74 | 0.356 | 14.57 | 0.735
| 13 | 12.88 | 0.02 | 19.56 | 2.72 |  | 9.41 | 0.366 | 13.14 | 1.05
| 14 | 13.63 | 0.02 | 20.36 | 2.82 |  | 9.79 | 0.443 | 13.58 | 1.04
15
16
| 17 | 15 | 0.02 | 20.38 | 2.64 |  | 11.37 | 0.444 | 15.16 | 1.06
| 18 | 13.94 | 0.02 | 18.68 | 2.37 |  | 11.81 | 0.467 | 15.44 | 1.02
| 19 | 14.53 | 0.02 | 20.99 | 2.68 |  | 11.58 | 0.411 | 15.45 | 0.772
| 20 | 13.62 | 0.02 | 19.52 | 1.53 |  | 11.11 | 0.382 | 14.76 | 0.72
| 21 | 14.19 | 0.02 | 20.21 | 1.82 |  | 11.03 | 0.439 | 14.84 | 0.72
22
23
| 24 | 13.82 | 0.217 | 20.55 | 2.72 |  | 10.5 | 0.38 | 14.94 | 1.03
| 25 | 14.59 | 0.242 | 21.61 | 2.66 |  | 11.67 | 0.482 | 15.91 | 1.19
| 26 | 14.81 | 0.303 | 19.53 | 2.2 |  | 11.57 | 0.371 | 15.72 | 1.24
| 27 | 13.39 | 0.264 | 19.27 | 2.07 |  | 10.15 | 0.193 | 14.57 | 1.34
| 28 | 10.88 | 0.268 | 17.5 | 2.03 |  | 8.04 | 0.477 | 12.36 | 1.25
29
30
| TOTAL | 268.47 | 1.65 | 381.3 | 47.45 | TOT. | 205.97 | 9.311 | 264.94 | 19.947
| AVERAGE | 13.4235 | 0.0825 | 19.065 | 2.3725 | AVG. | 10.2985 | 0.46555 | 13.247 | 0.99735
PAGE 6
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
REACTOR ONE PROCESS
RUN DATE
| 2026-07-30 |  | TRAIN "A" | [5 empty] | TRAIN "B"
| SEPTEMBER | MLSS | MLVSS | SS | SVI |  | MLSS | MLVSS | SS | SVI
| 2003 | "A" | "A" | "A" | "A" |  | "B" | "B" | "B" | "B"
| 1 | O/S | O/S | O/S |  |  | 1890 | 1550 | 18 | 95.2381
| 2 | O/S | O/S | O/S |  |  | 2380 | 1980 | 19 | 79.8319
| 3 | O/S | O/S | O/S |  |  | 2240 | 1860 | 19 | 84.8214
| 4 | O/S | O/S | O/S |  |  | 2270 | 1880 | 19 | 83.7004
| 5 | O/S | O/S | O/S |  |  | 1530 | 1320 | 21 | 137.2549
| 6 | O/S | O/S | O/S |  |  | 2250 | 1870 | 24 | 106.6667
| 7 | O/S | O/S | O/S |  |  | 2120 | 1760 | 21 | 99.0566
| 8 | O/S | O/S | O/S |  |  | 2480 | 2060 | 17 | 68.5484
| 9 | O/S | O/S | O/S |  |  | 1800 | 1500 | 19 | 105.5556
| 10 | O/S | O/S | O/S |  |  | 2200 | 1830 | 17 | 77.2727
| 11 | O/S | O/S | O/S |  |  | 2600 | 2170 | 17 | 65.3846
| 12 | O/S | O/S | O/S |  |  | 2100 | 1770 | 19 | 90.4762
| 13 | O/S | O/S | O/S |  |  | 2410 | 2000 | 23 | 95.4357
| 14 | O/S | O/S | O/S |  |  | 1970 | 1590 | 23 | 116.7513
| 15 | O/S | O/S | O/S |  |  | 1970 | 1590 | 23 | 116.7513
| 16 | O/S | O/S | O/S |  |  | 2230 | 1900 | 18 | 80.7175
| 17 | O/S | O/S | O/S |  |  | 1910 | 1580 | 17 | 89.0052
| 18 | O/S | O/S | O/S |  |  | 1770 | 1490 | 15 | 84.7458
| 19 | O/S | O/S | O/S |  |  | 2010 | 1720 | 19 | 94.5274
| 20 | O/S | O/S | O/S |  |  | 2110 | 1750 | 19 | 90.0474
| 21 | O/S | O/S | O/S |  |  | 2490 | 2070 | 22 | 88.3534
| 22 | O/S | O/S | O/S |  |  | 2460 | 2080 | 20 | 81.3008
| 23 | O/S | O/S | O/S |  |  | 1960 | 1630 | 18 | 91.8367
| 24 | O/S | O/S | O/S |  |  | 2280 | 1900 | 17 | 74.5614
| 25 | O/S | O/S | O/S |  |  | 1810 | 1450 | 13 | 71.8232
| 26 | O/S | O/S | O/S |  |  | 1910 | 1530 | 14 | 73.2984
| 27 | O/S | O/S | O/S |  |  | 1870 | 1510 | 14 | 74.8663
| 28 | O/S | O/S | O/S |  |  | 1620 | 1340 | 16 | 98.7654
| 29 | O/S | O/S | O/S |  |  | 1470 | 1220 | 13 | 88.4354
| 30 | O/S | O/S | O/S |  |  | 1350 | 1120 | 13 | 96.2963
|  | O/S | O/S | O/S
| TOTAL | 0 | 0 | 0 |  |  | 61460 | 51020 | 547
| AVERAGE | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 2048.6667 | 1700.6667 | 18.2333 | 89.001
PAGE 7
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
REACTOR TWO PROCESS
RUN DATE
| 2026-07-30 |  | TRAIN "C" | [5 empty] | TRAIN "D"
| SEPTEMBER | MLSS | MLVSS | SS | SVI |  | MLSS | MLVSS | SS | SVI
| 2003 | "C" | "C" | "C" | "C" |  | "D" | "D" | "D" | "D"
| 1 | O/S | O/S | O/S |  |  | 2060 | 1730 | 20 | 97.0874
| 2 | O/S | O/S | O/S |  |  | 2720 | 2260 | 19 | 69.8529
| 3 | O/S | O/S | O/S |  |  | 2420 | 2010 | 19 | 78.5124
| 4 | O/S | O/S | O/S |  |  | 2260 | 1880 | 19 | 84.0708
| 5 | O/S | O/S | O/S |  |  | 1900 | 1650 | 21 | 110.5263
| 6 | O/S | O/S | O/S |  |  | 2190 | 1820 | 23 | 105.0228
| 7 | O/S | O/S | O/S |  |  | 2620 | 2170 | 21 | 80.1527
| 8 | O/S | O/S | O/S |  |  | 2730 | 2290 | 19 | 69.5971
| 9 | O/S | O/S | O/S |  |  | 2420 | 1980 | 19 | 78.5124
| 10 | O/S | O/S | O/S |  |  | 2970 | 2430 | 17 | 57.2391
| 11 | O/S | O/S | O/S |  |  | 1000 | 940 | 19 | 190
| 12 | O/S | O/S | O/S |  |  | 1470 | 1260 | 20 | 136.0544
| 13 | O/S | O/S | O/S |  |  | 2240 | 1860 | 21 | 93.75
| 14 | O/S | O/S | O/S |  |  | 2280 | 1890 | 23 | 100.8772
| 15 | O/S | O/S | O/S |  |  | 2280 | 1890 | 23 | 100.8772
| 16 | O/S | O/S | O/S |  |  | 2150 | 1880 | 20 | 93.0233
| 17 | O/S | O/S | O/S |  |  | 1710 | 1390 | 18 | 105.2632
| 18 | O/S | O/S | O/S |  |  | 1870 | 1570 | 15 | 80.2139
| 19 | O/S | O/S | O/S |  |  | 1930 | 1620 | 20 | 103.6269
| 20 | O/S | O/S | O/S |  |  | 2190 | 1820 | 20 | 91.3242
| 21 | O/S | O/S | O/S |  |  | 2670 | 2240 | 22 | 82.397
| 22 | O/S | O/S | O/S |  |  | 2490 | 2120 | 20 | 80.3213
| 23 | O/S | O/S | O/S |  |  | 2880 | 2390 | 20 | 69.4444
| 24 | O/S | O/S | O/S |  |  | 2070 | 1650 | 18 | 86.9565
| 25 | O/S | O/S | O/S |  |  | 1900 | 1500 | 14 | 73.6842
| 26 | O/S | O/S | O/S |  |  | 1910 | 1520 | 14 | 73.2984
| 27 | O/S | O/S | O/S |  |  | 1810 | 1470 | 15 | 82.8729
| 28 | O/S | O/S | O/S |  |  | 1620 | 1360 | 16 | 98.7654
| 29 | O/S | O/S | O/S |  |  | 1460 | 1210 | 13 | 89.0411
| 30 | O/S | O/S | O/S |  |  | 1500 | 1240 | 13 | 86.6667
|  | O/S | O/S | O/S
| TOTAL | 0 | 0 | 0 |  |  | 63720 | 53040 | 561
| AVERAGE | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 2124 | 1768 | 18.7 | 88.0414
PAGE 8
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
RAS SUMMARY
RUN DATE
2026-07-30
| SEPTEMBER | R-1 | R-2 | TOTAL | F/M | TOTAL | SLUDGE | % TOT | % FIX | % VOL.
| 2003 | TOT. RAS | TOT. RAS | MLVSS | RATIO | MLSS | AGE | RAS | RAS | RAS
|  | MGD | MGD
| 1 | 3.953 | 6.099 | 3280 | 0.8655 | 3950 | 1.2755 | 0.52 | 25 | 75
| 2 | 5.606 | 6.155 | 4240 | 0.90002 | 5100 | 1.4771 | 0.98 | 22.4 | 77.6
| 3 | 4.637 | 6.245 | 3870 | 0.74315 | 4660 | 1.0532 | 0.92 | 22.1 | 77.9
| 4 | 5.172 | 6.806 | 3760 | 1.1267 | 4530 | 0.99447 | 0.92 | 20.6 | 79.4
| 5 | 5.339 | 7.149 | 2970 | 1.1483 | 3430 | 0.64489 | 0.92 | 23.5 | 76.5
| 6 | 5.333 | 7.164 | 3690 | 0.83972 | 4440 | 0.82525 | 0.92 | 23.9 | 76.1
| 7 | 4.618 | 7.307 | 3930 | 0.76107 | 4740 | 1.2312 | 0.87 | 22.3 | 77.7
| 8 | 4.258 | 6.749 | 4350 | 0.6188 | 5210 | 0.88712 | 0.87 | 22.1 | 77.9
| 9 | 5.396 | 6.501 | 3480 | 0.79685 | 4220 | 1.022 | 0.8 | 28.6 | 71.4
| 10 | 5.184 | 6.226 | 4260 | 0.74376 | 5170 | 1.3559 | 0.78 | 28.1 | 71.9
| 11 | 5.05 | 7.244 | 3110 | 0.84572 | 3600 | 0.87365 | 0.41 | 25.3 | 74.7
| 12 | 5.364 | 7.08 | 3030 | 1.7068 | 3570 | 0.94509 | 0.94 | 24.5 | 75.5
| 13 | 4.526 | 6.851 | 3860 | 0.62781 | 4650 | 1.1775 | 0.94 | 25.5 | 74.5
| 14 | 4.447 | 6.999 | 3480 | 1.0549 | 4250 | 0.63217 | 0.93 | 22.7 | 77.3
| 15 | 4.608 | 7.04 | 3480 | 1.0651 | 4250 | 0.62614 | 0.93 | 22.7 | 77.3
| 16 | 5.066 | 7.07 | 3780 | 0.62773 | 4380 | 1.0153 | 0.93 | 22.9 | 77.1
| 17 | 4.913 | 7.301 | 2970 | 1.1767 | 3620 | 0.98404 | 0.74 | 24.5 | 75.5
| 18 | 4.779 | 7.48 | 3060 | 0.81125 | 3640 | 1.4663 | 0.7 | 27 | 73
| 19 | 4.192 | 7.752 | 3340 | 0.78699 | 3940 | 0.92994 | 0.88 | 24.7 | 75.3
| 20 | 3.92 | 7.508 | 3570 | 0.68743 | 4300 | 1.025 | 0.85 | 26.3 | 73.7
| 21 | 3.969 | 7.928 | 4310 | 0.65878 | 5160 | 1.8972 | 0.72 | 27.3 | 72.7
| 22 | 4.135 | 7.258 | 4200 | 0.57005 | 4950 | 2.6924 | 0.55 | 28.9 | 71.1
| 23 | 4.15 | 7.269 | 4020 | 0.62039 | 4840 | 1.2594 | 0.7 | 27.1 | 72.9
| 24 | 4.232 | 6.808 | 3550 | 0.97045 | 4350 | 1.0733 | 0.76 | 29.4 | 70.6
| 25 | 4.804 | 7.062 | 2950 | 0.82764 | 3710 | 1.0748 | 0.64 | 29.3 | 70.7
| 26 | 5.317 | 7.28 | 3050 | 0.79822 | 3820 | 0.93163 | 0.8 | 27.1 | 72.9
| 27 | 5.038 | 7.017 | 2980 | 0.73721 | 3680 | 1.0094 | 0.64 | 24.6 | 75.4
| 28 | 5.365 | 7.52 | 2700 | 1.0293 | 3240 | 0.69397 | 0.82 | 24.1 | 75.9
| 29 | 6.35 | 6.62 | 2430 | 0.7976 | 2930 | 0.66138 | 0.76 | 25 | 75
| 30 | 5.817 | 6.991 | 2360 | 0.70895 | 2850 | 0.79492 | 0.76 | 24.8 | 75.2
| TOTAL | 145.538 | 210.479 | 104060 |  | 125180 |  | 23.9 | 752.3 | 2247.7
| AVERAGE | 4.8513 | 7.016 | 3468.6667 | 0.85392 | 4172.6667 | 1.0038 | 0.79667 | 25.0767 | 74.9233
PAGE 9
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
DEWATERING DATA
RUN DATE
| 2026-07-30 |  | FEED SLUDGE |  |  |  |  | FILTRATE RETURN
| SEPTEMBER | % TOT. | % FIX. | % VOL. | pH |  | % TOT. | % FIX. | % VOL. | pH
| 2003 | FEED | FEED | FEED |  |  | FILT. | FILT. | FILT.
| 1 | 1.08 | 25.9 | 74.1 | 6.9 |  | 0.45 | 33.3 | 66.7 | 7.34
| 2 | 0.9 | 25.6 | 74.4 | 6.84 |  | 0.41 | 34.1 | 65.9 | 7.24
| 3 | 1.23 | 21.1 | 78.9 | 6.81 |  | 0.53 | 28.3 | 71.7 | 7.18
| 4 | 1.53 | 19 | 81 | 6.78 |  | 0.43 | 30.2 | 69.8 | 7.2
5
6
| 7 | 0.9 | 24.4 | 75.6 | 6.79 |  | 0.31 | 35.5 | 64.5 | 7.19
| 8 | 1.42 | 19.7 | 80.3 | 6.78 |  | 0.26 | 42.3 | 57.7 | 7.47
| 9 | 1.49 | 20.8 | 79.2 | 6.79 |  | 0.23 | 56.5 | 43.5 | 7.24
| 10 | 1.43 | 21 | 79 | 6.64 |  | 0.3 | 43.3 | 56.7 | 7.37
| 11 | 1.56 | 19.2 | 80.8 | 6.68 |  | 0.36 | 36.1 | 63.9 | 7.33
12
13
| 14 | 1.5 | 20.7 | 79.3 | 6.47 |  | 0.27 | 51.8 | 48.2 | 7.28
| 15 | 1.5 | 20.7 | 79.3 | 6.47 |  | 0.27 | 51.9 | 48.1 | 7.28
| 16 | 1.44 | 20.8 | 79.2 | 6.49 |  | 0.28 | 46.4 | 53.6 | 7.14
| 17 | 0.97 | 24.7 | 75.3 | 6.53 |  | 0.29 | 48.3 | 51.7 | 7.14
18
19
20
| 21 | 1.5 | 21.3 | 78.7 | 6.36 |  | 0.23 | 60.9 | 39.1 | 7.34
| 22 | 0.78 | 29.5 | 70.5 | 6.33 |  | 0.27 | 48.1 | 51.9 | 7.26
| 23 | 1.21 | 24 | 76 | 6.79 |  | 0.32 | 34.4 | 65.6 | 7.21
| 24 | 1.42 | 23.2 | 76.8 | 6.51 |  | 0.35 | 42.9 | 57.1 | 7.19
| 25 | 1.04 | 38.5 | 61.5 | 6.5 |  | 0.37 | 43.2 | 56.8 | 7.19
26
27
| 28 | 1.19 | 22.7 | 77.3 | 6.74 |  | 0.3 | 43.3 | 56.7 | 7.21
| 29 | 0.62 | 30.6 | 69.4 | 6.78 |  | 0.3 | 46.7 | 53.3 | 7.24
| 30 | 1.51 | 25.2 | 74.8 | 6.78 |  | 0.31 | 48.4 | 51.6 | 7.2
| TOTAL | 26.22 | 498.6 | 1601.4 | 139.76 |  | 6.84 | 905.9 | 1194.1 | 152.24
| AVERAGE | 1.2486 | 23.7429 | 76.2571 | 6.6552 |  | 0.32571 | 43.1381 | 56.8619 | 7.2495
PAGE 10
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
SLUDGE VOLUME REMOVED
RUN DATE
2026-07-30
|  | SEPTEMBER | TRAILERS | TONS | DRY TONS | % LIME | % TOT. | % FIX. | % VOL.
|  | 2003 | REMOVED | SLUDGE | REMOVED | CAKE | CAKE | CAKE | CAKE
|  | 1 | 3 | 75 | 16.5732 |  | 17.32 | 16.2 | 83.8
|  | 2 | 5 | 125 | 20.2662 |  | 8.43 | 14.5 | 85.5
|  | 3 | 7 | 175 | 31.3901 |  | 18.4 | 17.7 | 82.3
|  | 4 | 6 | 150 | 33.1765 |  | 17.69 | 14.1 | 85.9
|  | 5 | 4 | 100
|  | 6 | 0 | 0
|  | 7 | 1 | 25 | 7.5811 |  | 17.57 | 14.7 | 85.3
|  | 8 | 6 | 150 | 29.3701 |  | 17.57 | 17.6 | 82.4
|  | 9 | 6 | 150 | 33.0548 |  | 18.07 | 14.9 | 85.1
|  | 10 | 6 | 150 | 32.9163 |  | 17.99 | 14.5 | 85.5
|  | 11 | 4 | 100 | 32.2007 |  | 17.86 | 14.22 | 85.78
|  | 12 | 4 | 100
|  | 13 | 0 | 0
|  | 14 | 1 | 25 | 11.5092 |  | 17.4 | 14.7 | 85.3
|  | 15 | 6 | 150 | 35.028 |  | 17.4 | 17.4 | 82.6
|  | 16 | 6 | 150 | 34.1073 |  | 18.65 | 16.2 | 83.8
|  | 17 | 6 | 150 | 22.8132 |  | 17.78 | 16.5 | 83.5
|  | 18 | 6 | 150
|  | 19 | 4 | 100
|  | 20 | 0 | 0
|  | 21 | 1 | 25 | 12.6976 |  | 16.44 | 16.1 | 83.9
|  | 22 | 6 | 150 | 17.9869 |  | 17.08 | 14.3 | 85.7
|  | 23 | 6 | 150 | 26.2376 |  | 18.45 | 15.8 | 84.2
|  | 24 | 4 | 100 | 29.5478 |  | 18.01 | 17.8 | 82.2
|  | 25 | 6 | 150 | 28.5795 |  | 18.99 | 18.3 | 81.7
|  | 26 | 4 | 100
|  | 27 | 0 | 0
|  | 28 | 1 | 25 | 11.711 |  | 18.14 | 14.3 | 85.7
|  | 29 | 6 | 150 | 15.2022 |  | 17.68 | 15.7 | 84.3
|  | 30 | 6 | 150 | 39.4173 |  | 18.98 | 15.8 | 84.2
|  | TOTAL | 121 | 3025 | 521.3668 | 0 | 365.9 | 331.32 | 1768.68
|  | AVERAGE | 4.0333 | 100.8333 | 24.827 | #DIV/0! | 17.4238 | 15.7771 | 84.2229
PAGE 11
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
CHEMICAL USEAGE
RUN DATE
2026-07-30
| SEPTEMBER | H2O2 | CL2 | POLYMER | POLYMER | LIME | GOX | O2 % | LOX | FPL
| 2003 | POUNDS | POUNDS | GALLONS | POUNDS | DELV. | TONS | PURITY | TONS | KW
| 1 | 2475 | 1280 | 15 | 125.1 | 0 | 21 | 99% | 143 | 31016
| 2 | 2215 | 1280 | 79 | 658.86 | 0 | 20.3 | 100% | 144 | 31045
| 3 | 2216 | 1180 | 83 | 692.22 | 0 | 19.3 | 100% | 144 | 30967
| 4 | 3254 | 1580 | 69 | 575.46 | 0 | 18.3 | 100% | 145 | 30974
| 5 | 2774 | 1540 | 0 | 0 | 0 | 18.9 | 99% | 144 | 31100
| 6 | 2624 | 1280 | 0 | 0 | 0 | 22.2 | 100% | 143 | 31110
| 7 | 2604 | 1360 | 17 | 141.78 | 0 | 23 | 100% | 143 | 31050
| 8 | 2355 | 1220 | 70 | 583.8 | 0 | 18.9 | 100% | 144 | 30931
| 9 | 2056 | 880 | 6 | 50.04 | 0 | 19.3 | 100% | 145 | 31004
| 10 | 1298 | 1060 | 62 | 517.08 | 0 | 23.9 | 99% | 145 | 31082
| 11 | 1581 | 1120 | 77 | 642.18 | 0 | 23.4 | 100% | 146 | ER
| 12 | 1188 | 1040 | 0 | 0 | 0 | 24.5 | 100% | 146 | 31097
| 13 | 1297 | 1200 | 0 | 0 | 0 | 24.6 | 100% | 144 | 30959
| 14 | 1398 | 1200 | 16 | 133.44 | 0 | 25.6 | 100% | 144 | 30962
| 15 | 1208 | 1140 | 56 | 467.04 | 0 | 26.1 | 100% | 145 | 30902
| 16 | 1178 | 1220 | 34 | 283.56 | 0 | 24.5 | 99% | 146 | 31011
| 17 | 958 | 960 | 45 | 375.3 | 0 | 24 | 99% | 146 | 31087
| 18 | 1258 | 940 | 34 | 283.56 | 0 | 23.4 | 100% | 147 | 31098
| 19 | 1187 | 1140 | 0 | 0 | 0 | 24 | 100% | 147 | 31200
| 20 | 2607 | 1160 | 42 | 350.28 | 0 | 23.8 | 100% | 146 | 31255
| 21 | 1070 | 1100 | 0 | 0 | 0 | 24.2 | 100% | 146 | 30887
| 22 | 1378 | 1060 | 64 | 533.76 | 0 | 24.1 | 100% | 147 | 30653
| 23 | 1108 | 980 | 33 | 275.22 | 0 | 24.4 | 100% | 148 | 31105
| 24 | 1547 | 1300 | 49 | 408.66 | 0 | 24.9 | 97% | 148 | 31055
| 25 | 1936 | 1140 | 53 | 442.02 | 0 | 29.5 | 99% | 148 | 29771
| 26 | 1796 | 1040 | 47 | 391.98 | 0 | 27 | 95% | 141 | 28326
| 27 | 5782 | 880 | 6 | 50.04 | 0 | 27.5 | 95% | 131 | 20546
| 28 | 1857 | 680 | 19 | 158.46 | 0 | 28 | 91% | 120 | 19649
| 29 | 1287 | 840 | 36 | 300.24 | 0 | 29.4 | 93% | 108 | 19734
| 30 | 2056 | 1180 | 49 | 408.66 | 0 | 24.6 | 96% | 103 | 19568
| TOTAL | 57548 | 33980 | 1061 | 8848.74 | 0 | 712.6 |  | 4237 | 851144
| AVERAGE | 1918.2667 | 1132.6667 | 35.3667 | 294.958 | 0 | 23.7533 | 98.7% | 141.2333 | 29349.7931
PAGE 12
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL ONE
|  | RUN DATE |  |  | PERMIT NUMBER UO-06-279401
|  | 2026-07-30 |  |  | 7/21/97 thru 7/21/02 |  |  | I.D. #:5006A11308
|  | SEPTEMBER | % INFL. | MAX | MIN | WELL 1 | MAX | MIN | AVG
|  | 2003 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 25.9% | 12.98 | 5.55 | 9.47 | 60.85 | 41.85 | 50.75
|  | 2 | 25.64% | 12.57 | 6.3 | 9.9 | 59.29 | 43.47 | 51.89
|  | 3 | 25.74% | 13.53 | 6.01 | 9.68 | 66.5 | 43.79 | 51.93
|  | 4 | 25.83% | 15.18 | 4.03 | 10 | 69.93 | 41.21 | 52.65
|  | 5 | 26.38% | 15.27 | 4.45 | 10.46 | 68.76 | 43.64 | 53.63
|  | 6 | 25.81% | 13.5 | 6.58 | 10.93 | 61.95 | 44.51 | 55
|  | 7 | 25.67% | 13.71 | 6.79 | 10.77 | 64.01 | 44.99 | 54.77
|  | 8 | 25.75% | 13.25 | 6.63 | 10.71 | 65.98 | 44.78 | 54.74
|  | 9 | 25.85% | 12.84 | 6.51 | 10.31 | 61.74 | 44.17 | 53.06
|  | 10 | 25.92% | 13.99 | 6.29 | 10 | 64.41 | 43.27 | 52.46
|  | 11 | 26.19% | 11.88 | 6.29 | 9.76 | 58.01 | 43.38 | 51.93
|  | 12 | 26.19% | 14.73 | 5.88 | 10.01 | 67.76 | 42.69 | 52.33
|  | 13 | 25.56% | 12.64 | 6.35 | 9.75 | 59.07 | 43.52 | 51.4
|  | 14 | 25.72% | 12.65 | 5.96 | 9.67 | 59.7 | 42.76 | 51.27
|  | 15 | 25.82% | 13.12 | 5.75 | 9.8 | 61.25 | 42.49 | 51.62
|  | 16 | 25.82% | 13.79 | 6.54 | 9.66 | 63.69 | 43.95 | 51.44
|  | 17 | 25.92% | 12.16 | 6.15 | 9.65 | 58.68 | 42.9 | 51.51
|  | 18 | 35.6% | 16.73 | 0.01 | 9.63 | 74.6 | 36.82 | 51.65
|  | 19 | 26.29% | 13.42 | 5.39 | 9.66 | 62.88 | 41.78 | 51.53
|  | 20 | 25.55% | 11.55 | 5.76 | 9.11 | 55.96 | 42.43 | 49.76
|  | 21 | 25.81% | 12.71 | 5.68 | 9.04 | 59.79 | 42.13 | 49.7
|  | 22 | 25.85% | 12.07 | 5.17 | 9.18 | 57.69 | 41.16 | 50.13
|  | 23 | 25.96% | 12.48 | 4.96 | 9.02 | 59.53 | 41.06 | 49.67
|  | 24 | 25.92% | 13.42 | 4.67 | 8.93 | 62.59 | 40.27 | 49.65
|  | 25 | 26.05% | 13.69 | 5.16 | 9.32 | 63.82 | 41.21 | 50.58
|  | 26 | 26.17% | 12 | 4.74 | 9.5 | 57.92 | 40.42 | 51.04
|  | 27 | 25.87% | 15.78 | 5.68 | 10.28 | 72.3 | 41.74 | 53.36
|  | 28 | 25.59% | 14.76 | 8.69 | 12.09 | 68.17 | 49.22 | 58.95
|  | 29 | 25.86% | 14.58 | 8.87 | 12.17 | 68.08 | 48.94 | 58.81
|  | 30 | 25.85% | 17.79 | 9.38 | 13.13 | 81.4 | 50.12 | 62.28
|  | TOTAL | 786.1% | 408.77 | 176.22 | 301.59 | 1916.31 | 1294.67 | 1579.49
|  | AVERAGE | 26.2% | 13.6257 | 5.874 | 10.053 | 63.877 | 43.1557 | 52.6497
|  | MAXIMUM | 35.6% | 17.79 | 9.38 | 13.13 | 81.4 | 50.12 | 62.28
|  | MINIMUM | 25.55% | 11.55 | 0.01 | 8.93 | 55.96 | 36.82 | 49.65
PAGE 13
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL TWO
|  | RUN DATE |  |  | PERMIT NUMBER UO-06-279508
|  | 2026-07-30 |  |  | 7/21/97 thru 7/21/02 |  |  | I.D. #:5006A11309
|  | SEPTEMBER | % INFL. | MAX | MIN | WELL 2 | MAX | MIN | AVG
|  | 2003 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 26.28% | 13.09 | 5.47 | 9.61 | 59.68 | 41.09 | 49.82
|  | 2 | 26.13% | 12.71 | 6.25 | 10.09 | 58.15 | 42.66 | 50.92
|  | 3 | 26.16% | 13.63 | 6.01 | 9.84 | 65.29 | 43 | 51.01
|  | 4 | 26.21% | 15.45 | 3.83 | 10.15 | 68.62 | 40.44 | 51.66
|  | 5 | 26.7% | 14.68 | 0.14 | 10.59 | 64.63 | 38.42 | 52.57
|  | 6 | 26.28% | 13.58 | 6.73 | 11.13 | 60.78 | 43.68 | 53.98
|  | 7 | 26.1% | 14.02 | 6.79 | 10.95 | 62.86 | 44.16 | 53.79
|  | 8 | 26.18% | 13.46 | 6.63 | 10.89 | 64.77 | 43.96 | 53.74
|  | 9 | 26.28% | 12.97 | 6.53 | 10.48 | 60.57 | 43.36 | 52.09
|  | 10 |  | 13.4 | ER | ER | 62.01 | 37.73 | 51.27
|  | 11 | 27.67% | 12.49 | 6.75 | 10.31 | 56.91 | 42.57 | 50.97
|  | 12 | 26.82% | 15.54 | ER | 10.25 | 66.46 | 41.88 | 51.34
|  | 13 | 27.05% | 13.25 | 6.74 | 10.32 | 57.98 | 42.7 | 50.44
|  | 14 | 27.26% | 13.33 | 6.29 | 10.25 | 73.1 | 41.96 | 50.29
|  | 15 | 27.24% | 13.77 | 6.14 | 10.34 | 60.11 | 41.71 | 50.63
|  | 16 | 27.34% | 14.47 | 6.98 | 10.23 | 62.45 | 43.11 | 50.47
|  | 17 | 27.27% | 12.76 | 6.54 | 10.15 | 57.53 | 42.09 | 50.53
|  | 18 | 37.11% | 17.54 | 0.13 | 10.04 | 73.1 | 37.53 | 50.46
|  | 19 | 27.84% | 14.07 | 5.79 | 10.23 | 61.68 | 41.02 | 50.58
|  | 20 | 27.12% | 12.13 | 6.08 | 9.67 | 54.96 | 41.65 | 48.83
|  | 21 | 27.49% | 13.35 | 6 | 9.63 | 58.69 | 41.37 | 48.78
|  | 22 | 27.45% | 12.57 | 5.44 | 9.75 | 56.6 | 40.42 | 49.2
|  | 23 | 27.57% | 13.16 | 5.11 | 9.58 | 58.41 | 40.3 | 48.74
|  | 24 | 27.49% | 14.08 | 4.87 | 9.47 | 61.42 | 39.52 | 48.73
|  | 25 | 27.61% | 14.36 | 5.34 | 9.88 | 62.59 | 40.44 | 49.62
|  | 26 | 27.76% | 12.7 | 4.9 | 10.08 | 56.81 | 39.67 | 50.07
|  | 27 | 27.43% | 16.56 | 6.15 | 10.9 | 70.9 | 40.94 | 52.35
|  | 28 | 26.95% | 15.46 | 9.34 | 12.73 | 66.93 | 48.28 | 57.86
|  | 29 | 27.15% | 15.38 | 9.42 | 12.78 | 66.83 | 48.01 | 57.72
|  | 30 | 27.07% | 18.57 | 9.97 | 13.75 | 79.8 | 49.18 | 61.08
|  | TOTAL | 793% | 422.53 | 166.36 | 304.07 | 1890.62 | 1262.85 | 1549.54
|  | AVERAGE | 27.35% | 14.0843 | 5.9414 | 10.4852 | 63.0207 | 42.095 | 51.6513
|  | MAXIMUM | 37.11% | 18.57 | 9.97 | 13.75 | 79.8 | 49.18 | 61.08
|  | MINIMUM | 26.1% | 12.13 | 0.13 | 9.47 | 54.96 | 37.53 | 48.73
PAGE 14
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL THREE
|  | RUN DATE |  |  | PERMIT NUMBER UO-06-279510
|  | 2026-07-30 |  |  | 7/21/97 thru 7/21/02 |  |  | I.D. #:5006A11310
|  | SEPTEMBER | % INFL. | MAX | MIN | WELL 3 | MAX | MIN | AVG
|  | 2003 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 23.08% | 11.48 | 4.77 | 8.44 | 61.17 | 41.96 | 51
|  | 2 | 22.89% | 11.19 | 5.48 | 8.84 | 59.67 | 43.63 | 52.12
|  | 3 | 22.95% | 11.95 | 5.33 | 8.63 | 66.9 | 43.95 | 52.17
|  | 4 | 23.14% | 13.7 | 3.37 | 8.96 | 70.3 | 41.33 | 52.87
|  | 5 | 23.73% | 13.59 | 2.78 | 9.41 | 69.08 | 43.09 | 54.01
|  | 6 | 23.14% | 11.99 | 5.82 | 9.8 | 62.31 | 44.67 | 55.28
|  | 7 | 23% | 12.34 | 6.02 | 9.65 | 64.45 | 45.16 | 55.07
|  | 8 | 23.08% | 11.88 | 5.88 | 9.6 | 66.34 | 44.96 | 54.99
|  | 9 | 23.14% | 11.42 | 5.76 | 9.23 | 62.15 | 44.33 | 53.35
|  | 10 | 23.22% | 12.51 | 5.56 | 8.96 | 64.69 | 43.41 | 52.7
|  | 11 | 23.46% | 10.69 | 5.54 | 8.74 | 58.34 | 43.51 | 52.15
|  | 12 | 23.47% | 13.35 | 5.13 | 8.97 | 68.21 | 42.81 | 52.57
|  | 13 | 22.86% | 11.3 | 5.57 | 8.72 | 59.45 | 43.65 | 51.61
|  | 14 | 22.98% | 11.35 | 5.18 | 8.64 | 59.98 | 42.88 | 51.46
|  | 15 | 23.05% | 11.79 | 5.02 | 8.75 | 61.62 | 42.61 | 51.87
|  | 16 | 23.04% | 12.36 | 5.79 | 8.62 | 64.09 | 44.1 | 51.65
|  | 17 | 23.1% | 10.83 | 5.37 | 8.6 | 58.96 | 43.05 | 51.74
|  | 18 | 31.86% | 14.73 | ER | 8.62 | 73.6 | 36.76 | 51.85
|  | 19 | 23.51% | 12.08 | 4.68 | 8.64 | 63.2 | 41.91 | 51.73
|  | 20 | 22.86% | 10.34 | 5.03 | 8.15 | 56.26 | 42.56 | 49.94
|  | 21 | 23.04% | 11.31 | 4.9 | 8.07 | 60.15 | 42.27 | 49.92
|  | 22 | 23.06% | 10.69 | 4.39 | 8.19 | 57.97 | 41.29 | 50.34
|  | 23 | 23.14% | 11.19 | 4.21 | 8.04 | 59.85 | 41.18 | 49.88
|  | 24 | 23.11% | 12.04 | 3.9 | 7.96 | 62.98 | 40.38 | 49.87
|  | 25 | 23.28% | 12.24 | 4.34 | 8.33 | 64.16 | 41.31 | 50.78
|  | 26 | 23.39% | 10.77 | 3.96 | 8.49 | 58.22 | 40.53 | 51.23
|  | 27 | 23.21% | 14.16 | 4.95 | 9.22 | 72.7 | 41.88 | 53.58
|  | 28 | 23.05% | 13.28 | 7.89 | 10.89 | 68.56 | 49.42 | 59.27
|  | 29 | 23.2% | 13.16 | 7.99 | 10.92 | 68.49 | 49.13 | 59.13
|  | 30 | 23.13% | 15.96 | 8.45 | 11.75 | 81.9 | 50.33 | 62.59
|  | TOTAL | 703.2% | 365.67 | 153.06 | 269.83 | 1925.75 | 1298.05 | 1586.72
|  | AVERAGE | 23.44% | 12.189 | 5.2779 | 8.9943 | 64.1917 | 43.2683 | 52.8907
|  | MAXIMUM | 31.86% | 15.96 | 8.45 | 11.75 | 81.9 | 50.33 | 62.59
|  | MINIMUM | 22.86% | 10.34 | 2.78 | 7.96 | 56.26 | 36.76 | 49.87
PAGE 15
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL FOUR
|  | RUN DATE |  |  | PERMIT NUMBER UC-06-264391 (IW-4)
2026-07-30
|  | SEPTEMBER | % INFL. | MAX | MIN | WELL 4 | MAX | MIN | AVG
|  | 2003 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 |  | ER | ER | ER | 38.55 | 36.63 | 37.64
|  | 2 |  | ER | ER | ER | 38.35 | 36.83 | 37.74
|  | 3 |  | ER | ER | ER | 39.01 | 36.99 | 37.83
|  | 4 |  | ER | ER | ER | 39.16 | 36.66 | 37.92
|  | 5 |  | ER | ER | ER | 38.89 | 37.13 | 38.01
|  | 6 |  | ER | ER | ER | 38.77 | 37.32 | 38.18
|  | 7 |  | ER | ER | ER | 38.95 | 37.39 | 38.17
|  | 8 |  | ER | ER | ER | 38.7 | 37.14 | 38.04
|  | 9 |  | ER | ER | ER | 38.59 | 36.95 | 37.8
|  | 10 |  | 11.86 | ER | ER | 38.61 | 36.75 | 37.66
|  | 11 |  | ER | ER | ER | 38.15 | 36.69 | 37.54
|  | 12 |  | ER | ER | ER | 38.78 | 36.48 | 37.5
|  | 13 |  | ER | ER | ER | 38.15 | 36.51 | 37.38
|  | 14 |  | ER | ER | ER | 64.41 | 36.33 | 37.27
|  | 15 |  | ER | ER | ER | 38.2 | 36.26 | 37.25
|  | 16 |  | ER | ER | ER | 38.08 | 36.34 | 37.2
|  | 17 |  | ER | ER | ER | 37.78 | 36.21 | 37.16
|  | 18 |  | ER | ER | ER | 38.41 | 35.95 | 37.11
|  | 19 |  | ER | ER | ER | 37.87 | 36.21 | 37.07
|  | 20 |  | ER | ER | ER | 37.36 | 36.1 | 36.84
|  | 21 |  | ER | ER | ER | 37.57 | 36.01 | 36.78
|  | 22 |  | ER | ER | ER | 37.54 | 35.95 | 36.88
|  | 23 |  | ER | ER | ER | 37.72 | 35.99 | 36.9
|  | 24 |  | ER | ER | ER | 38.11 | 35.91 | 36.92
|  | 25 |  | ER | ER | ER | 38.16 | 35.93 | 36.97
|  | 26 |  | ER | ER | ER | 37.75 | 35.75 | 37.02
|  | 27 |  | ER | ER | ER | 38.89 | 35.99 | 37.24
|  | 28 |  | ER | ER | ER | 38.71 | 36.73 | 37.8
|  | 29 |  | ER | ER | ER | 38.61 | 36.74 | 37.77
|  | 30 |  | ER | ER | ER | 39.81 | 36.92 | 38.04
|  | TOTAL | 0% | 11.86 | 0 | 0 | 1177.64 | 1094.79 | 1123.63
|  | AVERAGE | #DIV/0! | 11.86 | #DIV/0! | #DIV/0! | 39.2547 | 36.493 | 37.4543
|  | MAXIMUM | 0% | 11.86 | 0 | 0 | 64.41 | 37.39 | 38.18
|  | MINIMUM | 0% | 11.86 | 0 | 0 | 37.36 | 35.75 | 36.78
PAGE 16
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL FIVE
|  | RUN DATE |  |  | PERMIT NUMBER UO-06-279512
|  | 2026-07-30 |  |  | 7/21/97 thru 7/21/02 |  |  | I.D. #:5006A11311
|  | SEPTEMBER | % INFL. | MAX | MIN | WELL 5 | MAX | MIN | AVG
|  | 2003 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 23.28% | 11.41 | 5.11 | 8.51 | 61.18 | 32.51 | 48.37
|  | 2 | 23.02% | 11.04 | 5.8 | 8.89 | 59.06 | 30.87 | 49.73
|  | 3 | 23.08% | 11.92 | 5.58 | 8.68 | 57.9 | 33.53 | 49.12
|  | 4 | 23.09% | 13.4 | 3.53 | 8.94 | 64.46 | 29.29 | 50.11
|  | 5 | 23.1% | 13.15 | ER | 9.16 | 61.28 | 29.41 | 51.18
|  | 6 | 22.93% | 11.71 | 6.16 | 9.71 | 60.57 | 31.57 | 52.73
|  | 7 | 22.81% | 12.05 | 6.26 | 9.57 | 61.25 | 25.37 | 52.54
|  | 8 | 22.86% | 11.62 | 6.11 | 9.51 | 68.87 | 35.17 | 51.66
|  | 9 | 23.07% | 11.24 | 6 | 9.2 | 59.76 | 36.08 | 50.71
|  | 10 | 23.25% | 12.18 | 5.87 | 8.97 | 60.21 | 38.82 | 50.01
|  | 11 | 23.54% | 10.54 | 5.89 | 8.77 | 58.23 | 39.77 | 49.13
|  | 12 | 23.41% | 13.03 | 5.41 | 8.95 | 62 | 32.36 | 50.01
|  | 13 | 22.89% | 11.1 | 5.83 | 8.73 | 60.43 | 28.64 | 48.99
|  | 14 | 23.03% | 11.18 | 5.47 | 8.66 | 61.55 | 31.93 | 48.77
|  | 15 | 23.11% | 11.58 | 5.32 | 8.77 | 61.05 | 38.64 | 49.19
|  | 16 | 23.12% | 12.14 | 6.01 | 8.65 | 59.03 | 33.86 | 48.27
|  | 17 | 23.21% | 10.74 | 5.67 | 8.64 | 60.95 | 36.69 | 48.59
|  | 18 | 31.9% | 14.73 | ER | 8.63 | 73.1 | 36.61 | 48.67
|  | 19 | 23.67% | 11.93 | 5.13 | 8.7 | 58.18 | 29.05 | 48.31
|  | 20 | 23.02% | 10.25 | 5.3 | 8.21 | 56.71 | 25.54 | 47.27
|  | 21 | 23.3% | 11.22 | 5.23 | 8.16 | 58.49 | 37.2 | 47.31
|  | 22 | 23.26% | 10.57 | 4.81 | 8.26 | 57.88 | 34.8 | 47.24
|  | 23 | 23.39% | 11.08 | 4.55 | 8.13 | 58.35 | 26.85 | 47.16
|  | 24 | 23.37% | 11.84 | 4.32 | 8.05 | 61.57 | 20.75 | 47.11
|  | 25 | 23.42% | 12.11 | 4.7 | 8.38 | 59.64 | 23.63 | 47.85
|  | 26 | 23.5% | 10.67 | 2.79 | 8.53 | 61.12 | 28.6 | 48.09
|  | 27 | 23.13% | 13.94 | 5.29 | 9.19 | 65.68 | 23.01 | 49.83
|  | 28 | 22.67% | 13.02 | 7.9 | 10.71 | 68.26 | 44.96 | 55.18
|  | 29 | 22.84% | 12.93 | 8 | 10.75 | 65.49 | 40.55 | 56.51
|  | 30 | 22.74% | 15.58 | 8.41 | 11.55 | 81.2 | 33.63 | 60.77
|  | TOTAL | 703% | 359.9 | 156.45 | 269.56 | 1863.45 | 969.69 | 1500.41
|  | AVERAGE | 23.43% | 11.9967 | 5.5875 | 8.9853 | 62.115 | 32.323 | 50.0137
|  | MAXIMUM | 31.9% | 15.58 | 8.41 | 11.55 | 81.2 | 44.96 | 60.77
|  | MINIMUM | 22.67% | 10.25 | 2.79 | 8.05 | 56.71 | 20.75 | 47.11
PAGE 17
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
INJECTION WELL SUMMARY
RUN DATE
2026-07-30
| SEPTEMBER | INFLUENT | EFFLUENT | EFFLUENT | IW-1 | IW-2 | IW-3 | IW-4 | IW-5 | TOTAL
| 2003 | FLOW | FLOW | SS | LBS SS | LBS SS | LBS SS | LBS SS | LBS SS | LBS SS
|  | MGD | MGD
| 1 | 36.561 | 36.065 | 18 | 1421.6364 | 1442.6532 | 1267.0128 |  | 1277.5212 | 5408.8236
| 2 | 38.615 | 37.775 | 8 | 660.528 | 673.2048 | 589.8048 |  | 593.1408 | 2516.6784
| 3 | 37.609 | 36.979 | 24 | 1937.5488 | 1969.5744 | 1727.3808 |  | 1737.3888 | 7371.8928
| 4 | 38.719 | 38.033 | 13 | 1084.2 | 1100.463 | 971.4432 |  | 969.2748 | 4125.381
| 5 | 39.657 | 39.5 | 23 | 2006.4372 | 2031.3738 | 1805.0262 |  | 1757.0712 | 7599.9084
| 6 | 42.344 | 41.574 | 12 | 1093.8744 | 1113.8904 | 980.784 |  | 971.7768 | 4160.3256
| 7 | 41.953 | 40.927 | 11 | 988.0398 | 1004.553 | 885.291 |  | 877.9518 | 3755.8356
| 8 | 41.6 | 40.838 | 10 | 893.214 | 908.226 | 800.64 |  | 793.134 | 3395.214
| 9 | 39.883 | 39.198 | 8 | 687.8832 | 699.2256 | 615.8256 |  | 613.824 | 2616.7584
| 10 | 38.584 | 36.851 | 24 | 2001.6 |  | 1793.4336 |  | 1795.4352
| 11 | 37.261 | 37.245 | 13 | 1058.1792 | 1117.8102 | 947.5908 |  | 950.8434 | 4074.4236
| 12 | 38.224 | 38.155 | 9 | 751.3506 | 769.365 | 673.2882 |  | 671.787 | 2865.7908
| 13 | 38.145 | 37.658 | 10 | 813.15 | 860.688 | 727.248 |  | 728.082 | 3129.168
| 14 | 37.595 | 37.285 | 12 | 967.7736 | 1025.82 | 864.6912 |  | 866.6928 | 3724.9776
| 15 | 37.957 | 37.702 | 12 | 980.784 | 1034.8272 | 875.7 |  | 877.7016 | 3769.0128
| 16 | 37.419 | 37.297 | 7 | 563.9508 | 597.2274 | 503.2356 |  | 504.987 | 2169.4008
| 17 | 37.225 | 37.08 | 17 | 1368.177 | 1439.067 | 1219.308 |  | 1224.9792 | 5251.5312
| 18 | 27.052 | 36.952 | 13 | 1044.0846 | 1088.5368 | 934.5804 |  | 935.6646 | 4002.8664
| 19 | 36.748 | 37.254 | 11 | 886.2084 | 938.5002 | 792.6336 |  | 798.138 | 3415.4802
| 20 | 35.658 | 35.3 | 11 | 835.7514 | 887.1258 | 747.681 |  | 753.1854 | 3223.7436
| 21 | 35.028 | 34.992 | 17 | 1281.6912 | 1365.3414 | 1144.1646 |  | 1156.9248 | 4948.122
| 22 | 35.516 | 35.45 | 8 | 612.4896 | 650.52 | 546.4368 |  | 551.1072 | 2360.5536
| 23 | 34.752 | 34.879 | 11 | 827.4948 | 878.8692 | 737.5896 |  | 745.8462 | 3189.7998
| 24 | 34.451 | 34.516 | 12 | 893.7144 | 947.7576 | 796.6368 |  | 805.644 | 3443.7528
| 25 | 35.781 | 35.846 | 12 | 932.7456 | 988.7904 | 833.6664 |  | 838.6704 | 3593.8728
| 26 | 36.305 | 36.642 | 10 | 792.3 | 840.672 | 708.066 |  | 711.402 | 3052.44
| 27 | 39.731 | 39.307 | 10 | 857.352 | 909.06 | 768.948 |  | 766.446 | 3301.806
| 28 | 47.244 | 46.399 | 18 | 1814.9508 | 1911.0276 | 1634.8068 |  | 1607.7852 | 6968.5704
| 29 | 47.07 | 46.498 | 16 | 1623.9648 | 1705.3632 | 1457.1648 |  | 1434.48 | 6220.9728
| 30 | 50.791 | 49.933 | 10 | 1095.042 | 1146.75 | 979.95 |  | 963.27 | 4185.012
| TOTAL | 1155.478 | 1154.13 | 390 | 32776.1166 | 32046.2832 | 29330.0286 | 0 | 29280.1554 | 117842.115
| AVERAGE | 38.5159 | 38.471 | 13 | 1092.5372 | 1105.0442 | 977.6676 | #DIV/0! | 976.0052 | 4063.5212
PAGE 18
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
| RUN DATE |  |  |  | SOLIDS REMOVAL INVENTORY DATA SHEET
2026-07-30
| SEPTEMBER | TONS | CAKE |  |  |  | SEPTEMBER | RAGS | GRIT | OTHER
| 2003 | SLUDGE | TSS |  |  |  | 2003 |  |  | (vac)
| 1st - 7th | [5 empty] | 1st - 7th
| 1 | 75 | 17.32 |  |  |  | 1
| 2 | 125 | 8.43 |  |  |  | 2
| 3 | 175 | 18.4 |  |  |  | 3
| 4 | 150 | 17.69 |  |  |  | 4
| 5 | 100 |  |  |  |  | 5 | 10
| 6 | 0 |  |  |  |  | 6
| 7 | 25 | 17.57 |  |  |  | 7
| TOTAL = | 650 | 15.882 | = AVG. |  |  | TOTAL = | 10 | 0 | 0
| 8th - 14th | [5 empty] | 8th - 14th
| 8 | 150 | 17.57 |  |  |  | 8
| 9 | 150 | 18.07 |  |  |  | 9
| 10 | 150 | 17.99 |  |  |  | 10
| 11 | 100 | 17.86 |  |  |  | 11
| 12 | 100 |  |  |  |  | 12
| 13 | 0 |  |  |  |  | 13
| 14 | 25 | 17.4 |  |  |  | 14
| TOTAL = | 675 | 17.778 | = AVG. |  |  | TOTAL = | 0 | 0 | 0
| 15th - 22nd | [5 empty] | 15th-22nd
| 15 | 150 | 17.4 |  |  |  | 15 | 10
| 16 | 150 | 18.65 |  |  |  | 16
| 17 | 150 | 17.78 |  |  |  | 17
| 18 | 150 |  |  |  |  | 18 |  |  | 4500
| 19 | 100 |  |  |  |  | 19 | 10 | 10
| 20 | 0 |  |  |  |  | 20
| 21 | 25 | 16.44 |  |  |  | 21
| 22 | 150 | 17.08 |  |  |  | 22 |  | 10
| TOTAL = | 875 | 17.47 | = AVG. |  |  | TOTAL = | 20 | 20 | 4500
| 23rd - 31st | [5 empty] | 23rd-31st
| 23 | 150 | 18.45 |  |  |  | 23
| 24 | 100 | 18.01 |  |  |  | 24
| 25 | 150 | 18.99 |  |  |  | 25 |  | 10
| 26 | 100 |  |  |  |  | 26 | 10
| 27 | 0 |  |  |  |  | 27
| 28 | 25 | 18.14 |  |  |  | 28
| 29 | 150 | 17.68 |  |  |  | 29
| 30 | 150 | 18.98 |  |  |  | 30 |  | 10
| TOTAL = | 825 | 18.375 | = AVG. |  |  | TOTAL = | 10 | 20 | 0
RAGS & GRIT go to Central LandFill
Other(VAC) go to BCSR
PAGE 19

## INJECTION PAGES
|  |  |  | UNDERGROUND INJECTION CONTROL | [10 empty] | UNDERGROUND INJECTION CONTROL | [10 empty] | UNDERGROUND INJECTION CONTROL
[15 empty] | MONTHLY OPERATING REPORT | [10 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES |  |  |  |  | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES |  |  |  |  | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [10 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [10 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-1 | [7 empty] | Wet Well Description: |  |  | Effuent Wet Well for IW-1, IW-2, IW3, IW-4 and IW-5 | [7 empty] | Monitoring Well Decription: |  |  | UPPER ZONE OF MONITORING WELL MW-1
Permit #: |  | UO-06-279401 |  |  |  |  | Date of Issuance: |  | 1997-07-21 |  | Facility ID #: |  | 5006M02066 |  |  |  | Permit Number: |  |  | FLA041378 |  | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | UO-06-279512
[22 empty] | Monitoring Well ID #: |  |  | 5006A11311
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2002-07-21 | [7 empty] | Issue Date: |  |  | 1999-10-18 |  | As Identified in Permit: |  | Monitor Well MW-1 Upper Monitor Zone |  |  |  | Issue Date: |  |  | 1997-07-21
[22 empty] | Monitoring Well Interval: |  |  | 1288' to 1320'
Injection Well ID #: |  | 5006A11308 | [8 empty] | Wet Well ID #: |  | Well Facility U-001 |  |  |  | Expiration Date: |  |  | 2004-10-17 |  | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.3 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24 | Associated Injection Well(s):
Injection Interval: |  |  | 2799' to 3513' | [18 empty] | 500A11311 |  |  | INJECTION WELL IW-5
[11 empty] | Injection Well ID #: |  |  | Injection Well Description
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s): | [10 empty] | 5006A11308 |  |  | INJECTION WELL IW-1
[11 empty] | 5006A11309 |  |  | INJECTION WELL IW-2 | [7 empty] | REPORT MONTH / YEAR: |  | 2003-09-01 | DATE OF SAP / RECORDING: |  |  | 2003-09-02 | 2003-09-09 | 2003-09-16 | 2003-09-23 | 2003-09-30
Monitoring Zone ID #: | [5 empty] | Description |  |  |  |  | 5006A11310 |  |  | INJECTION WELL IW-3
[11 empty] | N/A |  |  | INJECTION WELL IW-4 | [7 empty] | OPERATOR'S NAME: |  |  | BAYLER, J.
UO-06-279401 |  | UPPER ZONE OF MONITORING WELL MW-2 | [8 empty] | 5006A11311 |  |  | INJECTION WELL IW-5
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A
UO-06-279401 |  | LOWER ZONE OF MONITORING WELL MW-2
[11 empty] | THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [10 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [10 empty] | REPORT MONTH / YEAR: |  | 2003-09-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous |  |  | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2003-09-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous |  |  | OPERATOR'S NAME: |  |  | BAYLER, J.
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
OPERATOR'S NAME: |  |  | BAYLER, J. | [7 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A | [7 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4474-A | [7 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: |  |  |  | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 49.08 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 45.35 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: |  |  |  | PARAMETER |  |  |  | Sampling Frequency |  |  |  | VALUE |  | UNITS | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 48.5197 | PSIG
[11 empty] | Nitrogen, Total as N |  |  |  |  | Daily/Monthly Average |  |  | 13.7126 |  | mg/L as N | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[11 empty] | Nitrogen, Nitrate, Total as N |  |  |  |  | Daily/Monthly Average |  |  | 0.46555 |  | mg/L as N | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7325 | mg/l
Total monthly flow | [7 empty] | 301.59 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 3820 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [7 empty] | Nitrogen, Total Kjeildahl as N |  |  |  |  | Daily/Monthly Average |  |  | 13.247 |  | mg/L as N | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.856 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 17.79 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.38 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 81.4 |  | PSIG | pH |  |  |  |  | Daily/Monthly Average |  |  | 6.6033 |  | s.u. | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7.828 | Std units
Monthly average of the daily flow rates | [7 empty] | 10.053 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 12078 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 15.7084 |  | MG | Phosphorus, Total as P |  |  |  |  | Daily/Monthly Average |  |  | 0.99735 |  | mg/L as P | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 2.498 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 73 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [10 empty] | Total Dissolved Solids (TDS) |  |  |  |  | Daily/Monthly Average |  |  | 1246.9333 |  | mg/L | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.042 | mg/l
Monthly average pressure | [7 empty] | 52.6497 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 850 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 37.5 |  | PSIG | Residue, Total filterable (TSS dried at 180 C) |  |  |  |  | Daily/Monthly Average |  |  | 13 |  | mg/L | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 184 | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.432 | mg/l
[11 empty] | Specific Conductance (Temperature Compensated) |  |  |  |  | Daily/Monthly Average |  |  | 2466.7667 |  | umhos/cm | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just | [6 empty] | Temperature, Water |  |  |  |  | Daily/Monthly Average |  |  | 84.7 |  | deg C
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [9 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just |  |  | Date: |  |  |  |  | (Signature):
Date:
(Signature):
|  |  |  | UNDERGROUND INJECTION CONTROL | [21 empty] | UNDERGROUND INJECTION CONTROL
|  |  |  | MONTHLY OPERATING REPORT | [21 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES | [15 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [21 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-2 | [18 empty] | Monitoring Well Decription: |  |  | LOWER ZONE OF MONITORING WELL MW-1
Permit #: |  | UO-06-279508 |  |  |  |  | Date of Issuance: |  | 1997-07-21 | [12 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | UO-06-279512
[22 empty] | Monitoring Well ID #: |  |  | 5006A11311
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2002-07-21 | [12 empty] | As Identified in Permit: |  | Monitor Well MW-1 Lower Monitor Zone |  |  |  | Issue Date: |  |  | 1997-07-21
[22 empty] | Monitoring Well Interval: |  |  | 1449' to 1557'
Injection Well ID #: |  | 5006A11309 | [19 empty] | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.3 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24
Injection Interval: |  |  | 2798' to 3518' | [18 empty] | 500A11311 |  |  | INJECTION WELL IW-5
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s):
[22 empty] | REPORT MONTH / YEAR: |  | 2003-09-01 | DATE OF SAP / RECORDING: |  |  | 2003-09-02 | 2003-09-09 | 2003-09-16 | 2003-09-23 | 2003-09-30
Monitoring Zone ID #: | [5 empty] | Description
[22 empty] | OPERATOR'S NAME: |  |  | BAYLER, J.
UO-06-279401 |  | UPPER ZONE OF MONITORING WELL MW-2
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A
UO-06-279401 |  | LOWER ZONE OF MONITORING WELL MW-2
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [21 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2003-09-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
OPERATOR'S NAME: |  |  | BAYLER, J. | [18 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4474-A | [18 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 42.77 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 28.11 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: | [14 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 40.7387 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 9260.8 | mg/l
Total monthly flow | [7 empty] | 304.07 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 5200 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [18 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 9.582 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 18.57 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 11.308 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 79.8 |  | PSIG | [11 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7.238 | Std units
Monthly average of the daily flow rates | [7 empty] | 10.4852 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 16726 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 16.3946 |  | MG | [11 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 2.498 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 72.6 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [21 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.042 | mg/l
Monthly average pressure | [7 empty] | 51.6513 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 790 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 38.1 |  | PSIG | [11 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 272 | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.016 | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [21 empty] | (Signature):
Date:
|  |  |  | UNDERGROUND INJECTION CONTROL | [21 empty] | UNDERGROUND INJECTION CONTROL
|  |  |  | MONTHLY OPERATING REPORT | [21 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES | [15 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [21 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-3 | [18 empty] | Monitoring Well Decription: |  |  | UPPER ZONE OF MONITORING WELL MW-2
Permit #: |  | UO-06-279510 |  |  |  |  | Date of Issuance: |  | 1997-07-21 | [12 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | UC-06-279401 & 508
[22 empty] | Monitoring Well ID #: |  |  | 5006A11308 & 309
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2002-07-21 | [12 empty] | As Identified in Permit: |  | Monitor Well MW-2 Upper Monitor Zone |  |  |  | Issue Date: |  |  | 1997-07-21
[22 empty] | Monitoring Well Interval: |  |  | 1300' to 1344'
Injection Well ID #: |  | 5006A11310 | [19 empty] | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.3 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24
Injection Interval: |  |  | 2800' to 3977' | [18 empty] | 5006A11308 |  |  | INJECTION WELL IW-1
[22 empty] | 5006A11309 |  |  | INJECTION WELL IW-2
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s):
[22 empty] | REPORT MONTH / YEAR: |  | 2003-09-01 | DATE OF SAP / RECORDING: |  |  | 2003-09-02 | 2003-09-09 | 2003-09-16 | 2003-09-23 | 2003-09-30
Monitoring Zone ID #: | [5 empty] | Description
[22 empty] | OPERATOR'S NAME: |  |  | BAYLER, J.
UO-06-279510 |  | UPPER ZONE OF MONITORING WELL MW-3
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A
UO-06-279510 |  | LOWER ZONE OF MONITORING WELL MW-3
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [21 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2003-09-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
OPERATOR'S NAME: |  |  | BAYLER, J. | [18 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4474-A | [18 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 0 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 0 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: | [14 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | #DIV/0! | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7215.8 | mg/l
Total monthly flow | [7 empty] | 269.83 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 3740 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [18 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.9624 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 15.96 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.558 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 81.9 |  | PSIG | [11 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7.942 | Std units
Monthly average of the daily flow rates | [7 empty] | 8.9943 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 11804 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 14.052 |  | MG | [11 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 2.498 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 71.4 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [21 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.042 | mg/l
Monthly average pressure | [7 empty] | 52.8907 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 840 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 38.2 |  | PSIG | [11 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 180 | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.956 | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [21 empty] | (Signature):
Date:
|  |  |  | UNDERGROUND INJECTION CONTROL | [21 empty] | UNDERGROUND INJECTION CONTROL
|  |  |  | MONTHLY OPERATING REPORT | [21 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES | [15 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [21 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-4 | [18 empty] | Monitoring Well Decription: |  |  | LOWER ZONE OF MONITORING WELL MW-2
Permit #: |  | UC-06-264391 |  |  |  |  | Date of Issuance: |  | N/A | [12 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | UC-06-279401 & 508
[22 empty] | Monitoring Well ID #: |  |  | 5006A11308 & 309
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2000-11-30 | [12 empty] | As Identified in Permit: |  | Monitor Well MW-2 Lower Monitor Zone |  |  |  | Issue Date: |  |  | 1997-07-21
[22 empty] | Monitoring Well Interval: |  |  | 1970' to 2025'
Injection Well ID #: |  | N/A | [19 empty] | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24
Injection Interval: |  |  | 2804' to 3977' | [18 empty] | 5006A11308 |  |  | INJECTION WELL IW-1
[22 empty] | 5006A11309 |  |  | INJECTION WELL IW-2
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s):
[22 empty] | REPORT MONTH / YEAR: |  | 2003-09-01 | DATE OF SAP / RECORDING: |  |  | 2003-09-02 | 2003-09-09 | 2003-09-16 | 2003-09-23 | 2003-09-30
Monitoring Zone ID #: | [5 empty] | Description
[22 empty] | OPERATOR'S NAME: |  |  | BAYLER, J.
UO-06-279510 |  | UPPER ZONE OF MONITORING WELL MW-3
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A
UO-06-279510 |  | LOWER ZONE OF MONITORING WELL MW-3
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [21 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2003-09-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
OPERATOR'S NAME: |  |  | BAYLER, J. | [18 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4474-A | [18 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 42.93 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 30.08 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: | [14 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 38.4953 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 31335.8 | mg/l
Total monthly flow | [7 empty] | 0 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 17880 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [18 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.364 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 11.86 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.75 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 64.41 |  | PSIG | [11 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7.27 | Std units
Monthly average of the daily flow rates | [7 empty] | #DIV/0! |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 46980 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | #DIV/0! |  | MG | [11 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 2.498 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 70.2 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [21 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.042 | mg/l
Monthly average pressure | [7 empty] | 37.4543 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 2440 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 38.4 |  | PSIG | [11 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 848 | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.036 | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [21 empty] | (Signature):
Date:
|  |  |  | UNDERGROUND INJECTION CONTROL | [21 empty] | UNDERGROUND INJECTION CONTROL
|  |  |  | MONTHLY OPERATING REPORT | [21 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES | [15 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [21 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-5 | [18 empty] | Monitoring Well Decription: |  |  | UPPER ZONE OF MONITORING WELL MW-3
Permit #: |  | UO-06-279512 |  |  |  |  | Date of Issuance: |  | 1997-07-21 | [12 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | UO-06-279510
[22 empty] | Monitoring Well ID #: |  |  | 5006A11310
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2002-07-21 | [12 empty] | As Identified in Permit: |  | Monitor Well MW-3 Upper Monitor Zone |  |  |  | Issue Date: |  |  | 1997-07-21
[22 empty] | Monitoring Well Interval: |  |  | 1300' to 1349'
Injection Well ID #: |  | 5006A11311 | [19 empty] | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.3 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24
Injection Interval: |  |  | 2818' to 3462' | [18 empty] | 5006A11310 |  |  | INJECTION WELL IW-3
[22 empty] | N/A |  |  | INJECTION WELL IW-4
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s):
[22 empty] | REPORT MONTH / YEAR: |  | 2003-09-01 | DATE OF SAP / RECORDING: |  |  | 2003-09-02 | 2003-09-09 | 2003-09-16 | 2003-09-23 | 2003-09-30
Monitoring Zone ID #: | [5 empty] | Description
[22 empty] | OPERATOR'S NAME: |  |  | BAYLER, J.
UO-06-279512 |  | UPPER ZONE OF MONITORING WELL MW-1
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A
UO-06-279512 |  | LOWER ZONE OF MONITORING WELL MW-1
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [21 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2003-09-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
OPERATOR'S NAME: |  |  | BAYLER, J. | [18 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4474-A | [18 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 32.18 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 17.32 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: | [14 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 29.963 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7300 | mg/l
Total monthly flow | [7 empty] | 269.56 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 3800 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [18 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.0038 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 15.58 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.342 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 81.2 |  | PSIG | [11 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 8.068 | Std units
Monthly average of the daily flow rates | [7 empty] | 8.9853 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 12052 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 14.0487 |  | MG | [11 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 2.498 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 70 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [21 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.042 | mg/l
Monthly average pressure | [7 empty] | 50.0137 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 840 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 38.2 |  | PSIG | [11 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 182 | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.796 | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [21 empty] | (Signature):
Date:
UNDERGROUND INJECTION CONTROL
MONTHLY OPERATING REPORT
[22 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
[22 empty] | Monitoring Well Decription: |  |  | LOWER ZONE OF MONITORING WELL MW-3
[22 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | UO-06-279510
[22 empty] | Monitoring Well ID #: |  |  | 5006A11310
[22 empty] | As Identified in Permit: |  | Monitor Well MW-3 Lower Monitor Zone |  |  |  | Issue Date: |  |  | 1997-07-21
[22 empty] | Monitoring Well Interval: |  |  | 1970 to 2027'
Associated Injection Well(s):
[22 empty] | Injection Well ID #: |  |  | Injection Well Description
[22 empty] | 5006A11310 |  |  | INJECTION WELL IW-3
[22 empty] | N/A |  |  | INJECTION WELL IW-4
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
[22 empty] | REPORT MONTH / YEAR: |  | 2003-09-01 | DATE OF SAP / RECORDING: |  |  | 2003-09-02 | 2003-09-09 | 2003-09-16 | 2003-09-23 | 2003-09-30
[22 empty] | OPERATOR'S NAME: |  |  | BAYLER, J.
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
[22 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
[22 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
[22 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 46.09 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 37.45 | PSIG
[22 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 44.4413 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
[22 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 29068.75 | mg/l
[22 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 16250 | mg/l
[22 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 2.4525 | mg/l
[22 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 2.8325 | mg/l
[22 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7.365 | Std units
[22 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 43625 | umho/cm
[22 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
[22 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 69 | deg. F
[22 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.04125 | mg/l
[22 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 2350 | mg/l
[22 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 782.5 | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.0325 | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
Date:

## DEP FORMS
Department of Environmental Protection Discharge Monitoring Report - Part A
When Completed mail this report to: Department of Environmental Protection, Wastewater Facilities Management Section, MS 3551, 2600 Blair Stone Road, Tallahassee, FL 32399-2400
PERMITEE NAME: | City of Fort Lauderdale |  |  |  |  | PERMIT NUMBER: |  | FLA041378 |  | REPORT: | Monthly
MAILING ADDRESS: | 949 NW 38th Street |  |  |  |  | LIMIT: |  | Final |  | GROUP: | Domestic
| Fort Lauderdale, FL 33309 |  |  |  |  | CLASS SIZE: |  | N/A |  | GMS TEST SITE
[6 empty] | GMS ID NO. |  | 5006M02066 |  | NO:
FACILITY: | City of Fort Lauderdale G. T. Lohmeyer WWTF |  |  |  |  | MONITORING GROUP NUMBER: |  | U-001
LOCATION: | 1765 SE 18th Street |  |  |  |  | PLANT SIZE/TREATMENT TYPE: |  | IIA
Fort Lauderdale, FL 33316
COUNTY: | Broward | [5 empty] | MONITORING PERIOD: |  |  | 2003-09-01
Parameter |  | Quantity of Loading |  | Units |  | Quality or Concentration |  | Units | No. Ex. | Frequency of Analysis | Sample Type
Flow | Sample Measurement | 15.7084 | 10.053 | [5 empty] | 0
PARM Code 50050 1 Mon.Site No. EFF-002 | Permit Requirement | 18.3 (Peak Hour.) | Report (Mo. Avg.) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
Flow | Sample Measurement | 16.3946 | 10.4852 | [5 empty] | 0
PARM Code 50050 1 Mon.Site No. EFF-003 | Permit Requirement | 18.3 (Peak Hour.) | Report (Mo. Avg.) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
Flow | Sample Measurement | 14.052 | 8.9943 | [5 empty] | 0
PARM Code 50050 1 Mon.Site No. EFF-004 | Permit Requirement | 18.3 (Peak Hour.) | Report (Mo. Avg.) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
Flow | Sample Measurement | #DIV/0! | #DIV/0! | [5 empty] | #DIV/0!
PARM Code 50050 1 Mon.Site No. EFF-005 | Permit Requirement | 18.0 (Peak Hour.) | Report (Mo. Avg.) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
Flow | Sample Measurement | 14.0487 | 8.9853 | [5 empty] | 0
PARM Code 50050 1 Mon.Site No. EFF-006 | Permit Requirement | 18.3 (Peak Hour.) | Report (Mo. Avg.) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
I certify under penalty of law that I have personally examined and am familiar with the informantion submitted herein; and based on my inquiry of those individuals immeadiately responsible for obtaining the information, I believe the submitted
information is true, accurate and complete. I am aware that there are significant penalties for submitting false information including the possiblity of fine and imprisonment.
NAME/TITLE OF PRINCIPAL EXECUTIVE OFFICER OR AUTHORIZED AGENT |  |  |  | SIGNATURE OF PRINCIPAL EXECUTIVE OFFICER OR AUTHORIZED AGENT |  |  |  |  | TELEPHONE |  | DATE (YY/MM/DD)
954-523-1002 ext 2021
REGIONAL WASTEWATER FACILITIES MANAGER
COMMENTS AND EXPLANATION OF ANY VIOLATIONS (Reference all attachments here):
Version 8/13/99
Department of Environmental Protection Discharge Monitoring Report - Part A (Continued)
[12 empty] | PERMITEE NAME: | City of Fort Lauderdale G. T. Lohmeyer WWTF |  |  |  | PERMIT NUMBER: |  | FLA041378 | MONITORING GROUP NUMBER: U-001 |  |  | REPORT: | Monthly
[20 empty] | MONITORING PERIOD: |  |  |  | 2003-09-01
[12 empty] | Parameter |  |  | Quantity of Loading |  | Units |  | Quality or Concentration |  | Units | No. Ex. | Frequency of Analysis | Sample Type
[12 empty] | BOD, Carbonaceous 5 day, 20C |  | Sample Measurement |  |  |  | 4.4 |  |  |  | 0
[12 empty] | PARM Code 80082 Y Mon.Site No. EFF-001 |  | Permit Requirement |  |  |  | 20.0 (An.Avg.) |  |  | mg/l |  | Daily | 24-hour FPC
[12 empty] | BOD, Carbonaceous 5 day, 20C |  | Sample Measurement |  |  |  | 3.716 | 3.6971 | 6.14 |  | 0
[12 empty] | PARM Code 80082 1 Mon.Site No. EFF-001 |  | Permit Requirement |  |  |  | 30.0 (Mo.Avg.) | 45.0 (Week.Avg.) | 60.0 (Max.) | mg/l |  | Daily | 24-hour FPC
[12 empty] | Solids, Total Suspended |  | Sample Measurement |  |  |  | 13.1 |  |  |  | 0
[12 empty] | PARM Code 00530 Y Mon.Site No. EFF-001 |  | Permit Requirement |  |  |  | 20.0 (An.Avg.) |  |  | mg/l |  | Daily | 24-hour FPC
[12 empty] | Solids, Total Suspended |  | Sample Measurement |  |  |  | 13 | 12.5924 | 24 |  | 0
[12 empty] | PARM Code 00530 1 Mon.Site No. EFF-001 |  | Permit Requirement |  |  |  | 30.0 (Mo.Avg.) | 45.0 (Week.Avg.) | 60.0 (Max.) | mg/l |  | Daily | 24-hour FPC
[12 empty] | pH |  | Sample Measurement |  |  |  | 6.4 |  |  |  | 0
[12 empty] | PARM Code 00400 1 Mon.Site No. EFF-001 |  | Permit Requirement |  |  |  | 6.0 (Min.) |  |  | s.u. |  | Continuous | Meter
[12 empty] | Flow |  | Sample Measurement | 35.2886 | 38.5159 | [5 empty] | 0
[12 empty] | PARM Code 50050 G Mon.Site No. INF-001 |  | Permit Requirement | 43.0 (3-Mo.Avg.) | Report (Mo.Avg.) | mgd | [5 empty] | Continuous | Flow meters with 24-hour recording chart
[12 empty] | BOD, Carbonaceous 5 day, 20C |  | Sample Measurement |  |  |  | 65.3667 |  |  |  | N/A
[12 empty] | PARM Code 80082 G Mon.Site No. INF-002 |  | Permit Requirement |  |  |  | Report (Mo.Avg.) |  |  | mg/l |  | Daily | 24-hour FPC
[12 empty] | Solids, Total Suspended |  | Sample Measurement |  |  |  | 91.7333 |  |  |  | N/A
[12 empty] | PARM Code 00530 G Mon.Site No. INF-002 |  | Permit Requirement |  |  |  | Report (Mo.Avg.) |  |  | mg/l |  | Daily | 24-hour FPC
Version 8/13/99

## JULIAN CONVERT
2003-09-01 | 37865 | 1999-01-01 | 1704
FROM DATE ON "DATA INPUT" PAGE | [5 empty] | 2003-09-01
1999
MONTHYY.PAR RANGE TO COMPILE (JULIAN DAY VALUES) FOR SPLIT PROGRAM ARE | [7 empty] | 244 | THROUGH | 1735
|  | 9 | SEPTEMBER
[5 empty] | 2003-09-01 | 2003-09-01 | 9
2003-09-01 |  |  |  |  | 1 | JANUARY |  | 1995 | 1995-01-01
[5 empty] | 2 | FEBRUARY |  | 1996 | 1996-01-01
[5 empty] | 3 | MARCH |  | 1997 | 1997-01-01
SEPTEMBER |  | 0 |  | 0 | 4 | APRIL |  | 1998 | 1998-01-01
|  | 1 |  | 2 | 5 | MAY |  | 1999 | 1999-01-01
|  | 0 |  |  | 6 | JUNE |  | 2000 | 2000-01-01
|  | 0 |  |  | 7 | JULY |  | 2001 | 2001-01-01
|  | 0 |  | 0 | 8 | AUGUST |  | 2002 | 2002-01-01
|  |  |  | 2 | 9 | SEPTEMBER |  | 2003 | 2003-01-01
[5 empty] | 10 | OCTOBER |  | 2004 | 2004-01-01
[5 empty] | 11 | NOVEMBER |  | 2005 | 2005-01-01
2003 |  |  |  |  | 12 | DECEMBER |  | 2006 | 2006-01-01
37865 | [6 empty] | SEPTEMBER | 2007 | 2007-01-01
37622 | [7 empty] | 2008 | 2008-01-01
243 | 1 |  | 1 | 244 | Monday
| 2 |  | 2 | 245 | Tuesday
| 3 |  | 3 | 246 | Wednesday
| 4 |  | 4 | 247 | Thursday
| 5 |  | 5 | 248 | Friday
| 6 |  | 6 | 249 | Saturday
| 7 |  | 7 | 250 | Sunday
| 8 |  | 8 | 251 | Monday
| 9 |  | 9 | 252 | Tuesday
| 10 |  | 10 | 253 | Wednesday
| 11 |  | 11 | 254 | Thursday
| 12 |  | 12 | 255 | Friday
| 13 |  | 13 | 256 | Saturday
| 14 |  | 14 | 257 | Sunday
| 15 |  | 15 | 258 | Monday
| 16 |  | 16 | 259 | Tuesday
| 17 |  | 17 | 260 | Wednesday
| 18 |  | 18 | 261 | Thursday
| 19 |  | 19 | 262 | Friday
| 20 |  | 20 | 263 | Saturday
| 21 |  | 21 | 264 | Sunday
| 22 |  | 22 | 265 | Monday
| 23 |  | 23 | 266 | Tuesday
| 24 |  | 24 | 267 | Wednesday
| 25 |  | 25 | 268 | Thursday
| 26 |  | 26 | 269 | Friday
| 27 |  | 27 | 270 | Saturday
| 28 |  | 28 | 271 | Sunday
| 29 |  | 29 | 272 | Monday
| 30 |  | 30 | 273 | Tuesday
30