## DATA INPUT
ENTER THE AVERAGE MONTHLY INFLUENT FLOW
INTO THE CORROSPONDING BOXES BELOW:
DECEMBER | 33.035 | NOVEMBER | 42.745
ENTER THE PRESENT MONTH AND YEAR IN BOX BELOW (A5) | [5 empty] | JANUARY
2004-01-01 | [5 empty] | 2004
IW-1 | IW-2 | IW-3 | IW-4 | IW-5
34.92 | 35.92 | 35.82 | 36.49 | 35.56 | 2004-01-13
|  | ENTER INJECTION WELL SHUT-IN PRESSURE ABOVE |  |  | ENTER DATE OF SHUT-IN READINGS
ENTER SLUDGE DISPOSAL SITE FOR EACH WEEK BELOW
| WEEK 1 | WEEK 2 | WEEK 3 | WEEK 4
1 st | Nutri-Cylcle Inc. | Nutri-Cylcle Inc. | Nutri-Cylcle\CSLOL Inc. | Nutri-Cylcle Inc.
2 nd | Arcadia, FL | Arcadia, FL | Arcadia, FL | Arcadia, FL
RAW DATA REPORT ENTRY CATEGORIES
GTL PLANT DAILY PROCESS SUMMARY
[6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TOTAL RAW INFLUENT FLOW (MGD) | [5 empty] | 31.093 | 31.813 | 31.481 | 31.009 | 31.168 | 30.687 | 30.514 | 30.866 | 31.036 | 31.043 | 30.52 | 31.341 | 31.249 | 31.577 | 31.714 | 31.357 | 31.323 | 32.044 | 33.128 | 32.485 | 32.144 | 32.621 | 32.502 | 32.38 | 32.273 | 32.662 | 32.446 | 31.538 | 31.301 | 32.201 | 37.134
TOTAL EFFLUENT FLOW (MGD) | [5 empty] | 30.421 | 30.567 | 30.253 | 29.905 | 30.318 | 29.761 | 29.703 | 30.111 | 30.739 | 30.11 | 29.885 | 30.507 | 30.371 | 30.65 | 31.007 | 31.043 | 30.444 | 31.022 | 32.144 | 31.526 | 31.36 | 31.418 | 31.86 | 31.2 | 30.931 | 31.544 | 31.725 | 30.632 | 30.217 | 31.777 | 35.426
MAXIMUM HOURLY RAW INFLUENT FLOW (MGD) | [5 empty] | 1.564 | 1.622 | 1.605 | 1.647 | 1.556 | 1.512 | 1.531 | 1.556 | 1.642 | 1.612 | 1.634 | 1.555 | 1.549 | 1.606 | 1.589 | 1.577 | 1.638 | 1.636 | 1.685 | 1.683 | 1.622 | 1.645 | 1.672 | 1.705 | 1.655 | 1.624 | 1.735 | 1.637 | 1.597 | 1.639 | 1.802
MAXIMUM INSTANANEOUS PEAK RAW INFUENT FLOW (MGD) | [5 empty] | 48.542 | 51.713 | 50.719 | 53.283 | 50.271 | 46.812 | 47.42 | 48.991 | 48.766 | 51.04 | 49.567 | 47.453 | 51.136 | 49.151 | 48.991 | 48.478 | 48.638 | 50.623 | 52.546 | 49.888 | 50.944 | 51.77 | 52.514 | 53.251 | 51.585 | 51.969 | 50.079 | 50.784 | 47.517 | 48.83 | 54.533
MINIMUM INSTANANEOUS PEAK RAW INFUENT FLOW (MGD) | [5 empty] | 0.96 | 0.255 | 0.8 | 0.255 | 0.031 | 0.095 | 0 | 0.159 | 0.383 | 0.768 | 0.127 | 0.127 | 0.832 | 6.023 | 0.928 | 0.447 | 0.96 | 0.479 | 0.543 | 4.1 | 0.235 | 0.191 | 0.928 | 0 | 0.832 | 0.768 | 0.96 | 0.896 | 0.703 | 1.312 | 13.361
TOTAL RETURN ACTIVATED SLUDGE FLOW (MGD) | [5 empty] | 10.668 | 9.944 | 10.43 | 10.605 | 10.346 | 10.064 | 9.465 | 9.402 | 9.33 | 8.956 | 8.881 | 8.925 | 9.846 | 9.396 | 9.811 | 10.144 | 9.496 | 10.585 | 10.105 | 8.632 | 8.655 | 9.724 | 9.004 | 8.531 | 8.824 | 10.612 | 10.377 | 8.121 | 9.203 | 10.835 | 9.941
TOTAL WASTE FLOW TO DEWATERING PROCESS (MG) | [5 empty] | 0 | 0 | 0 | 0.203 | 0.509 | 0.462 | 0.506 | 0.456 | 0.162 | 0 | 0.162 | 0.519 | 0.085 | 0.439 | 0.561 | 0.207 | 0 | 0.109 | 0.473 | 0.515 | 0.499 | 0.287 | 0.285 | 0 | 0.143 | 0.514 | 0.527 | 0.435 | 0.431 | 0.248 | 0
TOTAL DAILY RAINFALL | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0 | 0 | 0.86 | 1.22
RAW INFLUENT pH | [5 empty] | 7.1 | 7 | 7.1 | 7.1 | 7.1 | 7 | 7 | 7.1 | 7.1 | 7.2 | 7.2 | 7 | 7 | 7.1 | 7 | 7.1 | 7.1 | 7.2 | 7.1 | 7 | 7 | 7.1 | 7.1 | 7.2 | 7.2 | 7 | 6.9 | 7 | 7 | 7 | 7.1
RAW INFLUENT HYDROGEN SULFIDE (PPM) | [5 empty] | 8 | 6 | 7 | 7 | 7 | 6 | 5 | 5 | 5 | 5 | 7 | 6 | 5 | 7 | 6 | 5 | 6 | 6 | 8 | 5 | 6 | 5 | 5 | 5 | 5 | 7 | 7 | 6 | 5 | 5 | 4
RAW INFLUENT TEMPERATURE (F ) | [5 empty] | 78 | 78 | 78 | 77 | 78 | 78 | 77 | 77 | 77 | 78 | 77 | 77 | 77 | 77 | 76 | 77 | 76 | 77 | 77 | 77 | 77 | 76 | 76 | 73 | 76 | 75.8 | 76 | 76 | 76 | 77 | 76
TOTAL DAILY KILOWATTS (FPL POWER CONSUMPTION) | [5 empty] | 30783 | 31184 | 31141 | 31128 | 31165 | 31011 | 31421 | 31515 | 31369 | 31417 | 31720 | 31544 | 31477 | 31447 | 31437 | 31395 | 31114 | 31176 | 31371 | 31569 | 31622 | 31623 | 31746 | 31780 | 31578 | 31282 | 31224 | 31861 | 31855 | 31522 | 31432
GTL PLANT DAILY PROCESS SUMMARY
(CONTINUED)
[6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
FINAL EFFLUENT FREE CHLORINE RESIDUAL (PPM) | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FINAL EFFLUENT TOTAL CHLORINE RESIDUAL (PPM) | [5 empty] | 0.9 | 0.8 | 0.7 | 0.9 | 0.6 | 0.6 | 0.4 | 0.6 | 0.5 | 0.5 | 0.8 | 0.4 | 0.5 | 0.7 | 0.6 | 0.4 | 0.6 | 0.7 | 0.5 | 0.7 | 0.5 | 0.6 | 0.6 | 0.6 | 0.9 | 0.8 | 0.4 | 0.4 | 0.5 | 0.6 | 0.3
FINAL EFFLUENT pH (daily average) | [5 empty] | 6.5 | 6.5 | 6.5 | 6.4 | 6.4 | 6.4 | 6.5 | 6.5 | 6.5 | 6.4 | 6.5 | 6.5 | 6.4 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.4 | 6.4 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.4 | 6.5 | 6.6 | 6.8 | 6.5 | 6.5
FINAL EFFLUENT pH (daily minimum) | [5 empty] | 6.4 | 6.4 | 6.4 | 6.3 | 6.3 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.5 | 6.3 | 6.3 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.3 | 6.3 | 6.5 | 6.4 | 6.5 | 6.4 | 6.4 | 6.3 | 6.4 | 6.5 | 6.5 | 6.4 | 6.4
FINAL EFFLUENT pH (daily maximum) | [5 empty] | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.4 | 6.6 | 6.6 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.6 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.6 | 6.5 | 6.5 | 6.5 | 6.5 | 6.8 | 6.9 | 6.8 | 6.5
FINAL EFFLUENT TEMPARTURE (F ) | [5 empty] | 80 | 80 | 80 | 81 | 81 | 81 | 80 | 80 | 79 | 79 | 78 | 79 | 79 | 79 | 79 | 79 | 78.8 | 79 | 79 | 79 | 79 | 79 | 78 | 78 | 78 | 79 | 79 | 78 | 78 | 79 | 79
AVERAGE CLARIFIER BLANKET DEPTH (INCHES) | [5 empty] | 73 | 77 | 73 | 73 | 70 | 63 | 58 | 45 | 48 | 61 | 53 | 48 | 61 | 60 | 46 | 50 | 60 | 54 | 57 | 57 | 57 | 48 | 45 | 60 | 49 | 50 | 50 | 42 | 37 | 49 | 57
FINAL EFFLUENT SAMPLE TEMPARTURE (C ) | [5 empty] | 2 | 4 | 5 | 5 | 5 | 5 | 0 | 2 | 3 | 3 | 2 | 2 | 1 | 1 | 3 | 3 | 3 | 2 | 2 | 5 | 2 | 2 | 0 | 0 | 2 | 5 | 5 | 2 | 2 | 4 | 4
TOTAL RETURN ACTIVATED SLUDGE FLOW TO REACTOR ONE (MGD) | [5 empty] | 2.468 | 2.53 | 2.666 | 2.634 | 2.729 | 2.476 | 1.977 | 1.612 | 1.499 | 1.316 | 1.029 | 1.713 | 1.788 | 1.685 | 1.524 | 1.877 | 2.142 | 3.073 | 2.763 | 1.48 | 1.486 | 2.385 | 1.408 | 0.984 | 1.859 | 3.443 | 3.247 | 1.511 | 1.831 | 2.9 | 2.509
TOTAL RETURN ACTIVATED SLUDGE FLOW TO REACTOR TWO (MGD) | [5 empty] | 8 | 7.415 | 7.764 | 7.971 | 7.617 | 7.588 | 7.488 | 7.79 | 7.831 | 7.64 | 7.852 | 7.212 | 8.058 | 7.711 | 8.287 | 8.267 | 7.254 | 7.512 | 7.342 | 7.153 | 7.169 | 7.34 | 7.596 | 7.547 | 6.965 | 7.17 | 7.13 | 6.61 | 7.372 | 7.935 | 7.432
GTL PLANT DAILY PROCESS SUMMARY
CONTINUED
[6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TOTAL DAILY TRUCKING LOAD OF DEWATERED SLUDGE REMOVED | [5 empty] | 0 | 1 | 0 | 1 | 6 | 6 | 6 | 6 | 4 | 0 | 1 | 6 | 2 | 5 | 6 | 5 | 0 | 1 | 4 | 6 | 6 | 4 | 5 | 0 | 1 | 7 | 6 | 5 | 5 | 5 | 0
TOTAL DAILY HYDROGEN PEROXIDE CONSUMED (LBS) | [5 empty] | 988 | 1058 | 848 | 949 | 529 | 1028 | 1238 | 1048 | 809 | 1437 | 758 | 1667 | 2066 | 1886 | 2664 | 2934 | 3044 | 1000 | 3693 | 3503 | 1000 | 1000 | 5220 | 3443 | 3753 | 4780 | 1528 | 2445 | 1967 | 2308 | 1956
TOTAL DAILY CHLORINE CONSUMED (LBS) | [5 empty] | 1300 | 1160 | 1280 | 1200 | 1160 | 1180 | 1200 | 1200 | 1200 | 1320 | 1240 | 1040 | 1340 | 1180 | 1080 | 1160 | 1060 | 1220 | 1160 | 1060 | 1180 | 1240 | 2120 | 1280 | 1140 | 1180 | 360 | 780 | 1360 | 1020 | 940
TOTAL DAILY POLYMER CONSUMED (GALS) | [5 empty] | 0 | 13 | 0 | 38 | 67 | 87 | 66 | 21 | 56 | 62 | 0 | 45 | 45 | 53 | 98 | 6 | 0 | 7 | 107 | 94 | 16 | 47 | 33 | 0 | 25 | 71 | 81 | 0 | 0 | 254 | 0
TOTAL TONS OF LIME DELIVERED DAILY | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTAL DAILY GASIOUS OXYGEN PRODUCED (TONS) | [5 empty] | 26.4 | 22.1 | 21.4 | 20.3 | 21.7 | 20.8 | 19.1 | 17 | 19.4 | 19.9 | 18.3 | 22.5 | 21.7 | 22.7 | 23.7 | 19.9 | 18.8 | 20.7 | 19.8 | 19.6 | 18.9 | 17.8 | 18.1 | 19.8 | 18.2 | 20.7 | 20.3 | 17.7 | 19.8 | 20.2 | 22.9
AVERAGE PERCENT OXYGEN PRODUCT PURITY | [5 empty] | 96 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 98 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 99
TOTAL DAILY LIQUID OXYGEN IN STORAGE (TONS) | [5 empty] | 162 | 163 | 164 | 165 | 165 | 166 | 167 | 167 | 168 | 168 | 170 | 171 | 172 | 173.3 | 173 | 174 | 175 | 176.3 | 176.4 | 178 | 178 | 177 | 178 | 179 | 180 | 181 | 181 | 181 | 181 | 182 | 183
MONITORING WELL PRESSURE DATA
MONITORING WELL ONE UPPER/LOWER LEVEL
| MW-1 |  | UPPER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MINIMUM | [5 empty] | 47.93 | 47.97 | 48.01 | 48.03 | 45.29 | 45.67 | 47.98 | 47.95 | 48.05 | 48.19 | 48.01 | 44.91 | 45.3 | 48.02 | 48.13 | 48.1 | 48.13 | 48.16 | 46.64 | 46.89 | 47.88 | 47.89 | 47.88 | 47.88 | 48.01 | 46.66 | 47 | 47.96 | 48 | 48.16 | 48.24
MAXIMUM | [5 empty] | 48.17 | 48.21 | 48.27 | 48.3 | 48.32 | 48.58 | 48.23 | 48.27 | 48.4 | 48.42 | 48.29 | 48.17 | 48.24 | 48.34 | 48.37 | 48.38 | 48.4 | 48.57 | 48.56 | 48.52 | 48.25 | 48.24 | 48.19 | 48.24 | 48.3 | 48.3 | 48.38 | 48.27 | 48.21 | 48.39 | 48.43
AVERAGE | [5 empty] | 48.03 | 48.05 | 48.07 | 48.15 | 46.78 | 47.36 | 48.07 | 48.1 | 48.28 | 48.33 | 48.07 | 46.47 | 47.15 | 48.17 | 48.27 | 48.29 | 48.29 | 48.4 | 47.55 | 47.73 | 48.04 | 48.04 | 48.02 | 48.02 | 48.12 | 47.61 | 47.75 | 48.06 | 48.03 | 48.29 | 48.38
| MW-1 |  | LOWER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MINIMUM | [5 empty] | 41.79 | 41.86 | 41.91 | 41.94 | 37.33 | 27.85 | 41.42 | 41.43 | 41.48 | 41.45 | 41.35 | 34.64 | 34.61 | 41.18 | 41.31 | 41.33 | 41.34 | 41.49 | 36.93 | 36.89 | 41.14 | 41.19 | 41.24 | 41.25 | 41.39 | 38.39 | 38.32 | 41.16 | 41.21 | 41.38 | 41.5
MAXIMUM | [5 empty] | 42.1 | 42.16 | 42.16 | 42.19 | 42.2 | 41.88 | 41.6 | 41.63 | 41.84 | 41.67 | 41.6 | 41.44 | 41.3 | 41.57 | 41.7 | 41.72 | 41.72 | 41.78 | 41.8 | 41.36 | 41.38 | 41.6 | 41.48 | 41.64 | 41.78 | 41.79 | 41.58 | 41.43 | 41.58 | 41.62 | 41.65
AVERAGE | [5 empty] | 41.96 | 41.98 | 42 | 42.02 | 39.49 | 40.01 | 41.48 | 41.5 | 41.59 | 41.55 | 41.46 | 37.44 | 38.94 | 41.39 | 41.45 | 41.47 | 41.49 | 41.59 | 39.08 | 39.71 | 41.31 | 41.39 | 41.41 | 41.42 | 41.52 | 40.26 | 40.27 | 41.23 | 41.39 | 41.49 | 41.52
MONITORING WELL TWO UPPER/LOWER LEVEL
| MW-2 |  | UPPER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MINIMUM | [5 empty] | 28.98 | 29.29 | 29.45 | 29.63 | 25.44 | 25.13 | 29.39 | 29.57 | 29.27 | 29.02 | 28.62 | 24.66 | 24.09 | 27.78 | 28 | 28.22 | 28.5 | 29.25 | 24.12 | 23.86 | 27.82 | 28.3 | 28.05 | 27.72 | 28.09 | 27.64 | 26.72 | 25.86 | 25.73 | 26.38 | 26.54
MAXIMUM | [5 empty] | 30.29 | 30.4 | 30.47 | 30.62 | 30.04 | 31.06 | 30.3 | 30.64 | 31.26 | 30.27 | 30.57 | 29.85 | 29.54 | 30.05 | 30.22 | 30.44 | 30.34 | 30.37 | 29.56 | 29.4 | 29.33 | 29.9 | 29.65 | 30.09 | 30.27 | 30.42 | 28.4 | 27.42 | 27.67 | 27.78 | 27.11
AVERAGE | [5 empty] | 29.53 | 29.71 | 29.86 | 29.99 | 27.79 | 28.62 | 29.72 | 29.98 | 30.21 | 29.81 | 29.51 | 27.09 | 27.25 | 28.71 | 28.88 | 29.04 | 29.33 | 29.63 | 27.08 | 27.1 | 28.5 | 28.95 | 28.68 | 28.69 | 29.15 | 29.01 | 27.39 | 26.35 | 26.54 | 26.9 | 26.86
| MW-2 |  | LOWER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MINIMUM | [5 empty] | 41.71 | 41.79 | 41.89 | 41.97 | 38.95 | 38.92 | 41.76 | 41.86 | 42.01 | 42.19 | 42.06 | 37.8 | 37.66 | 41.84 | 42.04 | 42.11 | 42.15 | 42.23 | 31.09 | 31.08 | 41.72 | 41.89 | 41.98 | 42.02 | 42.18 | 39.31 | 38.69 | 39.42 | 39.46 | 39.59 | 39.69
MAXIMUM | [5 empty] | 41.86 | 41.98 | 42.07 | 42.15 | 42.21 | 41.87 | 41.94 | 42.07 | 42.28 | 42.3 | 42.19 | 42.14 | 41.86 | 42.1 | 42.23 | 42.31 | 42.34 | 42.52 | 42.52 | 41.85 | 42.02 | 42.11 | 42.14 | 42.24 | 42.36 | 42.41 | 39.72 | 39.63 | 39.63 | 39.77 | 39.81
AVERAGE | [5 empty] | 41.85 | 41.94 | 41.99 | 42.03 | 40.37 | 40.88 | 41.93 | 41.97 | 42.19 | 42.15 | 42.09 | 39.68 | 40.29 | 41.93 | 42.06 | 42.2 | 42.28 | 42.43 | 36 | 38.26 | 41.94 | 41.98 | 42 | 42.05 | 42.34 | 41.06 | 39.45 | 39.53 | 39.5 | 39.7 | 39.76
MONITORING WELL THREE UPPER/LOWER LEVEL
| MW-3 |  | UPPER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MINIMUM | [5 empty] | 30.86 | 30.93 | 31.03 | 31.09 | 17.15 | 16.98 | 30.59 | 30.73 | 30.9 | 31.09 | 30.89 | 17.12 | 16.99 | 30.66 | 30.92 | 31.01 | 31.03 | 31.1 | 18.12 | 18.07 | 30.6 | 30.78 | 30.82 | 30.85 | 31.01 | 22.63 | 22.43 | 30.95 | 31.06 | 31.27 | 31.39
MAXIMUM | [5 empty] | 31.09 | 31.2 | 31.25 | 31.3 | 31.31 | 30.75 | 30.89 | 31.05 | 31.25 | 31.26 | 31.14 | 31.05 | 30.73 | 31.09 | 31.21 | 31.29 | 31.31 | 31.47 | 31.44 | 30.81 | 31.02 | 31.09 | 31.1 | 31.19 | 31.28 | 31.34 | 31.08 | 31.19 | 31.34 | 31.54 | 31.59
AVERAGE | [5 empty] | 30.97 | 31.07 | 31.13 | 31.22 | 23.13 | 26.02 | 30.77 | 30.92 | 31.12 | 31.14 | 30.99 | 22.89 | 25.9 | 30.87 | 31.05 | 31.1 | 31.13 | 31.33 | 23.87 | 26.4 | 30.85 | 30.95 | 30.96 | 31 | 31.15 | 27.43 | 27.72 | 31.06 | 31.15 | 31.43 | 31.49
| MW-3 |  | LOWER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MINIMUM | [5 empty] | 44.89 | 44.98 | 45.1 | 45.18 | 38.88 | 38.86 | 44.8 | 44.93 | 45.11 | 45.3 | 45.19 | 37.88 | 37.83 | 44.89 | 45.14 | 45.23 | 45.26 | 45.37 | 36.77 | 36.6 | 44.86 | 45.02 | 45.1 | 45.15 | 45.34 | 40.37 | 40.33 | 44.92 | 45.01 | 45.21 | 45.4
MAXIMUM | [5 empty] | 45.06 | 45.19 | 45.27 | 45.36 | 45.39 | 44.88 | 44.99 | 45.15 | 45.39 | 45.41 | 45.3 | 45.23 | 44.89 | 45.18 | 45.33 | 45.43 | 45.47 | 45.65 | 45.64 | 44.95 | 45.13 | 45.22 | 45.24 | 45.37 | 45.5 | 45.56 | 45 | 45.06 | 45.22 | 45.46 | 45.54
AVERAGE | [5 empty] | 44.99 | 45.03 | 45.2 | 45.34 | 41.71 | 42.87 | 44.96 | 44.99 | 45.33 | 45.46 | 45.17 | 41.02 | 42.49 | 44.98 | 45.24 | 45.36 | 45.39 | 45.49 | 40.67 | 42.17 | 44.98 | 45.08 | 45.1 | 45.34 | 45.44 | 43.31 | 43.2 | 45 | 45.02 | 45.39 | 45.49
MONITORING WELL RMW-1 UPPER/LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
[5 empty] | JULIAN DATE | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
| RMW-1 |  | UPPER LEVEL
MINIMUM | [5 empty] | 44.11 | 44.18 | 44.23 | 44.26 | 42.44 | 42.63 | 43.82 | 43.98 | 44.12 | 44.21 | 44.09 | 44.04 | 44.09 | 44.21 | 44.3 | ER | ER | ER | ER | ER | 44.29 | 44.31 | 44.28 | ER | ER | 44.42 | 44.44 | 44.34 | 44.35 | 44.47 | 44.47
MAXIMUM | [5 empty] | 44.11 | 44.18 | 44.22 | 44.26 | 42.44 | 43.63 | 73.82 | 43.98 | 44.12 | 44.21 | 44.09 | 44 | 44.09 | 44.21 | 44.3 | ER | ER | ER | ER | ER | 44.29 | 44.31 | 44.28 | ER | ER | 44.49 | 44.54 | 44.47 | 44.47 | 44.63 | 44.63
AVERAGE | [5 empty] | 44.11 | 44.17 | 44.22 | 44.26 | 42.44 | 42.63 | 43.82 | 43.98 | 44.12 | 44.21 | 44.09 | 44.04 | 44.09 | 44.21 | 44.3 | ER | ER | ER | ER | ER | 44.29 | 44.31 | 44.28 | ER | ER | 44.46 | 44.49 | 44.38 | 44.4 | 44.56 | 44.56
| RMW-1 |  | LOWER LEVEL
MINIMUM | [5 empty] | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | 22.17 | 22.19 | 22.05 | 22.07 | 22.19 | 22.19
MAXIMUM | [5 empty] | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | 22.26 | 22.33 | 22.24 | 22.21 | 22.38 | 22.38
AVERAGE | [5 empty] | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | 22.22 | 22.25 | 22.13 | 22.14 | 22.3 | 22.3
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
| INJECTION WELL ONE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 10.24 | 12.04 | 11.06 | 11.63 | 11.91 | 10.06 | 10.08 | 10.1 | 12.1 | 11.31 | 15.59 | 10.72 | 12.51 | 11.09 | 10.15 | 10.14 | 11 | 11.76 | 11.96 | 11.95 | 12.15 | 13.68 | 12.86 | 12.12 | 11.63 | 11.11 | 14.79 | 12.14 | 12.14 | 12.43 | 15.71
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 4.79 | 3.9 | 4.49 | 4.09 | 4.12 | 4.28 | 4.47 | 3.85 | 3.94 | 4.68 | 5.39 | 5.47 | 3.8 | 4.69 | 4.46 | 4.59 | 4.38 | 4.77 | 4.75 | 4.7 | 4.75 | 4.79 | 4.42 | 4.83 | 4.82 | 4.81 | 0 | 4.54 | 3.98 | 4.57 | 5.78
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 8.07 | 8.08 | 8.02 | 8.11 | 8.02 | 7.89 | 7.9 | 7.99 | 8.16 | 7.99 | 10.13 | 8.5 | 8.07 | 8.12 | 8.2 | 8.21 | 8.05 | 8.21 | 8.51 | 8.33 | 8.29 | 8.31 | 8.42 | 8.24 | 8.18 | 8.33 | 7.69 | 8.07 | 7.98 | 7.81 | 11.73
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 51.12 | 57.64 | 54.05 | 56.35 | 57.46 | 50.92 | 50.9 | 50.88 | 57.77 | 55.28 | 69.72 | 52.88 | 57.81 | 54.2 | 50.59 | 50.6 | 54.84 | 56.71 | 57.66 | 57.07 | 57.31 | 63.41 | 59.75 | 56.79 | 55.24 | 53.93 | 67.08 | 57.73 | 58.12 | 59.49 | 71.4
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 39.23 | 37.66 | 38.62 | 37.98 | 38.08 | 38.3 | 38.68 | 37.46 | 37.33 | 38.62 | 39.37 | 39.68 | 37.31 | 38.57 | 38.17 | 38.82 | 38.15 | 38.76 | 38.81 | 38.63 | 38.48 | 38.4 | 37.69 | 38.33 | 38.39 | 38.45 | 34.78 | 38.19 | 37.25 | 38.52 | 41.08
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 46.01 | 46.14 | 46.1 | 46.51 | 46.53 | 45.75 | 45.69 | 45.85 | 46.39 | 45.93 | 51.79 | 46.79 | 45.9 | 46.04 | 46.03 | 46.11 | 45.93 | 46.58 | 47.27 | 46.74 | 46.46 | 46.39 | 46.7 | 46.14 | 46.25 | 46.61 | 45.89 | 45.54 | 45.51 | 45.4 | 57.08
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
| INJECTION WELL TWO |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 10.3 | 12.25 | 11.22 | 11.79 | 12.13 | 10.16 | 10.19 | 10.21 | 12.26 | 11.5 | 15.66 | 10.83 | 12.68 | 11.21 | 10.26 | 10.26 | 11.11 | 11.92 | 12.18 | 12.01 | 12.3 | 13.83 | 13.09 | 12.17 | 11.77 | 11.29 | 15.15 | 12.31 | 12.32 | 12.76 | 16.15
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 4.43 | 3.28 | 4.06 | 3.53 | 3.63 | 3.86 | 4.05 | 3.17 | 3.48 | 4.41 | 5.21 | 5.35 | 3.06 | 4.43 | 4.19 | 4.43 | 4.08 | 4.56 | 4.53 | 4.51 | 4.55 | 4.56 | 4.09 | 4.7 | 4.62 | 4.62 | 0.02 | 0.02 | 3.57 | 4.24 | 5.62
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 8.08 | 8.09 | 8.04 | 8.1 | 8.01 | 7.88 | 7.88 | 7.98 | 8.15 | 7.99 | 10.24 | 8.59 | 8.09 | 8.13 | 8.23 | 8.26 | 8.08 | 8.26 | 8.56 | 8.39 | 8.34 | 8.36 | 8.49 | 8.3 | 8.23 | 8.4 | 8.5 | 7.88 | 8.03 | 7.84 | 11.96
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 50.13 | 56.6 | 53.07 | 55.39 | 56.42 | 49.96 | 49.95 | 49.95 | 56.77 | 54.21 | 68.42 | 51.81 | 56.64 | 57.68 | 49.63 | 49.65 | 53.78 | 55.59 | 56.53 | 56.04 | 56.16 | 62.25 | 58.68 | 55.77 | 54.1 | 53 | 65.84 | 56.6 | 57.08 | 58.42 | 69.99
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 38.45 | 36.95 | 37.9 | 37.27 | 37.37 | 37.57 | 38.03 | 36.73 | 36.58 | 37.87 | 38.56 | 38.93 | 36.56 | 37.81 | 37.38 | 38.03 | 37.36 | 38.02 | 38.08 | 37.89 | 37.7 | 37.64 | 36.9 | 37.53 | 37.6 | 37.76 | 35.69 | 35.1 | 36.47 | 37.76 | 40.27
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 45.12 | 45.29 | 45.25 | 45.64 | 45.68 | 44.91 | 44.79 | 44.95 | 45.49 | 45.01 | 50.78 | 45.88 | 45.02 | 45.16 | 45.11 | 45.23 | 45.02 | 45.69 | 46.4 | 45.83 | 45.55 | 45.48 | 45.78 | 45.27 | 45.33 | 45.75 | 46.35 | 44.37 | 44.61 | 44.5 | 55.95
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
| INJECTION WELL THREE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 9.02 | 10.61 | 9.72 | 10.3 | 10.64 | 8.84 | 8.83 | 8.88 | 10.69 | 10.01 | 13.79 | 9.43 | 10.35 | 9.86 | 8.92 | 8.91 | 9.62 | 10.37 | 10.59 | 10.45 | 10.72 | 12.03 | 11.4 | 10.62 | 10.29 | 9.77 | 13.89 | 10.72 | 10.76 | 11.06 | 14.21
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 3.93 | 2.96 | 3.59 | ER | 3.23 | 3.42 | 2.27 | 2.86 | 3.09 | 3.83 | 4.57 | 4.73 | ER | 3.91 | 3.71 | 3.88 | 3.56 | 3.94 | 3.95 | 3.9 | 3.96 | 3.99 | 3.6 | 4.09 | 4.03 | 3.97 | ER | 3.78 | 3.17 | 3.71 | 4.9
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 7.05 | 7.04 | 6.98 | 6.41 | 7 | 6.86 | 6.84 | 6.95 | 7.11 | 6.96 | 9.05 | 7.52 | 7.03 | 7.12 | 7.18 | 7.2 | 7.05 | 7.18 | 7.45 | 7.3 | 7.26 | 7.27 | 7.39 | 7.22 | 7.15 | 7.31 | 7.3 | 7.06 | 7 | 6.75 | 10.53
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 51.37 | 57.99 | 54.37 | 56.67 | 57.83 | 51.16 | 51.13 | 51.12 | 58.08 | 55.58 | 70.3 | 53.14 | 55.86 | 54.47 | 50.82 | 50.85 | 55.04 | 57.01 | 57.98 | 57.47 | 57.66 | 63.83 | 60.09 | 57.15 | 55.42 | 54.25 | 71 | 58.09 | 58.49 | 59.85 | 72
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 39.32 | 37.78 | 38.75 | 35.53 | 38.2 | 38.43 | 37.63 | 37.58 | 37.47 | 38.75 | 39.57 | 39.87 | 35.89 | 38.74 | 38.32 | 38.97 | 38.27 | 38.89 | 38.96 | 38.79 | 38.65 | 38.55 | 37.83 | 38.49 | 38.54 | 38.62 | 35.58 | 38.33 | 37.39 | 38.65 | 41.25
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 46.2 | 46.37 | 46.3 | 45.77 | 46.75 | 45.94 | 45.83 | 46.03 | 46.6 | 46.1 | 52.1 | 47.01 | 46.02 | 46.23 | 46.22 | 46.31 | 46.11 | 46.78 | 47.52 | 46.94 | 46.69 | 46.6 | 46.92 | 46.38 | 46.4 | 46.84 | 47.36 | 45.76 | 45.71 | 45.59 | 57.47
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
FUTURE
| INJECTION WELL FOUR |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 0.16 | 0.16 | 0.16 | 0.16 | 0.15 | 0.17 | 0.13 | 0.16 | 0.16 | 0.13 | 0.14 | 0.15 | 0.16 | 0.15 | 0.15 | 0.16 | 0.15 | 0.14 | 0.15 | 0.15 | 0.13 | 0.15 | 0.15 | 0.15 | 0.15 | 0.14 | 19.56 | 15.42 | 0.15 | 10.19 | 0.12
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 0.12 | 0.13 | 0.13 | 0.13 | 0.13 | 0.12 | 0.12 | 0.12 | 0.12 | 0.11 | 0.1 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.12 | 0.12 | 0.11 | 0.11 | 0.11 | 0.11 | 0.1 | 0.1 | 0.12 | 0.12 | 0.11 | 0.11 | ER | 0.12
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 0.13 | 0.13 | 0.14 | 0.14 | 0.13 | 0.14 | 0.12 | 0.13 | 0.13 | 0.12 | 0.12 | 0.13 | 0.13 | 0.12 | 0.12 | 0.13 | 0.12 | 0.13 | 0.13 | 0.13 | 0.12 | 0.13 | 0.12 | 0.12 | 0.12 | 0.13 | 0.96 | 0.47 | 0.12 | ER | 0.12
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 36.77 | 37.36 | 37.13 | 37.42 | 37.64 | 36.94 | 36.91 | 36.89 | 37.66 | 37.32 | 36.06 | 36.88 | 36.9 | 55.28 | 36.73 | 36.77 | 37.06 | 37.35 | 37.42 | 37.22 | 37.19 | 37.31 | 36.94 | 37.08 | 37.09 | 36.86 | 60.48 | 50.85 | 37.45 | 48.35 | 36.44
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 35.18 | 35.02 | 35.29 | 35.22 | 35.25 | 35.28 | 35.23 | 35 | 35 | 35.17 | 34.61 | 34.42 | 34.8 | 34.98 | 34.98 | 35.13 | 35.05 | 35.12 | 35.07 | 34.96 | 34.81 | ER | ER | 34.62 | 34.66 | 34.71 | 34.77 | 35 | 35.03 | 35.17 | 35.22
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 36.06 | 36.16 | 36.24 | 36.28 | 36.37 | 36.29 | 36.18 | 36.21 | 36.26 | 36.15 | 35.27 | 35.88 | 36.06 | 36.09 | 36.04 | 36.06 | 35.99 | 36.09 | 36.14 | 36.01 | 35.92 | 13.88 | 16.9 | 35.77 | 35.81 | 35.88 | 36.99 | 36.32 | 36.09 | 38.56 | 35.72
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
| INJECTION WELL FIVE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 8.97 | 10.57 | 9.71 | 10.22 | 10.5 | 8.82 | 8.84 | 8.85 | 10.58 | 9.93 | 6.97 | 9.38 | 10.89 | 9.7 | 8.85 | 8.85 | 9.59 | 10.29 | 10.48 | 10.42 | 10.58 | 11.94 | 11.24 | 10.49 | 10.15 | 9.74 | 13.5 | 10.63 | 10.69 | 11.01 | 7.67
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 4.31 | 3.4 | 3.97 | 3.57 | 3.67 | 3.83 | 3.85 | 3.3 | 3.49 | 4.26 | ER | ER | 3.57 | 4.24 | 4.07 | 4.21 | 3.97 | 4.35 | 4.34 | 4.33 | 4.33 | 4.38 | 3.96 | 4.46 | 4.42 | 4.39 | ER | 4.14 | 3.57 | 4.12 | ER
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 7.2 | 7.19 | 7.15 | 7.23 | 7.15 | 7.03 | 7.02 | 7.1 | 7.24 | 7.12 | ER | ER | 7.21 | 7.21 | 7.27 | 7.29 | 7.17 | 7.31 | 7.55 | 7.42 | 7.38 | 7.39 | 7.49 | 7.34 | 7.28 | 7.43 | 7.34 | 7.19 | 7.14 | 6.85 | 0.98
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 50.84 | 57.36 | 53.7 | 55.98 | 57.37 | 51 | 50.84 | 51.06 | 58.23 | 55.44 | 45.85 | 56.48 | 59.43 | 55.15 | 54.32 | 53.8 | 54.74 | 57.68 | 58.75 | 57.09 | 58.36 | 64.72 | 59.72 | 59.53 | 54.8 | 57.61 | 64.92 | 53.48 | 55.43 | 56.08 | 47.08
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 39.13 | 37.57 | 38.55 | 37.94 | 37.99 | 38.26 | 38.54 | 37.31 | 37.3 | 38.36 | 31.62 | 31.25 | 38.09 | 36.76 | 29.48 | 28.02 | 37.14 | 37.14 | 38.08 | 36.32 | 37.65 | 35.04 | 33.42 | 14.69 | 24.49 | 26.03 | 26.48 | 24.82 | 25.55 | 0.98 | 33.83
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 45.68 | 45.95 | 45.84 | 46.24 | 46.42 | 45.5 | 45.54 | 45.72 | 46.29 | 45.98 | 34.28 | 43.59 | 46.22 | 44.44 | 44.25 | 43.88 | 45.68 | 46.66 | 47.13 | 47.18 | 46.72 | 46.4 | 45.17 | 42.91 | 43.26 | 43.47 | 43.74 | 42.6 | 42.92 | 43.78 | 35.7
GTL DAILY LABORATORY ANALYSIS REPORT DATA
| RAW INFLUENT DATA |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
RAW TOTAL SUSPENDED SOLIDS | [5 empty] | 116 | 114 | 100 | 40 | 120 | 126 | 112 | 630 | 400 | 72 | 70 | 56 | 120 | 104 | 110 | 112 | 102 | 104 | 104 | 114 | 118 | 100 | 142 | 130 | 106 | 106 | 60 | 340 | 140 | 102 | 148
RAW FIXED SUSPENDED SOLIDS | [5 empty] | 22 | 22 | 18 | 6 | 16 | 24 | 20 | 72 | 68 | 1 | 10 | 8 | 22 | 20 | 22 | 22 | 20 | 16 | 18 | 22 | 24 | 20 | 20 | 12 | 20 | 18 | 12 | 108 | 26 | 8 | 26
RAW ALKILINITY | [5 empty] | 194 | 204 | 196 | 192 | 204 | 204 | 206 | 240 | 206 | 202 | 208 | 210 | 200 | 206 | 204 | 206 | 208 | 206 | 210 | 208 | 208 | 210 | 204 | 206 | 206 | 206 | 208 | 228 | 210 | 218 | 210
RAW CHLORIDES | [5 empty] | 610 | 620 | 660 | 700 | 700 | 720 | 760 | 710 | 700 | 690 | 700 | 680 | 780 | 740 | 730 | 710 | 740 | 750 | 760 | 720 | 700 | 720 | 760 | 750 | 790 | 800 | 760 | 770 | 740 | 720 | 640
RAW COD | [5 empty] | 308 | 318 | 314 | 785 | 785 |  | 345 | 383 | 370 | 325 | 406 |  |  | 379 | 342 | 337 | 400 | 337 |  |  | 400 | 345 | 374 | 491 | 394 |  |  | 377 | 403 | 527 | 258
RAW CBOD | [5 empty] | 97 | 87.8 | 90 | 66 | 72 | 80.3 | 70.1 | 139 | 92 | 99 | 95.7 | 72 | 61 | 72.5 | 66 | 71 | 84.9 | 86 | 59.8 | 61 | 70 | 68.1 | 56 | 126 | 106 | 85 | 97 | 109 | 125 | 136 | 72
| EFFLUENT DATA |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
EFFLUENT TOTAL DISSOLVED SOLIDS | [5 empty] | 1220 | 1227 | 1276 | 1272 | 1213 | 1152 | 1168 | 1278 | 1086 | 1295 | 1285 | 1335 | 1445 | 1468 | 1499 | 1290 | 1386 | 1305 | 1410 | 1394 | 1388 | 1423 | 1539 | 1461 | 1523 | 1489 | 1389 | 1331 | 1249 | 1320 | 1336
EFFLUENT TOTAL SUSPENDED SOLIDS | [5 empty] | 11 | 22 | 16 | 23 | 18 | 13 | 10 | 17 | 15 | 19 | 18 | 17 | 19 | 30 | 13 | 18 | 14 | 13 | 24 | 20 | 18 | 26 | 21 | 18 | 20 | 18 | 21 | 26 | 16 | 14 | 20
EFFLUENT FIXED SUSPENDED SOLIDS | [5 empty] | 3 | 4 | 3 | 2 | 2 | 3 | 2 | 4 | 1 | 2 | 1 | 1 | 4 | 5 | 3 | 5 | 3 | 3 | 5 | 4 | 3 | 4 | 4 | 2 | 4 | 3 | 3 | 5 | 3 | 3 | 4
EFFLUENT ALKILINITY | [5 empty] | 186 | 176 | 186 | 182 | 198 | 196 | 196 | 194 | 188 | 200 | 198 | 200 | 188 | 200 | 196 | 196 | 196 | 190 | 194 | 194 | 196 | 194 | 176 | 190 | 196 | 200 | 198 | 200 | 190 | 192 | 190
EFFLUENT TURBIDITY | [5 empty] | 10.6 | 10.7 | 9.46 | 14.6 | 11.9 | 10.2 | 9.87 | 10.2 | 8.75 | 8.22 | 9.04 | 9.99 | 10.6 | 17 | 7.3 | 9.68 | 8.1 | 9.86 | 12.9 | 11 | 9.85 | 7.41 | 9.3 | 8.62 | 9.9 | 10.4 | 7.64 | 8.74 | 8.76 | 5.58 | 9.48
EFFLUENT CHLORIDES | [5 empty] | 670 | 650 | 670 | 740 | 740 | 710 | 720 | 720 | 730 | 720 | 740 | 700 | 760 | 780 | 770 | 760 | 790 | 770 | 760 | 740 | 770 | 740 | 730 | 770 | 780 | 790 | 770 | 720 | 760 | 740 | 660
EFFLUENT CONDUCTIVITY | [5 empty] | 2730 | 2660 | 2670 | 2580 | 2670 | 2730 | 2640 | 2770 | 2870 | 3100 | 3100 | 3030 | 3170 | 3150 | 3230 | 3190 | 3080 | 3010 | 3130 | 3110 | 3070 | 3270 | 3290 | 3270 | 3220 | 3260 | 3160 | 3090 | 2890 | 2910 | 2840
EFFLUENT TOTAL BACTERIA COUNT | [5 empty] | TNTC | 16000 | 40000 | 5500 | 64000 | 71 | 5600 | TNTC | 173 | 2500 | 400 | 2300 | TNTC | 700 | 116 | 9 | 116 | 152 | TNTC | 403 | TNTC | 84500 | 17000 | TNTC | 65000 | 500 | 28500 | TNTC | 71500 | TNTC | 44000
EFFLUENT FECAL BACTERIA COUNT | [5 empty] | 0 | 116 | 723 | 63 | 4000 | 0 | 9 | 45 | 0 | 0 | 0 | 500 | 18 | 0 | 0 | 0 | 0 | 9 | TNTC | 0 | 45 | 134 | 27 | 30000 | 9 | 0 | 9 | TNTC | 54 | 142 | 9
EFFLUENT COD | [5 empty] | 53.3 | 69.4 | 71 | 72.9 | 72.9 |  | 77.5 | 70.7 | 71.4 | 72.9 | 66.3 |  |  | 74.2 | 64.6 | 67.4 | 69.3 | 80.4 |  |  | 62.4 | 56.5 | 71.4 | 82.5 | 71.1 |  |  | 50.5 | 60.9 | 73.4 | 58.6
EFFLUENT CBOD | [5 empty] | 6 | 5.8 | 6.3 | 4.79 | 4.43 | 4.4 | 3.61 | 4 | 2.6 | 4 | 3.81 | 3.4 | 2 | 3.67 | 2.3 | 1.3 | 3.33 | 4.62 | 3.63 | 4.2 | 2.5 | 1.94 | 2.8 | 6.1 | 4.8 | 5 | 6 | 8 | 4 | 6 | 5
LABORATORY NUTRIENT DATA
RAW INFLUENT | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
RAW AMMONIA (PPM) | [5 empty] | 17.96 | 16.83 | 18.47 | 19.17 | 19.17 |  | 19.19 | 19.04 | 18.86 | 18.3 | 17.41 |  |  | 19.17 | 18.84 | 18.3 | 18.23 | 16.83 |  |  | 19.93 | 18.4 | 17.45 | 15.02 | 17.35 |  |  | 18 | 19 | 18 | 6.9
RAW NITRATES (PPM) | [5 empty] | 0.02 | 0.02 | 0.125 | 0.02 | 0.02 |  | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 |  |  | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 |  |  | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 |  |  | 0.02 | 0.02 | 0.071 | 0.02
RAW TOTAL KNEDJAHL NITRIGEN | [5 empty] | 21.21 | 20.62 | 21.83 | 23.46 | 23.46 |  | 22.22 | 22.19 | 22.11 | 21.87 | 20.71 |  |  | 22.67 | 22.04 | 21.87 | 22.1 | 20.48 |  |  | 21.41 | 21.79 | 21.39 | 21.55 | 20.91 |  |  | 24 | 27 | 25 | 13
RAW TOTAL PHOSPHORUS | [5 empty] | 3.06 | 2.02 | 2.93 | 4.99 | 4.99 |  | 3.37 | 3.62 | 3.24 | 3.23 | 3.18 |  |  | 3.6 | 3.04 | 2.96 | 3.42 | 2.96 |  |  | 3.18 | 3.39 | 3.13 | 2.73 | 3.18 |  |  | 3.5 | 3.2 | 2.1 | 0.84
EFFLUENT | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
EFFLUENT AMMONIA (PPM) | [5 empty] | 13.66 | 14.41 | 13.94 | 14.53 | 14.53 |  | 16.18 | 15.7 | 15.27 | 14.48 | 14.5 |  |  | 15.01 | 16.48 | 15.73 | 14.07 | 15.23 |  |  | 14.73 | 14.55 | 16.16 | 13.94 | 13.2 |  |  | 7.9 | 14 | 14 | 9.7
EFFLUENT NITRATES (PPM) | [5 empty] | 0.243 | 0.16 | 0.169 | 0.251 | 0.251 |  | 0.143 | 0.177 | 0.129 | 0.105 | 0.121 |  |  | 0.169 | 0.233 | 0.187 | 0.183 | 0.156 |  |  | 0.19 | 0.275 |  | 0.113 | 0.354 |  |  | 0.02 | 0.34 | 0.32 | 0.31
EFFLUENT TOTAL KNEDJAHL NITRIGEN | [5 empty] | 17.2 | 17.53 | 17.18 | 17.94 | 17.94 |  | 19.66 | 18.85 | 18.39 | 17.98 | 17.87 |  |  | 18.2 | 19.6 | 19.04 | 17.63 | 18.62 |  |  | 17.81 | 17.67 | 0 | 17.25 | 16.61 |  |  | 15 | 16 | 17 | 12
EFFLUENT TOTAL PHOSPHORUS | [5 empty] | 1.78 | 1.64 | 1.52 | 1.66 | 1.66 |  | 1.24 | 1.05 | 1.13 | 0.965 | 1.06 |  |  | 0.668 | 0.948 | 1.78 | 2.1 | 1.05 |  |  | 1.15 | 0.598 | 1.81 | 1.53 | 1.36 |  |  | 5.7 | 0.85 | 1.1 | 0.84
LABORATORY REACTOR PROCESSES DATA
| REACTOR ONE TRAIN A |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MIXED-LIQUIR SUSPENDED SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
AVERAGE SETTLABLE SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
MIXED LIQUIR VOLITLE SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
| REACTOR ONE TRAIN B |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MIXED-LIQUIR SUSPENDED SOLIDS | [5 empty] | 3950 | 2900 | 3330 | 4360 | 4420 | 4130 | 2660 | 2350 | 3020 | 2970 | 3250 | 3510 | 3820 | 2920 | 2600 | 2610 | 2940 | 3610 | 3530 | 4040 | 3280 | 3030 | 2760 | 3220 | 3740 | 4010 | 3860 | 2800 | 3420 | 3120 | 2630
AVERAGE SETTLABLE SOLIDS | [5 empty] | 42 | 43 | 40 | 38 | 44 | 40 | 46 | 30 | 30 | 39 | 36 | 33 | 39 | 39 | 35 | 35 | 34 | 44 | 36 | 37 | 37 | 29 | 37 | 36 | 33 | 35 | 38 | 24 | 25 | 46 | 38
MIXED LIQUIR VOLITLE SOLIDS | [5 empty] | 3280 | 2480 | 2760 | 3660 | 3720 | 3430 | 2210 | 1950 | 2610 | 2570 | 2470 | 2680 | 3170 | 2420 | 2160 | 2180 | 2440 | 3000 | 3000 | 3430 | 2790 | 2570 | 2290 | 2640 | 3050 | 3270 | 3140 | 2260 | 2760 | 2840 | 2210
LABORATORY REACTOR PROCESSES DATA
CONTINUED
| REACTOR TWO TRAIN C |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MIXED-LIQUIR SUSPENDED SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
AVERAGE SETTLABLE SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
MIXED LIQUIR VOLITLE SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
| REACTOR TWO TRAIN D |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MIXED-LIQUIR SUSPENDED SOLIDS | [5 empty] | 4160 | 3050 | 3310 | 3900 | 3950 | 3660 | 3020 | 3000 | 3230 | 2260 | 2950 | 4430 | 3320 | 3280 | 3180 | 3260 | 3310 | 3310 | 3580 | 3240 | 3070 | 2500 | 3220 | 3810 | 3400 | 3840 | 3950 | 2450 | 3240 | 2680 | 2580
AVERAGE SETTLABLE SOLIDS | [5 empty] | 44 | 47 | 39 | 38 | 42 | 43 | 42 | 31 | 35 | 41 | 40 | 32 | 41 | 34 | 34 | 36 | 37 | 32 | 34 | 36 | 32 | 30 | 46 | 42 | 32 | 32 | 40 | 21 | 30 | 37 | 39
MIXED LIQUIR VOLITLE SOLIDS | [5 empty] | 3450 | 2650 | 2750 | 3260 | 3290 | 3040 | 2510 | 2490 | 2760 | 1860 | 2280 | 3440 | 2760 | 2720 | 2640 | 2710 | 2750 | 2750 | 3080 | 2790 | 2610 | 2120 | 2630 | 3110 | 2730 | 3100 | 3240 | 2050 | 2710 | 2360 | 2170
LABORATORY RETURN ACTIVATED SLUDGE AND WASTE SLUDGE DATA
| RETURN ACTIVATED SLUDGE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
PERCENT RETURN SLUDGE TOTAL SUSPENDED SOLIDS | [5 empty] | 1.4 | 1.21 | 1.1 | 1.03 | 1 | 1.01 | 1.04 | 0.84 | 0.97 | 0.96 | 0.93 | 1 | 1.03 | 1.15 | 1.17 | 1.04 | 1.09 | 0.9 | 0.95 | 0.97 | 0.93 | 0.89 | 0.89 | 1.02 | 0.97 | 1.04 | 0.88 | 0.79 | 0.9 | 0.96 | 1.03
PERCENT RETURN SLUDGE FIXED SUSPENDED SOLIDS | [5 empty] | 16.4 | 23.6 | 19.6 | 22.3 | 20.2 | 20.8 | 19.4 | 24.2 | 20.7 | 23.6 | 21.2 | 20 | 20.5 | 20.4 | 19.7 | 22.5 | 22 | 20.3 | 20.8 | 22.1 | 23 | 23.3 | 23.5 | 22.2 | 21.7 | 24 | 23.6 | 23 | 19.6 | 21.2 | 22
|  | WASTE SLUDGE |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
PERCENT WASTE FEED TOTAL SUSPENDED SOLDS | [8 empty] | 1.34 | 1.3 | 1.3 | 1.33 | 1.32 |  |  | 1.18 | 1.4 |  | 1.41 | 1.4 |  |  | 1.41 | 1.32 | 1.36 | 1.42 | 1.37 |  |  | 1.31 | 1.2 | 1.39 | 1.39 | 1.36
PERCENT WASTE FEED FIXED SUSPENDED SOLIDS | [8 empty] | 23.1 | 20 | 20 | 20.3 | 22.7 |  |  | 22.9 | 20 |  | 19.9 | 18.6 |  |  | 21.3 | 22.7 | 22.1 | 21.8 | 21.9 |  |  | 22.9 | 24.2 | 23 | 23 | 21.3
WASTE FEED SLUDGE pH | [8 empty] | 6.6 | 6.69 | 6.7 | 6.69 | 6.8 |  |  | 6.89 | 6.9 |  | 6.81 | 6.79 |  |  | 6.79 | 6.67 | 6.7 | 6.8 | 6.86 |  |  | 6.79 | 6.8 | 6.52 | 6.81 | 6.77
DEWATERING FILTRATE TOTAL SUSPENDED SOLIDS | [8 empty] | 0.21 | 0.23 | 0.21 | 0.23 | 0.23 |  |  | 0.19 | 0.18 |  | 0.2 | 0.2 |  |  | 0.19 | 0.27 | 0.23 | 0.2 | 0.2 |  |  | 0.24 | 0.23 | 0.2 | 0.22 | 0.27
DEWATERING FILTRATE FIXED SUSPENDED SOLIDS | [8 empty] | 57.1 | 56.5 | 52.4 | 52.2 | 69.6 |  |  | 68.4 | 55.6 |  | 50 | 55 |  |  | 52.6 | 59.3 | 65.2 | 75 | 75 |  |  | 66.7 | 65.2 | 75 | 68.2 | 88.8
DEWATERING FILTRATE pH | [8 empty] | 7.18 | 7.18 | 7.19 | 7.19 | 7.2 |  |  | 7.27 | 7.2 |  | 7.21 | 7.19 |  |  | 7.18 | 7.18 | 7.19 | 7.21 | 7.14 |  |  | 7.17 | 7.2 | 7.08 | 7.2 | 7.18
| DEWATERED CAKE SLUDGE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
PERCENT TOTAL SOLIDS PRESS CAKE | [8 empty] | 17.44 | 17.73 | 17.86 | 18.36 | 17.68 |  |  | 17.58 | 18.53 |  | 17.11 | 17.3 |  |  | 17.64 | 17.54 | 17.7 | 17.78 | 17.55 |  |  | 17.3 | 17.81 | 18.04 | 17.52 | 17.58
PERCENT FIXED SOLIDS PRESS CAKE | [8 empty] | 15 | 12.5 | 14 | 14.5 | 13.3 |  |  | 13.2 | 18.53 |  | 14.7 | 18 |  |  | 14.3 | 13.1 | 13.3 | 13.2 | 17.9 |  |  | 13.8 | 18.6 | 14.7 | 14.3 | 20.7
PERCENT TOTAL SOLIDS LIME CAKE
OTHER SLUDGE REMOVAL
[6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
GRIT (CU.YDS.) | [5 empty] | 5: 10; 12: 10; 21: 10; 28: 10
RAGS (CU.YDS.) | [5 empty] | 5: 10; 9: 10; 15: 10; 22: 10; 29: 10
VACUUM DEBRIS (EST. GAL) | [5 empty] | 8: 4500; 30: 4500
MONITORING WELLS LABORATORY DATA
| MONITOR WELL ONE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
UPPER LEVEL
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
MONITORING WELLS LABORATORY DATA
| MONITOR WELL TWO |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
UPPER LEVEL
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
MONITORING WELLS LABORATORY DATA
| MONITOR WELL THREE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
FUTURE
UPPER LEVEL
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
MONITORING WELLS LABORATORY DATA
| REGIONAL MONITOR WELL ONE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
UPPER LEVEL
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
JANUARY |  | 1 |  | 3
|  | 0 |  | 0
1
0
|  | 1 |  | 0
3
[5 empty] | 1st WEEK | 1: 2nd WEEK; 2: 3rd WEEK; 3: 4th WEEK
| 1 |  | 1 |  | 1 | 1: 8; 2: 15; 3: 23
| 2 |  | 2 |  | 2 | 1: 9; 2: 16; 3: 24
| 3 |  | 3 |  | 3 | 1: 10; 2: 17; 3: 25
| 4 |  | 4 |  | 4 | 1: 11; 2: 18; 3: 26
| 5 |  | 5 |  | 5 | 1: 12; 2: 19; 3: 27
| 6 |  | 6 |  | 6 | 1: 13; 2: 20; 3: 28
| 7 |  | 7 |  | 7 | 1: 14; 2: 21; 3: 29
| 8 |  | 8 |  |  | 2: 22; 3: 30
| 9 |  | 9 |  |  | 3: 31
| 10 |  | 10
| 11 |  | 11
| 12 |  | 12
| 13 |  | 13
| 14 |  | 14
| 15 |  | 15
| 16 |  | 16
| 17 |  | 17
| 18 |  | 18
| 19 |  | 19
| 20 |  | 20
| 21 |  | 21
| 22 |  | 22
| 23 |  | 23
| 24 |  | 24
| 25 |  | 25
| 26 |  | 26
| 27 |  | 27
| 28 |  | 28
29
30
31
| APRIL | MARCH | FEBRUARY
| AUGUST | JULY | JUNE
| DECEMBER | NOVEMBER | OCTOBER
| FEBRUARY | JANUARY | DECEMBER
| JANUARY | DECEMBER | NOVEMBER
| JUNE | MAY | APRIL
| JULY | JUNE | MAY | DECEMBER
| MARCH | FEBRUARY | JANUARY | NOVEMBER
| MAY | APRIL | MARCH
| NOVEMBER | OCTOBER | SEPTEMBER
| OCTOBER | SEPTEMBER | AUGUST
| SEPTEMBER | AUGUST | JULY
| HYDROGEN PEROXIDE |  | 0.1395
| CHLORINE |  | 0.1475
| POLYMER |  | 0.61
| FPL |  | 0.055
[6 empty] | 1st WEEK |  |  | 2nd WEEK |  |  | 3rd WEEK |  |  | 4th WEEK
[7 empty] | G | H | I | J
[5 empty] | MW1 UP | 1: 311
312
313
314
315
316
317
318

## MONITOR DATA
UNDERGROUND INJECTION CONTROL SECTION
MONTHLY OPERATING REPORT DATA SUMMARY
FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT MONTH/YEAR |  |  | JANUARY |  | 2004
I.D. NUMBER: 5006M02066 | [5 empty] | LEAD OPERATOR: |  |  |  | MIKE JUST
TELEPHONE NUMBER: (954) 523-1002
MONITORING WELL 1 DATA | [6 empty] | I.D. # 5006A11311
MW-1
PERMIT/CERTIFICATION NUMBER | [6 empty] | 0054569-142-UO
PERMIT EXPIRATION DATE |  | 2009-01-06
UPPER MONITORING INTERVAL | [6 empty] | 1,288' - 1,320' |  |  |  | Ft. bls.
Sample Date |  | 2004-01-06 |  | 2004-01-13 |  | 2004-01-20 |  | 2004-01-27
Submittal Date |  | 2004-01-07 |  | 2004-01-14 |  | 2004-01-21 |  | 2004-01-28
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 48.58 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 44.91 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 74 |  | 69 |  | 74 |  | 75 |  |  | degrees (F) |  | 73
TDS |  | 7190 |  | 7190 |  | 7377 |  | 7125 |  |  | mg/l |  | 7220.5
CHLORIDE |  | 4050 |  | 3900 |  | 4000 |  | 4000 |  |  | mg/l |  | 3987.5
AMMONIA-N |  | 0.735 |  | 1.02 |  | 1 |  | 0.924 |  |  | mg/l |  | 0.91975
TKN |  | 1.56 |  | 1.58 |  | 1.58 |  | 0.99 |  |  | mg/l |  | 1.4275
pH |  | 8.13 |  | 7.89 |  | 8.12 |  | 8.07 |  |  | Std units |  | 8.0525
CONDUCTIVITY |  | 12660 |  | 12810 |  | 12760 |  | 12700 |  |  | umho/cm |  | 12732.5
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.05 | < | 0.05 | < | 0.05 | < | 0.05 |  |  | mg/l |  | 0.05
SULFATE |  | 850 |  | 800 |  | 900 |  | 850 |  |  | mg/l |  | 850
C.O.D. 'S |  | 190 |  | 200 |  | 200 |  | 180 |  |  | mg/l |  | 192.5
IRON |  | 0.67 |  | 0.66 |  | 0.85 |  | 0.94 |  |  | mg/l |  | 0.78
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
LOWER MONITORING INTERVAL | [6 empty] | 1,449' - 1,557' |  |  |  | Ft. bls
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 42.2 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 27.85 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 74 |  | 69 |  | 73 |  | 74 |  |  | degrees (F) |  | 72.5
TDS |  | 9190 |  | 9400 |  | 9310 |  | 9270 |  |  | mg/l |  | 9292.5
CHLORIDE |  | 5500 |  | 5300 |  | 5200 |  | 5300 |  |  | mg/l |  | 5325
AMMONIA-N |  | 9.71 |  | 9.79 |  | 9.66 |  | 9.16 |  |  | mg/l |  | 9.58
TKN |  | 11.06 |  | 11.54 |  | 11.49 |  | 8.2 |  |  | mg/l |  | 10.5725
pH |  | 7.4 |  | 7.22 |  | 7.39 |  | 7.37 |  |  | Std units |  | 7.345
CONDUCTIVITY |  | 16400 |  | 16560 |  | 16710 |  | 16620 |  |  | umho/cm |  | 16572.5
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.05 | < | 0.05 | < | 0.05 | < | 0.05 |  |  | mg/l |  | 0.05
SULFATE |  | 800 |  | 750 |  | 750 |  | 850 |  |  | mg/l |  | 787.5
C.O.D. 'S |  | 280 |  | 280 |  | 290 |  | 280 |  |  | mg/l |  | 282.5
IRON |  | 0.02 |  | 0.02 |  | 0.02 |  | 0.03 |  |  | mg/l |  | 0.0225
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
PAGE 24
UNDERGROUND INJECTION CONTROL SECTION
MONTHLY OPERATING REPORT DATA SUMMARY
FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT MONTH/YEAR |  |  | JANUARY |  | 2004
I.D. NUMBER: 5006M02066 | [5 empty] | LEAD OPERATOR: |  |  |  | MIKE JUST
TELEPHONE NUMBER: (954) 523-1002
MONITORING WELL 2 DATA | [6 empty] | I.D. # 5006A11308 & 309
MW-2
PERMIT/CERTIFICATION NUMBER | [6 empty] | 0054569-142-UO
PERMIT EXPIRATION DATE |  | 2009-01-06
UPPER MONITORING INTERVAL | [6 empty] | 1,300' - 1,344' |  |  |  | Ft. bls.
Sample Date |  | 2004-01-06 |  | 2004-01-13 |  | 2004-01-20 |  | 2004-01-27
Submittal Date |  | 2004-01-07 |  | 2004-01-14 |  | 2004-01-20 |  | 2004-01-28
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 31.26 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 23.86 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 72 |  | 70 |  | 70 |  | 74 |  |  | degrees (F) |  | 71.5
TDS |  | 6920 |  | 7270 |  | 7210 |  | 6892 |  |  | mg/l |  | 7073
CHLORIDE |  | 3800 |  | 3850 |  | 3900 |  | 3950 |  |  | mg/l |  | 3875
AMMONIA-N |  | 0.726 |  | 0.72 |  | 0.721 |  | 0.657 |  |  | mg/l |  | 0.706
TKN |  | 1.74 |  | 1.71 |  | 1.83 |  | 0.81 |  |  | mg/l |  | 1.5225
pH |  | 7.76 |  | 7.98 |  | 8.14 |  | 7.62 |  |  | Std units |  | 7.875
CONDUCTIVITY |  | 12270 |  | 12430 |  | 12520 |  | 12350 |  |  | umho/cm |  | 12392.5
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.05 | < | 0.05 | < | 0.05 | < | 0.05 |  |  | mg/l |  | 0.05
SULFATE |  | 800 |  | 800 |  | 750 |  | 800 |  |  | mg/l |  | 787.5
C.O.D. 'S |  | 170 |  | 180 |  | 190 |  | 180 |  |  | mg/l |  | 180
IRON |  | 7.8 |  | 3.1 |  | 1.25 |  | 4.6 |  |  | mg/l |  | 4.1875
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
LOWER MONITORING INTERVAL | [6 empty] | 1,970' - 2,025' |  |  |  | Ft. bls
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 42.52 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 31.08 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 71 |  | 68 |  | 69 |  | 72 |  |  | degrees (F) |  | 70
TDS |  | 30990 |  | 31360 |  | 30572 |  | 30371 |  |  | mg/l |  | 30823.25
CHLORIDE |  | 18400 |  | 18000 |  | 17800 |  | 18000 |  |  | mg/l |  | 18050
AMMONIA-N |  | 1.51 |  | 1.5 |  | 1.48 |  | 1.5 |  |  | mg/l |  | 1.4975
TKN |  | 2.12 |  | 2.15 |  | 2.15 |  | 1.3 |  |  | mg/l |  | 1.93
pH |  | 7.53 |  | 7.23 |  | 7.4 |  | 7.4 |  |  | Std units |  | 7.39
CONDUCTIVITY |  | 49100 |  | 49700 |  | 49900 |  | 49200 |  |  | umho/cm |  | 49475
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.05 | < | 0.05 | < | 0.05 | < | 0.05 |  |  | mg/l |  | 0.05
SULFATE |  | 2600 |  | 2600 |  | 2900 |  | 2400 |  |  | mg/l |  | 2625
C.O.D. 'S |  | 870 |  | 890 |  | 890 |  | 810 |  |  | mg/l |  | 865
IRON |  | 0.03 |  | 0.06 |  | 0.05 |  | 0.09 |  |  | mg/l |  | 0.0575
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
PAGE 25
UNDERGROUND INJECTION CONTROL SECTION
MONTHLY OPERATING REPORT DATA SUMMARY
FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT MONTH/YEAR |  |  | JANUARY |  | 2004
I.D. NUMBER: 5006M02066 | [5 empty] | LEAD OPERATOR: |  |  |  | MIKE JUST
TELEPHONE NUMBER: (954) 523-1002
MONITORING WELL 2 DATA | [6 empty] | I.D. # 5006A11310
MW-3
PERMIT/CERTIFICATION NUMBER | [6 empty] | 0054569-142-UO
PERMIT EXPIRATION DATE |  | 2009-01-06
UPPER MONITORING INTERVAL | [6 empty] | 1,300' - 1,349' |  |  |  | Ft. bls.
Sample Date |  | 2004-01-06 |  | 2004-01-13 |  | 2004-01-20 |  | 2004-01-27
Submittal Date |  | 2004-01-07 |  | 2004-01-14 |  | 2004-01-21 |  | 2004-01-28
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 31.59 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 16.98 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 70 |  | 68 |  | 70 |  | 72 |  |  | degrees (F) |  | 70
TDS |  | 7170 |  | 7200 |  | 7252 |  | 7028 |  |  | mg/l |  | 7162.5
CHLORIDE |  | 3950 |  | 3900 |  | 3950 |  | 4000 |  |  | mg/l |  | 3950
AMMONIA-N |  | 1.01 |  | 1.01 |  | 1.01 |  | 0.93 |  |  | mg/l |  | 0.99
TKN |  | 1.44 |  | 1.7 |  | 1.66 |  | LS |  |  | mg/l |  | 1.6
pH |  | 8.31 |  | 8.09 |  | 8.26 |  | 8.19 |  |  | Std units |  | 8.2125
CONDUCTIVITY |  | 12580 |  | 12640 |  | 12720 |  | 12600 |  |  | umho/cm |  | 12635
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.05 | < | 0.05 | < | 0.05 | < | 0.05 |  |  | mg/l |  | 0.05
SULFATE |  | 850 |  | 850 |  | 950 |  | 850 |  |  | mg/l |  | 875
C.O.D. 'S |  | 190 |  | 170 |  | 190 |  | 180 |  |  | mg/l |  | 182.5
IRON |  | 0.91 |  | 0.91 |  | 1.01 |  | 1.01 |  |  | mg/l |  | 0.96
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
LOWER MONITORING INTERVAL | [6 empty] | 1,970' - 2,027' |  |  |  | Ft. bls
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 45.65 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 36.6 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 69 |  | 67 |  | 69 |  | 71 |  |  | degrees (F) |  | 69
TDS |  | 28400 |  | 27930 |  | 28380 |  | 28112 |  |  | mg/l |  | 28205.5
CHLORIDE |  | 17000 |  | 17000 |  | 17200 |  | 17000 |  |  | mg/l |  | 17050
AMMONIA-N |  | 2.41 |  | 2.43 |  | 2.43 |  | 2.44 |  |  | mg/l |  | 2.4275
TKN |  | 3.15 |  | 3.27 |  | 0.421 |  | 2.3 |  |  | mg/l |  | 2.2853
pH |  | 7.48 |  | 7.25 |  | 7.49 |  | 7.38 |  |  | Std units |  | 7.4
CONDUCTIVITY |  | 45500 |  | 46200 |  | 46200 |  | 45600 |  |  | umho/cm |  | 45875
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.05 | < | 0.05 | < | 0.05 | < | 0.05 |  |  | mg/l |  | 0.05
SULFATE |  | 2400 |  | 2300 |  | 2400 |  | 2200 |  |  | mg/l |  | 2325
C.O.D. 'S |  | 860 |  | 810 |  | 820 |  | 810 |  |  | mg/l |  | 825
IRON |  | 0.05 |  | 0.07 |  | 0.04 |  | 0.05 |  |  | mg/l |  | 0.0525
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
PAGE 26
UNDERGROUND INJECTION CONTROL SECTION
MONTHLY OPERATING REPORT DATA SUMMARY
FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT MONTH/YEAR |  |  | JANUARY |  | 2004
I.D. NUMBER: 5006M02066 | [5 empty] | LEAD OPERATOR: |  |  |  | MIKE JUST
TELEPHONE NUMBER: (954) 523-1002
REGIONAL MONITORING WELL DATA
RMW-1
PERMIT NUMBER | [6 empty] | 0054569-142-UO
PERMIT EXPIRATION DATE |  | 2009-01-06
UPPER MONITORING INTERVAL | [6 empty] | 1300' - 1339' |  |  |  | Ft. bls.
Sample Date |  | 2004-01-06
Submittal Date |  | 2004-01-07
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 73.82 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 42.44 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 72 | [8 empty] | degrees (F) |  | 72
TDS |  | 5460 | [8 empty] | mg/l |  | 5460
CHLORIDE |  | 3050 | [8 empty] | mg/l |  | 3050
AMMONIA-N |  | 0.699 | [8 empty] | mg/l |  | 0.699
TKN |  | 1.28 | [8 empty] | mg/l |  | 1.28
pH |  | 8.59 | [8 empty] | Std units |  | 8.59
CONDUCTIVITY |  | 9650 | [8 empty] | umho/cm |  | 9650
FECAL COLIFORM |  | 0 | [8 empty] | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.05 | [8 empty] | mg/l |  | 0.05
SULFATE |  | 650 | [8 empty] | mg/l |  | 650
C.O.D. 'S |  | 120 | [8 empty] | mg/l |  | 120
IRON |  | 1.51 | [8 empty] | mg/l |  | 1.51
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
LOWER MONITORING INTERVAL | [6 empty] | 1500' - 1600' |  |  |  | Ft. bls
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 22.38 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 22.05 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 70 | [8 empty] | degrees (F) |  | 70
TDS |  | 26330 | [8 empty] | mg/l |  | 26330
CHLORIDE |  | 16400 | [8 empty] | mg/l |  | 16400
AMMONIA-N |  | 0.377 | [8 empty] | mg/l |  | 0.377
TKN |  | 0.883 | [8 empty] | mg/l |  | 0.883
pH |  | 7.62 | [8 empty] | Std units |  | 7.62
CONDUCTIVITY |  | 43500 | [8 empty] | umho/cm |  | 43500
FECAL COLIFORM |  | 0 | [8 empty] | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.05 | [8 empty] | mg/l |  | 0.05
SULFATE |  | 1500 | [8 empty] | mg/l |  | 1500
C.O.D. 'S |  | 670 | [8 empty] | mg/l |  | 670
IRON |  | 0.05 | [8 empty] | mg/l |  | 0.05
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
PAGE 27
Formulas:
LEAD OPERATOR: = [LEAD OPERATOR:, row above]+1

## WELL PRN DATA
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 1 |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
1 | 10.24 | 4.79 | 8.07 | 51.12 | 39.23 | 46.01
2 | 12.04 | 3.9 | 8.08 | 57.64 | 37.66 | 46.14 |  |  | FLOW
3 | 11.06 | 4.49 | 8.02 | 54.05 | 38.62 | 46.1 | I |  | MAX | 10.24 | 12.04 | 11.06 | 11.63 | 11.91 | 10.06 | 10.08 | 10.1 | 12.1 | 11.31 | 15.59 | 10.72 | 12.51 | 11.09 | 10.15 | 10.14 | 11 | 11.76 | 11.96 | 11.95 | 12.15 | 13.68 | 12.86 | 12.12 | 11.63 | 11.11 | 14.79 | 12.14 | 12.14 | 12.43 | 15.71
4 | 11.63 | 4.09 | 8.11 | 56.35 | 37.98 | 46.51 | N |  | MIN | 4.79 | 3.9 | 4.49 | 4.09 | 4.12 | 4.28 | 4.47 | 3.85 | 3.94 | 4.68 | 5.39 | 5.47 | 3.8 | 4.69 | 4.46 | 4.59 | 4.38 | 4.77 | 4.75 | 4.7 | 4.75 | 4.79 | 4.42 | 4.83 | 4.82 | 4.81 | 0 | 4.54 | 3.98 | 4.57 | 5.78
5 | 11.91 | 4.12 | 8.02 | 57.46 | 38.08 | 46.53 | J |  | TOT | 8.07 | 8.08 | 8.02 | 8.11 | 8.02 | 7.89 | 7.9 | 7.99 | 8.16 | 7.99 | 10.13 | 8.5 | 8.07 | 8.12 | 8.2 | 8.21 | 8.05 | 8.21 | 8.51 | 8.33 | 8.29 | 8.31 | 8.42 | 8.24 | 8.18 | 8.33 | 7.69 | 8.07 | 7.98 | 7.81 | 11.73
6 | 10.06 | 4.28 | 7.89 | 50.92 | 38.3 | 45.75 | E | INJECTION WELL ONE
7 | 10.08 | 4.47 | 7.9 | 50.9 | 38.68 | 45.69 | C |  | PSI
8 | 10.1 | 3.85 | 7.99 | 50.88 | 37.46 | 45.85 | T |  | MAX | 51.12 | 57.64 | 54.05 | 56.35 | 57.46 | 50.92 | 50.9 | 50.88 | 57.77 | 55.28 | 69.72 | 52.88 | 57.81 | 54.2 | 50.59 | 50.6 | 54.84 | 56.71 | 57.66 | 57.07 | 57.31 | 63.41 | 59.75 | 56.79 | 55.24 | 53.93 | 67.08 | 57.73 | 58.12 | 59.49 | 71.4
9 | 12.1 | 3.94 | 8.16 | 57.77 | 37.33 | 46.39 | O |  | MIN | 39.23 | 37.66 | 38.62 | 37.98 | 38.08 | 38.3 | 38.68 | 37.46 | 37.33 | 38.62 | 39.37 | 39.68 | 37.31 | 38.57 | 38.17 | 38.82 | 38.15 | 38.76 | 38.81 | 38.63 | 38.48 | 38.4 | 37.69 | 38.33 | 38.39 | 38.45 | 34.78 | 38.19 | 37.25 | 38.52 | 41.08
10 | 11.31 | 4.68 | 7.99 | 55.28 | 38.62 | 45.93 | N |  | AVG | 46.01 | 46.14 | 46.1 | 46.51 | 46.53 | 45.75 | 45.69 | 45.85 | 46.39 | 45.93 | 51.79 | 46.79 | 45.9 | 46.04 | 46.03 | 46.11 | 45.93 | 46.58 | 47.27 | 46.74 | 46.46 | 46.39 | 46.7 | 46.14 | 46.25 | 46.61 | 45.89 | 45.54 | 45.51 | 45.4 | 57.08
11 | 15.59 | 5.39 | 10.13 | 69.72 | 39.37 | 51.79
12 | 10.72 | 5.47 | 8.5 | 52.88 | 39.68 | 46.79 | W
13 | 12.51 | 3.8 | 8.07 | 57.81 | 37.31 | 45.9 | E
14 | 11.09 | 4.69 | 8.12 | 54.2 | 38.57 | 46.04 | L
15 | 10.15 | 4.46 | 8.2 | 50.59 | 38.17 | 46.03 | L
16 | 10.14 | 4.59 | 8.21 | 50.6 | 38.82 | 46.11 | O
17 | 11 | 4.38 | 8.05 | 54.84 | 38.15 | 45.93 | N
18 | 11.76 | 4.77 | 8.21 | 56.71 | 38.76 | 46.58 | E
19 | 11.96 | 4.75 | 8.51 | 57.66 | 38.81 | 47.27
20 | 11.95 | 4.7 | 8.33 | 57.07 | 38.63 | 46.74 | D
21 | 12.15 | 4.75 | 8.29 | 57.31 | 38.48 | 46.46 | A
22 | 13.68 | 4.79 | 8.31 | 63.41 | 38.4 | 46.39 | T
23 | 12.86 | 4.42 | 8.42 | 59.75 | 37.69 | 46.7 | A
24 | 12.12 | 4.83 | 8.24 | 56.79 | 38.33 | 46.14
25 | 11.63 | 4.82 | 8.18 | 55.24 | 38.39 | 46.25
26 | 11.11 | 4.81 | 8.33 | 53.93 | 38.45 | 46.61
27 | 14.79 | 0 | 7.69 | 67.08 | 34.78 | 45.89
28 | 12.14 | 4.54 | 8.07 | 57.73 | 38.19 | 45.54
29 | 12.14 | 3.98 | 7.98 | 58.12 | 37.25 | 45.51
30 | 12.43 | 4.57 | 7.81 | 59.49 | 38.52 | 45.4
31 | 15.71 | 5.78 | 11.73 | 71.4 | 41.08 | 57.08
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 2 |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
1 | 10.3 | 4.43 | 8.08 | 50.13 | 38.45 | 45.12
2 | 12.25 | 3.28 | 8.09 | 56.6 | 36.95 | 45.29 |  |  | FLOW
3 | 11.22 | 4.06 | 8.04 | 53.07 | 37.9 | 45.25 | I |  | MAX | 10.3 | 12.25 | 11.22 | 11.79 | 12.13 | 10.16 | 10.19 | 10.21 | 12.26 | 11.5 | 15.66 | 10.83 | 12.68 | 11.21 | 10.26 | 10.26 | 11.11 | 11.92 | 12.18 | 12.01 | 12.3 | 13.83 | 13.09 | 12.17 | 11.77 | 11.29 | 15.15 | 12.31 | 12.32 | 12.76 | 16.15
4 | 11.79 | 3.53 | 8.1 | 55.39 | 37.27 | 45.64 | N |  | MIN | 4.43 | 3.28 | 4.06 | 3.53 | 3.63 | 3.86 | 4.05 | 3.17 | 3.48 | 4.41 | 5.21 | 5.35 | 3.06 | 4.43 | 4.19 | 4.43 | 4.08 | 4.56 | 4.53 | 4.51 | 4.55 | 4.56 | 4.09 | 4.7 | 4.62 | 4.62 | 0.02 | 0.02 | 3.57 | 4.24 | 5.62
5 | 12.13 | 3.63 | 8.01 | 56.42 | 37.37 | 45.68 | J |  | TOT | 8.08 | 8.09 | 8.04 | 8.1 | 8.01 | 7.88 | 7.88 | 7.98 | 8.15 | 7.99 | 10.24 | 8.59 | 8.09 | 8.13 | 8.23 | 8.26 | 8.08 | 8.26 | 8.56 | 8.39 | 8.34 | 8.36 | 8.49 | 8.3 | 8.23 | 8.4 | 8.5 | 7.88 | 8.03 | 7.84 | 11.96
6 | 10.16 | 3.86 | 7.88 | 49.96 | 37.57 | 44.91 | E | INJECTION WELL TWO
7 | 10.19 | 4.05 | 7.88 | 49.95 | 38.03 | 44.79 | C |  | PSI
8 | 10.21 | 3.17 | 7.98 | 49.95 | 36.73 | 44.95 | T |  | MAX | 50.13 | 56.6 | 53.07 | 55.39 | 56.42 | 49.96 | 49.95 | 49.95 | 56.77 | 54.21 | 68.42 | 51.81 | 56.64 | 57.68 | 49.63 | 49.65 | 53.78 | 55.59 | 56.53 | 56.04 | 56.16 | 62.25 | 58.68 | 55.77 | 54.1 | 53 | 65.84 | 56.6 | 57.08 | 58.42 | 69.99
9 | 12.26 | 3.48 | 8.15 | 56.77 | 36.58 | 45.49 | I |  | MIN | 38.45 | 36.95 | 37.9 | 37.27 | 37.37 | 37.57 | 38.03 | 36.73 | 36.58 | 37.87 | 38.56 | 38.93 | 36.56 | 37.81 | 37.38 | 38.03 | 37.36 | 38.02 | 38.08 | 37.89 | 37.7 | 37.64 | 36.9 | 37.53 | 37.6 | 37.76 | 35.69 | 35.1 | 36.47 | 37.76 | 40.27
10 | 11.5 | 4.41 | 7.99 | 54.21 | 37.87 | 45.01 | O |  | AVG | 45.12 | 45.29 | 45.25 | 45.64 | 45.68 | 44.91 | 44.79 | 44.95 | 45.49 | 45.01 | 50.78 | 45.88 | 45.02 | 45.16 | 45.11 | 45.23 | 45.02 | 45.69 | 46.4 | 45.83 | 45.55 | 45.48 | 45.78 | 45.27 | 45.33 | 45.75 | 46.35 | 44.37 | 44.61 | 44.5 | 55.95
11 | 15.66 | 5.21 | 10.24 | 68.42 | 38.56 | 50.78 | N
12 | 10.83 | 5.35 | 8.59 | 51.81 | 38.93 | 45.88
13 | 12.68 | 3.06 | 8.09 | 56.64 | 36.56 | 45.02 | W
14 | 11.21 | 4.43 | 8.13 | 53.25 | 37.81 | 45.16 | E
15 | 10.26 | 4.19 | 8.23 | 49.63 | 37.38 | 45.11 | L
16 | 10.26 | 4.43 | 8.26 | 49.65 | 38.03 | 45.23 | L
17 | 11.11 | 4.08 | 8.08 | 53.78 | 37.36 | 45.02
18 | 11.92 | 4.56 | 8.26 | 55.59 | 38.02 | 45.69 | T
19 | 12.18 | 4.53 | 8.56 | 56.53 | 38.08 | 46.4 | W
20 | 12.01 | 4.51 | 8.39 | 56.04 | 37.89 | 45.83 | O
21 | 12.3 | 4.55 | 8.34 | 56.16 | 37.7 | 45.55
22 | 13.83 | 4.56 | 8.36 | 62.25 | 37.64 | 45.48 | D
23 | 13.09 | 4.09 | 8.49 | 58.68 | 36.9 | 45.78 | A
24 | 12.17 | 4.7 | 8.3 | 55.77 | 37.53 | 45.27 | T
25 | 11.77 | 4.62 | 8.23 | 54.1 | 37.6 | 45.33 | A
26 | 11.29 | 4.62 | 8.4 | 53 | 37.76 | 45.75
27 | 15.15 | 0.02 | 8.5 | 65.84 | 35.69 | 46.35
28 | 12.31 | 0.02 | 7.88 | 56.6 | 35.1 | 44.37
29 | 12.32 | 3.57 | 8.03 | 57.08 | 36.47 | 44.61
30 | 12.76 | 4.24 | 7.84 | 58.42 | 37.76 | 44.5
31 | 16.15 | 5.62 | 11.96 | 69.99 | 40.27 | 55.95
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 3 |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
1 | 9.02 | 3.93 | 7.05 | 51.37 | 39.32 | 46.2
2 | 10.61 | 2.96 | 7.04 | 57.99 | 37.78 | 46.37 |  |  | FLOW
3 | 9.72 | 3.59 | 6.98 | 54.37 | 38.75 | 46.3 | I |  | MAX | 9.02 | 10.61 | 9.72 | 10.3 | 10.64 | 8.84 | 8.83 | 8.88 | 10.69 | 10.01 | 13.79 | 9.43 | 10.35 | 9.86 | 8.92 | 8.91 | 9.62 | 10.37 | 10.59 | 10.45 | 10.72 | 12.03 | 11.4 | 10.62 | 10.29 | 9.77 | 13.89 | 10.72 | 10.76 | 11.06 | 14.21
4 | 10.3 | ER | 6.41 | 56.67 | 35.53 | 45.77 | N |  | MIN | 3.93 | 2.96 | 3.59 | ER | 3.23 | 3.42 | 2.27 | 2.86 | 3.09 | 3.83 | 4.57 | 4.73 | ER | 3.91 | 3.71 | 3.88 | 3.56 | 3.94 | 3.95 | 3.9 | 3.96 | 3.99 | 3.6 | 4.09 | 4.03 | 3.97 | ER | 3.78 | 3.17 | 3.71 | 4.9
5 | 10.64 | 3.23 | 7 | 57.83 | 38.2 | 46.75 | J |  | TOT | 7.05 | 7.04 | 6.98 | 6.41 | 7 | 6.86 | 6.84 | 6.95 | 7.11 | 6.96 | 9.05 | 7.52 | 7.03 | 7.12 | 7.18 | 7.2 | 7.05 | 7.18 | 7.45 | 7.3 | 7.26 | 7.27 | 7.39 | 7.22 | 7.15 | 7.31 | 7.3 | 7.06 | 7 | 6.75 | 10.53
6 | 8.84 | 3.42 | 6.86 | 51.16 | 38.43 | 45.94 | E | INJECTION WELL THREE
7 | 8.83 | 2.27 | 6.84 | 51.13 | 37.63 | 45.83 | C |  | PSI
8 | 8.88 | 2.86 | 6.95 | 51.12 | 37.58 | 46.03 | T |  | MAX | 51.37 | 57.99 | 54.37 | 56.67 | 57.83 | 51.16 | 51.13 | 51.12 | 58.08 | 55.58 | 70.3 | 53.14 | 55.86 | 54.47 | 50.82 | 50.85 | 55.04 | 57.01 | 57.98 | 57.47 | 57.66 | 63.83 | 60.09 | 57.15 | 55.42 | 54.25 | 71 | 58.09 | 58.49 | 59.85 | 72
9 | 10.69 | 3.09 | 7.11 | 58.08 | 37.47 | 46.6 | I |  | MIN | 39.32 | 37.78 | 38.75 | 35.53 | 38.2 | 38.43 | 37.63 | 37.58 | 37.47 | 38.75 | 39.57 | 39.87 | 35.89 | 38.74 | 38.32 | 38.97 | 38.27 | 38.89 | 38.96 | 38.79 | 38.65 | 38.55 | 37.83 | 38.49 | 38.54 | 38.62 | 35.58 | 38.33 | 37.39 | 38.65 | 41.25
10 | 10.01 | 3.83 | 6.96 | 55.58 | 38.75 | 46.1 | O |  | AVG | 46.2 | 46.37 | 46.3 | 45.77 | 46.75 | 45.94 | 45.83 | 46.03 | 46.6 | 46.1 | 52.1 | 47.01 | 46.02 | 46.23 | 46.22 | 46.31 | 46.11 | 46.78 | 47.52 | 46.94 | 46.69 | 46.6 | 46.92 | 46.38 | 46.4 | 46.84 | 47.36 | 45.76 | 45.71 | 45.59 | 57.47
11 | 13.79 | 4.57 | 9.05 | 70.3 | 39.57 | 52.1 | N
12 | 9.43 | 4.73 | 7.52 | 53.14 | 39.87 | 47.01
13 | 10.35 | ER | 7.03 | 55.86 | 35.89 | 46.02 | W
14 | 9.86 | 3.91 | 7.12 | 54.47 | 38.74 | 46.23 | E
15 | 8.92 | 3.71 | 7.18 | 50.82 | 38.32 | 46.22 | L
16 | 8.91 | 3.88 | 7.2 | 50.85 | 38.97 | 46.31 | L
17 | 9.62 | 3.56 | 7.05 | 55.04 | 38.27 | 46.11
18 | 10.37 | 3.94 | 7.18 | 57.01 | 38.89 | 46.78 | T
19 | 10.59 | 3.95 | 7.45 | 57.98 | 38.96 | 47.52 | H
20 | 10.45 | 3.9 | 7.3 | 57.47 | 38.79 | 46.94 | R
21 | 10.72 | 3.96 | 7.26 | 57.66 | 38.65 | 46.69 | E
22 | 12.03 | 3.99 | 7.27 | 63.83 | 38.55 | 46.6 | E
23 | 11.4 | 3.6 | 7.39 | 60.09 | 37.83 | 46.92
24 | 10.62 | 4.09 | 7.22 | 57.15 | 38.49 | 46.38 | D
25 | 10.29 | 4.03 | 7.15 | 55.42 | 38.54 | 46.4 | A
26 | 9.77 | 3.97 | 7.31 | 54.25 | 38.62 | 46.84 | T
27 | 13.89 | ER | 7.3 | 71 | 35.58 | 47.36 | A
28 | 10.72 | 3.78 | 7.06 | 58.09 | 38.33 | 45.76
29 | 10.76 | 3.17 | 7 | 58.49 | 37.39 | 45.71
30 | 11.06 | 3.71 | 6.75 | 59.85 | 38.65 | 45.59
31 | 14.21 | 4.9 | 10.53 | 72 | 41.25 | 57.47
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 4 |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
1 | 0.16 | 0.12 | 0.13 | 36.77 | 35.18 | 36.06
2 | 0.16 | 0.13 | 0.13 | 37.36 | 35.02 | 36.16 |  |  | FLOW
3 | 0.16 | 0.13 | 0.14 | 37.13 | 35.29 | 36.24 | I |  | MAX | 0.16 | 0.16 | 0.16 | 0.16 | 0.15 | 0.17 | 0.13 | 0.16 | 0.16 | 0.13 | 0.14 | 0.15 | 0.16 | 0.15 | 0.15 | 0.16 | 0.15 | 0.14 | 0.15 | 0.15 | 0.13 | 0.15 | 0.15 | 0.15 | 0.15 | 0.14 | 19.56 | 15.42 | 0.15 | 10.19 | 0.12
4 | 0.16 | 0.13 | 0.14 | 37.42 | 35.22 | 36.28 | N |  | MIN | 0.12 | 0.13 | 0.13 | 0.13 | 0.13 | 0.12 | 0.12 | 0.12 | 0.12 | 0.11 | 0.1 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.12 | 0.12 | 0.11 | 0.11 | 0.11 | 0.11 | 0.1 | 0.1 | 0.12 | 0.12 | 0.11 | 0.11 | ER | 0.12
5 | 0.15 | 0.13 | 0.13 | 37.64 | 35.25 | 36.37 | J |  | TOT | 0.13 | 0.13 | 0.14 | 0.14 | 0.13 | 0.14 | 0.12 | 0.13 | 0.13 | 0.12 | 0.12 | 0.13 | 0.13 | 0.12 | 0.12 | 0.13 | 0.12 | 0.13 | 0.13 | 0.13 | 0.12 | 0.13 | 0.12 | 0.12 | 0.12 | 0.13 | 0.96 | 0.47 | 0.12 | ER | 0.12
6 | 0.17 | 0.12 | 0.14 | 36.94 | 35.28 | 36.29 | E | INJECTION WELL FOUR
7 | 0.13 | 0.12 | 0.12 | 36.91 | 35.23 | 36.18 | C |  | PSI
8 | 0.16 | 0.12 | 0.13 | 36.89 | 35 | 36.21 | T |  | MAX | 36.77 | 37.36 | 37.13 | 37.42 | 37.64 | 36.94 | 36.91 | 36.89 | 37.66 | 37.32 | 36.06 | 36.88 | 36.9 | 55.28 | 36.73 | 36.77 | 37.06 | 37.35 | 37.42 | 37.22 | 37.19 | 37.31 | 36.94 | 37.08 | 37.09 | 36.86 | 60.48 | 50.85 | 37.45 | 48.35 | 36.44
9 | 0.16 | 0.12 | 0.13 | 37.66 | 35 | 36.26 | I |  | MIN | 35.18 | 35.02 | 35.29 | 35.22 | 35.25 | 35.28 | 35.23 | 35 | 35 | 35.17 | 34.61 | 34.42 | 34.8 | 34.98 | 34.98 | 35.13 | 35.05 | 35.12 | 35.07 | 34.96 | 34.81 | ER | ER | 34.62 | 34.66 | 34.71 | 34.77 | 35 | 35.03 | 35.17 | 35.22
10 | 0.13 | 0.11 | 0.12 | 37.32 | 35.17 | 36.15 | O |  | AVG | 36.06 | 36.16 | 36.24 | 36.28 | 36.37 | 36.29 | 36.18 | 36.21 | 36.26 | 36.15 | 35.27 | 35.88 | 36.06 | 36.09 | 36.04 | 36.06 | 35.99 | 36.09 | 36.14 | 36.01 | 35.92 | 13.88 | 16.9 | 35.77 | 35.81 | 35.88 | 36.99 | 36.32 | 36.09 | 38.56 | 35.72
11 | 0.14 | 0.1 | 0.12 | 36.06 | 34.61 | 35.27 | N
12 | 0.15 | 0.11 | 0.13 | 36.88 | 34.42 | 35.88
13 | 0.16 | 0.11 | 0.13 | 36.9 | 34.8 | 36.06 | W
14 | 0.15 | 0.11 | 0.12 | 37.11 | 34.98 | 36.09 | E
15 | 0.15 | 0.11 | 0.12 | 36.73 | 34.98 | 36.04 | L
16 | 0.16 | 0.11 | 0.13 | 36.77 | 35.13 | 36.06 | L
17 | 0.15 | 0.11 | 0.12 | 37.06 | 35.05 | 35.99
18 | 0.14 | 0.12 | 0.13 | 37.35 | 35.12 | 36.09 | F
19 | 0.15 | 0.12 | 0.13 | 37.42 | 35.07 | 36.14 | O
20 | 0.15 | 0.11 | 0.13 | 37.22 | 34.96 | 36.01 | U
21 | 0.13 | 0.11 | 0.12 | 37.19 | 34.81 | 35.92 | R
22 | 0.15 | 0.11 | 0.13 | 37.31 | ER | 13.88
23 | 0.15 | 0.11 | 0.12 | 36.94 | ER | 16.9 | D
24 | 0.15 | 0.1 | 0.12 | 37.08 | 34.62 | 35.77 | A
25 | 0.15 | 0.1 | 0.12 | 37.09 | 34.66 | 35.81 | T
26 | 0.14 | 0.12 | 0.13 | 36.86 | 34.71 | 35.88 | A
27 | 19.56 | 0.12 | 0.96 | 60.48 | 34.77 | 36.99
28 | 15.42 | 0.11 | 0.47 | 50.85 | 35 | 36.32
29 | 0.15 | 0.11 | 0.12 | 37.45 | 35.03 | 36.09
30 | 10.19 | ER | ER | 48.35 | 35.17 | 38.56
31 | 0.12 | 0.12 | 0.12 | 36.44 | 35.22 | 35.72
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 5 |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
1 | 8.97 | 4.31 | 7.2 | 50.84 | 39.13 | 45.68
2 | 10.57 | 3.4 | 7.19 | 57.36 | 37.57 | 45.95 |  |  | FLOW
3 | 9.71 | 3.97 | 7.15 | 53.7 | 38.55 | 45.84 | I |  | MAX | 8.97 | 10.57 | 9.71 | 10.22 | 10.5 | 8.82 | 8.84 | 8.85 | 10.58 | 9.93 | 6.97 | 9.38 | 10.89 | 9.7 | 8.85 | 8.85 | 9.59 | 10.29 | 10.48 | 10.42 | 10.58 | 11.94 | 11.24 | 10.49 | 10.15 | 9.74 | 13.5 | 10.63 | 10.69 | 11.01 | 7.67
4 | 10.22 | 3.57 | 7.23 | 55.98 | 37.94 | 46.24 | N |  | MIN | 4.31 | 3.4 | 3.97 | 3.57 | 3.67 | 3.83 | 3.85 | 3.3 | 3.49 | 4.26 | ER | ER | 3.57 | 4.24 | 4.07 | 4.21 | 3.97 | 4.35 | 4.34 | 4.33 | 4.33 | 4.38 | 3.96 | 4.46 | 4.42 | 4.39 | ER | 4.14 | 3.57 | 4.12 | ER
5 | 10.5 | 3.67 | 7.15 | 57.37 | 37.99 | 46.42 | J |  | TOT | 7.2 | 7.19 | 7.15 | 7.23 | 7.15 | 7.03 | 7.02 | 7.1 | 7.24 | 7.12 | ER | ER | 7.21 | 7.21 | 7.27 | 7.29 | 7.17 | 7.31 | 7.55 | 7.42 | 7.38 | 7.39 | 7.49 | 7.34 | 7.28 | 7.43 | 7.34 | 7.19 | 7.14 | 6.85 | 0.98
6 | 8.82 | 3.83 | 7.03 | 51 | 38.26 | 45.5 | E | INJECTION WELL FIVE
7 | 8.84 | 3.85 | 7.02 | 50.84 | 38.54 | 45.54 | C |  | PSI
8 | 8.85 | 3.3 | 7.1 | 51.06 | 37.31 | 45.72 | T |  | MAX | 50.84 | 57.36 | 53.7 | 55.98 | 57.37 | 51 | 50.84 | 51.06 | 58.23 | 55.44 | 45.85 | 56.48 | 59.43 | 55.15 | 54.32 | 53.8 | 54.74 | 57.68 | 58.75 | 57.09 | 58.36 | 64.72 | 59.72 | 59.53 | 54.8 | 57.61 | 64.92 | 53.48 | 55.43 | 56.08 | 47.08
9 | 10.58 | 3.49 | 7.24 | 58.23 | 37.3 | 46.29 | I |  | MIN | 39.13 | 37.57 | 38.55 | 37.94 | 37.99 | 38.26 | 38.54 | 37.31 | 37.3 | 38.36 | 31.62 | 31.25 | 38.09 | 36.76 | 29.48 | 28.02 | 37.14 | 37.14 | 38.08 | 36.32 | 37.65 | 35.04 | 33.42 | 14.69 | 24.49 | 26.03 | 26.48 | 24.82 | 25.55 | 0.98 | 33.83
10 | 9.93 | 4.26 | 7.12 | 55.44 | 38.36 | 45.98 | O |  | AVG | 45.68 | 45.95 | 45.84 | 46.24 | 46.42 | 45.5 | 45.54 | 45.72 | 46.29 | 45.98 | 34.28 | 43.59 | 46.22 | 44.44 | 44.25 | 43.88 | 45.68 | 46.66 | 47.13 | 47.18 | 46.72 | 46.4 | 45.17 | 42.91 | 43.26 | 43.47 | 43.74 | 42.6 | 42.92 | 43.78 | 35.7
11 | 6.97 | ER | ER | 45.85 | 31.62 | 34.28 | N
12 | 9.38 | ER | ER | 56.48 | 31.25 | 43.59
13 | 10.89 | 3.57 | 7.21 | 59.43 | 38.09 | 46.22 | W
14 | 9.7 | 4.24 | 7.21 | 55.15 | 36.76 | 44.44 | E
15 | 8.85 | 4.07 | 7.27 | 54.32 | 29.48 | 44.25 | L
16 | 8.85 | 4.21 | 7.29 | 53.8 | 28.02 | 43.88 | L
17 | 9.59 | 3.97 | 7.17 | 54.74 | 37.14 | 45.68
18 | 10.29 | 4.35 | 7.31 | 57.68 | 37.14 | 46.66 | F
19 | 10.48 | 4.34 | 7.55 | 58.75 | 38.08 | 47.13 | I
20 | 10.42 | 4.33 | 7.42 | 57.09 | 36.32 | 47.18 | V
21 | 10.58 | 4.33 | 7.38 | 58.36 | 37.65 | 46.72 | E
22 | 11.94 | 4.38 | 7.39 | 64.72 | 35.04 | 46.4
23 | 11.24 | 3.96 | 7.49 | 59.72 | 33.42 | 45.17 | D
24 | 10.49 | 4.46 | 7.34 | 59.53 | 14.69 | 42.91 | A
25 | 10.15 | 4.42 | 7.28 | 54.8 | 24.49 | 43.26 | T
26 | 9.74 | 4.39 | 7.43 | 57.61 | 26.03 | 43.47 | A
27 | 13.5 | ER | 7.34 | 64.92 | 26.48 | 43.74
28 | 10.63 | 4.14 | 7.19 | 53.48 | 24.82 | 42.6
29 | 10.69 | 3.57 | 7.14 | 55.43 | 25.55 | 42.92
30 | 11.01 | 4.12 | 6.85 | 56.08 | 0.98 | 43.78
31 | 7.67 | ER | 0.98 | 47.08 | 33.83 | 35.7

## RMW PRN DATA
julian | u-avg | u-min | u-max | l-avg | l-min | l-max
1 | ER | ER | ER | 44.11 | 44.11 | 44.11 | R |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
2 | ER | ER | ER | 44.17 | 44.18 | 44.18 | E
3 | ER | ER | ER | 44.22 | 44.23 | 44.22 | G |  | LOW
4 | ER | ER | ER | 44.26 | 44.26 | 44.26 | I |  | MIN | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | 22.17 | 22.19 | 22.05 | 22.07 | 22.19 | 22.19
5 | ER | ER | ER | 42.44 | 42.44 | 42.44 | O |  | MAX | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | 22.26 | 22.33 | 22.24 | 22.21 | 22.38 | 22.38
6 | ER | ER | ER | 42.63 | 42.63 | 43.63 | N |  | AVG | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | 22.22 | 22.25 | 22.13 | 22.14 | 22.3 | 22.3
7 | ER | ER | ER | 43.82 | 43.82 | 73.82 | A | RMW
8 | ER | ER | ER | 43.98 | 43.98 | 43.98 | L |  | UP
9 | ER | ER | ER | 44.12 | 44.12 | 44.12 |  |  | MIN | 44.11 | 44.18 | 44.23 | 44.26 | 42.44 | 42.63 | 43.82 | 43.98 | 44.12 | 44.21 | 44.09 | 44.04 | 44.09 | 44.21 | 44.3 | ER | ER | ER | ER | ER | 44.29 | 44.31 | 44.28 | ER | ER | 44.42 | 44.44 | 44.34 | 44.35 | 44.47 | 44.47
10 | ER | ER | ER | 44.21 | 44.21 | 44.21 | M |  | MAX | 44.11 | 44.18 | 44.22 | 44.26 | 42.44 | 43.63 | 73.82 | 43.98 | 44.12 | 44.21 | 44.09 | 44 | 44.09 | 44.21 | 44.3 | ER | ER | ER | ER | ER | 44.29 | 44.31 | 44.28 | ER | ER | 44.49 | 44.54 | 44.47 | 44.47 | 44.63 | 44.63
11 | ER | ER | ER | 44.09 | 44.09 | 44.09 | O |  | AVG | 44.11 | 44.17 | 44.22 | 44.26 | 42.44 | 42.63 | 43.82 | 43.98 | 44.12 | 44.21 | 44.09 | 44.04 | 44.09 | 44.21 | 44.3 | ER | ER | ER | ER | ER | 44.29 | 44.31 | 44.28 | ER | ER | 44.46 | 44.49 | 44.38 | 44.4 | 44.56 | 44.56
12 | ER | ER | ER | 44.04 | 44.04 | 44 | N
13 | ER | ER | ER | 44.09 | 44.09 | 44.09 | I
14 | ER | ER | ER | 44.21 | 44.21 | 44.21 | T
15 | ER | ER | ER | 44.3 | 44.3 | 44.3 | O
16 | ER | ER | ER | ER | ER | ER | R
17 | ER | ER | ER | ER | ER | ER
18 | ER | ER | ER | ER | ER | ER | W
19 | ER | ER | ER | ER | ER | ER | E
20 | ER | ER | ER | ER | ER | ER | L
21 | ER | ER | ER | 44.29 | 44.29 | 44.29 | L
22 | ER | ER | ER | 44.31 | 44.31 | 44.31
23 | ER | ER | ER | 44.28 | 44.28 | 44.28
24 | ER | ER | ER | ER | ER | ER | R
25 | ER | ER | ER | ER | ER | ER | M
26 | 22.22 | 22.17 | 22.26 | 44.46 | 44.42 | 44.49 | W
27 | 22.25 | 22.19 | 22.33 | 44.49 | 44.44 | 44.54
28 | 22.13 | 22.05 | 22.24 | 44.38 | 44.34 | 44.47 | O
29 | 22.14 | 22.07 | 22.21 | 44.4 | 44.35 | 44.47 | N
30 | 22.3 | 22.19 | 22.38 | 44.56 | 44.47 | 44.63 | E
31 | 22.3 | 22.19 | 22.38 | 44.56 | 44.47 | 44.63
31 | 22.36 | 22.3 | 22.4 | 44.63 | 44.59 | 44.69
1 | 41.96 | 41.79 | 42.1 | 48.03 | 47.93 | 48.17 | M |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
2 | 41.98 | 41.86 | 42.16 | 48.05 | 47.97 | 48.21 | O
3 | 42 | 41.91 | 42.16 | 48.07 | 48.01 | 48.27 | N |  | LOW
4 | 42.02 | 41.94 | 42.19 | 48.15 | 48.03 | 48.3 | I |  | MIN | 41.79 | 41.86 | 41.91 | 41.94 | 37.33 | 27.85 | 41.42 | 41.43 | 41.48 | 41.45 | 41.35 | 34.64 | 34.61 | 41.18 | 41.31 | 41.33 | 41.34 | 41.49 | 36.93 | 36.89 | 41.14 | 41.19 | 41.24 | 41.25 | 41.39 | 38.39 | 38.32 | 41.16 | 41.21 | 41.38 | 41.5
5 | 39.49 | 37.33 | 42.2 | 46.78 | 45.29 | 48.32 | T |  | MAX | 42.1 | 42.16 | 42.16 | 42.19 | 42.2 | 41.88 | 41.6 | 41.63 | 41.84 | 41.67 | 41.6 | 41.44 | 41.3 | 41.57 | 41.7 | 41.72 | 41.72 | 41.78 | 41.8 | 41.36 | 41.38 | 41.6 | 41.48 | 41.64 | 41.78 | 41.79 | 41.58 | 41.43 | 41.58 | 41.62 | 41.65
6 | 40.01 | 27.85 | 41.88 | 47.36 | 45.67 | 48.58 | O |  | AVG | 41.96 | 41.98 | 42 | 42.02 | 39.49 | 40.01 | 41.48 | 41.5 | 41.59 | 41.55 | 41.46 | 37.44 | 38.94 | 41.39 | 41.45 | 41.47 | 41.49 | 41.59 | 39.08 | 39.71 | 41.31 | 41.39 | 41.41 | 41.42 | 41.52 | 40.26 | 40.27 | 41.23 | 41.39 | 41.49 | 41.52
7 | 41.48 | 41.42 | 41.6 | 48.07 | 47.98 | 48.23 | R | MW-1
8 | 41.5 | 41.43 | 41.63 | 48.1 | 47.95 | 48.27 |  |  | UP
9 | 41.59 | 41.48 | 41.84 | 48.28 | 48.05 | 48.4 | W |  | MIN | 47.93 | 47.97 | 48.01 | 48.03 | 45.29 | 45.67 | 47.98 | 47.95 | 48.05 | 48.19 | 48.01 | 44.91 | 45.3 | 48.02 | 48.13 | 48.1 | 48.13 | 48.16 | 46.64 | 46.89 | 47.88 | 47.89 | 47.88 | 47.88 | 48.01 | 46.66 | 47 | 47.96 | 48 | 48.16 | 48.24
10 | 41.55 | 41.45 | 41.67 | 48.33 | 48.19 | 48.42 | E |  | MAX | 48.17 | 48.21 | 48.27 | 48.3 | 48.32 | 48.58 | 48.23 | 48.27 | 48.4 | 48.42 | 48.29 | 48.17 | 48.24 | 48.34 | 48.37 | 48.38 | 48.4 | 48.57 | 48.56 | 48.52 | 48.25 | 48.24 | 48.19 | 48.24 | 48.3 | 48.3 | 48.38 | 48.27 | 48.21 | 48.39 | 48.43
11 | 41.46 | 41.35 | 41.6 | 48.07 | 48.01 | 48.29 | L |  | AVG | 48.03 | 48.05 | 48.07 | 48.15 | 46.78 | 47.36 | 48.07 | 48.1 | 48.28 | 48.33 | 48.07 | 46.47 | 47.15 | 48.17 | 48.27 | 48.29 | 48.29 | 48.4 | 47.55 | 47.73 | 48.04 | 48.04 | 48.02 | 48.02 | 48.12 | 47.61 | 47.75 | 48.06 | 48.03 | 48.29 | 48.38
12 | 37.44 | 34.64 | 41.44 | 46.47 | 44.91 | 48.17 | L
13 | 38.94 | 34.61 | 41.3 | 47.15 | 45.3 | 48.24
14 | 41.39 | 41.18 | 41.57 | 48.17 | 48.02 | 48.34 | O
15 | 41.45 | 41.31 | 41.7 | 48.27 | 48.13 | 48.37 | N
16 | 41.47 | 41.33 | 41.72 | 48.29 | 48.1 | 48.38 | E
17 | 41.49 | 41.34 | 41.72 | 48.29 | 48.13 | 48.4
18 | 41.59 | 41.49 | 41.78 | 48.4 | 48.16 | 48.57 | I
19 | 39.08 | 36.93 | 41.8 | 47.55 | 46.64 | 48.56 | N
20 | 39.71 | 36.89 | 41.36 | 47.73 | 46.89 | 48.52 | J
21 | 41.31 | 41.14 | 41.38 | 48.04 | 47.88 | 48.25 | E
22 | 41.39 | 41.19 | 41.6 | 48.04 | 47.89 | 48.24 | C
23 | 41.41 | 41.24 | 41.48 | 48.02 | 47.88 | 48.19 | T
24 | 41.42 | 41.25 | 41.64 | 48.02 | 47.88 | 48.24 | I
25 | 41.52 | 41.39 | 41.78 | 48.12 | 48.01 | 48.3 | O
26 | 40.26 | 38.39 | 41.79 | 47.61 | 46.66 | 48.3 | N
27 | 40.27 | 38.32 | 41.58 | 47.75 | 47 | 48.38
28 | 41.23 | 41.16 | 41.43 | 48.06 | 47.96 | 48.27 | W
29 | 41.39 | 41.21 | 41.58 | 48.03 | 48 | 48.21 | E
30 | 41.49 | 41.38 | 41.62 | 48.29 | 48.16 | 48.39 | L
31 | 41.52 | 41.5 | 41.65 | 48.38 | 48.24 | 48.43 | L
1 | 41.85 | 41.71 | 41.86 | 29.53 | 28.98 | 30.29 | M |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
2 | 41.94 | 41.79 | 41.98 | 29.71 | 29.29 | 30.4 | O
3 | 41.99 | 41.89 | 42.07 | 29.86 | 29.45 | 30.47 | N |  | LOW
4 | 42.03 | 41.97 | 42.15 | 29.99 | 29.63 | 30.62 | I |  | MIN | 41.71 | 41.79 | 41.89 | 41.97 | 38.95 | 38.92 | 41.76 | 41.86 | 42.01 | 42.19 | 42.06 | 37.8 | 37.66 | 41.84 | 42.04 | 42.11 | 42.15 | 42.23 | 31.09 | 31.08 | 41.72 | 41.89 | 41.98 | 42.02 | 42.18 | 39.31 | 38.69 | 39.42 | 39.46 | 39.59 | 39.69
5 | 40.37 | 38.95 | 42.21 | 27.79 | 25.44 | 30.04 | T |  | MAX | 41.86 | 41.98 | 42.07 | 42.15 | 42.21 | 41.87 | 41.94 | 42.07 | 42.28 | 42.3 | 42.19 | 42.14 | 41.86 | 42.1 | 42.23 | 42.31 | 42.34 | 42.52 | 42.52 | 41.85 | 42.02 | 42.11 | 42.14 | 42.24 | 42.36 | 42.41 | 39.72 | 39.63 | 39.63 | 39.77 | 39.81
6 | 40.88 | 38.92 | 41.87 | 28.62 | 25.13 | 31.06 | O |  | AVG | 41.85 | 41.94 | 41.99 | 42.03 | 40.37 | 40.88 | 41.93 | 41.97 | 42.19 | 42.15 | 42.09 | 39.68 | 40.29 | 41.93 | 42.06 | 42.2 | 42.28 | 42.43 | 36 | 38.26 | 41.94 | 41.98 | 42 | 42.05 | 42.34 | 41.06 | 39.45 | 39.53 | 39.5 | 39.7 | 39.76
7 | 41.93 | 41.76 | 41.94 | 29.72 | 29.39 | 30.3 | R | MW-2
8 | 41.97 | 41.86 | 42.07 | 29.98 | 29.57 | 30.64 |  |  | UP
9 | 42.19 | 42.01 | 42.28 | 30.21 | 29.27 | 31.26 | W |  | MIN | 28.98 | 29.29 | 29.45 | 29.63 | 25.44 | 25.13 | 29.39 | 29.57 | 29.27 | 29.02 | 28.62 | 24.66 | 24.09 | 27.78 | 28 | 28.22 | 28.5 | 29.25 | 24.12 | 23.86 | 27.82 | 28.3 | 28.05 | 27.72 | 28.09 | 27.64 | 26.72 | 25.86 | 25.73 | 26.38 | 26.54
10 | 42.15 | 42.19 | 42.3 | 29.81 | 29.02 | 30.27 | E |  | MAX | 30.29 | 30.4 | 30.47 | 30.62 | 30.04 | 31.06 | 30.3 | 30.64 | 31.26 | 30.27 | 30.57 | 29.85 | 29.54 | 30.05 | 30.22 | 30.44 | 30.34 | 30.37 | 29.56 | 29.4 | 29.33 | 29.9 | 29.65 | 30.09 | 30.27 | 30.42 | 28.4 | 27.42 | 27.67 | 27.78 | 27.11
11 | 42.09 | 42.06 | 42.19 | 29.51 | 28.62 | 30.57 | L |  | AVG | 29.53 | 29.71 | 29.86 | 29.99 | 27.79 | 28.62 | 29.72 | 29.98 | 30.21 | 29.81 | 29.51 | 27.09 | 27.25 | 28.71 | 28.88 | 29.04 | 29.33 | 29.63 | 27.08 | 27.1 | 28.5 | 28.95 | 28.68 | 28.69 | 29.15 | 29.01 | 27.39 | 26.35 | 26.54 | 26.9 | 26.86
12 | 39.68 | 37.8 | 42.14 | 27.09 | 24.66 | 29.85 | L
13 | 40.29 | 37.66 | 41.86 | 27.25 | 24.09 | 29.54
14 | 41.93 | 41.84 | 42.1 | 28.71 | 27.78 | 30.05 | T
15 | 42.06 | 42.04 | 42.23 | 28.88 | 28 | 30.22 | W
16 | 42.2 | 42.11 | 42.31 | 29.04 | 28.22 | 30.44 | O
17 | 42.28 | 42.15 | 42.34 | 29.33 | 28.5 | 30.34
18 | 42.43 | 42.23 | 42.52 | 29.63 | 29.25 | 30.37 | I
19 | 36 | 31.09 | 42.52 | 27.08 | 24.12 | 29.56 | N
20 | 38.26 | 31.08 | 41.85 | 27.1 | 23.86 | 29.4 | J
21 | 41.94 | 41.72 | 42.02 | 28.5 | 27.82 | 29.33 | E
22 | 41.98 | 41.89 | 42.11 | 28.95 | 28.3 | 29.9 | C
23 | 42 | 41.98 | 42.14 | 28.68 | 28.05 | 29.65 | T
24 | 42.05 | 42.02 | 42.24 | 28.69 | 27.72 | 30.09 | I
25 | 42.34 | 42.18 | 42.36 | 29.15 | 28.09 | 30.27 | O
26 | 41.06 | 39.31 | 42.41 | 29.01 | 27.64 | 30.42 | N
27 | 39.45 | 38.69 | 39.72 | 27.39 | 26.72 | 28.4
28 | 39.53 | 39.42 | 39.63 | 26.35 | 25.86 | 27.42 | W
29 | 39.5 | 39.46 | 39.63 | 26.54 | 25.73 | 27.67 | E
30 | 39.7 | 39.59 | 39.77 | 26.9 | 26.38 | 27.78 | L
31 | 39.76 | 39.69 | 39.81 | 26.86 | 26.54 | 27.11 | L
1 | 44.99 | 44.89 | 45.06 | 30.97 | 30.86 | 31.09 | M |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
2 | 45.03 | 44.98 | 45.19 | 31.07 | 30.93 | 31.2 | O
3 | 45.2 | 45.1 | 45.27 | 31.13 | 31.03 | 31.25 | N |  | LOW
4 | 45.34 | 45.18 | 45.36 | 31.22 | 31.09 | 31.3 | I |  | MIN | 44.89 | 44.98 | 45.1 | 45.18 | 38.88 | 38.86 | 44.8 | 44.93 | 45.11 | 45.3 | 45.19 | 37.88 | 37.83 | 44.89 | 45.14 | 45.23 | 45.26 | 45.37 | 36.77 | 36.6 | 44.86 | 45.02 | 45.1 | 45.15 | 45.34 | 40.37 | 40.33 | 44.92 | 45.01 | 45.21 | 45.4
5 | 41.71 | 38.88 | 45.39 | 23.13 | 17.15 | 31.31 | T |  | MAX | 45.06 | 45.19 | 45.27 | 45.36 | 45.39 | 44.88 | 44.99 | 45.15 | 45.39 | 45.41 | 45.3 | 45.23 | 44.89 | 45.18 | 45.33 | 45.43 | 45.47 | 45.65 | 45.64 | 44.95 | 45.13 | 45.22 | 45.24 | 45.37 | 45.5 | 45.56 | 45 | 45.06 | 45.22 | 45.46 | 45.54
6 | 42.87 | 38.86 | 44.88 | 26.02 | 16.98 | 30.75 | O |  | AVG | 44.99 | 45.03 | 45.2 | 45.34 | 41.71 | 42.87 | 44.96 | 44.99 | 45.33 | 45.46 | 45.17 | 41.02 | 42.49 | 44.98 | 45.24 | 45.36 | 45.39 | 45.49 | 40.67 | 42.17 | 44.98 | 45.08 | 45.1 | 45.34 | 45.44 | 43.31 | 43.2 | 45 | 45.02 | 45.39 | 45.49
7 | 44.96 | 44.8 | 44.99 | 30.77 | 30.59 | 30.89 | R | MW-3
8 | 44.99 | 44.93 | 45.15 | 30.92 | 30.73 | 31.05 |  |  | UP
9 | 45.33 | 45.11 | 45.39 | 31.12 | 30.9 | 31.25 | W |  | MIN | 30.86 | 30.93 | 31.03 | 31.09 | 17.15 | 16.98 | 30.59 | 30.73 | 30.9 | 31.09 | 30.89 | 17.12 | 16.99 | 30.66 | 30.92 | 31.01 | 31.03 | 31.1 | 18.12 | 18.07 | 30.6 | 30.78 | 30.82 | 30.85 | 31.01 | 22.63 | 22.43 | 30.95 | 31.06 | 31.27 | 31.39
10 | 45.46 | 45.3 | 45.41 | 31.14 | 31.09 | 31.26 | E |  | MAX | 31.09 | 31.2 | 31.25 | 31.3 | 31.31 | 30.75 | 30.89 | 31.05 | 31.25 | 31.26 | 31.14 | 31.05 | 30.73 | 31.09 | 31.21 | 31.29 | 31.31 | 31.47 | 31.44 | 30.81 | 31.02 | 31.09 | 31.1 | 31.19 | 31.28 | 31.34 | 31.08 | 31.19 | 31.34 | 31.54 | 31.59
11 | 45.17 | 45.19 | 45.3 | 30.99 | 30.89 | 31.14 | L |  | AVG | 30.97 | 31.07 | 31.13 | 31.22 | 23.13 | 26.02 | 30.77 | 30.92 | 31.12 | 31.14 | 30.99 | 22.89 | 25.9 | 30.87 | 31.05 | 31.1 | 31.13 | 31.33 | 23.87 | 26.4 | 30.85 | 30.95 | 30.96 | 31 | 31.15 | 27.43 | 27.72 | 31.06 | 31.15 | 31.43 | 31.49
12 | 41.02 | 37.88 | 45.23 | 22.89 | 17.12 | 31.05 | L
13 | 42.49 | 37.83 | 44.89 | 25.9 | 16.99 | 30.73
14 | 44.98 | 44.89 | 45.18 | 30.87 | 30.66 | 31.09 | T
15 | 45.24 | 45.14 | 45.33 | 31.05 | 30.92 | 31.21 | H
16 | 45.36 | 45.23 | 45.43 | 31.1 | 31.01 | 31.29 | R
17 | 45.39 | 45.26 | 45.47 | 31.13 | 31.03 | 31.31 | E
18 | 45.49 | 45.37 | 45.65 | 31.33 | 31.1 | 31.47 | E
19 | 40.67 | 36.77 | 45.64 | 23.87 | 18.12 | 31.44
20 | 42.17 | 36.6 | 44.95 | 26.4 | 18.07 | 30.81 | I
21 | 44.98 | 44.86 | 45.13 | 30.85 | 30.6 | 31.02 | N
22 | 45.08 | 45.02 | 45.22 | 30.95 | 30.78 | 31.09 | J
23 | 45.1 | 45.1 | 45.24 | 30.96 | 30.82 | 31.1 | E
24 | 45.34 | 45.15 | 45.37 | 31 | 30.85 | 31.19 | C
25 | 45.44 | 45.34 | 45.5 | 31.15 | 31.01 | 31.28 | T
26 | 43.31 | 40.37 | 45.56 | 27.43 | 22.63 | 31.34 | I
27 | 43.2 | 40.33 | 45 | 27.72 | 22.43 | 31.08 | O
28 | 45 | 44.92 | 45.06 | 31.06 | 30.95 | 31.19 | N
29 | 45.02 | 45.01 | 45.22 | 31.15 | 31.06 | 31.34
30 | 45.39 | 45.21 | 45.46 | 31.43 | 31.27 | 31.54 | W
31 | 45.49 | 45.4 | 45.54 | 31.49 | 31.39 | 31.59 | E
L
L

## SHIFT DATA
PERSONNEL LIST
|  | SHIFT CODE |  | OPERATOR NAME |  | CERTIFICATION NUMBER |  | SOCIAL SECURITY NUMBER
CHIEF OPERATORS
HOSTNICK, N. | CO# 3207-A | 3 |  | BAYLER, J. | 3 | CO# 4474-A | "A" |  | "A" | 4474 | 3207 | 2D | J. BAROFSKY | 5096-C
McGEARY, J. | CO# 4545-A | 1 |  | HOSTNICK, N. | 1 | CO# 3207-A | "A" |  | "A" | 3207 | 4545 | 5 | S. HULL | 5613-C
BAYLER, J. | CO# 4474-A | 2 |  | McGEARY, J. | 2 | CO# 4545-A | "A" |  | "A" | 4545 | 4474 | 4 | VACANT | X
POMEROY, D. | CO# 421-B | 5 |  | POMEROY, D. | 5 | CO# 421-B | "B" |  | "B" | 421 | 421 | 3 | J. TINKER | 3291-C
[12 empty] | 1 | G. SLAYTON | 2606-B
[12 empty] | 2 | H. WALKER | 4700-A
OPERATOR II' S
THOMAS, P. | CO# 12833 C | 2D |  | BAROFSKY, J. | 2D | CO# 5096-C | [5 empty] | 5 | J. BENTLEY | X
HULL, S. | CO# 5613-C | 4 |  | BENTLEY, J. | 4 | CO# 9366-C | [5 empty] | 1D | S. CURMODE | X
JONES, K. | CO# 2466-B | 5 |  | CURMODE, S. | 5 | CO# 9379-A | [5 empty] | 4 | K. HENDERSON | 5087-B
BENTLEY, J. | CO# 9366-C | 2 |  | HULL, S. | 2 | CO# 5613-C | [5 empty] | 3D | K. JONES | 2466-C
CURMODE, S. | CO# 9379-A | 3 |  | JONES, K. | 3 | CO# 2466-B | [5 empty] | 3 | G. KLEYNHANS | 7367-C
BAROFSKY, J. | CO# 5096-C | 1 |  | THOMAS, P. | 1 | CO# 12833 C | [5 empty] | 2 | A. MORROW | 9164-C
[12 empty] | 1 | J. RAINFORTH | 2718-C
OPERATOR I' S
HENDERSON, K. | CO# 5087-B | 3D |  | FREIDLAND, M. | 3D | CO# 13437-C
SANDERS, C. | CO# 13500-C | 1 |  | HENDERSON, K. | 1 | CO# 5087-B
PEUGEOT, P. | CO# 12817-C | 3 |  | KOKLAS, D. | 3 | CO# 13506-C
KOKLAS, D. | CO# 13506-C | 5 |  | NOBERT, B. | 5 | CO# 9661-C
FREIDLAND, M. | CO# 13437-C | 2 |  | PEUGEOT, P. | 2 | CO# 12817-C
VERBOSH, R. | CO# 12667-C | 1D |  | SANDERS, C. | 1D | CO# 13500-C
NOBERT, B. | CO# 9661-C | 4 |  | VERBOSH, R. | 4 | CO# 12667-C
|  | 4 | 1 | BERNARDI, J | 4 | CO# XXXX-X
|  | 3 | 2 | FREIDLAND, M. | 3 | CO# 13437-C
|  | 5A | 3 | FUTURE, 5A | 5A | CO# XXXX-X
|  | 1 | 4 | HENDERSON, K. | 1 | CO# 5087-B
|  | 2 | 5 | KOKLAS, D. | 2 | CO# 13506-C
|  | 5 | 6 | NOBERT, B. | 5 | CO# 9661-C
|  | 4A | 7 | PEUGEOT, P. | 4A | CO# 12817-C
|  | 1D | 8 | SANDERS, C. | 1D | CO# 13500-C
|  | 3D | 9 | VERBOSH, R. | 3D | CO# 12667-C

## COVER PAGE
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
|  | JANUARY |  | 2004
| OPERATOR | TITLE | CERTIFICATE # | TOTAL COST |  |  | 74732.1123
1 ST SHIFT | HOSTNICK, N. | CHIEF | CO# 3207-A | PEAK TO FLOW RATIO |  |  | 1.1667
2230-0630 | THOMAS, P. | OP. II | CO# 12833 C
| HENDERSON, K. | OP. I | CO# 5087-B |  | TOTAL SUSPENDED SOLIDS
| SANDERS, C. | OP. I DEWAT | CO# 13500-C |  |  |  | LBS/DAY
|  |  |  | RAW INFLUENT |  |  | 36973.3176
2 ND SHIFT |  |  |  | FINAL EFFLUENT |  |  | 4863.5582
0630-1430 | McGEARY, J. | CHIEF | CO# 4545-A |  | TOTAL CBOD
| HULL, S. | OP. II RELIEF | CO# 5613-C |  |  |  | LBS/DAY
| BAROFSKY, J. | OP. II DEWAT | CO# 5096-C | RAW INFLUENT |  |  | 22889.549
| PEUGEOT, P. | OP. I RELIEF | CO# 12817-C | FINAL EFFLUENT |  |  | 1115.964
CHEMICALS
3 RD SHIFT | BAYLER, J. | CHIEF | CO# 4474-A |  |  | COST | POUNDS
1430-2230 | JONES, K. | OP. II | CO# 2466-B | HYDROGEN PEROXIDE |  | 8725.3065 | 62547
| KOKLAS, D. | OP. I | CO# 13506-C | CHLORINE |  | 5360.15 | 36340
| FREIDLAND, M. | OP. I DEWAT | CO# 13437-C | POLYMER |  | 7081.6608 | 11609.28
SLUDGE REMOVED
4 TH SHIFT | [6 empty] | TONS
WEEKEND | BENTLEY, J. | OP. II | CO# 9366-C | DRY TONS |  |  | 435.3088
2230-1030 | VERBOSH, R. | OP. I | CO# 12667-C |  | ENERGY
[6 empty] | COST | KILOWATTS
5 TH SHIFT | POMEROY, D. | CHIEF | 0 | FPL CONSUMPTION |  | 53564.995 | 973909
WEEKEND | CURMODE, S. | OP. II | CO# 9379-A
1030-2230 | NOBERT, B. | OP. I | CO# 9661-C | POPULATION EQUIVALENCE |  |  | 134644.4059
This Monthly Operation Report prepared by: |  |  | BAYLER, J. | CO# 4474-A
State DEP Plant Classification: Class "A" Level "II"
I certify that I am familiar with the information contained in this report and that to the best of my knowledge and
belief, such information is true, complete and accurate.
Facilitiy Manager's Signature: ____________________________________ CO# __________________
Division Manager's Signature: ____________________________________ CO# __________________
Please direct all inquiries reguarding this report to the City Official Mailing Address:
Director of Public Services |  |  | Phone (954) 776-5151
City of Fort Lauderdale
P.O. Drawer 14250 |  |  | Copies mailed: Date ________________ To: DEP _____
Fort Lauderdale, Florida | [5 empty] | DNRP _____
33302
PAGE 1

## PRINT PAGES
UNDERGROUND INJECTION CONTROL SECTION
[28 empty] | MONTHLY OPERATING REPORT DATA SUMMARY | [13 empty] | DEP From # 17-801.900 (1) | [11 empty] | DEP From # 17-801.900 (1) | [19 empty] | DAILY SAMPLE RESULTS - PART B
[25 empty] | FACILITY: GEORGE T. LOHMEYER WWTP |  |  |  |  | REPORT DATE: |  | JANUARY | 2004 | [8 empty] | Form Title:Domestic Wastewater Treatment | [11 empty] | Form Title:Domestic Wastewater Treatment
[25 empty] | I.D. NUMBER: 5006M02066 |  |  |  | CHIEF OPERATOR: |  |  | BAYLER, J. | CO# 4474-A | [8 empty] | Plant Monthly Operating Report | [11 empty] | Plant Monthly Operating Report | [15 empty] | Permit Number: |  | FLA041378 |  |  |  |  | Three-month Average Daily Flow: | [5 empty] | 35.8691
[25 empty] | TELEPHONE NUMBER: (954) 523-1002 | [16 empty] | Effective Date: July 1, 1991 | [11 empty] | Effective Date: July 1, 1991 | [15 empty] | Monitoring Period |  | From: | 2004-01-01 | To: | 2004-01-31 |  | (TMADF):/Permitted Capacity)x100: | [5 empty] | 83.42%
[19 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [8 empty] | INJECTION WELL DATA | [13 empty] | DEP Application No. __________________ | [11 empty] | DEP Application No. __________________ | [11 empty] | Department of Natural Resource Protection
[5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [13 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [6 empty] | IW-1 | IW-2 | IW-3 |  | IW-4 | IW-5 | [35 empty] | Laboratory/Licensing/Enforcement |  |  |  | Flow | Flow | Flow | Flow | Flow | Flow | CBOD5 | CBOD5 | TSS | TSS | pH | pH | TDS | NH-3 | TKN | pH | cond. | temp. | TP
[5 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [13 empty] | MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING | [5 empty] | PERMIT/CERTIFICATION NUMBER: | 0054569-142-UO | 0054569-142-UO | 0054569-142-UO |  | 0054569-142-UO | 0054569-142-UO | [19 empty] | DOMESTIC WASTEWATER TREATMENT PLANT | [11 empty] | BROWARD COUNTY DEPARTMENT OF NATURAL RESOURCE PROTECTION | [5 empty] | 218 S. W. 1st Avenue |  |  | (MGD) | (MGD) | (MGD) | (MGD) | (MGD) | (mg/l) | (mg/l) | (mg/l) | (mg/l) | (Min) | (Max) | mg/L | mg/L | mg/L | units | umho/ | F | mg/L
[5 empty] | MONTHLY OPERATIONAL REPORT | [13 empty] | MONITORING WELL ONE |  |  |  | 1/07/04 thru 1/06/09 |  | PERMIT EXPIRATION DATE: | 2009-01-06 | 2009-01-06 | 2009-01-06 |  | 2009-01-06 | 2009-01-06 | [19 empty] | MONTHLY OPERATING REPORT | [11 empty] | WASTEWATER TREATMENT PLANT | [5 empty] | Fort Lauderdale, FL 33301 | [17 empty] | cm
[5 empty] | PROCESS DATA | [11 empty] | MW-1 | I.D. #: 5066A11311 |  |  | PERMIT # 0054569-142-UO |  |  |  | CASING DEPTH | 2799' | 2798' | 2800' |  | 2804' | 2818' | [8 empty] | DOMESTIC WASTEWATER TREATMENT PLANT |  |  |  |  | (34) | [8 empty] | MONTH: | JANUARY |  | YEAR: | 2004 |  |  |  |  | MONTHLY SLUDGE REPORTS | [5 empty] | Tel. No. (954) 765-4804 | Code | 50050 | 50050 | 50050 | 50050 | 50050 | 50050 | 80082 | 80082 | 00530 | 00530 | 00400 | 00400
| RUN DATE | [14 empty] | RUN DATE | [8 empty] | TOTAL DEPTH | 3513' | 3518' | 3977' |  | 3305' | 3462' | [8 empty] | MONTHLY OPERATING REPORT |  |  |  |  | DAY OF | FLOW | CHLORINE | CHLORINE | CBOD5 | TSS | CBOD5 | TSS | PH |  |  | EFFLUENT NUTRIENTS (MG/L) |  |  | I. | [10 empty] | Mon. Site | INF-001 | EFF-002 | EFF-003 | EFF-004 | EFF-005 | EFF-006 | INF-002 | EFF-001 | INF-002 | EFF-001 | EFF-001 | EFF-001
| 2026-07-30 | [14 empty] | 2026-07-30 |  | UPPER MONITOR ZONE |  |  |  |  | LOWER MONITOR ZONE |  | AVERAGE DAILY FLOW: | 8.31 | 8.3665 | 7.2748 |  | 0.166 | 7.0231 | MGD | [7 empty] | Part II - General Information |  |  |  |  | THE |  | RESIDUAL | RESIDUAL | INFLUENT | INFLUENT | EFFLUENT | EFFLUENT | EFFLUENT | TKN | NH3-N | NITRATE | TOTAL | FECAL | Plant Name: | GEORGE T. LOHMEYER WASTEWATER TREATMENT FACILITY | [6 empty] | MONTH: | JANUARY |  | 1 | 31.093 | 8.07 | 8.08 | 7.05 | 0.13 | 7.2 | 97 | 6 | 116 | 11 | 6.5 | 6.5 | 1220 | 13.66 | 17.2 | 6.5 | 2730 | 80 | 1.78
[17 empty] | MIN | MAX | AVG |  |  | MIN | MAX | AVG | **MAX DAILY FLOW PER MO (mg): | 11.73 | 11.96 | 10.53 |  | 0.96 | 7.55 | MG | [12 empty] | MONTH | (MGD) | AFTER | AFTER DE- | [8 empty] | P | COLIFORM | II. | [7 empty] | YEAR: | 2004 |  | 2 | 31.813 | 8.08 | 8.09 | 7.04 | 0.13 | 7.19 | 87.8 | 5.8 | 114 | 22 | 6.4 | 6.4 | 1227 | 14.41 | 17.53 | 6.5 | 2660 | 80 | 1.64
| JANUARY | INFLUENT | HOURLY | INFLUENT | INFLUENT | RAS | PERCENT | WAS | RAIN | SPARE | [5 empty] | JANUARY | FT HEAD | FT HEAD | FT HEAD |  |  | FT HEAD | FT HEAD | FT HEAD | ** PEAK HR FLOW (MGD) ON MAX DAY: | 11.2845 | 11.3588 | 9.8759 |  | 0.22534 | 9.5756 | MGD |  | (1) Month: |  | JANUARY |  | Year: | 2004 |  | Parameter | Units | STORET | Value |  |  | CONTACT | CHLORINATION | MG/L | MG/L | MG/L | MG/L | [6 empty] | A) | Sludge Treatment Provided: |  |  |  |  | B) | Sludge Dewater Processes |  |  |  | 3 | 31.481 | 8.02 | 8.04 | 6.98 | 0.14 | 7.15 | 90 | 6.3 | 100 | 16 | 6.4 | 6.5 | 1276 | 13.94 | 17.18 | 6.5 | 2670 | 80 | 1.52
| 2004 | FLOW | MAXIMUM | MAXIMUM | MINIMUM | FLOW | RAS | FLOW | INCHES | [6 empty] | 2004 | ABOVE | ABOVE | ABOVE |  |  | ABOVE | ABOVE | ABOVE | MAX SUSTAINED INJECTION PRESSURE: | 71.4 | 69.99 | 72 |  | 60.48 | 64.92 | PSIG |  | (2) Plant's DEP Identification Number: |  |  |  |  | 5006M02066 |  |  |  | Code |  | 1 | 31.093 | 0.9 |  | 97 | 116 | 6 | 11 | 6.5 | 17.2 | 13.66 | 0.243 | 1.78 | 0 |  |  | Aerobic Digestion | [5 empty] | Thickner |  |  | 4 | 31.009 | 8.11 | 8.1 | 6.41 | 0.14 | 7.23 | 66 | 4.79 | 40 | 23 | 6.3 | 6.5 | 1272 | 14.53 | 17.94 | 6.4 | 2580 | 81 | 1.66
|  | MGD | MGD | MGD | MGD | MGD |  | MGD | [8 empty] | NGVD | NGVD | NGVD |  |  | NGVD | NGVD | NGVD | MONTHLY AVG. INJECTION PRESSURE: | 46.7113 | 45.8448 | 46.9306 |  | 34.8281 | 44.4884 | PSIG |  | (3) Plant Name: |  |  |  | George T. Lohmeyer Regional Wastewater |  |  | (16) Monthly average daily flow | mgd | 050053 | 31.8274 | 2 | 31.813 | 0.8 |  | 87.8 | 114 | 5.8 | 22 | 6.5 | 17.53 | 14.41 | 0.16 | 1.64 | 116 |  |  | Anaerobic Digestion | [5 empty] | DGA___X___Filter Press |  |  | 5 | 31.168 | 8.02 | 8.01 | 7 | 0.13 | 7.15 | 72 | 4.43 | 120 | 18 | 6.3 | 6.5 | 1213 | 14.53 | 17.94 | 6.4 | 2670 | 81 | 1.66
| 1 | 31.093 | 1.564 | 48.542 | 0.96 | 10.668 | 34.31% | 0 | 0 |  |  | 1 |  |  |  | 1 | 47.93 | 48.17 | 48.21 |  |  | 41.79 | 42.1 | 41.96 | *** MAX INJECTION PRESSURE PERMITTED: | 99 | 99 | 99 |  | 99 | 99 | PSIG |  |  |  |  | Treatment Facility |  |  |  | (17) Permitted capacity | mgd | - | 43 | 3 | 31.481 | 0.7 |  | 90 | 100 | 6.3 | 16 | 6.5 | 17.18 | 13.94 | 0.169 | 1.52 | 723 |  |  | Other | [5 empty] | Centrifuge Drying Beds, Bed #______ |  |  | 6 | 30.687 | 7.89 | 7.88 | 6.86 | 0.14 | 7.03 | 80.3 | 4.4 | 126 | 13 | 6.4 | 6.4 | 1152 |  |  | 6.4 | 2730 | 81
| 2 | 31.813 | 1.622 | 51.713 | 0.255 | 9.944 | 31.26% | 0 | 0 |  |  | 2 |  |  |  | 2 | 47.97 | 48.21 | 48.03 |  |  | 41.86 | 42.16 | 41.98 | ***NOTE: (INJECTION PRESSURE NOT TO EXCEED 66% TESTED PRESSURE | [8 empty] | (4) Plant Address: |  |  | 1765 S.E. 18th Street at |  |  |  | (18) Three-month average daily flow | mgd | - | 35.8691 | 4 | 31.009 | 0.9 |  | 66 | 40 | 4.79 | 23 | 6.4 | 17.94 | 14.53 | 0.251 | 1.66 | 63 | [8 empty] | Heat Treatment____No Treatment |  |  | 7 | 30.514 | 7.9 | 7.88 | 6.84 | 0.12 | 7.02 | 70.1 | 3.61 | 112 | 10 | 6.4 | 6.6 | 1168 | 16.18 | 19.66 | 6.5 | 2640 | 80 | 1.24
| 3 | 31.481 | 1.605 | 50.719 | 0.8 | 10.43 | 33.13% | 0 | 0 |  |  | 3 |  |  |  | 3 | 48.01 | 48.27 | 48.07 |  |  | 41.91 | 42.16 | 42 | TESTED CASING PRESSURE DURING MIT | 150 | 150 | 150 |  | 150 | 150 | PSIG |  |  |  |  | Eisenhower Boulevard |  |  |  | (19) Percent of permitted capacity | % | - | 83.42% | 5 | 31.168 | 0.6 |  | 72 | 120 | 4.43 | 18 | 6.4 | 17.94 | 14.53 | 0.251 | 1.66 | 4000 | [7 empty] | x | Other: | LIME STABILIZATION |  | 8 | 30.866 | 7.99 | 7.98 | 6.95 | 0.13 | 7.1 | 139 | 4 | 630 | 17 | 6.4 | 6.6 | 1278 | 15.7 | 18.85 | 6.5 | 2770 | 80 | 1.05
| 4 | 31.009 | 1.647 | 53.283 | 0.255 | 10.605 | 34.2% | 0.203 | 0 |  |  | 4 |  |  |  | 4 | 48.03 | 48.3 | 48.15 |  |  | 41.94 | 42.19 | 42.02 | [9 empty] | (5) City: |  | Fort Lauderdale |  |  |  |  | (20) CBOD5 Effluent | mg/L | 080082 | 4.2042 | 6 | 30.687 | 0.6 |  | 80.3 | 126 | 4.4 | 13 | 6.4 |  |  |  |  | 0 | [9 empty] | CLASS "AA" |  | 9 | 31.036 | 8.16 | 8.15 | 7.11 | 0.13 | 7.24 | 92 | 2.6 | 400 | 15 | 6.4 | 6.5 | 1086 | 15.27 | 18.39 | 6.5 | 2870 | 79 | 1.13
| 5 | 31.168 | 1.556 | 50.271 | 0.031 | 10.346 | 33.19% | 0.509 | 0 |  |  | 5 |  |  |  | 5 | 45.29 | 48.32 | 46.78 |  |  | 37.33 | 42.2 | 39.49 |  |  | MONITORING WELL DATA | [6 empty] | (6) County: |  | Broward |  |  |  |  | (21) CBOD5 Effluent | lbs/day | - | 1115.964 | 7 | 30.514 | 0.4 |  | 70.1 | 112 | 3.61 | 10 | 6.5 | 19.66 | 16.18 | 0.143 | 1.24 | 9 | III. | Final Sludge Disposal: | [7 empty] | RMF-Azurix (Nutri-Cycle) |  | 10 | 31.043 | 7.99 | 7.99 | 6.96 | 0.12 | 7.12 | 99 | 4 | 72 | 19 | 6.4 | 6.5 | 1295 | 14.48 | 17.98 | 6.4 | 3100 | 79 | 0.965
| 6 | 30.687 | 1.512 | 46.812 | 0.095 | 10.064 | 32.8% | 0.462 | 0 |  |  | 6 |  |  |  | 6 | 45.67 | 48.58 | 47.36 |  |  | 27.85 | 41.88 | 40.01 |  | MW-1 | MW-2 | MW-3 |  | RMW-1 |  |  |  | (7) Phone Number: |  |  | (954) 523-1002 |  |  |  | (22) TSS Effluent | mg/L | 900201 | 18.3226 | 8 | 30.866 | 0.6 |  | 139 | 630 | 4 | 17 | 6.5 | 18.85 | 15.7 | 0.177 | 1.05 | 45 | A) | Liquid Sludge Disposal: | [9 empty] | 11 | 30.52 | 10.13 | 10.24 | 9.05 | 0.12 | ER | 95.7 | 3.81 | 70 | 18 | 6.5 | 6.5 | 1285 | 14.5 | 17.87 | 6.5 | 3100 | 78 | 1.06
| 7 | 30.514 | 1.531 | 47.42 | 0 | 9.465 | 31.02% | 0.506 | 0 |  |  | 7 |  |  |  | 7 | 47.98 | 48.23 | 48.07 |  |  | 41.42 | 41.6 | 41.48 | PERMIT NUMBER | 0054569-142-UO | 0054569-142-UO | 0054569-142-UO |  | 0054569-142-UO |  |  |  | (8) Permit Number: |  |  | FLA041378 |  |  |  | (23) TSS Effluent | lbs/day | - | 4863.5582 | 9 | 31.036 | 0.5 |  | 92 | 400 | 2.6 | 15 | 6.5 | 18.39 | 15.27 | 0.129 | 1.13 | 0 |  | WEEK OF | JANUARY | GALLONS | % SOLIDS |  |  | HAULERS |  |  | DISPOSAL SITE | 12 | 31.341 | 8.5 | 8.59 | 7.52 | 0.13 | ER | 72 | 3.4 | 56 | 17 | 6.3 | 6.5 | 1335 |  |  | 6.5 | 3030 | 79
| 8 | 30.866 | 1.556 | 48.991 | 0.159 | 9.402 | 30.46% | 0.456 | 0 |  |  | 8 |  |  |  | 8 | 47.95 | 48.27 | 48.1 |  |  | 41.43 | 41.63 | 41.5 | UPPER MONITORING INTERVAL | 1288'-1320' | 1300'-1344' | 1300'-1349' |  | 1300'-1339' |  | Ft. bls. |  | (9) Plant Type: |  |  | Oxygen Activated Sludge |  |  |  | (24) Minimum pH |  | - | 6.3 | 10 | 31.043 | 0.5 |  | 99 | 72 | 4 | 19 | 6.4 | 17.98 | 14.48 | 0.105 | 0.965 | 0 | [11 empty] | 13 | 31.249 | 8.07 | 8.09 | 7.03 | 0.13 | 7.21 | 61 | 2 | 120 | 19 | 6.3 | 6.5 | 1445 |  |  | 6.4 | 3170 | 79
| 9 | 31.036 | 1.642 | 48.766 | 0.383 | 9.33 | 30.06% | 0.162 | 0 |  |  | 9 |  |  |  | 9 | 48.05 | 48.4 | 48.28 |  |  | 41.48 | 41.84 | 41.59 | MONTHLY MAX DAILY PRESSURE | 48.58 | 31.26 | 31.59 |  | 73.82 |  | FT. HEAD |  | (10) Test Site Identification Number: |  |  |  |  | 5006X10744 |  | (25) Maximum pH |  | - | 6.9 | 11 | 30.52 | 0.8 |  | 95.7 | 70 | 3.81 | 18 | 6.5 | 17.87 | 14.5 | 0.121 | 1.06 | 0 |  | FIRST THRU SEVENTH | [9 empty] | 14 | 31.577 | 8.12 | 8.13 | 7.12 | 0.12 | 7.21 | 72.5 | 3.67 | 104 | 30 | 6.4 | 6.5 | 1445 | 15.01 | 18.2 | 6.5 | 3150 | 79 | 0.668
| 10 | 31.043 | 1.612 | 51.04 | 0.768 | 8.956 | 28.85% | 0 | 0 |  |  | 10 |  |  |  | 10 | 48.19 | 48.42 | 48.33 |  |  | 41.45 | 41.67 | 41.55 | MONTHLY MIN DAILY PRESSURE | 44.91 | 23.86 | 16.98 |  | 42.44 |  | FT. HEAD |  | (11) Fecal Coliform Method | [6 empty] | (26) Total N | mg/L | 000600 | 16.9904 | 12 | 31.341 | 0.4 |  | 72 | 56 | 3.4 | 17 | 6.5 |  |  |  |  | 500 | [11 empty] | 15 | 31.714 | 8.2 | 8.23 | 7.18 | 0.12 | 7.27 | 66 | 2.3 | 110 | 13 | 6.4 | 6.6 | 1499 | 16.48 | 19.6 | 6.5 | 3230 | 79 | 0.948
| 11 | 30.52 | 1.634 | 49.567 | 0.127 | 8.881 | 29.1% | 0.162 | 0 |  |  | 11 |  |  |  | 11 | 48.01 | 48.29 | 48.07 |  |  | 41.35 | 41.6 | 41.46 | TDS (MONTHLY AVERAGE) | 7220.5 | 7073 | 7162.5 |  | 5460 |  | mg/l |  |  | XX | Membrane Filter |  |  |  |  | (27) TKN | mg/L | 000625 | 16.7904 | 13 | 31.249 | 0.5 |  | 61 | 120 | 2 | 19 | 6.4 |  |  |  |  | 18 |  | EIGHT THRU FORTEENTH | [9 empty] | 16 | 31.357 | 8.21 | 8.26 | 7.2 | 0.13 | 7.29 | 71 | 1.3 | 112 | 18 | 6.4 | 6.5 | 1290 | 15.73 | 19.04 | 6.5 | 3190 | 79 | 1.78
| 12 | 31.341 | 1.555 | 47.453 | 0.127 | 8.925 | 28.48% | 0.519 | 0 |  |  | 12 |  |  |  | 12 | 44.91 | 48.17 | 46.47 |  |  | 34.64 | 41.44 | 37.44 | CHLORIDE (MONTHLY AVERAGE) | 3987.5 | 3875 | 3950 |  | 3050 |  | mg/l |  |  |  | Most Probable Number |  |  |  |  | (28) Ammonia (NH3 - N) | mg/L | 000610 | 14.2458 | 14 | 31.577 | 0.7 |  | 72.5 | 104 | 3.67 | 30 | 6.5 | 18.2 | 15.01 | 0.169 | 0.668 | 0 |  | FIFTHTEENTH THRU | [9 empty] | 17 | 31.323 | 8.05 | 8.08 | 7.05 | 0.12 | 7.17 | 84.9 | 3.33 | 102 | 14 | 6.4 | 6.5 | 1386 | 14.07 | 17.63 | 6.5 | 3080 | 78.8 | 2.1
| 13 | 31.249 | 1.549 | 51.136 | 0.832 | 9.846 | 31.51% | 0.085 | 0 |  |  | 13 |  |  |  | 13 | 45.3 | 48.24 | 47.15 |  |  | 34.61 | 41.3 | 38.94 | AMMONIA-N (MONTHLY AVERAGE) | 0.91975 | 0.706 | 0.99 |  | 0.699 |  | mg/l |  | (12) Type of Effluent Disposal or Reclaimed Water Reuse | [6 empty] | (29) Nitrate | mg/L | 071850 | 0.19996 | 15 | 31.714 | 0.6 |  | 66 | 110 | 2.3 | 13 | 6.5 | 19.6 | 16.48 | 0.233 | 0.948 | 0 |  | TWENTY SECOND | [9 empty] | 18 | 32.044 | 8.21 | 8.26 | 7.18 | 0.13 | 7.31 | 86 | 4.62 | 104 | 13 | 6.4 | 6.5 | 1305 | 15.23 | 18.62 | 6.5 | 3010 | 79 | 1.05
| 14 | 31.577 | 1.606 | 49.151 | 6.023 | 9.396 | 29.76% | 0.439 | 0 |  |  | 14 |  |  |  | 14 | 48.02 | 48.34 | 48.17 |  |  | 41.18 | 41.57 | 41.39 | TKN (MONTHLY AVERAGE) | 1.4275 | 1.5225 | 1.6 |  | 1.28 |  | mg/l |  |  |  | Deep Well Injection |  |  |  |  | (30) Total Phosphorus | mg/L | 000665 | 1.4662 | 16 | 31.357 | 0.4 |  | 71 | 112 | 1.3 | 18 | 6.5 | 19.04 | 15.73 | 0.187 | 1.78 | 0 |  | TWENTY THIRD THRU | [9 empty] | 19 | 33.128 | 8.51 | 8.56 | 7.45 | 0.13 | 7.55 | 59.8 | 3.63 | 104 | 24 | 6.3 | 6.5 | 1410 |  |  | 6.4 | 3130 | 79
| 15 | 31.714 | 1.589 | 48.991 | 0.928 | 9.811 | 30.94% | 0.561 | 0 |  |  | 15 |  |  |  | 15 | 48.13 | 48.37 | 48.27 |  |  | 41.31 | 41.7 | 41.45 | pH (MONTHLY AVERAGE) | 8.0525 | 7.875 | 8.2125 |  | 8.59 |  | Std units |  | (13) Limited Wet Wheather Discharge Activated | [6 empty] | (31) Minimum Chlorine Residual | mg/L | - | 0.3 | 17 | 31.323 | 0.6 |  | 84.9 | 102 | 3.33 | 14 | 6.5 | 17.63 | 14.07 | 0.183 | 2.1 | 0 |  | THIRTY FIRST | [9 empty] | 20 | 32.485 | 8.33 | 8.39 | 7.3 | 0.13 | 7.42 | 61 | 4.2 | 114 | 20 | 6.3 | 6.5 | 1394 |  |  | 6.4 | 3110 | 79
| 16 | 31.357 | 1.577 | 48.478 | 0.447 | 10.144 | 32.35% | 0.207 | 0 |  |  | 16 |  |  |  | 16 | 48.1 | 48.38 | 48.29 |  |  | 41.33 | 41.72 | 41.47 | CONDUCTIVITY (MONTHLY AVERAGE) | 12732.5 | 12392.5 | 12635 |  | 9650 |  | umho/cm |  |  |  | YES |  | XX | Not Applicable |  | (32) Maximum Chlorine Residual | mg/L | - | 0.9 | 18 | 32.044 | 0.7 |  | 86 | 104 | 4.62 | 13 | 6.5 | 18.62 | 15.23 | 0.156 | 1.05 | 9 | [11 empty] | 21 | 32.144 | 8.29 | 8.34 | 7.26 | 0.12 | 7.38 | 70 | 2.5 | 118 | 18 | 6.5 | 6.5 | 1388 | 14.73 | 17.81 | 6.5 | 3070 | 79 | 1.15
| 17 | 31.323 | 1.638 | 48.638 | 0.96 | 9.496 | 30.32% | 0 | 0 |  |  | 17 |  |  |  | 17 | 48.13 | 48.4 | 48.29 |  |  | 41.34 | 41.72 | 41.49 | FECAL COLIFORM (MONTHLY AVERAGE) | 0 | 0 | 0 |  | 0 |  | # col/100ml |  |  |  | NO |  |  |  |  | (33) Other Effluent Parameters |  |  |  | 19 | 33.128 | 0.5 |  | 59.8 | 104 | 3.63 | 24 | 6.4 |  |  |  |  | TNTC | B) | Solid Sludge Hauled from Plant: | [9 empty] | 22 | 32.621 | 8.31 | 8.36 | 7.27 | 0.13 | 7.39 | 68.1 | 1.94 | 100 | 26 | 6.4 | 6.5 | 1423 | 14.55 | 17.67 | 6.5 | 3270 | 79 | 0.598
| 18 | 32.044 | 1.636 | 50.623 | 0.479 | 10.585 | 33.03% | 0.109 | 0.67 |  |  | 18 |  |  |  | 18 | 48.16 | 48.57 | 48.4 |  |  | 41.49 | 41.78 | 41.59 | TEMPERATURE (MONTHLY AVERAGE) | 73 | 71.5 | 70 |  | 72 |  | deg. F | [12 empty] | 20 | 32.485 | 0.7 |  | 61 | 114 | 4.2 | 20 | 6.4 |  |  |  |  | 0 |  | WEEK OF | JANUARY | TONS |  | % SOLIDS |  | HAULERS |  |  | DISPOSAL SITE | 23 | 32.502 | 8.42 | 8.49 | 7.39 | 0.12 | 7.49 | 56 | 2.8 | 142 | 21 | 6.5 | 6.6 | 1539 | 16.16 | 0 | 6.5 | 3290 | 78 | 1.81
| 19 | 33.128 | 1.685 | 52.546 | 0.543 | 10.105 | 30.5% | 0.473 | 0 |  |  | 19 |  |  |  | 19 | 46.64 | 48.56 | 47.55 |  |  | 36.93 | 41.8 | 39.08 | TOTAL PHOSPHOROUS (MONTHLY AVG.) | 0.05 | 0.05 | 0.05 |  | 0.05 |  | mg/l |  | (14) Cumulative Days of Wet Wheather Discharge | [10 empty] | 21 | 32.144 | 0.5 |  | 70 | 118 | 2.5 | 18 | 6.5 | 17.81 | 14.73 | 0.19 | 1.15 | 45 | [10 empty] | Nutri-Cylcle Inc. | 24 | 32.38 | 8.24 | 8.3 | 7.22 | 0.12 | 7.34 | 126 | 6.1 | 130 | 18 | 6.4 | 6.5 | 1461 | 13.94 | 17.25 | 6.5 | 3270 | 78 | 1.53
| 20 | 32.485 | 1.683 | 49.888 | 4.1 | 8.632 | 26.57% | 0.515 | 0 |  |  | 20 |  |  |  | 20 | 46.89 | 48.52 | 47.73 |  |  | 36.89 | 41.36 | 39.71 | SULFATE (MONTHLY AVERAGE) | 850 | 787.5 | 875 |  | 650 |  | mg/l |  |  |  | N/A | [8 empty] | 22 | 32.621 | 0.6 |  | 68.1 | 100 | 1.94 | 26 | 6.5 | 17.67 | 14.55 | 0.275 | 0.598 | 134 |  | FIRST THRU SEVENTH |  | 500 |  | 17.8475 |  | AZURIX |  |  | Arcadia, FL | 25 | 32.273 | 8.18 | 8.23 | 7.15 | 0.12 | 7.28 | 106 | 4.8 | 106 | 20 | 6.4 | 6.5 | 1523 | 13.2 | 16.61 | 6.5 | 3220 | 78 | 1.36
| 21 | 32.144 | 1.622 | 50.944 | 0.235 | 8.655 | 26.93% | 0.499 | 0 |  |  | 21 |  |  |  | 21 | 47.88 | 48.25 | 48.04 |  |  | 41.14 | 41.38 | 41.31 | C.O.D. (MONTHLY AVERAGE) | 192.5 | 180 | 182.5 |  | 120 |  | mg/l |  | (15) Plant Staffing: | [10 empty] | 23 | 32.502 | 0.6 |  | 56 | 142 | 2.8 | 21 | 6.5 | 0 | 16.16 |  | 1.81 | 27 | [10 empty] | Nutri-Cylcle Inc. | 26 | 32.662 | 8.33 | 8.4 | 7.31 | 0.13 | 7.43 | 85 | 5 | 106 | 18 | 6.3 | 6.5 | 1489 |  |  | 6.4 | 3260 | 79
| 22 | 32.621 | 1.645 | 51.77 | 0.191 | 9.724 | 29.81% | 0.287 | 0 |  |  | 22 |  |  |  | 22 | 47.89 | 48.24 | 48.04 |  |  | 41.19 | 41.6 | 41.39 | IRON (MONTHLY AVERAGE) | 0.78 | 4.1875 | 0.96 |  | 1.51 |  | mg/l | [12 empty] | 24 | 32.38 | 0.6 |  | 126 | 130 | 6.1 | 18 | 6.5 | 17.25 | 13.94 | 0.113 | 1.53 | 30000 |  | EIGHT THRU FORTEENTH |  | 600 |  | 17.725 |  | AZURIX |  |  | Arcadia, FL | 27 | 32.446 | 7.69 | 8.5 | 7.3 | 0.96 | 7.34 | 97 | 6 | 60 | 21 | 6.4 | 6.5 | 1389 |  |  | 6.5 | 3160 | 79
| 23 | 32.502 | 1.672 | 52.514 | 0.928 | 9.004 | 27.7% | 0.285 | 0 |  |  | 23 |  |  |  | 23 | 47.88 | 48.19 | 48.02 |  |  | 41.24 | 41.48 | 41.41 | SULFIDE (MONTHLY AVERAGE) | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! |  | mg/l |  |  | Day Shift Operator: |  |  | Class | "A" | Cert. No. | 4545 |  |  |  | 25 | 32.273 | 0.9 |  | 106 | 106 | 4.8 | 20 | 6.5 | 16.61 | 13.2 | 0.354 | 1.36 | 9 |  | FIFTHTEENTH THRU | [8 empty] | Nutri-Cylcle\CSLOL Inc. | 28 | 31.538 | 8.07 | 7.88 | 7.06 | 0.47 | 7.19 | 109 | 8 | 340 | 26 | 6.5 | 6.8 | 1331 | 7.9 | 15 | 6.6 | 3090 | 78 | 5.7
| 24 | 32.38 | 1.705 | 53.251 | 0 | 8.531 | 26.35% | 0 | 0 |  |  | 24 |  |  |  | 24 | 47.88 | 48.24 | 48.02 |  |  | 41.25 | 41.64 | 41.42 | LOWER MONITORING INTERVAL | 1449'-1557' | 1970'-2025' | 1970'-2027' |  | 1500'-1600' |  | Ft. bls | [12 empty] | 26 | 32.662 | 0.8 |  | 85 | 106 | 5 | 18 | 6.4 |  |  |  |  | 0 |  | TWENTY SECOND |  | 800 |  | 17.725 |  | AZURIX |  |  | Arcadia, FL | 29 | 31.301 | 7.98 | 8.03 | 7 | 0.12 | 7.14 | 125 | 4 | 140 | 16 | 6.5 | 6.9 | 1249 | 14 | 16 | 6.8 | 2890 | 78 | 0.85
| 25 | 32.273 | 1.655 | 51.585 | 0.832 | 8.824 | 27.34% | 0.143 | 0 |  |  | 25 |  |  |  | 25 | 48.01 | 48.3 | 48.12 |  |  | 41.39 | 41.78 | 41.52 | MONTHLY MAX DAILY PRESSURE | 42.2 | 42.52 | 45.65 |  | 22.38 |  | FT. HEAD |  |  | Evening Shift Operator: |  |  | Class | "A" | Cert. No. | 4474 |  |  |  | 27 | 32.446 | 0.4 |  | 97 | 60 | 6 | 21 | 6.5 |  |  |  |  | 9 |  | TWENTY THIRD THRU | [8 empty] | Nutri-Cylcle Inc. | 30 | 32.201 | 7.81 | 7.84 | 6.75 | ER | 6.85 | 136 | 6 | 102 | 14 | 6.4 | 6.8 | 1320 | 14 | 17 | 6.5 | 2910 | 79 | 1.1
| 26 | 32.662 | 1.624 | 51.969 | 0.768 | 10.612 | 32.49% | 0.514 | 0 |  |  | 26 |  |  |  | 26 | 46.66 | 48.3 | 47.61 |  |  | 38.39 | 41.79 | 40.26 | MONTHLY MIN DAILY PRESSURE | 27.85 | 31.08 | 36.6 |  | 22.05 |  | FT. HEAD | [12 empty] | 28 | 31.538 | 0.4 |  | 109 | 340 | 8 | 26 | 6.6 | 15 | 7.9 | 0.02 | 5.7 | TNTC |  | THIRTY FIRST |  | 850 |  | 17.65 |  | AZURIX |  |  | Arcadia, FL | 31 | 37.134 | 11.73 | 11.96 | 10.53 | 0.12 | 0.98 | 72 | 5 | 148 | 20 | 6.4 | 6.5 | 1336 | 9.7 | 12 | 6.5 | 2840 | 79 | 0.84
| 27 | 32.446 | 1.735 | 50.079 | 0.96 | 10.377 | 31.98% | 0.527 | 0.12 |  |  | 27 |  |  |  | 27 | 47 | 48.38 | 47.75 |  |  | 38.32 | 41.58 | 40.27 | TDS (MONTHLY AVERAGE) | 9292.5 | 30823.25 | 28205.5 |  | 26330 |  | mg/l |  |  | Night Shift Operator: |  |  | Class | "A" | Cert. No. | 3207 |  |  |  | 29 | 31.301 | 0.5 |  | 125 | 140 | 4 | 16 | 6.8 | 16 | 14 | 0.34 | 0.85 | 54 | C) | Monthly quantities of solid sludge stockpiled at plant.Solid Sludge Hauled from Plant: | [9 empty] | TOT | 986.65 | 257.61 | 259.36 | 225.52 | 4.98 | 203.67 | 2673.2 | 130.33 | 4318 | 568 | 198.3 | 202.7 | 41429 | 341.9 | 402.97 | 201.1 | 92890 | 2453.8 | 35.189
| 28 | 31.538 | 1.637 | 50.784 | 0.896 | 8.121 | 25.75% | 0.435 | 0 |  |  | 28 |  |  |  | 28 | 47.96 | 48.27 | 48.06 |  |  | 41.16 | 41.43 | 41.23 | CHLORIDE (MONTHLY AVERAGE) | 5325 | 18050 | 17050 |  | 16400 |  | mg/l | [12 empty] | 30 | 32.201 | 0.6 |  | 136 | 102 | 6 | 14 | 6.5 | 17 | 14 | 0.32 | 1.1 | 142 |  | 1) | Additions |  |  | Cubic Yards | [5 empty] | AVG | 31.8274 | 8.31 | 8.3665 | 7.2748 | 0.166 | 7.0231 | 86.2323 | 4.2042 | 139.2903 | 18.3226 | 6.3968 | 6.5387 | 1336.4194 | 14.2458 | 16.7904 | 6.4871 | 2996.4516 | 79.1548 | 1.4662
| 29 | 31.301 | 1.597 | 47.517 | 0.703 | 9.203 | 29.4% | 0.431 | 0 |  |  | 29 |  |  |  | 29 | 48 | 48.21 | 48.03 |  |  | 41.21 | 41.58 | 41.39 | AMMONIA-N (MONTHLY AVERAGE) | 9.58 | 1.4975 | 2.4275 |  | 0.377 |  | mg/l |  |  | Lead Operator:_________________________________ | [9 empty] | 31 | 37.134 | 0.3 |  | 72 | 148 | 5 | 20 | 6.5 | 12 | 9.7 | 0.31 | 0.84 | 9 | [5 empty] | Tons | [5 empty] | MAX | 37.134 | 11.73 | 11.96 | 10.53 | 0.96 | 7.55 | 139 | 8 | 630 | 30 | 6.5 | 6.9 | 1539 | 16.48 | 19.66 | 6.8 | 3290 | 81 | 5.7
| 30 | 32.201 | 1.639 | 48.83 | 1.312 | 10.835 | 33.65% | 0.248 | 0.86 |  |  | 30 |  |  |  | 30 | 48.16 | 48.39 | 48.29 |  |  | 41.38 | 41.62 | 41.49 | TKN (MONTHLY AVERAGE) | 10.5725 | 1.93 | 2.2853 |  | 0.883 |  | mg/l | [5 empty] | Signature |  | Cert. No. |  |  |  |  | Lead Operator : This is to certify that I am familar with the information contained on this report and that to the best of | [14 empty] | 2) | Removals |  |  | Cubic Yards | [5 empty] | MIN | 30.514 | 7.69 | 7.84 | 6.41 | 0.12 | 0.98 | 56 | 1.3 | 40 | 10 | 6.3 | 6.4 | 1086 | 7.9 | 0 | 6.4 | 2580 | 78 | 0.598
| 31 | 37.134 | 1.802 | 54.533 | 13.361 | 9.941 | 26.77% | 0 | 1.22 |  |  | 31 |  |  |  | 31 | 48.24 | 48.43 | 48.38 |  |  | 41.5 | 41.65 | 41.52 | pH (MONTHLY AVERAGE) | 7.345 | 7.39 | 7.4 |  | 7.62 |  | Std units | [12 empty] | my knowledge and belief, this information is true, complete and accuate. | [16 empty] | X |  | Tons | [6 empty] | item #1 | 11.2845 | 11.3588 | 9.8759 | 0.22534 | 9.5756 | MAX HOURLY FLOW (MG) = |  |  |  | 1.802 | ON THE | 31 | DAY OF THIS MONTH
| TOTAL | 986.65 | 50.332 | 1557.804 | 38.458 | 298.858 |  | 8.737 | 2.87 | [6 empty] | TOTAL | 1472.92 | 1498.21 | 1486.13 |  |  | 1237.7 | 1292.95 | 1270.81 | CONDUCTIVITY (MONTHLY AVERAGE) | 16572.5 | 49475 | 45875 |  | 43500 |  | umho/cm | [33 empty] | Signature |  |  |  |  | item #2 | 46.7113 | 45.8448 | 46.9306 | 34.8281 | 44.4884
| AVERAGE | 31.8274 | 1.6236 | 50.2517 | 1.3261 | 9.6406 | 30.29% | 0.36404 | 0.092581 | [6 empty] | AVERAGE | 47.5135 | 48.3294 | 47.9397 |  |  | 39.9258 | 41.7081 | 40.9939 | FECAL COLIFORM (MONTHLY AVERAGE) | 0 | 0 | 0 |  | 0 |  | # col/100ml | [12 empty] | Signed: ____________________________ Date: ___________________ | [20 empty] | Title |  |  |  |  | item #3 | 34.92 | 35.92 | 35.82 | 36.49 | 35.56
[16 empty] | MAXIMUM | 48.24 | 48.58 | 48.4 |  |  | 41.94 | 42.2 | 42.02 | TEMPERATURE (MONTHLY AVERAGE) | 72.5 | 70 | 69 |  | 70 |  | deg. F | [33 empty] | Date |  |  |  | item #1 | =monthly maximum of the daily flows (MG), with peakhour flow (MGD) on the day of the month with maximum flow = | [14 empty] | 1.802 | MG/hour multiplied by
[16 empty] | MINIMUM | 44.91 | 48.17 | 46.47 |  |  | 27.85 | 41.3 | 37.44 | TOTAL PHOSPHOROUS (MONTHLY AVG.) | 0.05 | 0.05 | 0.05 |  | 0.05 |  | mg/l | [12 empty] | Name: Michael A. Just | [14 empty] | * Sludge Reports should be submitted along with the monthly operating reports to Broward County Department | [10 empty] | the % of average % of TOTAL RAW FLOW to each Injection well.
[25 empty] | SULFATE (MONTHLY AVERAGE) | 787.5 | 2625 | 2325 |  | 1500 |  | mg/l | [27 empty] | of Natural Resource Protection, 218 S. W. 1st Avenue, Fort Lauderdale, Florida 33301 | [9 empty] | item #2 | =monthly average injection well pressure at injection well (psig)
[25 empty] | C.O.D. (MONTHLY AVERAGE) | 282.5 | 865 | 825 |  | 670 |  | mg/l | [12 empty] | Company Name: City of Fort Lauderdale Telephone No. (954) 523-1002 | [24 empty] | item #3 | =monthly wellhead pressure with no flow (shut-in pressure,psig)
[25 empty] | IRON (MONTHLY AVERAGE) | 0.0225 | 0.0575 | 0.0525 |  | 0.05 |  | mg/l | [37 empty] | PLANT STAFFING
[5 empty] | PAGE 2 | [19 empty] | SULFIDE (MONTHLY AVERAGE) | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! |  | mg/l | [37 empty] | Day Shift Operator |  |  | Class: | "A" | Certificate No. | 4545 | Name: |  | McGEARY, J.
[70 empty] | Evening Shift Operator |  |  | Class: | "A" | Certificate No. | 4474 | Name: |  | BAYLER, J.
[20 empty] | PAGE 20 | [49 empty] | Night Shift Operator |  |  | Class: | "A" | Certificate No. | 3207 | Name: |  | HOSTNICK, N.
[70 empty] | Lead Operator |  |  | Class: | "A" | Certificate No. | 2769 | Name: |  | JUST, M.
[70 empty] | Type of Effluent Disposal or Reclaimed Water Reuse: |  |  |  |  | DEEPWELL INJECTION
[70 empty] | Permited Wet Weather Discharge Activated: |  |  |  | YES: |  | NO: |  |  | Not Applicable |  | X
If Yes, cumulative days of wet weather:
Attach additional sheets if necessary to list all certified operators. See page 1 "COVER PAGE" of supplental attachements.
DEP form 62-620.910(10), effective November 29, 1994
[19 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [46 empty] | Department of Natural Resource Protection
[5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [13 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [46 empty] | Division of Pollution Prevention and Remediation Programs
[5 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [13 empty] | MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING | [49 empty] | 218 S. W. 1st Avenue
[5 empty] | MONTHLY OPERATIONAL REPORT | [13 empty] | MONITORING WELL TWO |  |  |  | 1/07/04 thru 1/06/09 | [38 empty] | SLUDGE HAULERS MONTHLY REPORT | [6 empty] | Fort Lauderdale, FL 33301
[5 empty] | INFLUENT DATA | [11 empty] | MW-2 | I.D. #: 5066A11308 & 09 |  |  | PERMIT # 0054569-142-UO | [40 empty] | BROWARD COUNTY CODE SECTION 27-356 (d)(4)(1) | [5 empty] | Tel. No. (954) 523-1002
| RUN DATE | [14 empty] | RUN DATE | [51 empty] | *FAX (954) 519-1245
| 2026-07-30 | [14 empty] | 2026-07-30 |  | UPPER MONITOR ZONE |  |  |  |  | LOWER MONITOR ZONE
[17 empty] | MIN | MAX | AVG |  |  | MIN | MAX | AVG | [34 empty] | Plant Name: | GEORGE T. LOHMEYER WASTEWATER TREATMENT FACILITY
| JANUARY | RAW | RAW TSS | RAW SS | RAW | RAW | RAW | RAW | RAW | RAW | [5 empty] | JANUARY | FT HEAD | FT HEAD | FT HEAD |  |  | FT HEAD | FT HEAD | FT HEAD | [34 empty] | Address: | 1765 S.E. 18th Street at Eisenhower Boulevard | [6 empty] | MONTH: | JANUARY
| 2004 | CBOD | TOTAL | FIXED | COD | pH | CL_ | ALK. | H2S | TEMP.(F) | [5 empty] | 2004 | ABOVE | ABOVE | ABOVE |  |  | ABOVE | ABOVE | ABOVE | [34 empty] | Phone: | (954) 523-1002 * FAX (954) 468-1577 | [6 empty] | YEAR: | 2004
[17 empty] | NGVD | NGVD | NGVD |  |  | NGVD | NGVD | NGVD
| 1 | 97 | 116 | 22 | 308 | 7.1 | 610 | 194 | 8 | 78 | [5 empty] | 1 | 28.98 | 30.29 | 29.53 |  |  | 41.71 | 41.86 | 41.85 | [34 empty] | a) | WEEK OF | JANUARY |  | Type of Sludge |  |  | Disopsal Site |  |  | Cubic Yards
| 2 | 87.8 | 114 | 22 | 318 | 7 | 620 | 204 | 6 | 78 | [5 empty] | 2 | 29.29 | 30.4 | 29.71 |  |  | 41.79 | 41.98 | 41.94
| 3 | 90 | 100 | 18 | 314 | 7.1 | 660 | 196 | 7 | 78 | [5 empty] | 3 | 29.45 | 30.47 | 29.86 |  |  | 41.89 | 42.07 | 41.99 | [35 empty] | FIRST THRU SEVENTH |  |  | GRIT |  |  | Central Landfill |  |  | 10
| 4 | 66 | 40 | 6 | 785 | 7.1 | 700 | 192 | 7 | 77 | [5 empty] | 4 | 29.63 | 30.62 | 29.99 |  |  | 41.97 | 42.15 | 42.03
| 5 | 72 | 120 | 16 | 785 | 7.1 | 700 | 204 | 7 | 78 | [5 empty] | 5 | 25.44 | 30.04 | 27.79 |  |  | 38.95 | 42.21 | 40.37 | [35 empty] | EIGHT THRU FORTEENTH |  |  | GRIT |  |  | Central Landfill |  |  | 10
| 6 | 80.3 | 126 | 24 |  | 7 | 720 | 204 | 6 | 78 | [5 empty] | 6 | 25.13 | 31.06 | 28.62 |  |  | 38.92 | 41.87 | 40.88 | [35 empty] | FIFTHTEENTH THRU
| 7 | 70.1 | 112 | 20 | 345 | 7 | 760 | 206 | 5 | 77 | [5 empty] | 7 | 29.39 | 30.3 | 29.72 |  |  | 41.76 | 41.94 | 41.93 | [35 empty] | TWENTY SECOND |  |  | GRIT |  |  | Central Landfill |  |  | 10
| 8 | 139 | 630 | 72 | 383 | 7.1 | 710 | 240 | 5 | 77 | [5 empty] | 8 | 29.57 | 30.64 | 29.98 |  |  | 41.86 | 42.07 | 41.97 | [35 empty] | TWENTY THIRD THRU
| 9 | 92 | 400 | 68 | 370 | 7.1 | 700 | 206 | 5 | 77 | [5 empty] | 9 | 29.27 | 31.26 | 30.21 |  |  | 42.01 | 42.28 | 42.19 | [35 empty] | THIRTY FIRST |  |  | GRIT |  |  | Central Landfill |  |  | 10
| 10 | 99 | 72 | 1 | 325 | 7.2 | 690 | 202 | 5 | 78 | [5 empty] | 10 | 29.02 | 30.27 | 29.81 |  |  | 42.19 | 42.3 | 42.15
| 11 | 95.7 | 70 | 10 | 406 | 7.2 | 700 | 208 | 7 | 77 | [5 empty] | 11 | 28.62 | 30.57 | 29.51 |  |  | 42.06 | 42.19 | 42.09 | [34 empty] | b) | WEEK OF | JANUARY |  | Type of Sludge |  |  | Disopsal Site |  |  | Cubic Yards
| 12 | 72 | 56 | 8 |  | 7 | 680 | 210 | 6 | 77 | [5 empty] | 12 | 24.66 | 29.85 | 27.09 |  |  | 37.8 | 42.14 | 39.68
| 13 | 61 | 120 | 22 |  | 7 | 780 | 200 | 5 | 77 | [5 empty] | 13 | 24.09 | 29.54 | 27.25 |  |  | 37.66 | 41.86 | 40.29 | [35 empty] | FIRST THRU SEVENTH |  |  | RAGS |  |  | Central Landfill |  |  | 10
| 14 | 72.5 | 104 | 20 | 379 | 7.1 | 740 | 206 | 7 | 77 | [5 empty] | 14 | 27.78 | 30.05 | 28.71 |  |  | 41.84 | 42.1 | 41.93
| 15 | 66 | 110 | 22 | 342 | 7 | 730 | 204 | 6 | 76 | [5 empty] | 15 | 28 | 30.22 | 28.88 |  |  | 42.04 | 42.23 | 42.06 | [35 empty] | EIGHT THRU FORTEENTH |  |  | RAGS |  |  | Central Landfill |  |  | 10
| 16 | 71 | 112 | 22 | 337 | 7.1 | 710 | 206 | 5 | 77 | [5 empty] | 16 | 28.22 | 30.44 | 29.04 |  |  | 42.11 | 42.31 | 42.2 | [35 empty] | FIFTHTEENTH THRU
| 17 | 84.9 | 102 | 20 | 400 | 7.1 | 740 | 208 | 6 | 76 | [5 empty] | 17 | 28.5 | 30.34 | 29.33 |  |  | 42.15 | 42.34 | 42.28 | [35 empty] | TWENTY SECOND |  |  | RAGS |  |  | Central Landfill |  |  | 20
| 18 | 86 | 104 | 16 | 337 | 7.2 | 750 | 206 | 6 | 77 | [5 empty] | 18 | 29.25 | 30.37 | 29.63 |  |  | 42.23 | 42.52 | 42.43 | [35 empty] | TWENTY THIRD THRU
| 19 | 59.8 | 104 | 18 |  | 7.1 | 760 | 210 | 8 | 77 | [5 empty] | 19 | 24.12 | 29.56 | 27.08 |  |  | 31.09 | 42.52 | 36 | [35 empty] | THIRTY FIRST |  |  | RAGS |  |  | Central Landfill |  |  | 10
| 20 | 61 | 114 | 22 |  | 7 | 720 | 208 | 5 | 77 | [5 empty] | 20 | 23.86 | 29.4 | 27.1 |  |  | 31.08 | 41.85 | 38.26 | [35 empty] | BCSR = Broward County Septage Receiving
| 21 | 70 | 118 | 24 | 400 | 7 | 700 | 208 | 6 | 77 | [5 empty] | 21 | 27.82 | 29.33 | 28.5 |  |  | 41.72 | 42.02 | 41.94 | [34 empty] | c) | WEEK OF | JANUARY |  | Type of Sludge |  |  | Disopsal Site |  |  | Gallons
| 22 | 68.1 | 100 | 20 | 345 | 7.1 | 720 | 210 | 5 | 76 | [5 empty] | 22 | 28.3 | 29.9 | 28.95 |  |  | 41.89 | 42.11 | 41.98
| 23 | 56 | 142 | 20 | 374 | 7.1 | 760 | 204 | 5 | 76 | [5 empty] | 23 | 28.05 | 29.65 | 28.68 |  |  | 41.98 | 42.14 | 42 | [35 empty] | FIRST THRU SEVENTH |  |  | VAC/Plastic & Rags |  |  | BCSR |  |  | 0
| 24 | 126 | 130 | 12 | 491 | 7.2 | 750 | 206 | 5 | 73 | [5 empty] | 24 | 27.72 | 30.09 | 28.69 |  |  | 42.02 | 42.24 | 42.05
| 25 | 106 | 106 | 20 | 394 | 7.2 | 790 | 206 | 5 | 76 | [5 empty] | 25 | 28.09 | 30.27 | 29.15 |  |  | 42.18 | 42.36 | 42.34 | [35 empty] | EIGHT THRU FORTEENTH |  |  | VAC/Plastic & Rags |  |  | BCSR |  |  | 4500
| 26 | 85 | 106 | 18 |  | 7 | 800 | 206 | 7 | 75.8 | [5 empty] | 26 | 27.64 | 30.42 | 29.01 |  |  | 39.31 | 42.41 | 41.06 | [35 empty] | FIFTHTEENTH THRU
| 27 | 97 | 60 | 12 |  | 6.9 | 760 | 208 | 7 | 76 | [5 empty] | 27 | 26.72 | 28.4 | 27.39 |  |  | 38.69 | 39.72 | 39.45 | [35 empty] | TWENTY SECOND |  |  | VAC/Plastic & Rags |  |  | BSCR |  |  | 0
| 28 | 109 | 340 | 108 | 377 | 7 | 770 | 228 | 6 | 76 | [5 empty] | 28 | 25.86 | 27.42 | 26.35 |  |  | 39.42 | 39.63 | 39.53 | [35 empty] | TWENTY THIRD THRU
| 29 | 125 | 140 | 26 | 403 | 7 | 740 | 210 | 5 | 76 | [5 empty] | 29 | 25.73 | 27.67 | 26.54 |  |  | 39.46 | 39.63 | 39.5 | [35 empty] | THIRTY FIRST |  |  | VAC/Plastic & Rags |  |  | BSCR |  |  | 4500
| 30 | 136 | 102 | 8 | 527 | 7 | 720 | 218 | 5 | 77 | [5 empty] | 30 | 26.38 | 27.78 | 26.9 |  |  | 39.59 | 39.77 | 39.7 | [34 empty] | TOTALS
| 31 | 72 | 148 | 26 | 258 | 7.1 | 640 | 210 | 4 | 76 | [5 empty] | 31 | 26.54 | 27.11 | 26.86 |  |  | 39.69 | 39.81 | 39.76 | [35 empty] | a) | 40 | cu.yds |  | GRIT |  | Signature
| TOTAL | 2673.2 | 4318 | 743 | 9703 | 219.2 | 22330 | 6428 | 182 | 2378.8 | [5 empty] | TOTAL | 851.12 | 923.73 | 885.86 |  |  | 1249.06 | 1294.63 | 1273.83 | [35 empty] | b) | 50 | cu.yds |  | RAGS |  | Title
| AVERAGE | 86.2323 | 139.2903 | 23.9677 | 404.2917 | 7.071 | 720.3226 | 207.3548 | 5.871 | 76.7355 | [5 empty] | AVERAGE | 27.4555 | 29.7977 | 28.5761 |  |  | 40.2923 | 41.7623 | 41.0913 | [35 empty] | c) | 9000 | gal. |  | VAC/Plastic & Rags |  | Date
[16 empty] | MAXIMUM | 29.63 | 31.26 | 30.21 |  |  | 42.23 | 42.52 | 42.43
[16 empty] | MINIMUM | 23.86 | 27.11 | 26.35 |  |  | 31.08 | 39.63 | 36 | [35 empty] | * Sludge Reports should be submitted along with the monthly operating reports to Broward County Department
of Natural Resource Protection, 218 S. W. 1st Avenue, Fort Lauderdale, Florida 33301
PAGE 3
PAGE 21
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
[5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [13 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
[5 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [13 empty] | MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
[5 empty] | MONTHLY OPERATIONAL REPORT | [13 empty] | MONITORING WELL THREE |  |  |  | 1/07/04 thru 1/06/09
[5 empty] | EFFLUENT DATA PART 1 | [11 empty] | MW-3 | I.D. #: 5066A11310 |  |  | PERMIT # 0054569-142-UO
RUN DATE
[16 empty] | 2026-07-30 |  | UPPER MONITOR ZONE |  |  |  |  | LOWER MONITOR ZONE
| RUN DATE | [15 empty] | MIN | MAX | AVG |  |  | MIN | MAX | AVG
| 2026-07-30 | [14 empty] | JANUARY | FT HEAD | FT HEAD | FT HEAD |  |  | FT HEAD | FT HEAD | FT HEAD
[14 empty] | BOD | TSS | 2004 | ABOVE | ABOVE | ABOVE |  |  | ABOVE | ABOVE | ABOVE
| JANUARY | EFFLUENT | EFFL. TSS | EFFL. SS | EFFLUENT | EFFL. | EFFL. | EFFL. | EFFL. | EFFL. | TDS |  |  | MONTHLY AVG OVER 30 | MONTHLY AVG OVER 30 |  | NGVD | NGVD | NGVD |  |  | NGVD | NGVD | NGVD
| 2004 | CBOD | TOTAL | FIXED | COD | CL_ | ALK. | TURB. | COND. | TEMP.(F) |  |  |  | 0 | 0 | 1 | 30.86 | 31.09 | 30.97 |  |  | 44.89 | 45.06 | 44.99
[14 empty] | WEKKLY OVER 45 | WEKKLY OVER 45 | 2 | 30.93 | 31.2 | 31.07 |  |  | 44.98 | 45.19 | 45.03
| 1 | 6 | 11 | 3 | 53.3 | 670 | 186 | 10.6 | 2730 | 80 | 1220 | 1 |  | 0 | 0 | 3 | 31.03 | 31.25 | 31.13 |  |  | 45.1 | 45.27 | 45.2
| 2 | 5.8 | 22 | 4 | 69.4 | 650 | 176 | 10.7 | 2660 | 80 | 1227 | 1 |  | SINGLE DAY OVER 60 | SINGLE DAY OVER 60 | 4 | 31.09 | 31.3 | 31.22 |  |  | 45.18 | 45.36 | 45.34
| 3 | 6.3 | 16 | 3 | 71 | 670 | 186 | 9.46 | 2670 | 80 | 1276 | 1 |  | 0 | 0 | 5 | 17.15 | 31.31 | 23.13 |  |  | 38.88 | 45.39 | 41.71
| 4 | 4.79 | 23 | 2 | 72.9 | 740 | 182 | 14.6 | 2580 | 81 | 1272 | 1 |  | 0 | 0 | 6 | 16.98 | 30.75 | 26.02 |  |  | 38.86 | 44.88 | 42.87
| 5 | 4.43 | 18 | 2 | 72.9 | 740 | 198 | 11.9 | 2670 | 81 | 1213 | 1 |  |  |  | 7 | 30.59 | 30.89 | 30.77 |  |  | 44.8 | 44.99 | 44.96
| 6 | 4.4 | 13 | 3 |  | 710 | 196 | 10.2 | 2730 | 81 | 1152 | 1 |  |  |  | 8 | 30.73 | 31.05 | 30.92 |  |  | 44.93 | 45.15 | 44.99
| 7 | 3.61 | 10 | 2 | 77.5 | 720 | 196 | 9.87 | 2640 | 80 | 1168 | 1 | 5.0471 | 5.0471 | 16.1429 | 9 | 30.9 | 31.25 | 31.12 |  |  | 45.11 | 45.39 | 45.33
| 8 | 4 | 17 | 4 | 70.7 | 720 | 194 | 10.2 | 2770 | 80 | 1278 | 1 |  | 4.7614 | 17 | 10 | 31.09 | 31.26 | 31.14 |  |  | 45.3 | 45.41 | 45.46
| 9 | 2.6 | 15 | 1 | 71.4 | 730 | 188 | 8.75 | 2870 | 79 | 1086 | 1 |  | 4.3043 | 16 | 11 | 30.89 | 31.14 | 30.99 |  |  | 45.19 | 45.3 | 45.17
| 10 | 4 | 19 | 2 | 72.9 | 720 | 200 | 8.22 | 3100 | 79 | 1295 | 1 |  | 3.9757 | 16.4286 | 12 | 17.12 | 31.05 | 22.89 |  |  | 37.88 | 45.23 | 41.02
| 11 | 3.81 | 18 | 1 | 66.3 | 740 | 198 | 9.04 | 3100 | 78 | 1285 | 1 |  | 3.8357 | 15.7143 | 13 | 16.99 | 30.73 | 25.9 |  |  | 37.83 | 44.89 | 42.49
| 12 | 3.4 | 17 | 1 |  | 700 | 200 | 9.99 | 3030 | 79 | 1335 | 1 |  | 3.6886 | 15.5714 | 14 | 30.66 | 31.09 | 30.87 |  |  | 44.89 | 45.18 | 44.98
| 13 | 2 | 19 | 4 |  | 760 | 188 | 10.6 | 3170 | 79 | 1445 | 1 |  | 3.3457 | 16.4286 | 15 | 30.92 | 31.21 | 31.05 |  |  | 45.14 | 45.33 | 45.24
| 14 | 3.67 | 30 | 5 | 74.2 | 780 | 200 | 17 | 3150 | 79 | 1445 | 1 | 3.3543 | 3.3543 | 19.2857 | 16 | 31.01 | 31.29 | 31.1 |  |  | 45.23 | 45.43 | 45.36
| 15 | 2.3 | 13 | 3 | 64.6 | 770 | 196 | 7.3 | 3230 | 79 | 1499 | 1 |  | 3.1114 | 18.7143 | 17 | 31.03 | 31.31 | 31.13 |  |  | 45.26 | 45.47 | 45.39
| 16 | 1.3 | 18 | 5 | 67.4 | 760 | 196 | 9.68 | 3190 | 79 | 1290 | 1 |  | 2.9257 | 19.1429 | 18 | 31.1 | 31.47 | 31.33 |  |  | 45.37 | 45.65 | 45.49
| 17 | 3.33 | 14 | 3 | 69.3 | 790 | 196 | 8.1 | 3080 | 78.8 | 1386 | 1 |  | 2.83 | 18.4286 | 19 | 18.12 | 31.44 | 23.87 |  |  | 36.77 | 45.64 | 40.67
| 18 | 4.62 | 13 | 3 | 80.4 | 770 | 190 | 9.86 | 3010 | 79 | 1305 | 1 |  | 2.9457 | 17.7143 | 20 | 18.07 | 30.81 | 26.4 |  |  | 36.6 | 44.95 | 42.17
| 19 | 3.63 | 24 | 5 |  | 760 | 194 | 12.9 | 3130 | 79 | 1410 | 1 |  | 2.9786 | 18.7143 | 21 | 30.6 | 31.02 | 30.85 |  |  | 44.86 | 45.13 | 44.98
| 20 | 4.2 | 20 | 4 |  | 740 | 194 | 11 | 3110 | 79 | 1394 | 1 |  | 3.2929 | 18.8571 | 22 | 30.78 | 31.09 | 30.95 |  |  | 45.02 | 45.22 | 45.08
| 21 | 2.5 | 18 | 3 | 62.4 | 770 | 196 | 9.85 | 3070 | 79 | 1388 | 1 | 3.1257 | 3.1257 | 17.1429 | 23 | 30.82 | 31.1 | 30.96 |  |  | 45.1 | 45.24 | 45.1
| 22 | 1.94 | 26 | 4 | 56.5 | 740 | 194 | 7.41 | 3270 | 79 | 1423 | 1 |  | 3.0743 | 19 | 24 | 30.85 | 31.19 | 31 |  |  | 45.15 | 45.37 | 45.34
| 23 | 2.8 | 21 | 4 | 71.4 | 730 | 176 | 9.3 | 3290 | 78 | 1539 | 1 |  | 3.2886 | 19.4286 | 25 | 31.01 | 31.28 | 31.15 |  |  | 45.34 | 45.5 | 45.44
| 24 | 6.1 | 18 | 2 | 82.5 | 770 | 190 | 8.62 | 3270 | 78 | 1461 | 1 |  | 3.6843 | 20 | 26 | 22.63 | 31.34 | 27.43 |  |  | 40.37 | 45.56 | 43.31
| 25 | 4.8 | 20 | 4 | 71.1 | 780 | 196 | 9.9 | 3220 | 78 | 1523 | 1 |  | 3.71 | 21 | 27 | 22.43 | 31.08 | 27.72 |  |  | 40.33 | 45 | 43.2
| 26 | 5 | 18 | 3 |  | 790 | 200 | 10.4 | 3260 | 79 | 1489 | 1 |  | 3.9057 | 20.1429 | 28 | 30.95 | 31.19 | 31.06 |  |  | 44.92 | 45.06 | 45
| 27 | 6 | 21 | 3 |  | 770 | 198 | 7.64 | 3160 | 79 | 1389 | 1 |  | 4.1629 | 20.2857 | 29 | 31.06 | 31.34 | 31.15 |  |  | 45.01 | 45.22 | 45.02
| 28 | 8 | 26 | 5 | 50.5 | 720 | 200 | 8.74 | 3090 | 78 | 1331 | 1 |  | 4.9486 | 21.4286 | 30 | 31.27 | 31.54 | 31.43 |  |  | 45.21 | 45.46 | 45.39
| 29 | 4 | 16 | 3 | 60.9 | 760 | 190 | 8.76 | 2890 | 78 | 1249 | 1 |  | 5.2429 | 20 | 31 | 31.39 | 31.59 | 31.49 |  |  | 45.4 | 45.54 | 45.49
| 30 | 6 | 14 | 3 | 73.4 | 740 | 192 | 5.58 | 2910 | 79 | 1320 | 1 |  | 5.7 | 19 | TOTAL | 861.05 | 966.65 | 918.21 |  |  | 1344.9 | 1403.46 | 1377.21
| 31 | 5 | 20 | 4 | 58.6 | 660 | 190 | 9.48 | 2840 | 79 | 1336 | 1 | 4.964 | 5.5429 | 19.2857 | AVERAGE | 27.7758 | 31.1823 | 29.6197 |  |  | 43.3839 | 45.2729 | 44.4261
| TOTAL | 130.33 | 568 | 98 | 1641.5 | 22870 | 5976 | 305.65 | 92890 | 2453.8 | 41429 |  |  |  |  | MAXIMUM | 31.39 | 31.59 | 31.49 |  |  | 45.4 | 45.65 | 45.49
| AVERAGE | 4.2042 | 18.3226 | 3.1613 | 68.3958 | 737.7419 | 192.7742 | 9.8597 | 2996.4516 | 79.1548 | 1336.4194 |  |  | 3.8713 | 18.4343 | MINIMUM | 16.98 | 30.73 | 22.89 |  |  | 36.6 | 44.88 | 40.67
| MAXIMUM | 8 | 30
[5 empty] | PAGE 4 | [14 empty] | PAGE 22
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
[5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [13 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
[5 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [13 empty] | MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
[5 empty] | MONTHLY OPERATIONAL REPORT | [13 empty] | REGIONAL MONITORING WELL ONE
[5 empty] | EFFLUENT DATA PART 2 | [13 empty] | RMW-1 |  |  |  | 1/07/04 thru 1/06/09
[16 empty] | RUN DATE |  |  |  |  | PERMIT # 0054569-142-UO
[16 empty] | 2026-07-30 |  | UPPER MONITOR ZONE |  |  |  |  | LOWER MONITOR ZONE
RUN DATE | [16 empty] | MIN | MAX | AVG |  |  | MIN | MAX | AVG
2026-07-30 | [15 empty] | JANUARY | FT HEAD | FT HEAD | FT HEAD |  |  | FT HEAD | FT HEAD | FT HEAD
[16 empty] | 2004 | ABOVE | ABOVE | ABOVE |  |  | ABOVE | ABOVE | ABOVE
| JANUARY | EFF. BACT. | EFF. BACT. | FREE | TOTAL | EFFL. | EFF PH | EFF PH | EFF. SAP | AVG. | [6 empty] | NGVD | NGVD | NGVD |  |  | NGVD | NGVD | NGVD
| 2004 | TOTAL | FECAL | CL2 | CL2 | pH | MIN | MAX | TEMP.(C) | BLK. | [5 empty] | 1 | 44.11 | 44.11 | 44.11 |  |  | ER | ER | ER
[16 empty] | 2 | 44.18 | 44.18 | 44.17 |  |  | ER | ER | ER
| 1 | TNTC | 0 | 0 | 0.9 | 6.5 | 6.5 | 6.5 | 2 | 73 | [5 empty] | 3 | 44.23 | 44.22 | 44.22 |  |  | ER | ER | ER
| 2 | 16000 | 116 | 0 | 0.8 | 6.5 | 6.4 | 6.4 | 4 | 77 | [5 empty] | 4 | 44.26 | 44.26 | 44.26 |  |  | ER | ER | ER
| 3 | 40000 | 723 | 0 | 0.7 | 6.5 | 6.4 | 6.5 | 5 | 73 | [5 empty] | 5 | 42.44 | 42.44 | 42.44 |  |  | ER | ER | ER
| 4 | 5500 | 63 | 0 | 0.9 | 6.4 | 6.3 | 6.5 | 5 | 73 | [5 empty] | 6 | 42.63 | 43.63 | 42.63 |  |  | ER | ER | ER
| 5 | 64000 | 4000 | 0 | 0.6 | 6.4 | 6.3 | 6.5 | 5 | 70 | [5 empty] | 7 | 43.82 | 73.82 | 43.82 |  |  | ER | ER | ER
| 6 | 71 | 0 | 0 | 0.6 | 6.4 | 6.4 | 6.4 | 5 | 63 | [5 empty] | 8 | 43.98 | 43.98 | 43.98 |  |  | ER | ER | ER
| 7 | 5600 | 9 | 0 | 0.4 | 6.5 | 6.4 | 6.6 | 0 | 58 | [5 empty] | 9 | 44.12 | 44.12 | 44.12 |  |  | ER | ER | ER
| 8 | TNTC | 45 | 0 | 0.6 | 6.5 | 6.4 | 6.6 | 2 | 45 | [5 empty] | 10 | 44.21 | 44.21 | 44.21 |  |  | ER | ER | ER
| 9 | 173 | 0 | 0 | 0.5 | 6.5 | 6.4 | 6.5 | 3 | 48 | [5 empty] | 11 | 44.09 | 44.09 | 44.09 |  |  | ER | ER | ER
| 10 | 2500 | 0 | 0 | 0.5 | 6.4 | 6.4 | 6.5 | 3 | 61 | [5 empty] | 12 | 44.04 | 44 | 44.04 |  |  | ER | ER | ER
| 11 | 400 | 0 | 0 | 0.8 | 6.5 | 6.5 | 6.5 | 2 | 53 | [5 empty] | 13 | 44.09 | 44.09 | 44.09 |  |  | ER | ER | ER
| 12 | 2300 | 500 | 0 | 0.4 | 6.5 | 6.3 | 6.5 | 2 | 48 | [5 empty] | 14 | 44.21 | 44.21 | 44.21 |  |  | ER | ER | ER
| 13 | TNTC | 18 | 0 | 0.5 | 6.4 | 6.3 | 6.5 | 1 | 61 | [5 empty] | 15 | 44.3 | 44.3 | 44.3 |  |  | ER | ER | ER
| 14 | 700 | 0 | 0 | 0.7 | 6.5 | 6.4 | 6.5 | 1 | 60 | [5 empty] | 16 | ER | ER | ER |  |  | ER | ER | ER
| 15 | 116 | 0 | 0 | 0.6 | 6.5 | 6.4 | 6.6 | 3 | 46 | [5 empty] | 17 | ER | ER | ER |  |  | ER | ER | ER
| 16 | 9 | 0 | 0 | 0.4 | 6.5 | 6.4 | 6.5 | 3 | 50 | [5 empty] | 18 | ER | ER | ER |  |  | ER | ER | ER
| 17 | 116 | 0 | 0 | 0.6 | 6.5 | 6.4 | 6.5 | 3 | 60 | [5 empty] | 19 | ER | ER | ER |  |  | ER | ER | ER
| 18 | 152 | 9 | 0.1 | 0.7 | 6.5 | 6.4 | 6.5 | 2 | 54 | [5 empty] | 20 | ER | ER | ER |  |  | ER | ER | ER
| 19 | TNTC | TNTC | 0 | 0.5 | 6.4 | 6.3 | 6.5 | 2 | 57 | [5 empty] | 21 | 44.29 | 44.29 | 44.29 |  |  | ER | ER | ER
| 20 | 403 | 0 | 0 | 0.7 | 6.4 | 6.3 | 6.5 | 5 | 57 | [5 empty] | 22 | 44.31 | 44.31 | 44.31 |  |  | ER | ER | ER
| 21 | TNTC | 45 | 0 | 0.5 | 6.5 | 6.5 | 6.5 | 2 | 57 | [5 empty] | 23 | 44.28 | 44.28 | 44.28 |  |  | ER | ER | ER
| 22 | 84500 | 134 | 0 | 0.6 | 6.5 | 6.4 | 6.5 | 2 | 48 | [5 empty] | 24 | ER | ER | ER |  |  | ER | ER | ER
| 23 | 17000 | 27 | 0 | 0.6 | 6.5 | 6.5 | 6.6 | 0 | 45 | [5 empty] | 25 | ER | ER | ER |  |  | ER | ER | ER
| 24 | TNTC | 30000 | 0 | 0.6 | 6.5 | 6.4 | 6.5 | 0 | 60 | [5 empty] | 26 | 44.42 | 44.49 | 44.46 |  |  | 22.17 | 22.26 | 22.22
| 25 | 65000 | 9 | 0 | 0.9 | 6.5 | 6.4 | 6.5 | 2 | 49 | [5 empty] | 27 | 44.44 | 44.54 | 44.49 |  |  | 22.19 | 22.33 | 22.25
| 26 | 500 | 0 | 0 | 0.8 | 6.4 | 6.3 | 6.5 | 5 | 50 | [5 empty] | 28 | 44.34 | 44.47 | 44.38 |  |  | 22.05 | 22.24 | 22.13
| 27 | 28500 | 9 | 0 | 0.4 | 6.5 | 6.4 | 6.5 | 5 | 50 | [5 empty] | 29 | 44.35 | 44.47 | 44.4 |  |  | 22.07 | 22.21 | 22.14
| 28 | TNTC | TNTC | 0 | 0.4 | 6.6 | 6.5 | 6.8 | 2 | 42 | [5 empty] | 30 | 44.47 | 44.63 | 44.56 |  |  | 22.19 | 22.38 | 22.3
| 29 | 71500 | 54 | 0 | 0.5 | 6.8 | 6.5 | 6.9 | 2 | 37 | [5 empty] | 31 | 44.47 | 44.63 | 44.56 |  |  | 22.19 | 22.38 | 22.3
| 30 | TNTC | 142 | 0 | 0.6 | 6.5 | 6.4 | 6.8 | 4 | 49 | [5 empty] | TOTAL | 1058.08 | 1089.77 | 1058.42 |  |  | 132.86 | 133.8 | 133.34
| 31 | 44000 | 9 | 0 | 0.3 | 6.5 | 6.4 | 6.5 | 4 | 57 | [5 empty] | AVERAGE | 44.0867 | 45.4071 | 44.1008 |  |  | 22.1433 | 22.3 | 22.2233
| TOTAL | 449040 | 35912 | 0.1 | 18.6 | 201.1 | 198.3 | 202.7 | 86 | 1731 | [5 empty] | MAXIMUM | 44.47 | 73.82 | 44.56 |  |  | 22.19 | 22.38 | 22.3
| AVERAGE | 19523.4783 | 1238.3448 | 0.0032258 | 0.6 | 6.4871 | 6.3968 | 6.5387 | 2.7742 | 55.8387 | [5 empty] | MINIMUM | 42.44 | 42.44 | 42.44 |  |  | 22.05 | 22.21 | 22.13
[7 empty] | 6.3 | 6.9
[7 empty] | MIN | MAX
PAGE 5
PAGE 23
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
NUTRIENTS
RUN DATE
| 2026-07-30 |  | INFLUENT | [5 empty] | EFFLUENT
| JANUARY | INFLUENT | INFLUENT | INFLUENT | INFLUENT |  | EFFL. | EFFL. | EFFL. | EFFL.
| 2004 | NH-3 | N03-N | TKN | TOT P |  | NH-3 | N03-N | TKN | TOT P
| 1 | 17.96 | 0.02 | 21.21 | 3.06 |  | 13.66 | 0.243 | 17.2 | 1.78
| 2 | 16.83 | 0.02 | 20.62 | 2.02 |  | 14.41 | 0.16 | 17.53 | 1.64
| 3 | 18.47 | 0.125 | 21.83 | 2.93 |  | 13.94 | 0.169 | 17.18 | 1.52
| 4 | 19.17 | 0.02 | 23.46 | 4.99 |  | 14.53 | 0.251 | 17.94 | 1.66
| 5 | 19.17 | 0.02 | 23.46 | 4.99 |  | 14.53 | 0.251 | 17.94 | 1.66
6
| 7 | 19.19 | 0.02 | 22.22 | 3.37 |  | 16.18 | 0.143 | 19.66 | 1.24
| 8 | 19.04 | 0.02 | 22.19 | 3.62 |  | 15.7 | 0.177 | 18.85 | 1.05
| 9 | 18.86 | 0.02 | 22.11 | 3.24 |  | 15.27 | 0.129 | 18.39 | 1.13
| 10 | 18.3 | 0.02 | 21.87 | 3.23 |  | 14.48 | 0.105 | 17.98 | 0.965
| 11 | 17.41 | 0.02 | 20.71 | 3.18 |  | 14.5 | 0.121 | 17.87 | 1.06
12
13
| 14 | 19.17 | 0.02 | 22.67 | 3.6 |  | 15.01 | 0.169 | 18.2 | 0.668
| 15 | 18.84 | 0.02 | 22.04 | 3.04 |  | 16.48 | 0.233 | 19.6 | 0.948
| 16 | 18.3 | 0.02 | 21.87 | 2.96 |  | 15.73 | 0.187 | 19.04 | 1.78
| 17 | 18.23 | 0.02 | 22.1 | 3.42 |  | 14.07 | 0.183 | 17.63 | 2.1
| 18 | 16.83 | 0.02 | 20.48 | 2.96 |  | 15.23 | 0.156 | 18.62 | 1.05
19
20
| 21 | 19.93 | 0.02 | 21.41 | 3.18 |  | 14.73 | 0.19 | 17.81 | 1.15
| 22 | 18.4 | 0.02 | 21.79 | 3.39 |  | 14.55 | 0.275 | 17.67 | 0.598
| 23 | 17.45 | 0.02 | 21.39 | 3.13 |  | 16.16 |  | 0 | 1.81
| 24 | 15.02 | 0.02 | 21.55 | 2.73 |  | 13.94 | 0.113 | 17.25 | 1.53
| 25 | 17.35 | 0.02 | 20.91 | 3.18 |  | 13.2 | 0.354 | 16.61 | 1.36
26
27
| 28 | 18 | 0.02 | 24 | 3.5 |  | 7.9 | 0.02 | 15 | 5.7
| 29 | 19 | 0.02 | 27 | 3.2 |  | 14 | 0.34 | 16 | 0.85
| 30 | 18 | 0.071 | 25 | 2.1 |  | 14 | 0.32 | 17 | 1.1
| 31 | 6.9 | 0.02 | 13 | 0.84 |  | 9.7 | 0.31 | 12 | 0.84
| TOTAL | 425.82 | 0.636 | 524.89 | 75.86 | TOT. | 341.9 | 4.599 | 402.97 | 35.189
| AVERAGE | 17.7425 | 0.0265 | 21.8704 | 3.1608 | AVG. | 14.2458 | 0.19996 | 16.7904 | 1.4662
PAGE 6
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
REACTOR ONE PROCESS
RUN DATE
| 2026-07-30 |  | TRAIN "A" | [5 empty] | TRAIN "B"
| JANUARY | MLSS | MLVSS | SS | SVI |  | MLSS | MLVSS | SS | SVI
| 2004 | "A" | "A" | "A" | "A" |  | "B" | "B" | "B" | "B"
| 1 | O/S | O/S | O/S |  |  | 3950 | 3280 | 42 | 106.3291
| 2 | O/S | O/S | O/S |  |  | 2900 | 2480 | 43 | 148.2759
| 3 | O/S | O/S | O/S |  |  | 3330 | 2760 | 40 | 120.1201
| 4 | O/S | O/S | O/S |  |  | 4360 | 3660 | 38 | 87.156
| 5 | O/S | O/S | O/S |  |  | 4420 | 3720 | 44 | 99.5475
| 6 | O/S | O/S | O/S |  |  | 4130 | 3430 | 40 | 96.8523
| 7 | O/S | O/S | O/S |  |  | 2660 | 2210 | 46 | 172.9323
| 8 | O/S | O/S | O/S |  |  | 2350 | 1950 | 30 | 127.6596
| 9 | O/S | O/S | O/S |  |  | 3020 | 2610 | 30 | 99.3377
| 10 | O/S | O/S | O/S |  |  | 2970 | 2570 | 39 | 131.3131
| 11 | O/S | O/S | O/S |  |  | 3250 | 2470 | 36 | 110.7692
| 12 | O/S | O/S | O/S |  |  | 3510 | 2680 | 33 | 94.0171
| 13 | O/S | O/S | O/S |  |  | 3820 | 3170 | 39 | 102.0942
| 14 | O/S | O/S | O/S |  |  | 2920 | 2420 | 39 | 133.5616
| 15 | O/S | O/S | O/S |  |  | 2600 | 2160 | 35 | 134.6154
| 16 | O/S | O/S | O/S |  |  | 2610 | 2180 | 35 | 134.0996
| 17 | O/S | O/S | O/S |  |  | 2940 | 2440 | 34 | 115.6463
| 18 | O/S | O/S | O/S |  |  | 3610 | 3000 | 44 | 121.8837
| 19 | O/S | O/S | O/S |  |  | 3530 | 3000 | 36 | 101.983
| 20 | O/S | O/S | O/S |  |  | 4040 | 3430 | 37 | 91.5842
| 21 | O/S | O/S | O/S |  |  | 3280 | 2790 | 37 | 112.8049
| 22 | O/S | O/S | O/S |  |  | 3030 | 2570 | 29 | 95.7096
| 23 | O/S | O/S | O/S |  |  | 2760 | 2290 | 37 | 134.058
| 24 | O/S | O/S | O/S |  |  | 3220 | 2640 | 36 | 111.8012
| 25 | O/S | O/S | O/S |  |  | 3740 | 3050 | 33 | 88.2353
| 26 | O/S | O/S | O/S |  |  | 4010 | 3270 | 35 | 87.2818
| 27 | O/S | O/S | O/S |  |  | 3860 | 3140 | 38 | 98.4456
| 28 | O/S | O/S | O/S |  |  | 2800 | 2260 | 24 | 85.7143
| 29 | O/S | O/S | O/S |  |  | 3420 | 2760 | 25 | 73.0994
| 30 | O/S | O/S | O/S |  |  | 3120 | 2840 | 46 | 147.4359
| 31 | O/S | O/S | O/S |  |  | 2630 | 2210 | 38 | 144.4867
| TOTAL | 0 | 0 | 0 |  |  | 102790 | 85440 | 1138
| AVERAGE | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 3315.8065 | 2756.129 | 36.7097 | 110.7112
PAGE 7
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
REACTOR TWO PROCESS
RUN DATE
| 2026-07-30 |  | TRAIN "C" | [5 empty] | TRAIN "D"
| JANUARY | MLSS | MLVSS | SS | SVI |  | MLSS | MLVSS | SS | SVI
| 2004 | "C" | "C" | "C" | "C" |  | "D" | "D" | "D" | "D"
| 1 | O/S | O/S | O/S |  |  | 4160 | 3450 | 44 | 105.7692
| 2 | O/S | O/S | O/S |  |  | 3050 | 2650 | 47 | 154.0984
| 3 | O/S | O/S | O/S |  |  | 3310 | 2750 | 39 | 117.8248
| 4 | O/S | O/S | O/S |  |  | 3900 | 3260 | 38 | 97.4359
| 5 | O/S | O/S | O/S |  |  | 3950 | 3290 | 42 | 106.3291
| 6 | O/S | O/S | O/S |  |  | 3660 | 3040 | 43 | 117.4863
| 7 | O/S | O/S | O/S |  |  | 3020 | 2510 | 42 | 139.0728
| 8 | O/S | O/S | O/S |  |  | 3000 | 2490 | 31 | 103.3333
| 9 | O/S | O/S | O/S |  |  | 3230 | 2760 | 35 | 108.3591
| 10 | O/S | O/S | O/S |  |  | 2260 | 1860 | 41 | 181.4159
| 11 | O/S | O/S | O/S |  |  | 2950 | 2280 | 40 | 135.5932
| 12 | O/S | O/S | O/S |  |  | 4430 | 3440 | 32 | 72.2348
| 13 | O/S | O/S | O/S |  |  | 3320 | 2760 | 41 | 123.494
| 14 | O/S | O/S | O/S |  |  | 3280 | 2720 | 34 | 103.6585
| 15 | O/S | O/S | O/S |  |  | 3180 | 2640 | 34 | 106.9182
| 16 | O/S | O/S | O/S |  |  | 3260 | 2710 | 36 | 110.4294
| 17 | O/S | O/S | O/S |  |  | 3310 | 2750 | 37 | 111.7825
| 18 | O/S | O/S | O/S |  |  | 3310 | 2750 | 32 | 96.6767
| 19 | O/S | O/S | O/S |  |  | 3580 | 3080 | 34 | 94.9721
| 20 | O/S | O/S | O/S |  |  | 3240 | 2790 | 36 | 111.1111
| 21 | O/S | O/S | O/S |  |  | 3070 | 2610 | 32 | 104.2345
| 22 | O/S | O/S | O/S |  |  | 2500 | 2120 | 30 | 120
| 23 | O/S | O/S | O/S |  |  | 3220 | 2630 | 46 | 142.8571
| 24 | O/S | O/S | O/S |  |  | 3810 | 3110 | 42 | 110.2362
| 25 | O/S | O/S | O/S |  |  | 3400 | 2730 | 32 | 94.1176
| 26 | O/S | O/S | O/S |  |  | 3840 | 3100 | 32 | 83.3333
| 27 | O/S | O/S | O/S |  |  | 3950 | 3240 | 40 | 101.2658
| 28 | O/S | O/S | O/S |  |  | 2450 | 2050 | 21 | 85.7143
| 29 | O/S | O/S | O/S |  |  | 3240 | 2710 | 30 | 92.5926
| 30 | O/S | O/S | O/S |  |  | 2680 | 2360 | 37 | 138.0597
| 31 | O/S | O/S | O/S |  |  | 2580 | 2170 | 39 | 151.1628
| TOTAL | 0 | 0 | 0 |  |  | 102140 | 84810 | 1139
| AVERAGE | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 3294.8387 | 2735.8065 | 36.7419 | 111.5136
PAGE 8
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
RAS SUMMARY
RUN DATE
2026-07-30
| JANUARY | R-1 | R-2 | TOTAL | F/M | TOTAL | SLUDGE | % TOT | % FIX | % VOL.
| 2004 | TOT. RAS | TOT. RAS | MLVSS | RATIO | MLSS | AGE | RAS | RAS | RAS
|  | MGD | MGD
| 1 | 2.468 | 8 | 6730 | 0.52723 | 8110 | 1.9113 | 1.4 | 16.4 | 83.6
| 2 | 2.53 | 7.415 | 5130 | 0.64056 | 5950 | 1.3945 | 1.21 | 23.6 | 76.4
| 3 | 2.666 | 7.764 | 5510 | 0.60495 | 6640 | 1.7928 | 1.1 | 19.6 | 80.4
| 4 | 2.634 | 7.971 | 6920 | 0.34794 | 8260 | 5.6605 | 1.03 | 22.3 | 77.7
| 5 | 2.729 | 7.617 | 7010 | 0.37662 | 8370 | 1.9022 | 1 | 20.2 | 79.8
| 6 | 2.476 | 7.588 | 6470 | 0.44807 | 7790 | 1.7125 | 1.01 | 20.8 | 79.2
| 7 | 1.977 | 7.488 | 4720 | 0.53316 | 5680 | 1.4127 | 1.04 | 19.4 | 80.6
| 8 | 1.612 | 7.79 | 4440 | 1.1368 | 5350 | 0.23386 | 0.84 | 24.2 | 75.8
| 9 | 1.499 | 7.831 | 5370 | 0.62555 | 6250 | 0.42793 | 0.97 | 20.7 | 79.3
| 10 | 1.316 | 7.64 | 4430 | 0.81616 | 5230 | 1.989 | 0.96 | 23.6 | 76.4
| 11 | 1.029 | 7.852 | 4750 | 0.72341 | 6200 | 2.4668 | 0.93 | 21.2 | 78.8
| 12 | 1.713 | 7.212 | 6120 | 0.43379 | 7940 | 3.8454 | 1 | 20 | 80
| 13 | 1.788 | 8.058 | 5930 | 0.37817 | 7140 | 1.6185 | 1.03 | 20.5 | 79.5
| 14 | 1.685 | 7.711 | 5140 | 0.52399 | 6200 | 1.6047 | 1.15 | 20.4 | 79.6
| 15 | 1.524 | 8.287 | 4800 | 0.51302 | 5780 | 1.4083 | 1.17 | 19.7 | 80.3
| 16 | 1.877 | 8.267 | 4890 | 0.53563 | 5870 | 1.4207 | 1.04 | 22.5 | 77.5
| 17 | 2.142 | 7.254 | 5190 | 0.60282 | 6250 | 1.6628 | 1.09 | 22 | 78
| 18 | 3.073 | 7.512 | 5750 | 0.56384 | 6920 | 1.765 | 0.9 | 20.3 | 79.7
| 19 | 2.763 | 7.342 | 6080 | 0.38333 | 7110 | 1.7541 | 0.95 | 20.8 | 79.2
| 20 | 1.48 | 7.153 | 6220 | 0.3748 | 7280 | 1.6709 | 0.97 | 22.1 | 77.9
| 21 | 1.486 | 7.169 | 5400 | 0.49021 | 6350 | 1.423 | 0.93 | 23 | 77
| 22 | 2.385 | 7.34 | 4690 | 0.55725 | 5530 | 1.4409 | 0.89 | 23.3 | 76.7
| 23 | 1.408 | 7.596 | 4920 | 0.43523 | 5980 | 1.1013 | 0.89 | 23.5 | 76.5
| 24 | 0.984 | 7.547 | 5750 | 0.83476 | 7030 | 1.4196 | 1.02 | 22.2 | 77.8
| 25 | 1.859 | 6.965 | 5780 | 0.6963 | 7140 | 1.7741 | 0.97 | 21.7 | 78.3
| 26 | 3.443 | 7.17 | 6370 | 0.51275 | 7850 | 1.9273 | 1.04 | 24 | 76
| 27 | 3.247 | 7.13 | 6380 | 0.58035 | 7810 | 3.41 | 0.88 | 23.6 | 76.4
| 28 | 1.511 | 6.61 | 4310 | 0.93835 | 5250 | 0.41616 | 0.79 | 23 | 77
| 29 | 1.831 | 7.372 | 5470 | 0.84152 | 6660 | 1.2918 | 0.9 | 19.6 | 80.4
| 30 | 2.9 | 7.935 | 5200 | 0.9908 | 5800 | 1.501 | 0.96 | 21.2 | 78.8
| 31 | 2.509 | 7.432 | 4380 | 0.71814 | 5210 | 0.80579 | 1.03 | 22 | 78
| TOTAL | 64.544 | 234.018 | 170250 |  | 204930 |  | 31.09 | 667.4 | 2432.6
| AVERAGE | 2.0821 | 7.549 | 5491.9355 | 0.58793 | 6610.6452 | 1.2675 | 1.0029 | 21.529 | 78.471
PAGE 9
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
DEWATERING DATA
RUN DATE
| 2026-07-30 |  | FEED SLUDGE |  |  |  |  | FILTRATE RETURN
| JANUARY | % TOT. | % FIX. | % VOL. | pH |  | % TOT. | % FIX. | % VOL. | pH
| 2004 | FEED | FEED | FEED |  |  | FILT. | FILT. | FILT.
1
2
3
| 4 | 1.34 | 23.1 | 76.9 | 6.6 |  | 0.21 | 57.1 | 42.9 | 7.18
| 5 | 1.3 | 20 | 80 | 6.69 |  | 0.23 | 56.5 | 43.5 | 7.18
| 6 | 1.3 | 20 | 80 | 6.7 |  | 0.21 | 52.4 | 47.6 | 7.19
| 7 | 1.33 | 20.3 | 79.7 | 6.69 |  | 0.23 | 52.2 | 47.8 | 7.19
| 8 | 1.32 | 22.7 | 77.3 | 6.8 |  | 0.23 | 69.6 | 30.4 | 7.2
9
10
| 11 | 1.18 | 22.9 | 77.1 | 6.89 |  | 0.19 | 68.4 | 31.6 | 7.27
| 12 | 1.4 | 20 | 80 | 6.9 |  | 0.18 | 55.6 | 44.4 | 7.2
13
| 14 | 1.41 | 19.9 | 80.1 | 6.81 |  | 0.2 | 50 | 50 | 7.21
| 15 | 1.4 | 18.6 | 81.4 | 6.79 |  | 0.2 | 55 | 45 | 7.19
16
17
| 18 | 1.41 | 21.3 | 78.7 | 6.79 |  | 0.19 | 52.6 | 47.4 | 7.18
| 19 | 1.32 | 22.7 | 77.3 | 6.67 |  | 0.27 | 59.3 | 40.7 | 7.18
| 20 | 1.36 | 22.1 | 77.9 | 6.7 |  | 0.23 | 65.2 | 34.8 | 7.19
| 21 | 1.42 | 21.8 | 78.2 | 6.8 |  | 0.2 | 75 | 25 | 7.21
| 22 | 1.37 | 21.9 | 78.1 | 6.86 |  | 0.2 | 75 | 25 | 7.14
23
24
| 25 | 1.31 | 22.9 | 77.1 | 6.79 |  | 0.24 | 66.7 | 33.3 | 7.17
| 26 | 1.2 | 24.2 | 75.8 | 6.8 |  | 0.23 | 65.2 | 34.8 | 7.2
| 27 | 1.39 | 23 | 77 | 6.52 |  | 0.2 | 75 | 25 | 7.08
| 28 | 1.39 | 23 | 77 | 6.81 |  | 0.22 | 68.2 | 31.8 | 7.2
| 29 | 1.36 | 21.3 | 78.7 | 6.77 |  | 0.27 | 88.8 | 11.2 | 7.18
30
31
| TOTAL | 25.51 | 411.7 | 1488.3 | 128.38 |  | 4.13 | 1207.8 | 692.2 | 136.54
| AVERAGE | 1.3426 | 21.6684 | 78.3316 | 6.7568 |  | 0.21737 | 63.5684 | 36.4316 | 7.1863
PAGE 10
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
SLUDGE VOLUME REMOVED
RUN DATE
2026-07-30
|  | JANUARY | TRAILERS | TONS | DRY TONS | % LIME | % TOT. | % FIX. | % VOL.
|  | 2004 | REMOVED | SLUDGE | REMOVED | CAKE | CAKE | CAKE | CAKE
|  | 1 | 0 | 0
|  | 2 | 1 | 25
|  | 3 | 0 | 0
|  | 4 | 1 | 25 | 11.3432 |  | 17.44 | 15 | 85
|  | 5 | 6 | 150 | 27.5929 |  | 17.73 | 12.5 | 87.5
|  | 6 | 6 | 150 | 25.045 |  | 17.86 | 14 | 86
|  | 7 | 6 | 150 | 28.0633 |  | 18.36 | 14.5 | 85.5
|  | 8 | 6 | 150 | 25.1001 |  | 17.68 | 13.3 | 86.7
|  | 9 | 4 | 100
|  | 10 | 0 | 0
|  | 11 | 1 | 25 | 7.9714 |  | 17.58 | 13.2 | 86.8
|  | 12 | 6 | 150 | 30.2992 |  | 18.53 | 18.53 | 81.47
|  | 13 | 2 | 50
|  | 14 | 5 | 125 | 25.8119 |  | 17.11 | 14.7 | 85.3
|  | 15 | 6 | 150 | 32.7512 |  | 17.3 | 18 | 82
|  | 16 | 5 | 125
|  | 17 | 0 | 0
|  | 18 | 1 | 25 | 6.4089 |  | 17.64 | 14.3 | 85.7
|  | 19 | 4 | 100 | 26.0358 |  | 17.54 | 13.1 | 86.9
|  | 20 | 6 | 150 | 29.2067 |  | 17.7 | 13.3 | 86.7
|  | 21 | 6 | 150 | 29.5478 |  | 17.78 | 13.2 | 86.8
|  | 22 | 4 | 100 | 16.396 |  | 17.55 | 17.9 | 82.1
|  | 23 | 5 | 125
|  | 24 | 0 | 0
|  | 25 | 1 | 25 | 7.8117 |  | 17.3 | 13.8 | 86.2
|  | 26 | 7 | 175 | 25.7206 |  | 17.81 | 18.6 | 81.4
|  | 27 | 6 | 150 | 30.5465 |  | 18.04 | 14.7 | 85.3
|  | 28 | 5 | 125 | 25.2139 |  | 17.52 | 14.3 | 85.7
|  | 29 | 5 | 125 | 24.4429 |  | 17.58 | 20.7 | 79.3
|  | 30 | 5 | 125
|  | 31 | 0 | 0
|  | TOTAL | 110 | 2750 | 435.3088 | 0 | 336.05 | 287.63 | 1612.37
|  | AVERAGE | 3.5484 | 88.7097 | 22.911 | #DIV/0! | 17.6868 | 15.1384 | 84.8616
PAGE 11
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
CHEMICAL USEAGE
RUN DATE
2026-07-30
| JANUARY | H2O2 | CL2 | POLYMER | POLYMER | LIME | GOX | O2 % | LOX | FPL
| 2004 | POUNDS | POUNDS | GALLONS | POUNDS | DELV. | TONS | PURITY | TONS | KW
| 1 | 988 | 1300 | 0 | 0 | 0 | 26.4 | 96% | 162 | 30783
| 2 | 1058 | 1160 | 13 | 108.42 | 0 | 22.1 | 100% | 163 | 31184
| 3 | 848 | 1280 | 0 | 0 | 0 | 21.4 | 100% | 164 | 31141
| 4 | 949 | 1200 | 38 | 316.92 | 0 | 20.3 | 100% | 165 | 31128
| 5 | 529 | 1160 | 67 | 558.78 | 0 | 21.7 | 100% | 165 | 31165
| 6 | 1028 | 1180 | 87 | 725.58 | 0 | 20.8 | 100% | 166 | 31011
| 7 | 1238 | 1200 | 66 | 550.44 | 0 | 19.1 | 100% | 167 | 31421
| 8 | 1048 | 1200 | 21 | 175.14 | 0 | 17 | 100% | 167 | 31515
| 9 | 809 | 1200 | 56 | 467.04 | 0 | 19.4 | 100% | 168 | 31369
| 10 | 1437 | 1320 | 62 | 517.08 | 0 | 19.9 | 98% | 168 | 31417
| 11 | 758 | 1240 | 0 | 0 | 0 | 18.3 | 100% | 170 | 31720
| 12 | 1667 | 1040 | 45 | 375.3 | 0 | 22.5 | 100% | 171 | 31544
| 13 | 2066 | 1340 | 45 | 375.3 | 0 | 21.7 | 100% | 172 | 31477
| 14 | 1886 | 1180 | 53 | 442.02 | 0 | 22.7 | 100% | 173.3 | 31447
| 15 | 2664 | 1080 | 98 | 817.32 | 0 | 23.7 | 100% | 173 | 31437
| 16 | 2934 | 1160 | 6 | 50.04 | 0 | 19.9 | 100% | 174 | 31395
| 17 | 3044 | 1060 | 0 | 0 | 0 | 18.8 | 100% | 175 | 31114
| 18 | 1000 | 1220 | 7 | 58.38 | 0 | 20.7 | 100% | 176.3 | 31176
| 19 | 3693 | 1160 | 107 | 892.38 | 0 | 19.8 | 100% | 176.4 | 31371
| 20 | 3503 | 1060 | 94 | 783.96 | 0 | 19.6 | 100% | 178 | 31569
| 21 | 1000 | 1180 | 16 | 133.44 | 0 | 18.9 | 100% | 178 | 31622
| 22 | 1000 | 1240 | 47 | 391.98 | 0 | 17.8 | 100% | 177 | 31623
| 23 | 5220 | 2120 | 33 | 275.22 | 0 | 18.1 | 100% | 178 | 31746
| 24 | 3443 | 1280 | 0 | 0 | 0 | 19.8 | 100% | 179 | 31780
| 25 | 3753 | 1140 | 25 | 208.5 | 0 | 18.2 | 100% | 180 | 31578
| 26 | 4780 | 1180 | 71 | 592.14 | 0 | 20.7 | 100% | 181 | 31282
| 27 | 1528 | 360 | 81 | 675.54 | 0 | 20.3 | 100% | 181 | 31224
| 28 | 2445 | 780 | 0 | 0 | 0 | 17.7 | 100% | 181 | 31861
| 29 | 1967 | 1360 | 0 | 0 | 0 | 19.8 | 100% | 181 | 31855
| 30 | 2308 | 1020 | 254 | 2118.36 | 0 | 20.2 | 100% | 182 | 31522
| 31 | 1956 | 940 | 0 | 0 | 0 | 22.9 | 99% | 183 | 31432
| TOTAL | 62547 | 36340 | 1392 | 11609.28 | 0 | 630.2 |  | 5375 | 973909
| AVERAGE | 2017.6452 | 1172.2581 | 44.9032 | 374.4929 | 0 | 20.329 | 99.77% | 173.3871 | 31416.4194
PAGE 12
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL ONE
|  | RUN DATE |  |  | PERMIT NUMBER 0054569-142-UO
|  | 2026-07-30 |  |  | 1/07/04 thru 1/06/09 |  |  | I.D. #:5006A11308
|  | JANUARY | % INFL. | MAX | MIN | WELL 1 | MAX | MIN | AVG
|  | 2004 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 25.95% | 10.24 | 4.79 | 8.07 | 51.12 | 39.23 | 46.01
|  | 2 | 25.4% | 12.04 | 3.9 | 8.08 | 57.64 | 37.66 | 46.14
|  | 3 | 25.48% | 11.06 | 4.49 | 8.02 | 54.05 | 38.62 | 46.1
|  | 4 | 26.15% | 11.63 | 4.09 | 8.11 | 56.35 | 37.98 | 46.51
|  | 5 | 25.73% | 11.91 | 4.12 | 8.02 | 57.46 | 38.08 | 46.53
|  | 6 | 25.71% | 10.06 | 4.28 | 7.89 | 50.92 | 38.3 | 45.75
|  | 7 | 25.89% | 10.08 | 4.47 | 7.9 | 50.9 | 38.68 | 45.69
|  | 8 | 25.89% | 10.1 | 3.85 | 7.99 | 50.88 | 37.46 | 45.85
|  | 9 | 26.29% | 12.1 | 3.94 | 8.16 | 57.77 | 37.33 | 46.39
|  | 10 | 25.74% | 11.31 | 4.68 | 7.99 | 55.28 | 38.62 | 45.93
|  | 11 | 33.19% | 15.59 | 5.39 | 10.13 | 69.72 | 39.37 | 51.79
|  | 12 | 27.12% | 10.72 | 5.47 | 8.5 | 52.88 | 39.68 | 46.79
|  | 13 | 25.82% | 12.51 | 3.8 | 8.07 | 57.81 | 37.31 | 45.9
|  | 14 | 25.71% | 11.09 | 4.69 | 8.12 | 54.2 | 38.57 | 46.04
|  | 15 | 25.86% | 10.15 | 4.46 | 8.2 | 50.59 | 38.17 | 46.03
|  | 16 | 26.18% | 10.14 | 4.59 | 8.21 | 50.6 | 38.82 | 46.11
|  | 17 | 25.7% | 11 | 4.38 | 8.05 | 54.84 | 38.15 | 45.93
|  | 18 | 25.62% | 11.76 | 4.77 | 8.21 | 56.71 | 38.76 | 46.58
|  | 19 | 25.69% | 11.96 | 4.75 | 8.51 | 57.66 | 38.81 | 47.27
|  | 20 | 25.64% | 11.95 | 4.7 | 8.33 | 57.07 | 38.63 | 46.74
|  | 21 | 25.79% | 12.15 | 4.75 | 8.29 | 57.31 | 38.48 | 46.46
|  | 22 | 25.47% | 13.68 | 4.79 | 8.31 | 63.41 | 38.4 | 46.39
|  | 23 | 25.91% | 12.86 | 4.42 | 8.42 | 59.75 | 37.69 | 46.7
|  | 24 | 25.45% | 12.12 | 4.83 | 8.24 | 56.79 | 38.33 | 46.14
|  | 25 | 25.35% | 11.63 | 4.82 | 8.18 | 55.24 | 38.39 | 46.25
|  | 26 | 25.5% | 11.11 | 4.81 | 8.33 | 53.93 | 38.45 | 46.61
|  | 27 | 23.7% | 14.79 | 0 | 7.69 | 67.08 | 34.78 | 45.89
|  | 28 | 25.59% | 12.14 | 4.54 | 8.07 | 57.73 | 38.19 | 45.54
|  | 29 | 25.49% | 12.14 | 3.98 | 7.98 | 58.12 | 37.25 | 45.51
|  | 30 | 24.25% | 12.43 | 4.57 | 7.81 | 59.49 | 38.52 | 45.4
|  | 31 | 31.59% | 15.71 | 5.78 | 11.73 | 71.4 | 41.08 | 57.08
|  | TOTAL | 808.9% | 368.16 | 136.9 | 257.61 | 1764.7 | 1187.79 | 1448.05
|  | AVERAGE | 26.09% | 11.8761 | 4.4161 | 8.31 | 56.9258 | 38.3158 | 46.7113
|  | MAXIMUM | 33.19% | 15.71 | 5.78 | 11.73 | 71.4 | 41.08 | 57.08
|  | MINIMUM | 23.7% | 10.06 | 0 | 7.69 | 50.59 | 34.78 | 45.4
PAGE 13
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL TWO
|  | RUN DATE |  |  | PERMIT NUMBER 0054569-142-UO
|  | 2026-07-30 |  |  | 1/07/04 thru 1/06/09 |  |  | I.D. #:5006A11309
|  | JANUARY | % INFL. | MAX | MIN | WELL 2 | MAX | MIN | AVG
|  | 2004 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 25.99% | 10.3 | 4.43 | 8.08 | 50.13 | 38.45 | 45.12
|  | 2 | 25.43% | 12.25 | 3.28 | 8.09 | 56.6 | 36.95 | 45.29
|  | 3 | 25.54% | 11.22 | 4.06 | 8.04 | 53.07 | 37.9 | 45.25
|  | 4 | 26.12% | 11.79 | 3.53 | 8.1 | 55.39 | 37.27 | 45.64
|  | 5 | 25.7% | 12.13 | 3.63 | 8.01 | 56.42 | 37.37 | 45.68
|  | 6 | 25.68% | 10.16 | 3.86 | 7.88 | 49.96 | 37.57 | 44.91
|  | 7 | 25.82% | 10.19 | 4.05 | 7.88 | 49.95 | 38.03 | 44.79
|  | 8 | 25.85% | 10.21 | 3.17 | 7.98 | 49.95 | 36.73 | 44.95
|  | 9 | 26.26% | 12.26 | 3.48 | 8.15 | 56.77 | 36.58 | 45.49
|  | 10 | 25.74% | 11.5 | 4.41 | 7.99 | 54.21 | 37.87 | 45.01
|  | 11 | 33.55% | 15.66 | 5.21 | 10.24 | 68.42 | 38.56 | 50.78
|  | 12 | 27.41% | 10.83 | 5.35 | 8.59 | 51.81 | 38.93 | 45.88
|  | 13 | 25.89% | 12.68 | 3.06 | 8.09 | 56.64 | 36.56 | 45.02
|  | 14 | 25.75% | 11.21 | 4.43 | 8.13 | 57.68 | 37.81 | 45.16
|  | 15 | 25.95% | 10.26 | 4.19 | 8.23 | 49.63 | 37.38 | 45.11
|  | 16 | 26.34% | 10.26 | 4.43 | 8.26 | 49.65 | 38.03 | 45.23
|  | 17 | 25.8% | 11.11 | 4.08 | 8.08 | 53.78 | 37.36 | 45.02
|  | 18 | 25.78% | 11.92 | 4.56 | 8.26 | 55.59 | 38.02 | 45.69
|  | 19 | 25.84% | 12.18 | 4.53 | 8.56 | 56.53 | 38.08 | 46.4
|  | 20 | 25.83% | 12.01 | 4.51 | 8.39 | 56.04 | 37.89 | 45.83
|  | 21 | 25.95% | 12.3 | 4.55 | 8.34 | 56.16 | 37.7 | 45.55
|  | 22 | 25.63% | 13.83 | 4.56 | 8.36 | 62.25 | 37.64 | 45.48
|  | 23 | 26.12% | 13.09 | 4.09 | 8.49 | 58.68 | 36.9 | 45.78
|  | 24 | 25.63% | 12.17 | 4.7 | 8.3 | 55.77 | 37.53 | 45.27
|  | 25 | 25.5% | 11.77 | 4.62 | 8.23 | 54.1 | 37.6 | 45.33
|  | 26 | 25.72% | 11.29 | 4.62 | 8.4 | 53 | 37.76 | 45.75
|  | 27 | 26.2% | 15.15 | 0.02 | 8.5 | 65.84 | 35.69 | 46.35
|  | 28 | 24.99% | 12.31 | 0.02 | 7.88 | 56.6 | 35.1 | 44.37
|  | 29 | 25.65% | 12.32 | 3.57 | 8.03 | 57.08 | 36.47 | 44.61
|  | 30 | 24.35% | 12.76 | 4.24 | 7.84 | 58.42 | 37.76 | 44.5
|  | 31 | 32.21% | 16.15 | 5.62 | 11.96 | 69.99 | 40.27 | 55.95
|  | TOTAL | 814.2% | 373.27 | 122.86 | 259.36 | 1736.11 | 1163.76 | 1421.19
|  | AVERAGE | 26.26% | 12.041 | 3.9632 | 8.3665 | 56.0035 | 37.5406 | 45.8448
|  | MAXIMUM | 33.55% | 16.15 | 5.62 | 11.96 | 69.99 | 40.27 | 55.95
|  | MINIMUM | 24.35% | 10.16 | 0.02 | 7.84 | 49.63 | 35.1 | 44.37
PAGE 14
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL THREE
|  | RUN DATE |  |  | PERMIT NUMBER 0054569-142-UO
|  | 2026-07-30 |  |  | 1/07/04 thru 1/06/09 |  |  | I.D. #:5006A11310
|  | JANUARY | % INFL. | MAX | MIN | WELL 3 | MAX | MIN | AVG
|  | 2004 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 22.67% | 9.02 | 3.93 | 7.05 | 51.37 | 39.32 | 46.2
|  | 2 | 22.13% | 10.61 | 2.96 | 7.04 | 57.99 | 37.78 | 46.37
|  | 3 | 22.17% | 9.72 | 3.59 | 6.98 | 54.37 | 38.75 | 46.3
|  | 4 | 20.67% | 10.3 | ER | 6.41 | 56.67 | 35.53 | 45.77
|  | 5 | 22.46% | 10.64 | 3.23 | 7 | 57.83 | 38.2 | 46.75
|  | 6 | 22.35% | 8.84 | 3.42 | 6.86 | 51.16 | 38.43 | 45.94
|  | 7 | 22.42% | 8.83 | 2.27 | 6.84 | 51.13 | 37.63 | 45.83
|  | 8 | 22.52% | 8.88 | 2.86 | 6.95 | 51.12 | 37.58 | 46.03
|  | 9 | 22.91% | 10.69 | 3.09 | 7.11 | 58.08 | 37.47 | 46.6
|  | 10 | 22.42% | 10.01 | 3.83 | 6.96 | 55.58 | 38.75 | 46.1
|  | 11 | 29.65% | 13.79 | 4.57 | 9.05 | 70.3 | 39.57 | 52.1
|  | 12 | 23.99% | 9.43 | 4.73 | 7.52 | 53.14 | 39.87 | 47.01
|  | 13 | 22.5% | 10.35 | ER | 7.03 | 55.86 | 35.89 | 46.02
|  | 14 | 22.55% | 9.86 | 3.91 | 7.12 | 54.47 | 38.74 | 46.23
|  | 15 | 22.64% | 8.92 | 3.71 | 7.18 | 50.82 | 38.32 | 46.22
|  | 16 | 22.96% | 8.91 | 3.88 | 7.2 | 50.85 | 38.97 | 46.31
|  | 17 | 22.51% | 9.62 | 3.56 | 7.05 | 55.04 | 38.27 | 46.11
|  | 18 | 22.41% | 10.37 | 3.94 | 7.18 | 57.01 | 38.89 | 46.78
|  | 19 | 22.49% | 10.59 | 3.95 | 7.45 | 57.98 | 38.96 | 47.52
|  | 20 | 22.47% | 10.45 | 3.9 | 7.3 | 57.47 | 38.79 | 46.94
|  | 21 | 22.59% | 10.72 | 3.96 | 7.26 | 57.66 | 38.65 | 46.69
|  | 22 | 22.29% | 12.03 | 3.99 | 7.27 | 63.83 | 38.55 | 46.6
|  | 23 | 22.74% | 11.4 | 3.6 | 7.39 | 60.09 | 37.83 | 46.92
|  | 24 | 22.3% | 10.62 | 4.09 | 7.22 | 57.15 | 38.49 | 46.38
|  | 25 | 22.15% | 10.29 | 4.03 | 7.15 | 55.42 | 38.54 | 46.4
|  | 26 | 22.38% | 9.77 | 3.97 | 7.31 | 54.25 | 38.62 | 46.84
|  | 27 | 22.5% | 13.89 | ER | 7.3 | 71 | 35.58 | 47.36
|  | 28 | 22.39% | 10.72 | 3.78 | 7.06 | 58.09 | 38.33 | 45.76
|  | 29 | 22.36% | 10.76 | 3.17 | 7 | 58.49 | 37.39 | 45.71
|  | 30 | 20.96% | 11.06 | 3.71 | 6.75 | 59.85 | 38.65 | 45.59
|  | 31 | 28.36% | 14.21 | 4.9 | 10.53 | 72 | 41.25 | 57.47
|  | TOTAL | 707.9% | 325.3 | 104.53 | 225.52 | 1776.07 | 1187.59 | 1454.85
|  | AVERAGE | 22.84% | 10.4935 | 3.7332 | 7.2748 | 57.2926 | 38.3094 | 46.9306
|  | MAXIMUM | 29.65% | 14.21 | 4.9 | 10.53 | 72 | 41.25 | 57.47
|  | MINIMUM | 20.67% | 8.83 | 2.27 | 6.41 | 50.82 | 35.53 | 45.59
PAGE 15
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL FOUR
|  | RUN DATE |  |  | PERMIT NUMBER 0054569-142-UO
|  | 2026-07-30 |  |  | 1/07/04 thru 1/06/09
|  | JANUARY | % INFL. | MAX | MIN | WELL 4 | MAX | MIN | AVG
|  | 2004 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 0.4181% | 0.16 | 0.12 | 0.13 | 36.77 | 35.18 | 36.06
|  | 2 | 0.4086% | 0.16 | 0.13 | 0.13 | 37.36 | 35.02 | 36.16
|  | 3 | 0.4447% | 0.16 | 0.13 | 0.14 | 37.13 | 35.29 | 36.24
|  | 4 | 0.4515% | 0.16 | 0.13 | 0.14 | 37.42 | 35.22 | 36.28
|  | 5 | 0.4171% | 0.15 | 0.13 | 0.13 | 37.64 | 35.25 | 36.37
|  | 6 | 0.4562% | 0.17 | 0.12 | 0.14 | 36.94 | 35.28 | 36.29
|  | 7 | 0.3933% | 0.13 | 0.12 | 0.12 | 36.91 | 35.23 | 36.18
|  | 8 | 0.4212% | 0.16 | 0.12 | 0.13 | 36.89 | 35 | 36.21
|  | 9 | 0.4189% | 0.16 | 0.12 | 0.13 | 37.66 | 35 | 36.26
|  | 10 | 0.3866% | 0.13 | 0.11 | 0.12 | 37.32 | 35.17 | 36.15
|  | 11 | 0.3932% | 0.14 | 0.1 | 0.12 | 36.06 | 34.61 | 35.27
|  | 12 | 0.4148% | 0.15 | 0.11 | 0.13 | 36.88 | 34.42 | 35.88
|  | 13 | 0.416% | 0.16 | 0.11 | 0.13 | 36.9 | 34.8 | 36.06
|  | 14 | 0.38% | 0.15 | 0.11 | 0.12 | 55.28 | 34.98 | 36.09
|  | 15 | 0.3784% | 0.15 | 0.11 | 0.12 | 36.73 | 34.98 | 36.04
|  | 16 | 0.4146% | 0.16 | 0.11 | 0.13 | 36.77 | 35.13 | 36.06
|  | 17 | 0.3831% | 0.15 | 0.11 | 0.12 | 37.06 | 35.05 | 35.99
|  | 18 | 0.4057% | 0.14 | 0.12 | 0.13 | 37.35 | 35.12 | 36.09
|  | 19 | 0.3924% | 0.15 | 0.12 | 0.13 | 37.42 | 35.07 | 36.14
|  | 20 | 0.4002% | 0.15 | 0.11 | 0.13 | 37.22 | 34.96 | 36.01
|  | 21 | 0.3733% | 0.13 | 0.11 | 0.12 | 37.19 | 34.81 | 35.92
|  | 22 | 0.3985% | 0.15 | 0.11 | 0.13 | 37.31 | ER | 13.88
|  | 23 | 0.3692% | 0.15 | 0.11 | 0.12 | 36.94 | ER | 16.9
|  | 24 | 0.3706% | 0.15 | 0.1 | 0.12 | 37.08 | 34.62 | 35.77
|  | 25 | 0.3718% | 0.15 | 0.1 | 0.12 | 37.09 | 34.66 | 35.81
|  | 26 | 0.398% | 0.14 | 0.12 | 0.13 | 36.86 | 34.71 | 35.88
|  | 27 | 2.959% | 19.56 | 0.12 | 0.96 | 60.48 | 34.77 | 36.99
|  | 28 | 1.49% | 15.42 | 0.11 | 0.47 | 50.85 | 35 | 36.32
|  | 29 | 0.3834% | 0.15 | 0.11 | 0.12 | 37.45 | 35.03 | 36.09
|  | 30 |  | 10.19 | ER | ER | 48.35 | 35.17 | 38.56
|  | 31 | 0.3232% | 0.12 | 0.12 | 0.12 | 36.44 | 35.22 | 35.72
|  | TOTAL | 15.63% | 49.35 | 3.45 | 4.98 | 1215.75 | 1014.75 | 1079.67
|  | AVERAGE | 0.5211% | 1.5919 | 0.115 | 0.166 | 39.2177 | 34.9914 | 34.8281
|  | MAXIMUM | 2.959% | 19.56 | 0.13 | 0.96 | 60.48 | 35.29 | 38.56
|  | MINIMUM | 0.3232% | 0.12 | 0.1 | 0.12 | 36.06 | 34.42 | 13.88
PAGE 16
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL FIVE
|  | RUN DATE |  |  | PERMIT NUMBER 0054569-142-UO
|  | 2026-07-30 |  |  | 1/07/04 thru 1/06/09 |  |  | I.D. #:5006A11311
|  | JANUARY | % INFL. | MAX | MIN | WELL 5 | MAX | MIN | AVG
|  | 2004 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 23.16% | 8.97 | 4.31 | 7.2 | 50.84 | 39.13 | 45.68
|  | 2 | 22.6% | 10.57 | 3.4 | 7.19 | 57.36 | 37.57 | 45.95
|  | 3 | 22.71% | 9.71 | 3.97 | 7.15 | 53.7 | 38.55 | 45.84
|  | 4 | 23.32% | 10.22 | 3.57 | 7.23 | 55.98 | 37.94 | 46.24
|  | 5 | 22.94% | 10.5 | 3.67 | 7.15 | 57.37 | 37.99 | 46.42
|  | 6 | 22.91% | 8.82 | 3.83 | 7.03 | 51 | 38.26 | 45.5
|  | 7 | 23.01% | 8.84 | 3.85 | 7.02 | 50.84 | 38.54 | 45.54
|  | 8 | 23% | 8.85 | 3.3 | 7.1 | 51.06 | 37.31 | 45.72
|  | 9 | 23.33% | 10.58 | 3.49 | 7.24 | 58.23 | 37.3 | 46.29
|  | 10 | 22.94% | 9.93 | 4.26 | 7.12 | 55.44 | 38.36 | 45.98
|  | 11 |  | 6.97 | ER | ER | 45.85 | 31.62 | 34.28
|  | 12 |  | 9.38 | ER | ER | 56.48 | 31.25 | 43.59
|  | 13 | 23.07% | 10.89 | 3.57 | 7.21 | 59.43 | 38.09 | 46.22
|  | 14 | 22.83% | 9.7 | 4.24 | 7.21 | 55.15 | 36.76 | 44.44
|  | 15 | 22.92% | 8.85 | 4.07 | 7.27 | 54.32 | 29.48 | 44.25
|  | 16 | 23.25% | 8.85 | 4.21 | 7.29 | 53.8 | 28.02 | 43.88
|  | 17 | 22.89% | 9.59 | 3.97 | 7.17 | 54.74 | 37.14 | 45.68
|  | 18 | 22.81% | 10.29 | 4.35 | 7.31 | 57.68 | 37.14 | 46.66
|  | 19 | 22.79% | 10.48 | 4.34 | 7.55 | 58.75 | 38.08 | 47.13
|  | 20 | 22.84% | 10.42 | 4.33 | 7.42 | 57.09 | 36.32 | 47.18
|  | 21 | 22.96% | 10.58 | 4.33 | 7.38 | 58.36 | 37.65 | 46.72
|  | 22 | 22.65% | 11.94 | 4.38 | 7.39 | 64.72 | 35.04 | 46.4
|  | 23 | 23.04% | 11.24 | 3.96 | 7.49 | 59.72 | 33.42 | 45.17
|  | 24 | 22.67% | 10.49 | 4.46 | 7.34 | 59.53 | 14.69 | 42.91
|  | 25 | 22.56% | 10.15 | 4.42 | 7.28 | 54.8 | 24.49 | 43.26
|  | 26 | 22.75% | 9.74 | 4.39 | 7.43 | 57.61 | 26.03 | 43.47
|  | 27 | 22.62% | 13.5 | ER | 7.34 | 64.92 | 26.48 | 43.74
|  | 28 | 22.8% | 10.63 | 4.14 | 7.19 | 53.48 | 24.82 | 42.6
|  | 29 | 22.81% | 10.69 | 3.57 | 7.14 | 55.43 | 25.55 | 42.92
|  | 30 | 21.27% | 11.01 | 4.12 | 6.85 | 56.08 | 0.98 | 43.78
|  | 31 | 2.639% | 7.67 | ER | 0.98 | 47.08 | 33.83 | 35.7
|  | TOTAL | 642.1% | 310.05 | 108.5 | 203.67 | 1726.84 | 1007.83 | 1379.14
|  | AVERAGE | 22.14% | 10.0016 | 4.0185 | 7.0231 | 55.7045 | 32.5106 | 44.4884
|  | MAXIMUM | 23.33% | 13.5 | 4.46 | 7.55 | 64.92 | 39.13 | 47.18
|  | MINIMUM | 2.639% | 6.97 | 3.3 | 0.98 | 45.85 | 0.98 | 34.28
PAGE 17
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
INJECTION WELL SUMMARY
RUN DATE
2026-07-30
| JANUARY | INFLUENT | EFFLUENT | EFFLUENT | IW-1 | IW-2 | IW-3 | IW-4 | IW-5 | TOTAL
| 2004 | FLOW | FLOW | SS | LBS SS | LBS SS | LBS SS | LBS SS | LBS SS | LBS SS
|  | MGD | MGD
| 1 | 31.093 | 30.421 | 11 | 740.3418 | 741.2592 | 646.767 | 11.9262 | 660.528 | 2788.896
| 2 | 31.813 | 30.567 | 22 | 1482.5184 | 1484.3532 | 1291.6992 | 23.8524 | 1319.2212 | 5577.792
| 3 | 31.481 | 30.253 | 16 | 1070.1888 | 1072.8576 | 931.4112 | 18.6816 | 954.096 | 4028.5536
| 4 | 31.009 | 29.905 | 23 | 1555.6602 | 1553.742 | 1229.5662 | 26.8548 | 1386.8586 | 5725.827
| 5 | 31.168 | 30.318 | 18 | 1203.9624 | 1202.4612 | 1050.84 | 19.5156 | 1073.358 | 4530.6216
| 6 | 30.687 | 29.761 | 13 | 855.4338 | 854.3496 | 743.7612 | 15.1788 | 762.1926 | 3215.7372
| 7 | 30.514 | 29.703 | 10 | 658.86 | 657.192 | 570.456 | 10.008 | 585.468 | 2471.976
| 8 | 30.866 | 30.111 | 17 | 1132.8222 | 1131.4044 | 985.371 | 18.4314 | 1006.638 | 4256.2356
| 9 | 31.036 | 30.739 | 15 | 1020.816 | 1019.565 | 889.461 | 16.263 | 905.724 | 3835.566
| 10 | 31.043 | 30.11 | 19 | 1266.0954 | 1266.0954 | 1102.8816 | 19.0152 | 1128.2352 | 4763.3076
| 11 | 30.52 | 29.885 | 18 | 1520.7156 | 1537.2288 | 1358.586 | 18.0144
| 12 | 31.341 | 30.507 | 17 | 1205.13 | 1217.8902 | 1066.1856 | 18.4314
| 13 | 31.249 | 30.371 | 19 | 1278.7722 | 1281.9414 | 1113.9738 | 20.5998 | 1142.4966 | 4817.184
| 14 | 31.577 | 30.65 | 30 | 2031.624 | 2034.126 | 1781.424 | 30.024 | 1803.942 | 7651.116
| 15 | 31.714 | 31.007 | 13 | 889.044 | 892.2966 | 778.4556 | 13.0104 | 788.2134 | 3348.0096
| 16 | 31.357 | 31.043 | 18 | 1232.4852 | 1239.9912 | 1080.864 | 19.5156 | 1094.3748 | 4647.7152
| 17 | 31.323 | 30.444 | 14 | 939.918 | 943.4208 | 823.158 | 14.0112 | 837.1692 | 3543.666
| 18 | 32.044 | 31.022 | 13 | 890.1282 | 895.5492 | 778.4556 | 14.0946 | 792.5502 | 3356.6832
| 19 | 33.128 | 32.144 | 24 | 1703.3616 | 1713.3696 | 1491.192 | 26.0208 | 1511.208 | 6419.1312
| 20 | 32.485 | 31.526 | 20 | 1389.444 | 1399.452 | 1217.64 | 21.684 | 1237.656 | 5244.192
| 21 | 32.144 | 31.36 | 18 | 1244.4948 | 1252.0008 | 1089.8712 | 18.0144 | 1107.8856 | 4694.2524
| 22 | 32.621 | 31.418 | 26 | 1801.9404 | 1812.7824 | 1576.4268 | 28.1892 | 1602.4476 | 6793.5972
| 23 | 32.502 | 31.86 | 21 | 1474.6788 | 1486.9386 | 1294.2846 | 21.0168 | 1311.7986 | 5567.7006
| 24 | 32.38 | 31.2 | 18 | 1236.9888 | 1245.996 | 1083.8664 | 18.0144 | 1101.8808 | 4668.732
| 25 | 32.273 | 30.931 | 20 | 1364.424 | 1372.764 | 1192.62 | 20.016 | 1214.304 | 5144.112
| 26 | 32.662 | 31.544 | 18 | 1250.4996 | 1261.008 | 1097.3772 | 19.5156 | 1115.3916 | 4724.2764
| 27 | 32.446 | 31.725 | 21 | 1346.8266 | 1488.69 | 1278.522 | 168.1344 | 1285.5276 | 5399.5662
| 28 | 31.538 | 30.632 | 26 | 1749.8988 | 1708.6992 | 1530.8904 | 101.9148 | 1559.0796 | 6548.568
| 29 | 31.301 | 30.217 | 16 | 1064.8512 | 1071.5232 | 934.08 | 16.0128 | 952.7616 | 4023.216
| 30 | 32.201 | 31.777 | 14 | 911.8956 | 915.3984 | 788.13 |  | 799.806 | 3415.23
| 31 | 37.134 | 35.426 | 20 | 1956.564 | 1994.928 | 1756.404 | 20.016 | 163.464 | 5871.36
| TOTAL | 986.65 | 958.577 | 568 | 39470.3844 | 39749.274 | 34554.6216 | 805.9776 | 31204.2768 | 137072.8206
| AVERAGE | 31.8274 | 30.9218 | 18.3226 | 1273.2382 | 1282.2346 | 1114.6652 | 26.8659 | 1076.0095 | 4726.649
PAGE 18
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
| RUN DATE |  |  |  | SOLIDS REMOVAL INVENTORY DATA SHEET
2026-07-30
| JANUARY | TONS | CAKE |  |  |  | JANUARY | RAGS | GRIT | OTHER
| 2004 | SLUDGE | TSS |  |  |  | 2004 |  |  | (vac)
| 1st - 7th | [5 empty] | 1st - 7th
| 1 | 0 |  |  |  |  | 1
| 2 | 25 |  |  |  |  | 2
| 3 | 0 |  |  |  |  | 3
| 4 | 25 | 17.44 |  |  |  | 4
| 5 | 150 | 17.73 |  |  |  | 5 | 10 | 10
| 6 | 150 | 17.86 |  |  |  | 6
| 7 | 150 | 18.36 |  |  |  | 7
| TOTAL = | 500 | 17.8475 | = AVG. |  |  | TOTAL = | 10 | 10 | 0
| 8th - 14th | [5 empty] | 8th - 14th
| 8 | 150 | 17.68 |  |  |  | 8 |  |  | 4500
| 9 | 100 |  |  |  |  | 9 | 10
| 10 | 0 |  |  |  |  | 10
| 11 | 25 | 17.58 |  |  |  | 11
| 12 | 150 | 18.53 |  |  |  | 12 |  | 10
| 13 | 50 |  |  |  |  | 13
| 14 | 125 | 17.11 |  |  |  | 14
| TOTAL = | 600 | 17.725 | = AVG. |  |  | TOTAL = | 10 | 10 | 4500
| 15th - 22nd | [5 empty] | 15th-22nd
| 15 | 150 | 17.3 |  |  |  | 15 | 10
| 16 | 125 |  |  |  |  | 16
| 17 | 0 |  |  |  |  | 17
| 18 | 25 | 17.64 |  |  |  | 18
| 19 | 100 | 17.54 |  |  |  | 19
| 20 | 150 | 17.7 |  |  |  | 20
| 21 | 150 | 17.78 |  |  |  | 21 |  | 10
| 22 | 100 | 17.55 |  |  |  | 22 | 10
| TOTAL = | 800 | 17.585 | = AVG. |  |  | TOTAL = | 20 | 10 | 0
| 23rd - 31st | [5 empty] | 23rd-31st
| 23 | 125 |  |  |  |  | 23
| 24 | 0 |  |  |  |  | 24
| 25 | 25 | 17.3 |  |  |  | 25
| 26 | 175 | 17.81 |  |  |  | 26
| 27 | 150 | 18.04 |  |  |  | 27
| 28 | 125 | 17.52 |  |  |  | 28 |  | 10
| 29 | 125 | 17.58 |  |  |  | 29 | 10
| 30 | 125 |  |  |  |  | 30 |  |  | 4500
| 31 | 0 |  |  |  |  | 31
| TOTAL = | 850 | 17.65 | = AVG. |  |  | TOTAL = | 10 | 10 | 4500
RAGS & GRIT go to Central LandFill
Other(VAC) go to BCSR
PAGE 19

## INJECTION PAGES
|  |  |  | UNDERGROUND INJECTION CONTROL | [10 empty] | UNDERGROUND INJECTION CONTROL | [10 empty] | UNDERGROUND INJECTION CONTROL
[15 empty] | MONTHLY OPERATING REPORT | [10 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES |  |  |  |  | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES |  |  |  |  | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [10 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [10 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-1 | [7 empty] | Wet Well Description: |  |  | Effuent Wet Well for IW-1, IW-2, IW3, IW-4 and IW-5 | [7 empty] | Monitoring Well Decription: |  |  | UPPER ZONE OF MONITORING WELL MW-1
Permit #: |  | 0054569-142-UO |  |  |  |  | Date of Issuance: |  | 2004-01-07 |  | Facility ID #: |  | 5006M02066 |  |  |  | Permit Number: |  |  | FLA041378 |  | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | 0054569-142-UO
[22 empty] | Monitoring Well ID #: |  |  | 5006A11311
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2009-01-06 | [7 empty] | Issue Date: |  |  | 1999-10-18 |  | As Identified in Permit: |  | Monitor Well MW-1 Upper Monitor Zone |  |  |  | Issue Date: |  |  | 2004-01-07
[22 empty] | Monitoring Well Interval: |  |  | 1288' to 1320'
Injection Well ID #: |  | 5006A11308 | [8 empty] | Wet Well ID #: |  | Well Facility U-001 |  |  |  | Expiration Date: |  |  | 2004-10-17 |  | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.7 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24 | Associated Injection Well(s):
Injection Interval: |  |  | 2799' to 3513' | [18 empty] | 500A11311 |  |  | INJECTION WELL IW-5
[11 empty] | Injection Well ID #: |  |  | Injection Well Description
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s): | [10 empty] | 5006A11308 |  |  | INJECTION WELL IW-1
[11 empty] | 5006A11309 |  |  | INJECTION WELL IW-2 | [7 empty] | REPORT MONTH / YEAR: |  | 2004-01-01 | DATE OF SAP / RECORDING: |  |  | 2004-01-06 | 2004-01-13 | 2004-01-20 | 2004-01-27
Monitoring Zone ID #: | [5 empty] | Description |  |  |  |  | 5006A11310 |  |  | INJECTION WELL IW-3
[11 empty] | N/A |  |  | INJECTION WELL IW-4 | [7 empty] | OPERATOR'S NAME: |  |  | BAYLER, J.
UO-06-279401 |  | UPPER ZONE OF MONITORING WELL MW-2 | [8 empty] | 5006A11311 |  |  | INJECTION WELL IW-5
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A
UO-06-279401 |  | LOWER ZONE OF MONITORING WELL MW-2
[11 empty] | THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [10 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [10 empty] | REPORT MONTH / YEAR: |  | 2004-01-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous |  |  | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2004-01-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous |  |  | OPERATOR'S NAME: |  |  | BAYLER, J.
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
OPERATOR'S NAME: |  |  | BAYLER, J. | [7 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A | [7 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4474-A | [7 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: |  |  |  | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 48.58 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 44.91 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: |  |  |  | PARAMETER |  |  |  | Sampling Frequency |  |  |  | VALUE |  | UNITS | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 47.9397 | PSIG
[11 empty] | Nitrogen, Total as N |  |  |  |  | Daily/Monthly Average |  |  | 16.9904 |  | mg/L as N | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[11 empty] | Nitrogen, Nitrate, Total as N |  |  |  |  | Daily/Monthly Average |  |  | 0.19996 |  | mg/L as N | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7220.5 | mg/l
Total monthly flow | [7 empty] | 257.61 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 3987.5 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [7 empty] | Nitrogen, Total Kjeildahl as N |  |  |  |  | Daily/Monthly Average |  |  | 16.7904 |  | mg/L as N | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.91975 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 15.71 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.4275 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 71.4 |  | PSIG | pH |  |  |  |  | Daily/Monthly Average |  |  | 6.4871 |  | s.u. | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 8.0525 | Std units
Monthly average of the daily flow rates | [7 empty] | 8.31 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 12732.5 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 11.2845 |  | MG | Phosphorus, Total as P |  |  |  |  | Daily/Monthly Average |  |  | 1.4662 |  | mg/L as P | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 1.802 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 73 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [10 empty] | Total Dissolved Solids (TDS) |  |  |  |  | Daily/Monthly Average |  |  | 1336.4194 |  | mg/L | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.05 | mg/l
Monthly average pressure | [7 empty] | 46.7113 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 850 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 34.92 |  | PSIG | Residue, Total filterable (TSS dried at 180 C) |  |  |  |  | Daily/Monthly Average |  |  | 18.3226 |  | mg/L | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 192.5 | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.78 | mg/l
[11 empty] | Specific Conductance (Temperature Compensated) |  |  |  |  | Daily/Monthly Average |  |  | 2996.4516 |  | umhos/cm | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just | [6 empty] | Temperature, Water |  |  |  |  | Daily/Monthly Average |  |  | 79.1548 |  | deg C
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [9 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just |  |  | Date: |  |  |  |  | (Signature):
Date:
(Signature):
|  |  |  | UNDERGROUND INJECTION CONTROL | [21 empty] | UNDERGROUND INJECTION CONTROL
|  |  |  | MONTHLY OPERATING REPORT | [21 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES | [15 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [21 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-2 | [18 empty] | Monitoring Well Decription: |  |  | LOWER ZONE OF MONITORING WELL MW-1
Permit #: |  | 0054569-142-UO |  |  |  |  | Date of Issuance: |  | 2004-01-07 | [12 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | 0054569-142-UO
[22 empty] | Monitoring Well ID #: |  |  | 5006A11311
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2009-01-06 | [12 empty] | As Identified in Permit: |  | Monitor Well MW-1 Lower Monitor Zone |  |  |  | Issue Date: |  |  | 2004-01-07
[22 empty] | Monitoring Well Interval: |  |  | 1449' to 1557'
Injection Well ID #: |  | 5006A11309 | [19 empty] | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.7 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24
Injection Interval: |  |  | 2798' to 3518' | [18 empty] | 500A11311 |  |  | INJECTION WELL IW-5
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s):
[22 empty] | REPORT MONTH / YEAR: |  | 2004-01-01 | DATE OF SAP / RECORDING: |  |  | 2004-01-06 | 2004-01-13 | 2004-01-20 | 2004-01-27
Monitoring Zone ID #: | [5 empty] | Description
[22 empty] | OPERATOR'S NAME: |  |  | BAYLER, J.
UO-06-279401 |  | UPPER ZONE OF MONITORING WELL MW-2
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A
UO-06-279401 |  | LOWER ZONE OF MONITORING WELL MW-2
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [21 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2004-01-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
OPERATOR'S NAME: |  |  | BAYLER, J. | [18 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4474-A | [18 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 42.2 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 27.85 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: | [14 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 40.9939 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 9292.5 | mg/l
Total monthly flow | [7 empty] | 259.36 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 5325 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [18 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 9.58 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 16.15 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 10.5725 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 69.99 |  | PSIG | [11 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7.345 | Std units
Monthly average of the daily flow rates | [7 empty] | 8.3665 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 16572.5 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 11.3588 |  | MG | [11 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 1.802 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 72.5 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [21 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.05 | mg/l
Monthly average pressure | [7 empty] | 45.8448 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 787.5 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 35.92 |  | PSIG | [11 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 282.5 | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.0225 | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [21 empty] | (Signature):
Date:
|  |  |  | UNDERGROUND INJECTION CONTROL | [21 empty] | UNDERGROUND INJECTION CONTROL
|  |  |  | MONTHLY OPERATING REPORT | [21 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES | [15 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [21 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-3 | [18 empty] | Monitoring Well Decription: |  |  | UPPER ZONE OF MONITORING WELL MW-2
Permit #: |  | 0054569-142-UO |  |  |  |  | Date of Issuance: |  | 2004-01-07 | [12 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | 0054569-142-UO
[22 empty] | Monitoring Well ID #: |  |  | 5006A11308 & 309
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2009-01-06 | [12 empty] | As Identified in Permit: |  | Monitor Well MW-2 Upper Monitor Zone |  |  |  | Issue Date: |  |  | 2004-01-07
[22 empty] | Monitoring Well Interval: |  |  | 1300' to 1344'
Injection Well ID #: |  | 5006A11310 | [19 empty] | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.7 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24
Injection Interval: |  |  | 2800' to 3977' | [18 empty] | 5006A11308 |  |  | INJECTION WELL IW-1
[22 empty] | 5006A11309 |  |  | INJECTION WELL IW-2
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s):
[22 empty] | REPORT MONTH / YEAR: |  | 2004-01-01 | DATE OF SAP / RECORDING: |  |  | 2004-01-06 | 2004-01-13 | 2004-01-20 | 2004-01-27
Monitoring Zone ID #: | [5 empty] | Description
[22 empty] | OPERATOR'S NAME: |  |  | BAYLER, J.
UO-06-279510 |  | UPPER ZONE OF MONITORING WELL MW-3
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A
UO-06-279510 |  | LOWER ZONE OF MONITORING WELL MW-3
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [21 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2004-01-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
OPERATOR'S NAME: |  |  | BAYLER, J. | [18 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4474-A | [18 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 31.26 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 23.86 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: | [14 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 28.5761 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7073 | mg/l
Total monthly flow | [7 empty] | 225.52 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 3875 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [18 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.706 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 14.21 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.5225 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 72 |  | PSIG | [11 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7.875 | Std units
Monthly average of the daily flow rates | [7 empty] | 7.2748 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 12392.5 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 9.8759 |  | MG | [11 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 1.802 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 71.5 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [21 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.05 | mg/l
Monthly average pressure | [7 empty] | 46.9306 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 787.5 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 35.82 |  | PSIG | [11 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 180 | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 4.1875 | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [21 empty] | (Signature):
Date:
|  |  |  | UNDERGROUND INJECTION CONTROL | [21 empty] | UNDERGROUND INJECTION CONTROL
|  |  |  | MONTHLY OPERATING REPORT | [21 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES | [15 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [21 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-4 | [18 empty] | Monitoring Well Decription: |  |  | LOWER ZONE OF MONITORING WELL MW-2
Permit #: |  | 0054569-142-UO |  |  |  |  | Date of Issuance: |  | 2004-01-07 | [12 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | 0054569-142-UO
[22 empty] | Monitoring Well ID #: |  |  | 5006A11308 & 309
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2009-01-06 | [12 empty] | As Identified in Permit: |  | Monitor Well MW-2 Lower Monitor Zone |  |  |  | Issue Date: |  |  | 2004-01-07
[22 empty] | Monitoring Well Interval: |  |  | 1970' to 2025'
Injection Well ID #: |  | N/A | [19 empty] | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.7 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24
Injection Interval: |  |  | 2804' to 3977' | [18 empty] | 5006A11308 |  |  | INJECTION WELL IW-1
[22 empty] | 5006A11309 |  |  | INJECTION WELL IW-2
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s):
[22 empty] | REPORT MONTH / YEAR: |  | 2004-01-01 | DATE OF SAP / RECORDING: |  |  | 2004-01-06 | 2004-01-13 | 2004-01-20 | 2004-01-27
Monitoring Zone ID #: | [5 empty] | Description
[22 empty] | OPERATOR'S NAME: |  |  | BAYLER, J.
UO-06-279510 |  | UPPER ZONE OF MONITORING WELL MW-3
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A
UO-06-279510 |  | LOWER ZONE OF MONITORING WELL MW-3
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [21 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2004-01-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
OPERATOR'S NAME: |  |  | BAYLER, J. | [18 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4474-A | [18 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 42.52 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 31.08 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: | [14 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 41.0913 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 30823.25 | mg/l
Total monthly flow | [7 empty] | 4.98 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 18050 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [18 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.4975 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 19.56 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.93 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 60.48 |  | PSIG | [11 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7.39 | Std units
Monthly average of the daily flow rates | [7 empty] | 0.166 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 49475 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 0.22534 |  | MG | [11 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 1.802 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 70 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [21 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.05 | mg/l
Monthly average pressure | [7 empty] | 34.8281 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 2625 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 36.49 |  | PSIG | [11 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 865 | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.0575 | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [21 empty] | (Signature):
Date:
|  |  |  | UNDERGROUND INJECTION CONTROL | [21 empty] | UNDERGROUND INJECTION CONTROL
|  |  |  | MONTHLY OPERATING REPORT | [21 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES | [15 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [21 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-5 | [18 empty] | Monitoring Well Decription: |  |  | UPPER ZONE OF MONITORING WELL MW-3
Permit #: |  | 0054569-142-UO |  |  |  |  | Date of Issuance: |  | 2004-01-07 | [12 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | 0054569-142-UO
[22 empty] | Monitoring Well ID #: |  |  | 5006A11310
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2009-01-06 | [12 empty] | As Identified in Permit: |  | Monitor Well MW-3 Upper Monitor Zone |  |  |  | Issue Date: |  |  | 2004-01-07
[22 empty] | Monitoring Well Interval: |  |  | 1300' to 1349'
Injection Well ID #: |  | 5006A11311 | [19 empty] | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.7 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24
Injection Interval: |  |  | 2818' to 3462' | [18 empty] | 5006A11310 |  |  | INJECTION WELL IW-3
[22 empty] | N/A |  |  | INJECTION WELL IW-4
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s):
[22 empty] | REPORT MONTH / YEAR: |  | 2004-01-01 | DATE OF SAP / RECORDING: |  |  | 2004-01-06 | 2004-01-13 | 2004-01-20 | 2004-01-27
Monitoring Zone ID #: | [5 empty] | Description
[22 empty] | OPERATOR'S NAME: |  |  | BAYLER, J.
UO-06-279512 |  | UPPER ZONE OF MONITORING WELL MW-1
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A
UO-06-279512 |  | LOWER ZONE OF MONITORING WELL MW-1
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [21 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2004-01-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
OPERATOR'S NAME: |  |  | BAYLER, J. | [18 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4474-A | [18 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 31.59 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 16.98 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: | [14 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 29.6197 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7162.5 | mg/l
Total monthly flow | [7 empty] | 203.67 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 3950 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [18 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.99 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 13.5 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.6 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 64.92 |  | PSIG | [11 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 8.2125 | Std units
Monthly average of the daily flow rates | [7 empty] | 7.0231 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 12635 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 9.5756 |  | MG | [11 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 1.802 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 70 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [21 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.05 | mg/l
Monthly average pressure | [7 empty] | 44.4884 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 875 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 35.56 |  | PSIG | [11 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 182.5 | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.96 | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [21 empty] | (Signature):
Date:
UNDERGROUND INJECTION CONTROL
MONTHLY OPERATING REPORT
[22 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
[22 empty] | Monitoring Well Decription: |  |  | LOWER ZONE OF MONITORING WELL MW-3
[22 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | 0054569-142-UO
[22 empty] | Monitoring Well ID #: |  |  | 5006A11310
[22 empty] | As Identified in Permit: |  | Monitor Well MW-3 Lower Monitor Zone |  |  |  | Issue Date: |  |  | 2004-01-07
[22 empty] | Monitoring Well Interval: |  |  | 1970 to 2027'
Associated Injection Well(s):
[22 empty] | Injection Well ID #: |  |  | Injection Well Description
[22 empty] | 5006A11310 |  |  | INJECTION WELL IW-3
[22 empty] | N/A |  |  | INJECTION WELL IW-4
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
[22 empty] | REPORT MONTH / YEAR: |  | 2004-01-01 | DATE OF SAP / RECORDING: |  |  | 2004-01-06 | 2004-01-13 | 2004-01-20 | 2004-01-27
[22 empty] | OPERATOR'S NAME: |  |  | BAYLER, J.
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
[22 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
[22 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
[22 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 45.65 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 36.6 | PSIG
[22 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 44.4261 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
[22 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 28205.5 | mg/l
[22 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 17050 | mg/l
[22 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 2.4275 | mg/l
[22 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 2.2853 | mg/l
[22 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7.4 | Std units
[22 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 45875 | umho/cm
[22 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
[22 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 69 | deg. F
[22 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.05 | mg/l
[22 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 2325 | mg/l
[22 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 825 | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.0525 | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
Date:

## DEP FORMS
Department of Environmental Protection Discharge Monitoring Report - Part A
When Completed mail this report to: Department of Environmental Protection, Wastewater Facilities Management Section, MS 3551, 2600 Blair Stone Road, Tallahassee, FL 32399-2400
PERMITEE NAME: | City of Fort Lauderdale |  |  |  |  | PERMIT NUMBER: |  | FLA041378 |  | REPORT: | Monthly
MAILING ADDRESS: | 949 NW 38th Street |  |  |  |  | LIMIT: |  | Final |  | GROUP: | Domestic
| Fort Lauderdale, FL 33309 |  |  |  |  | CLASS SIZE: |  | N/A |  | GMS TEST SITE
[6 empty] | GMS ID NO. |  | 5006M02066 |  | NO:
FACILITY: | City of Fort Lauderdale G. T. Lohmeyer WWTF |  |  |  |  | MONITORING GROUP NUMBER: |  | U-001
LOCATION: | 1765 SE 18th Street |  |  |  |  | PLANT SIZE/TREATMENT TYPE: |  | IIA
Fort Lauderdale, FL 33316
COUNTY: | Broward | [5 empty] | MONITORING PERIOD: |  |  | 2004-01-01
Parameter |  | Quantity of Loading |  | Units |  | Quality or Concentration |  | Units | No. Ex. | Frequency of Analysis | Sample Type
Flow | Sample Measurement | 11.2845 | 8.31 | [5 empty] | 0
PARM Code 50050 1 Mon.Site No. EFF-002 | Permit Requirement | 18.3 (Peak Hour.) | Report (Mo. Avg.) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
Flow | Sample Measurement | 11.3588 | 8.3665 | [5 empty] | 0
PARM Code 50050 1 Mon.Site No. EFF-003 | Permit Requirement | 18.3 (Peak Hour.) | Report (Mo. Avg.) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
Flow | Sample Measurement | 9.8759 | 7.2748 | [5 empty] | 0
PARM Code 50050 1 Mon.Site No. EFF-004 | Permit Requirement | 18.3 (Peak Hour.) | Report (Mo. Avg.) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
Flow | Sample Measurement | 0.22534 | 0.166 | [5 empty] | 0
PARM Code 50050 1 Mon.Site No. EFF-005 | Permit Requirement | 18.0 (Peak Hour.) | Report (Mo. Avg.) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
Flow | Sample Measurement | 9.5756 | 7.0231 | [5 empty] | 0
PARM Code 50050 1 Mon.Site No. EFF-006 | Permit Requirement | 18.3 (Peak Hour.) | Report (Mo. Avg.) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
I certify under penalty of law that I have personally examined and am familiar with the informantion submitted herein; and based on my inquiry of those individuals immeadiately responsible for obtaining the information, I believe the submitted
information is true, accurate and complete. I am aware that there are significant penalties for submitting false information including the possiblity of fine and imprisonment.
NAME/TITLE OF PRINCIPAL EXECUTIVE OFFICER OR AUTHORIZED AGENT |  |  |  | SIGNATURE OF PRINCIPAL EXECUTIVE OFFICER OR AUTHORIZED AGENT |  |  |  |  | TELEPHONE |  | DATE (YY/MM/DD)
954-523-1002 ext 2021
REGIONAL WASTEWATER FACILITIES MANAGER
COMMENTS AND EXPLANATION OF ANY VIOLATIONS (Reference all attachments here):
Version 8/13/99
Department of Environmental Protection Discharge Monitoring Report - Part A (Continued)
[12 empty] | PERMITEE NAME: | City of Fort Lauderdale G. T. Lohmeyer WWTF |  |  |  | PERMIT NUMBER: |  | FLA041378 | MONITORING GROUP NUMBER: U-001 |  |  | REPORT: | Monthly
[20 empty] | MONITORING PERIOD: |  |  |  | 2004-01-01
[12 empty] | Parameter |  |  | Quantity of Loading |  | Units |  | Quality or Concentration |  | Units | No. Ex. | Frequency of Analysis | Sample Type
[12 empty] | BOD, Carbonaceous 5 day, 20C |  | Sample Measurement |  |  |  | 4.4 |  |  |  | 0
[12 empty] | PARM Code 80082 Y Mon.Site No. EFF-001 |  | Permit Requirement |  |  |  | 20.0 (An.Avg.) |  |  | mg/l |  | Daily | 24-hour FPC
[12 empty] | BOD, Carbonaceous 5 day, 20C |  | Sample Measurement |  |  |  | 4.2042 | 3.8713 | 8 |  | 0
[12 empty] | PARM Code 80082 1 Mon.Site No. EFF-001 |  | Permit Requirement |  |  |  | 30.0 (Mo.Avg.) | 45.0 (Week.Avg.) | 60.0 (Max.) | mg/l |  | Daily | 24-hour FPC
[12 empty] | Solids, Total Suspended |  | Sample Measurement |  |  |  | 14.3 |  |  |  | 0
[12 empty] | PARM Code 00530 Y Mon.Site No. EFF-001 |  | Permit Requirement |  |  |  | 20.0 (An.Avg.) |  |  | mg/l |  | Daily | 24-hour FPC
[12 empty] | Solids, Total Suspended |  | Sample Measurement |  |  |  | 18.3226 | 18.4343 | 30 |  | 0
[12 empty] | PARM Code 00530 1 Mon.Site No. EFF-001 |  | Permit Requirement |  |  |  | 30.0 (Mo.Avg.) | 45.0 (Week.Avg.) | 60.0 (Max.) | mg/l |  | Daily | 24-hour FPC
[12 empty] | pH |  | Sample Measurement |  |  |  | 6.3 |  |  |  | 0
[12 empty] | PARM Code 00400 1 Mon.Site No. EFF-001 |  | Permit Requirement |  |  |  | 6.0 (Min.) |  |  | s.u. |  | Continuous | Meter
[12 empty] | Flow |  | Sample Measurement | 35.8691 | 31.8274 | [5 empty] | 0
[12 empty] | PARM Code 50050 G Mon.Site No. INF-001 |  | Permit Requirement | 43.0 (3-Mo.Avg.) | Report (Mo.Avg.) | mgd | [5 empty] | Continuous | Flow meters with 24-hour recording chart
[12 empty] | BOD, Carbonaceous 5 day, 20C |  | Sample Measurement |  |  |  | 86.2323 |  |  |  | N/A
[12 empty] | PARM Code 80082 G Mon.Site No. INF-002 |  | Permit Requirement |  |  |  | Report (Mo.Avg.) |  |  | mg/l |  | Daily | 24-hour FPC
[12 empty] | Solids, Total Suspended |  | Sample Measurement |  |  |  | 139.2903 |  |  |  | N/A
[12 empty] | PARM Code 00530 G Mon.Site No. INF-002 |  | Permit Requirement |  |  |  | Report (Mo.Avg.) |  |  | mg/l |  | Daily | 24-hour FPC
Version 8/13/99

## JULIAN CONVERT
2004-01-01 | 37987 | 1999-01-01 | 1826
FROM DATE ON "DATA INPUT" PAGE | [5 empty] | 2004-01-01
1999
MONTHYY.PAR RANGE TO COMPILE (JULIAN DAY VALUES) FOR SPLIT PROGRAM ARE | [7 empty] | 1 | THROUGH | 1858
|  | 1 | JANUARY
[5 empty] | 2004-01-01 | 2004-01-01 | 1
2004-01-01 |  |  |  |  | 1 | JANUARY |  | 1995 | 1995-01-01
[5 empty] | 2 | FEBRUARY |  | 1996 | 1996-01-01
[5 empty] | 3 | MARCH |  | 1997 | 1997-01-01
JANUARY |  | 1 |  | 3 | 4 | APRIL |  | 1998 | 1998-01-01
|  | 0 |  | 0 | 5 | MAY |  | 1999 | 1999-01-01
|  | 0 |  |  | 6 | JUNE |  | 2000 | 2000-01-01
|  | 0 |  |  | 7 | JULY |  | 2001 | 2001-01-01
|  | 0 |  | 0 | 8 | AUGUST |  | 2002 | 2002-01-01
|  |  |  | 3 | 9 | SEPTEMBER |  | 2003 | 2003-01-01
[5 empty] | 10 | OCTOBER |  | 2004 | 2004-01-01
[5 empty] | 11 | NOVEMBER |  | 2005 | 2005-01-01
2004 |  |  |  |  | 12 | DECEMBER |  | 2006 | 2006-01-01
37987 | [6 empty] | JANUARY | 2007 | 2007-01-01
37987 | [7 empty] | 2008 | 2008-01-01
0 | 1 |  | 1 | 1 | Thursday
| 2 |  | 2 | 2 | Friday
| 3 |  | 3 | 3 | Saturday
| 4 |  | 4 | 4 | Sunday
| 5 |  | 5 | 5 | Monday
| 6 |  | 6 | 6 | Tuesday
| 7 |  | 7 | 7 | Wednesday
| 8 |  | 8 | 8 | Thursday
| 9 |  | 9 | 9 | Friday
| 10 |  | 10 | 10 | Saturday
| 11 |  | 11 | 11 | Sunday
| 12 |  | 12 | 12 | Monday
| 13 |  | 13 | 13 | Tuesday
| 14 |  | 14 | 14 | Wednesday
| 15 |  | 15 | 15 | Thursday
| 16 |  | 16 | 16 | Friday
| 17 |  | 17 | 17 | Saturday
| 18 |  | 18 | 18 | Sunday
| 19 |  | 19 | 19 | Monday
| 20 |  | 20 | 20 | Tuesday
| 21 |  | 21 | 21 | Wednesday
| 22 |  | 22 | 22 | Thursday
| 23 |  | 23 | 23 | Friday
| 24 |  | 24 | 24 | Saturday
| 25 |  | 25 | 25 | Sunday
| 26 |  | 26 | 26 | Monday
| 27 |  | 27 | 27 | Tuesday
| 28 |  | 28 | 28 | Wednesday
| 29 |  | 29 | 29 | Thursday
| 30 |  | 30 | 30 | Friday
| 31 |  | 31 | 31 | Saturday
31