## DATA INPUT
ENTER THE AVERAGE MONTHLY INFLUENT FLOW
INTO THE CORROSPONDING BOXES BELOW:
SEPTEMBER | 38.516 | AUGUST | 35.748
ENTER THE PRESENT MONTH AND YEAR IN BOX BELOW (A5) | [5 empty] | OCTOBER
2003-10-01 | [5 empty] | 2003
IW-1 | IW-2 | IW-3 | IW-4 | IW-5
37.5 | 37.8 | 38 | 38.1 | 36.1 | 2003-10-07
|  | ENTER INJECTION WELL SHUT-IN PRESSURE ABOVE |  |  | ENTER DATE OF SHUT-IN READINGS
ENTER SLUDGE DISPOSAL SITE FOR EACH WEEK BELOW
| WEEK 1 | WEEK 2 | WEEK 3 | WEEK 4
1 st | Nutri-Cylcle Inc. | Nutri-Cylcle Inc. | Nutri-Cylcle Inc. | Nutri-Cylcle Inc.
2 nd | Arcadia, FL | Arcadia, FL | Arcadia, FL | Arcadia, FL
RAW DATA REPORT ENTRY CATEGORIES
GTL PLANT DAILY PROCESS SUMMARY
[6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TOTAL RAW INFLUENT FLOW (MGD) | [5 empty] | 50.362 | 48.529 | 48 | 45.967 | 43.104 | 41.423 | 40.251 | 38.943 | 37.949 | 36.261 | 37.945 | 37.11 | 37.113 | 36.736 | 36.813 | 35.282 | 36.075 | 36.448 | 35.154 | 32.326 | 35.791 | 35.704 | 36.372 | 36.447 | 34.966 | 34.525 | 34.384 | 34.13 | 40.309 | 37.184 | 35.3
TOTAL EFFLUENT FLOW (MGD) | [5 empty] | 49.269 | 47.503 | 47.249 | 44.906 | 42.193 | 40.954 | 40.308 | 38.485 | 37.646 | 36.397 | 37.376 | 36.554 | 35.593 | 36.433 | 36.54 | 35.28 | 36.543 | 36.298 | 34.789 | 32.134 | 35.611 | 35.863 | 36.218 | 36.741 | 34.739 | 33.721 | 33.885 | 33.982 | 39.875 | 36.983 | 35.2
MAXIMUM HOURLY RAW INFLUENT FLOW (MGD) | [5 empty] | 2.196 | 2.178 | 2.249 | 2.159 | 2.044 | 1.971 | 1.986 | 1.873 | 1.821 | 1.941 | 1.895 | 1.892 | 1.787 | 1.741 | 1.769 | 1.76 | 1.829 | 1.864 | 1.731 | 1.879 | 1.785 | 1.77 | 1.879 | 1.88 | 1.833 | 1.812 | 1.711 | 1.745 | 1.949 | 1.872 | 1.793
MAXIMUM INSTANANEOUS PEAK RAW INFUENT FLOW (MGD) | [5 empty] | 60.172 | 59.019 | 59.5 | 59.243 | 57.737 | 54.212 | 56.263 | 53.059 | 54.693 | 53.956 | 51.264 | 51.841 | 50.495 | 48.606 | 47.42 | 48.093 | 48.19 | 51.489 | 48.478 | 49.343 | 42.816 | 50.591 | 51.841 | 50.591 | 51.392 | 51.168 | 49.888 | 47.068 | 52.482 | 52.258 | 48.702
MINIMUM INSTANANEOUS PEAK RAW INFUENT FLOW (MGD) | [5 empty] | 36.461 | 32.746 | 0 | 32.329 | 25.504 | 22.011 | 23.197 | 16.661 | 19.095 | 18.518 | 18.55 | 16.724 | 18.454 | 18.614 | 18.55 | 18.903 | 17.845 | 19.191 | 18.743 | 18.775 | 23.328 | 16.405 | 15.251 | 17.14 | 16.117 | 17.461 | 15.892 | 15.604 | 20.217 | 21.37 | 0
TOTAL RETURN ACTIVATED SLUDGE FLOW (MGD) | [5 empty] | 12.877 | 13.206 | 13.75 | 12.752 | 12.09 | 12.488 | 11.797 | 10.947 | 11.681 | 10.94 | 11.524 | 11.439 | 10.311 | 10.285 | 11.212 | 12.091 | 12.209 | 12.052 | 13.096 | 11.035 | 11.737 | 12.425 | 12.99 | 12.741 | 12.2 | 11.597 | 10.793 | 10.581 | 10.91 | 9.634 | 10.155
TOTAL WASTE FLOW TO DEWATERING PROCESS (MG) | [5 empty] | 0.468 | 0.568 | 0.12 | 0 | 0.233 | 0.599 | 0.617 | 0.564 | 0.444 | 0.211 | 0 | 0.28 | 0.645 | 0.623 | 0.659 | 0.626 | 0.257 | 0 | 0.224 | 0.474 | 0.554 | 0.549 | 0.547 | 0.272 | 0 | 0.02 | 0.497 | 0.511 | 0.52 | 0.558 | 0.201
TOTAL DAILY RAINFALL | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0 | 0 | 0.24 | 0.02 | 0 | 0.46 | 0 | 0 | 0 | 0 | 0.06 | 0 | 0 | 0 | 1.37 | 0.06 | 0
RAW INFLUENT pH | [5 empty] | 7.2 | 7.2 | 7.1 | 7 | 7.1 | 7 | 7.1 | 7.1 | 7.1 | 7 | 6.9 | 7 | 7.1 | 7.1 | 7 | 7 | 7 | 6.9 | 7 | 7.1 | 7 | 7.1 | 7.1 | 7 | 7.1 | 7.1 | 7 | 7 | 7 | 7.1 | 7.1
RAW INFLUENT HYDROGEN SULFIDE (PPM) | [5 empty] | 3 | 3 | 4 | 4 | 5 | 5 | 5 | 4 | 5 | 5 | 5 | 6 | 7 | 7 | 7 | 5 | 7 | 6 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 5 | 5 | 6 | 6 | 6 | 6
RAW INFLUENT TEMPERATURE (F ) | [5 empty] | 82 | 82 | 81 | 81 | 81 | 81 | 81 | 81 | 79.8 | ER | 84 | 84 | 84 | 84 | 85 | 83 | 84 | 84 | 83 | ER | 85 | 83 | 84 | 84 | 82 | 81 | 81 | 81 | 81 | 81 | 81
TOTAL DAILY KILOWATTS (FPL POWER CONSUMPTION) | [5 empty] | 19506 | 32333 | 29404 | 30876 | 30696 | 31007 | 30957 | 30821 | 30773 | 30603 | 30523 | 30744 | 30762 | 30825 | 28715 | 30882 | 30740 | 30908 | 30645 | 30688 | 30817 | 30598 | 25154 | 31002 | 31244 | 31356 | 31172 | 31136 | 31136 | 31217 | 31208
GTL PLANT DAILY PROCESS SUMMARY
(CONTINUED)
[6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
FINAL EFFLUENT FREE CHLORINE RESIDUAL (PPM) | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FINAL EFFLUENT TOTAL CHLORINE RESIDUAL (PPM) | [5 empty] | 0.8 | 0.8 | 0.8 | 0.7 | 0.8 | 0.7 | 0.9 | 0.8 | 0.8 | 0.9 | 1.2 | 1.3 | 1 | 0.6 | 0 | 0 | 0.2 | 0.9 | 0.9 | 0.4 | 0.2 | 0.9 | 0.9 | 0.9 | 1 | 1 | 0.6 | 0.9 | 0.6 | 0.7 | 0.6
FINAL EFFLUENT pH (daily average) | [5 empty] | 6.8 | 6.7 | 6.7 | 6.7 | 6.7 | 6.8 | 6.7 | 6.8 | 6.8 | 6.8 | 6.7 | 6.7 | 6.6 | 6.6 | 6.7 | 6.8 | 6.8 | 6.7 | 6.6 | 6.7 | 6.7 | 6.8 | 6.7 | 6.7 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.7 | 6.8
FINAL EFFLUENT pH (daily minimum) | [5 empty] | 6.7 | 6.6 | 6.7 | 6.7 | 6.6 | 6.7 | 6.6 | 6.7 | 6.7 | 6.7 | 6.6 | 6.6 | 6.5 | 6.5 | 6.6 | 6.7 | 6.7 | 6.6 | 6.5 | 6.5 | 6.7 | 6.7 | 6.7 | 6.6 | 6.5 | 6.5 | 6.4 | 6.5 | 6.6 | 6.6 | 6.7
FINAL EFFLUENT pH (daily maximum) | [5 empty] | 6.8 | 6.7 | 6.8 | 6.8 | 6.8 | 6.9 | 6.8 | 6.8 | 6.8 | 6.8 | 6.7 | 6.8 | 6.7 | 6.7 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.7 | 6.7 | 6.7 | 6.8 | 6.6 | 6.6 | 6.8 | 6.8
FINAL EFFLUENT TEMPARTURE (F ) | [5 empty] | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 82 | ER | 87 | 87 | 87 | 88 | 85 | 86 | 87 | 85 | ER | 86 | 86 | 86 | 86 | 84 | 84 | 83.6 | 84 | 83 | 83 | 83
AVERAGE CLARIFIER BLANKET DEPTH (INCHES) | [5 empty] | 18 | 12 | 14 | 20 | 19 | 20 | 20 | 14 | 20 | 17 | 23 | 28 | 23 | 20 | 18 | 13 | 13 | 21 | 20 | 19 | 15 | 14 | 11 | 16 | 15 | 12 | 13 | 13 | 9 | 8 | 9
FINAL EFFLUENT SAMPLE TEMPARTURE (C ) | [5 empty] | 5 | 5 | 5 | 0 | 5 | 4 | 5 | 4 | 4 | 5 | 5 | 4 | 4 | 4 | 4 | 4 | 5 | 5 | 3 | 4 | 3 | 4 | 4 | 5 | 5 | 3 | 4 | 5 | 4 | 5 | 6
TOTAL RETURN ACTIVATED SLUDGE FLOW TO REACTOR ONE (MGD) | [5 empty] | 5.697 | 6.015 | 5.825 | 5.173 | 5.095 | 5.021 | 5.208 | 4.368 | 4.145 | 3.746 | 3.466 | 3.656 | 3.754 | 3.812 | 4.556 | 5.418 | 4.898 | 4.869 | 5.593 | 5.011 | 5.045 | 5.546 | 5.321 | 4.753 | 4.383 | 4.2 | 4.071 | 3.835 | 4.475 | 4.043 | 3.583
TOTAL RETURN ACTIVATED SLUDGE FLOW TO REACTOR TWO (MGD) | [5 empty] | 7.181 | 7.19 | 7.925 | 7.579 | 6.995 | 7.468 | 6.589 | 6.579 | 7.536 | 7.194 | 8.058 | 7.782 | 6.557 | 6.473 | 6.656 | 6.674 | 7.31 | 7.183 | 7.503 | 6.024 | 6.692 | 6.879 | 7.669 | 7.988 | 7.817 | 7.397 | 6.721 | 6.746 | 6.44 | 5.591 | 6.568
GTL PLANT DAILY PROCESS SUMMARY
CONTINUED
[6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TOTAL DAILY TRUCKING LOAD OF DEWATERED SLUDGE REMOVED | [5 empty] | 4 | 6 | 3 | 0 | 1 | 6 | 6 | 5 | 4 | 2 | 0 | 1 | 5 | 5 | 6 | 6 | 4 | 0 | 1 | 6 | 6 | 6 | 6 | 4 | 0 | 0 | 5 | 6 | 6 | 6 | 3
TOTAL DAILY HYDROGEN PEROXIDE CONSUMED (LBS) | [5 empty] | 1896 | 2076 | 1577 | 4515 | 1497 | 1647 | 1687 | 1377 | 1308 | 1088 | 1328 | 977 | 1357 | 1107 | 1676 | 958 | 1597 | 2637 | 1436 | 1477 | 1068 | 2016 | 1437 | 1008 | 1327 | 949 | 1288 | 818 | 2117 | 1077 | 1835
TOTAL DAILY CHLORINE CONSUMED (LBS) | [5 empty] | 1000 | 900 | 960 | 1080 | 1080 | 1000 | 1080 | 1100 | 1000 | 1260 | 1440 | 1440 | 1400 | 560 | 0 | 220 | 620 | 1240 | 1400 | 420 | 560 | 1100 | 1100 | 1520 | 1320 | 1160 | 1060 | 1060 | 1280 | 1120 | 1120
TOTAL DAILY POLYMER CONSUMED (GALS) | [5 empty] | 17 | 60 | 4 | 9 | 17 | 68 | 60 | 68 | 34 | 34 | 2 | 24 | 57 | 75 | 75 | 55 | 0 | 19 | 47 | 83 | 62 | 66 | 47 | 0 | 0 | 47 | 0 | 81 | 44 | 17 | 20
TOTAL TONS OF LIME DELIVERED DAILY | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTAL DAILY GASIOUS OXYGEN PRODUCED (TONS) | [5 empty] | 28.2 | 22.8 | 25.7 | 26.8 | 28.2 | 26.6 | 27.1 | 26.9 | 30 | 34.7 | 37.9 | 32.6 | 28.8 | 26.1 | 32.3 | 33.2 | 41.5 | 40 | 23.3 | 21.3 | 25 | 22.2 | 16 | 11 | 12 | 11 | 11 | 14.5 | 18.9 | 16.5 | 20.9
AVERAGE PERCENT OXYGEN PRODUCT PURITY | [5 empty] | 100 | 100 | 100 | 100 | 99 | 100 | 100 | 100 | 97 | 99 | 95 | 100 | 99 | 100 | 99 | 99 | 96 | 100 | 100 | 100 | 100 | 99 | 100 | 100 | 100 | 100 | 100 | 100 | 99 | 99 | 99
TOTAL DAILY LIQUID OXYGEN IN STORAGE (TONS) | [5 empty] | 101 | 101 | 101 | 101 | 101 | 102 | 104 | 106 | 106 | 107 | 107 | 106 | 107 | 108 | 108 | 109 | 109 | 108 | 108 | 109 | 110 | 111 | 111 | 113 | 113 | 112 | 113 | 114 | 114 | 115 | 116
MONITORING WELL PRESSURE DATA
MONITORING WELL ONE UPPER/LOWER LEVEL
| MW-1 |  | UPPER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MINIMUM | [5 empty] | 48.68 | 48.85 | 48.87 | 48.87 | 48.82 | 46.39 | 45.89 | 48.75 | 48.79 | 48.85 | 48.82 | 48.78 | 44.82 | 41.83 | 48.74 | 48.61 | 48.62 | 48.69 | 48.61 | 39.26 | 39.71 | 48.61 | 48.64 | 48.5 | 48.42 | 48.38 | 44.53 | 44.8 | 48.61 | 48.47 | ER
MAXIMUM | [5 empty] | 49.06 | 49.17 | 49.2 | 49.19 | 49.15 | 49.07 | 49.27 | 49.07 | 49.08 | 49.08 | 49.04 | 49.03 | 48.93 | 49.1 | 48.94 | 48.83 | 48.87 | 48.93 | 48.88 | 48.82 | 49.09 | 49 | 49 | 48.88 | 48.77 | 48.82 | 48.93 | 49 | 48.9 | 48.78 | ER
AVERAGE | [5 empty] | 48.91 | 48.97 | 49.02 | 49.02 | 48.99 | 47.35 | 48.33 | 48.94 | 48.97 | 48.97 | 48.97 | 48.95 | 46.4 | 47.88 | 48.92 | 48.71 | 48.86 | 48.9 | 48.79 | 42.58 | 46.22 | 48.8 | 48.85 | 48.69 | 48.56 | 48.63 | 46.54 | 47.69 | 48.73 | 48.61 | ER
| MW-1 |  | LOWER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MINIMUM | [5 empty] | 42.23 | 42.39 | 42.47 | 42.49 | 42.46 | 32.54 | 32.54 | 42.26 | 42.43 | 42.52 | 42.46 | 42.42 | 36.48 | 36.38 | 42.2 | 42.13 | 42.17 | 42.27 | 42.25 | 35.14 | 35.16 | 42.06 | 42.17 | 42.1 | 42.01 | 42.06 | 36.27 | 36.25 | 42.13 | 42.11 | ER
MAXIMUM | [5 empty] | 42.56 | 42.65 | 42.67 | 42.64 | 42.64 | 42.6 | 42.31 | 42.43 | 42.66 | 42.75 | 42.61 | 42.63 | 42.49 | 42.43 | 42.41 | 42.3 | 42.35 | 42.45 | 42.51 | 42.33 | 42.19 | 42.37 | 42.53 | 42.33 | 42.26 | 42.35 | 42.44 | 42.25 | 42.39 | 42.3 | ER
AVERAGE | [5 empty] | 42.39 | 42.47 | 42.5 | 42.53 | 42.53 | 35.26 | 39.58 | 42.39 | 42.5 | 42.55 | 42.52 | 42.48 | 38.32 | 40.56 | 42.26 | 42.17 | 42.28 | 42.38 | 42.41 | 37.5 | 40.07 | 42.28 | 42.36 | 42.15 | 42.08 | 42.27 | 39 | 40.29 | 42.21 | 42.14 | ER
MONITORING WELL TWO UPPER/LOWER LEVEL
| MW-2 |  | UPPER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MINIMUM | [5 empty] | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | 23.79 | 28.34 | 28.2 | ER
MAXIMUM | [5 empty] | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | 26.15 | 29.55 | 29.71 | 29.41 | ER
AVERAGE | [5 empty] | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | 15.41 | 27.37 | 28.86 | 28.76 | ER
| MW-2 |  | LOWER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MINIMUM | [5 empty] | 42.13 | 42.38 | 42.5 | 42.58 | 42.62 | 32.31 | 32.32 | 42.3 | 42.45 | 42.56 | 42.59 | 42.6 | 37.32 | 36.57 | 42.27 | 42.26 | 42.34 | 42.44 | 42.43 | 38.24 | 36.47 | 42.12 | 42.32 | 42.26 | 42.23 | 42.25 | 37.16 | 37.07 | 42.22 | 42.23 | ER
MAXIMUM | [5 empty] | 42.42 | 42.6 | 42.73 | 42.77 | 42.79 | 42.79 | 42.37 | 42.56 | 42.64 | 42.69 | 42.68 | 42.72 | 42.67 | 42.32 | 42.38 | 42.4 | 42.5 | 42.61 | 42.6 | 42.56 | 42.18 | 42.47 | 42.54 | 42.45 | 42.4 | 42.5 | 42.59 | 42.28 | 42.39 | 42.39 | ER
AVERAGE | [5 empty] | 42.33 | 42.48 | 42.54 | 42.66 | 42.72 | 35.25 | 39.45 | 42.46 | 42.5 | 42.59 | 42.6 | 42.61 | 39.04 | 40.77 | 42.38 | 42.37 | 42.44 | 42.5 | 42.51 | 39.71 | 40.9 | 42.35 | 42.48 | 42.43 | 42.39 | 42.44 | 39.43 | 40.52 | 42.38 | 42.37 | ER
MONITORING WELL THREE UPPER/LOWER LEVEL
| MW-3 |  | UPPER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MINIMUM | [5 empty] | 31.71 | 31.99 | 32.1 | 32.14 | 32.12 | 22.6 | 22.58 | 31.81 | 31.98 | 32.1 | 32.11 | 32.1 | 17.46 | 17.34 | 31.37 | 31.38 | 31.46 | 31.58 | 31.54 | 17.3 | 17.3 | 31.17 | 31.42 | 31.39 | 31.31 | 31.31 | 17.39 | 16.91 | 31.24 | 31.24 | ER
MAXIMUM | [5 empty] | 32.13 | 32.32 | 32.43 | 32.42 | 32.38 | 32.27 | 31.94 | 32.16 | 32.25 | 32.29 | 32.29 | 32.31 | 32.23 | 31.49 | 31.61 | 31.62 | 31.74 | 31.86 | 31.83 | 31.72 | 31.27 | 31.64 | 31.74 | 31.62 | 31.57 | 31.67 | 31.79 | 31.4 | 31.57 | 31.57 | ER
AVERAGE | [5 empty] | 31.92 | 32.1 | 32.28 | 32.31 | 32.25 | 25.34 | 29.12 | 31.97 | 32.08 | 32.25 | 32.24 | 32.21 | 21.88 | 27.14 | 31.47 | 31.48 | 31.58 | 31.68 | 31.66 | 21.88 | 27.18 | 31.4 | 31.55 | 31.51 | 31.46 | 31.46 | 23.53 | 26.88 | 31.42 | 31.43 | ER
| MW-3 |  | LOWER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MINIMUM | [5 empty] | 45.36 | 45.62 | 45.75 | 45.83 | 45.86 | 40.07 | 40.07 | 45.48 | 45.64 | 45.75 | 45.78 | 45.79 | 37.19 | 37.15 | 45.36 | 45.36 | 45.47 | 45.58 | 45.58 | 35.66 | 35.67 | 45.16 | 45.39 | 45.36 | 45.34 | 45.37 | 37.45 | 37.38 | 45.3 | 45.31 | ER
MAXIMUM | [5 empty] | 45.63 | 45.84 | 45.98 | 46.01 | 46.03 | 46.01 | 45.54 | 45.74 | 45.82 | 45.88 | 45.88 | 45.89 | 45.84 | 45.38 | 45.48 | 45.51 | 45.63 | 45.77 | 45.76 | 45.7 | 45.19 | 45.53 | 45.62 | 45.53 | 45.49 | 45.62 | 45.72 | 45.32 | 45.46 | 45.48 | ER
AVERAGE | [5 empty] | 45.46 | 45.83 | 45.89 | 45.94 | 45.98 | 41.73 | 43.88 | 45.52 | 45.8 | 45.87 | 45.88 | 45.92 | 39.79 | 42.89 | 45.45 | 45.46 | 45.5 | 45.6 | 45.61 | 38.87 | 42.38 | 45.37 | 45.49 | 45.49 | 45.47 | 45.47 | 41.02 | 42.75 | 45.41 | 45.43 | ER
MONITORING WELL RMW-1 UPPER/LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
[5 empty] | JULIAN DATE | 274 | 275 | 276 | 277 | 278 | 279 | 280 | 281 | 282 | 283 | 284 | 285 | 286 | 287 | 288 | 289 | 290 | 291 | 292 | 293 | 294 | 295 | 296 | 297 | 298 | 299 | 300 | 301 | 302 | 303 | 304
| RMW-1 |  | UPPER LEVEL
MINIMUM | [5 empty] | 44.38 | 44.51 | 44.63 | 44.69 | 44.71 | 30.66 | 27.48 | 44.05 | 44.18 | 44.24 | 44.23 | 44.22 | 44.21 | 44.21 | 44.15 | 44.1 | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER
MAXIMUM | [5 empty] | 44.53 | 44.66 | 44.75 | 44.79 | 44.82 | 44.83 | 44.05 | 44.24 | 44.31 | 44.34 | 44.34 | 44.33 | 44.32 | 44.34 | 44.28 | 44.18 | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER
AVERAGE | [5 empty] | 44.45 | 44.59 | 44.69 | 44.75 | 44.77 | 35.42 | 40.1 | 44.15 | 44.25 | 44.29 | 44.29 | 44.28 | 44.27 | 44.27 | 44.23 | 44.15 | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER
| RMW-1 |  | LOWER LEVEL
MINIMUM | [5 empty] | 22.47 | 22.59 | 22.63 | 22.64 | 22.62 | 20.39 | 20.8 | 22.41 | 22.61 | 22.73 | 22.75 | 22.76 | 22.73 | 22.72 | 22.69 | 22.6 | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER
MAXIMUM | [5 empty] | 22.65 | 22.76 | 22.8 | 22.8 | 22.76 | 22.72 | 33.03 | 22.64 | 22.74 | 22.82 | 22.82 | 22.82 | 22.84 | 22.88 | 22.82 | 22.7 | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER
AVERAGE | [5 empty] | 22.56 | 22.68 | 22.72 | 22.73 | 22.7 | 21.48 | 21.9 | 22.53 | 22.69 | 22.77 | 22.78 | 22.79 | 22.79 | 22.8 | 22.76 | 22.67 | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
| INJECTION WELL ONE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 14.81 | 14.21 | 16.32 | 14.93 | 13.22 | 13.13 | 14.67 | 12.62 | 13.2 | 12.66 | 15.03 | 12.24 | 11.78 | 11.51 | 12.31 | 11.71 | 11.62 | 11.98 | 12.74 | 11.83 | 11.91 | 12.28 | 13.14 | 12.29 | 12.16 | 13.22 | 11.5 | 13.48 | 13.52 | 12.82 | ER
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 9.51 | 9.63 | 8.75 | 8.84 | 7.45 | 6.87 | 6.49 | 5.73 | 5.78 | 5.4 | 5.48 | 5.41 | 5.5 | 4.6 | 5.32 | 5.27 | 5.23 | 5.89 | 5.74 | 6.06 | 4.41 | 5 | 5.09 | 4.76 | 4.51 | 5.07 | 4.33 | 4.76 | 5.82 | 6.18 | ER
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 12.91 | 12.45 | 12.38 | 11.74 | 11 | 10.7 | 10.61 | 9.99 | 9.76 | 9.73 | 9.33 | 9.2 | 9.26 | 9.13 | 9.04 | 8.93 | 9.17 | 9.05 | 8.86 | 9.23 | 9.03 | 9.09 | 9.11 | 9.17 | 8.94 | 8.69 | 8.75 | 8.81 | 10.33 | 9.54 | ER
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 68.13 | 65.76 | 73.8 | 67.76 | 61.12 | 61.14 | 66.63 | 60.81 | 61.74 | 59.98 | 71.3 | 58.33 | 57.43 | 56.34 | 59.23 | 57.33 | 56.95 | 57.48 | 60.02 | 57.06 | 57.78 | 58.39 | 61.45 | 58.49 | 57.6 | 61.84 | 56.89 | 62.78 | 62.85 | 60.54 | ER
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 52.42 | 51.51 | 48.93 | 49.11 | 45.79 | 44.47 | 43.85 | 42.36 | 42.4 | 41.56 | 41.86 | 41.5 | 41.73 | 40.29 | 41.31 | 40.83 | 41.2 | 42.45 | 42.21 | 42.66 | 39.65 | 40.93 | 40.71 | 39.91 | 39.75 | 40.38 | 39.43 | 39.81 | 41.94 | 42.65 | ER
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 61.38 | 59.73 | 59.33 | 57.13 | 54.76 | 54.04 | 53.84 | 52.31 | 51.6 | 51.54 | 50.76 | 50.23 | 50.38 | 50.11 | 49.71 | 49.23 | 49.99 | 49.67 | 49.23 | 50.01 | 49.63 | 49.7 | 49.76 | 49.82 | 49.11 | 48.77 | 48.87 | 49.02 | 53.03 | 50.78 | ER
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
| INJECTION WELL TWO |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 15.42 | 14.91 | 17.11 | 15.62 | 13.84 | 13.81 | 15.14 | 13.27 | 13.95 | 13.42 | 15.68 | 12.79 | 12.39 | 12.13 | 12.92 | 12.51 | 12.29 | 12.65 | 13.49 | 12.34 | 12.54 | 12.97 | 13.83 | 13.07 | 12.86 | 13.97 | 12.19 | 14.24 | 13.9 | 13.36 | ER
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 10.15 | 10.12 | 9.37 | 9.38 | 8 | 7.27 | 6.93 | 6.13 | 6.13 | 5.71 | 5.83 | 5.85 | ER | 4.84 | 5.66 | 5.67 | 5.6 | 6.18 | 6.03 | 6.41 | 4.67 | 4.51 | 5.32 | 5.03 | 4.69 | 5.31 | 4.6 | ER | 6.57 | 6.94 | ER
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 13.51 | 13.06 | 13.01 | 12.34 | 11.6 | 11.3 | 11.18 | 10.58 | 10.35 | 10.32 | 9.89 | 9.73 | 8.87 | 9.66 | 9.57 | 9.47 | 9.69 | 9.57 | 9.38 | 9.78 | 9.56 | 9.63 | 9.68 | 9.75 | 9.52 | 9.26 | 9.33 | ER | 10.92 | 10.18 | ER
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 66.9 | 64.53 | 72.4 | 66.58 | 60.05 | 59.98 | 64.93 | 59.65 | 60.53 | 58.86 | 70.1 | 57.41 | 56.48 | 57.35 | 58.08 | 56.22 | 55.85 | 56.51 | 58.88 | 55.93 | 56.65 | 57.23 | 60.23 | 57.35 | 56.52 | 60.76 | 55.94 | 61.62 | 61.62 | 59.43 | ER
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 51.43 | 50.52 | 47.99 | 48.19 | 44.93 | 43.64 | 43.02 | 41.57 | 41.59 | 40.77 | 41.08 | 40.71 | 40.94 | 39.53 | 40.52 | 40.02 | 40.41 | 41.62 | 41.38 | 41.81 | 38.91 | 39.64 | 39.91 | 39.15 | 38.99 | 39.61 | 38.66 | 39.05 | 41.16 | 41.79 | ER
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 60.26 | 58.59 | 58.21 | 56.06 | 53.74 | 53.03 | 52.8 | 51.33 | 50.61 | 50.56 | 49.84 | 49.3 | 49.45 | 49.18 | 48.78 | 48.3 | 49.04 | 48.74 | 48.28 | 49.07 | 48.73 | 48.78 | 48.84 | 48.9 | 48.17 | 47.86 | 47.96 | 48.09 | 52.03 | 49.82 | ER
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
| INJECTION WELL THREE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 13.29 | 12.69 | 14.6 | 13.36 | 11.78 | 11.68 | 13.33 | 11.36 | 11.88 | 11.4 | 13.51 | 10.95 | 10.57 | 10.28 | 10.96 | 10.55 | 10.39 | 10.73 | 11.41 | 10.4 | 10.63 | 10.92 | 11.64 | 11.01 | 10.79 | 11.83 | 10.32 | 11.96 | 12.03 | 11.47 | ER
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 8.57 | 8.62 | 7.8 | 7.89 | 6.61 | 5.94 | 5.73 | 5.05 | 5.03 | 4.64 | 4.76 | 4.72 | ER | 3.91 | 4.6 | 4.64 | 4.53 | 5.07 | 4.92 | 5.27 | 3.76 | 4.2 | 4.37 | 4.03 | 3.75 | 4.23 | 3.67 | 3.99 | 5 | 5.41 | ER
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 11.57 | 11.12 | 11.06 | 10.46 | 9.8 | 9.51 | 9.43 | 8.93 | 8.73 | 8.67 | 8.33 | 8.21 | 7.97 | 8.13 | 8.04 | 7.93 | 8.14 | 8.04 | 7.86 | 8.19 | 8.02 | 8.07 | 8.09 | 8.15 | 7.93 | 7.71 | 7.78 | 7.83 | 9.21 | 8.5 | ER
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 68.56 | 66.13 | 74.2 | 68.1 | 61.49 | 61.46 | 67.76 | 61.16 | 62.08 | 60.31 | 71.8 | 58.67 | 57.74 | 56.66 | 59.57 | 57.67 | 57.22 | 57.8 | 60.36 | 57.34 | 58.08 | 58.7 | 61.77 | 58.81 | 57.91 | 62.2 | 57.2 | 63.14 | 63.2 | 60.88 | ER
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 52.65 | 51.7 | 49.11 | 49.3 | 45.95 | 44.62 | 44 | 42.5 | 42.54 | 41.69 | 42 | 41.63 | 41.86 | 40.4 | 41.44 | 40.96 | 41.34 | 42.61 | 42.34 | 42.8 | 39.77 | 41.04 | 40.84 | 40.02 | 39.84 | 40.51 | 39.52 | 39.92 | 42.08 | 42.78 | ER
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 61.71 | 60.01 | 59.63 | 57.39 | 55.06 | 54.25 | 54.06 | 52.55 | 51.85 | 51.77 | 50.99 | 50.47 | 50.6 | 50.33 | 49.94 | 49.42 | 50.19 | 49.89 | 49.44 | 50.23 | 49.81 | 49.94 | 49.96 | 50.04 | 49.32 | 48.98 | 49.09 | 49.21 | 53.29 | 51.01 | ER
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
FUTURE
| INJECTION WELL FOUR |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | 0.15 | 0.16 | 0.15 | ER
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | 0.13 | 0.13 | ER
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | 0.14 | 0.13 | ER
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 38.94 | 38.67 | 39.16 | 38.7 | 38.25 | 38.19 | 38.6 | 38.35 | 38.33 | 38.14 | 38.93 | 37.99 | 37.92 | 59.98 | 37.82 | 37.65 | 37.63 | 37.72 | 37.88 | 37.63 | 37.65 | 37.83 | 38.17 | 37.92 | 37.74 | 38.21 | 37.87 | 38.32 | 38.19 | 38.03 | ER
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 37.22 | 37.47 | 37.16 | 37.19 | 36.92 | 36.68 | 36.56 | 36.45 | 36.4 | 36.18 | 36.09 | 36.07 | 36.08 | 29.78 | 36.06 | 35.94 | 36.02 | 36.21 | 36.19 | 36.22 | 35.9 | 35.62 | 35.97 | 35.92 | 35.78 | 35.76 | 35.64 | 35.8 | 36.24 | 36.21 | ER
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 38.18 | 38.13 | 38.05 | 37.86 | 37.68 | 37.59 | 37.52 | 37.48 | 37.34 | 37.25 | 37.12 | 37.1 | 37.1 | 37.07 | 37 | 36.9 | 36.99 | 37.01 | 36.95 | 36.99 | 36.95 | 36.98 | 37.02 | 36.99 | 36.84 | 36.81 | 36.92 | 36.98 | 37.38 | 37.21 | ER
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
| INJECTION WELL FIVE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 12.99 | 12.47 | 14.31 | 13.08 | 11.57 | 11.51 | 12.93 | 11.14 | 11.67 | 11.23 | 13.36 | 10.8 | 10.44 | 10.23 | 10.89 | 10.48 | 10.35 | 10.61 | 11.31 | 10.39 | 10.58 | 10.82 | 11.55 | 10.89 | 10.71 | 11.68 | 10.25 | 11.89 | 11.88 | 11.38 | ER
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 8.54 | 8.63 | 7.33 | 7.97 | 6.84 | 6.25 | ER | 5.31 | 5.32 | 4.44 | 5.1 | 5.09 | 5.16 | 4.26 | 4.96 | 4.91 | 4.86 | 5.37 | 5.26 | 5.57 | 4.17 | ER | 4.64 | 4.44 | 4.17 | 4.64 | 4.04 | 4.34 | 5.39 | 5.74 | ER
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 11.36 | 10.96 | 10.89 | 10.35 | 9.74 | 9.49 | 9.07 | 8.92 | 8.73 | 8.68 | 8.38 | 8.28 | 8.32 | 8.21 | 8.12 | 8.03 | 8.23 | 8.14 | 7.98 | 8.29 | 8.14 | 7.97 | 8.16 | 8.22 | 8.02 | 7.82 | 7.88 | 7.94 | 9.2 | 8.56 | ER
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 67.78 | 65.54 | 73.7 | 67.53 | 60.88 | 60.99 | 67.16 | 60.65 | 61.66 | 59.87 | 71 | 58.03 | 57.26 | 56.18 | 59.06 | 57.21 | 56.76 | 57.35 | 59.88 | 56.92 | 57.65 | 58.37 | 61.34 | 58.39 | 57.4 | 61.65 | 56.66 | 62.68 | 62.76 | 60.38 | ER
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 52.25 | 51.29 | 48.78 | 48.92 | 45.61 | 44.31 | 36.1 | 42.25 | 42.29 | 41.42 | 41.71 | 41.37 | 41.6 | 40.17 | 41.2 | 40.79 | 41.1 | 42.36 | 42.1 | 42.54 | 39.55 | 35.38 | 40.67 | 39.87 | 39.61 | 40.27 | 39.32 | 39.76 | 41.79 | 42.57 | ER
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 61.17 | 59.51 | 59.07 | 56.94 | 54.54 | 53.8 | 52.87 | 52.11 | 51.39 | 51.29 | 50.57 | 50.06 | 50.2 | 49.91 | 49.54 | 49.01 | 49.83 | 49.51 | 49.04 | 49.83 | 49.49 | 49.35 | 49.62 | 49.68 | 48.95 | 48.62 | 48.73 | 48.89 | 52.84 | 50.56 | ER
GTL DAILY LABORATORY ANALYSIS REPORT DATA
| RAW INFLUENT DATA |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
RAW TOTAL SUSPENDED SOLIDS | [5 empty] | 80 | 68 | 98 | 72 | 70 | 76 | 96 | 40 | 86 | 100 | 94 | 86 | 90 | 106 | 104 | 102 | 100 | 78 | 104 | 94 | 104 | 94 | 88 | 100 | 94 | 60 | 100 | 60 | 94 | 128 | 110
RAW FIXED SUSPENDED SOLIDS | [5 empty] | 16 | 12 | 8 | 12 | 12 | 6 | 10 | 8 | 12 | 10 | 8 | 26 | 14 | 12 | 18 | 20 | 18 | 10 | 18 | 16 | 16 | 14 | 16 | 10 | 14 | 10 | 20 | 12 | 18 | 24 | 8
RAW ALKILINITY | [5 empty] | 198 | 204 | 204 | 198 | 192 | 198 | 204 | 202 | 200 | 202 | 200 | 198 | 196 | 188 | 196 | 196 | 198 | 196 | 198 | 202 | 196 | 198 | 200 | 184 | 194 | 198 | 200 | 200 | 202 | 202 | 186
RAW CHLORIDES | [5 empty] | 750 | 710 | 760 | 750 | 750 | 740 | 730 | 760 | 760 | 720 | 730 | 690 | 680 | 670 | 690 | 680 | 700 | 680 | 680 | 730 | 740 | 700 | 720 | 750 | 720 | 700 | 680 | 690 | 730 | 710 | 690
RAW COD | [5 empty] | 265 | 281 | 264 | 250 | 250 |  |  | 240 | 225 | 230 | 210 | 242 |  |  | 286 | 259 | 202 | 192 | 206 |  |  | 232 | 264 | 208 | 241 | 250 |  |  | 257 | 307 | 268
RAW CBOD | [5 empty] | 21.2 | 55.3 | 40 | 52 | 59 | 54.6 | 81 | 51 | 65 | 57 | 90 | 91.4 | 75 | 64 | 72 | 63 | 81 | 77 | 70.5 | 67.3 | 67 | 77 | 67 | 73 | 55 | 64 | 70 | 55 | 91 | 52 | 41
| EFFLUENT DATA |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
EFFLUENT TOTAL DISSOLVED SOLIDS | [5 empty] | 1150 | 1377 | 1168 | 638 | 1336 | 1292 | 1366 | 1389 | 1280 | 1349 | 1398 | 1331 | 1340 | 1422 | 1290 | 1395 | 1294 | 1220 | 1525 | 1453 | 1473 | 1432 | 1555 | 1638 | 1430 | 1548 | 1440 | 1605 | 1470 | 1383 | 1380
EFFLUENT TOTAL SUSPENDED SOLIDS | [5 empty] | 16 | 11 | 11 | 9 | 8 | 10 | 10 | 17 | 15 | 19 | 14 | 20 | 9 | 11 | 9 | 12 | 12 | 9 | 11 | 16 | 18 | 14 | 17 | 27 | 18 | 13 | 10 | 14 | 16 | 18 | 21
EFFLUENT FIXED SUSPENDED SOLIDS | [5 empty] | 5 | 3 | 3 | 2 | 1 | 1 | 1 | 2 | 3 | 5 | 2 | 7 | 1 | 1 | 2 | 5 | 3 | 1 | 2 | 3 | 6 | 3 | 5 | 11 | 6 | 3 | 2 | 4 | 4 | 4 | 2
EFFLUENT ALKILINITY | [5 empty] | 190 | 190 | 190 | 192 | 192 | 190 | 192 | 190 | 192 | 186 | 182 | 180 | 180 | 188 | 186 | 196 | 192 | 186 | 186 | 190 | 192 | 190 | 192 | 190 | 190 | 190 | 192 | 190 | 194 | 192 | 188
EFFLUENT TURBIDITY | [5 empty] | 6.85 | 6.91 | 6.97 | 6.84 | 4.29 | 2.98 | 5.04 | 4.91 | 6.25 | 4.73 | 5.33 | 5.99 | 4.99 | 5.44 | 4.9 | 4.68 | 5.03 | 5.11 | 5.91 | 6.47 | 7.4 | 5.64 | 7.72 | 6.49 | 6.63 | 5.58 | 6.13 | 5.13 | 5.92 | 5.23 | 12.8
EFFLUENT CHLORIDES | [5 empty] | 710 | 710 | 740 | 740 | 740 | 690 | 720 | 720 | 740 | 680 | 700 | 680 | 690 | 670 | 660 | 680 | 670 | 680 | 760 | 830 | 760 | 720 | 710 | 730 | 760 | 720 | 700 | 720 | 740 | 720 | 710
EFFLUENT CONDUCTIVITY | [5 empty] | 2410 | 2650 | 2660 | 2560 | 2670 | 2590 | 2640 | 2650 | 2650 | NR | 2740 | 2640 | 2780 | 2720 | 2740 | 2740 | 2750 | 2510 | 2820 | 2890 | 2890 | 2880 | 3050 | 3111 | 3070 | 3050 | 3150 | 3230 | 2930 | 2890 | 2680
EFFLUENT TOTAL BACTERIA COUNT | [5 empty] | 8667 | 36500 | 4000 | 839 | 5100 | 3500 | 455 | 3500 | 18000 | 4900 | 107 | 320 | 3900 | 0 | TNTC | TNTC | TNTC | 4500 | 610 | 205 | TNTC | 44500 | 25500 | TNTC | 18 | 0 | 4000 | 4700 | 167 | 700 | TNTC
EFFLUENT FECAL BACTERIA COUNT | [5 empty] | 0 | 36 | 9 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 9 | 0 | 0 | 0 | TNTC | TNTC | TNTC | 36 | 0 | 0 | 70500 | 63 | 36 | 9 | 0 | 0 | 0 | 54 | 0 | 0 | 240
EFFLUENT COD | [5 empty] | 54.1 | 50.6 | 53.2 | 58.4 | 58.4 |  |  | 59.1 | 60.2 | 61.2 | 58.4 | 54.3 |  |  | 51.2 | 53.4 | 54.8 | 59.6 | 54.2 |  |  | 58.6 | 51.4 | 60.3 | 54.4 | 53.6 |  |  | 52.5 | 56.9 | 77.3
EFFLUENT CBOD | [5 empty] | 4.74 | 4.42 | 4 | 2.7 | 2 | 1.13 | 4.1 | 3.8 | 5.56 | 2.7 | 3.1 | 4.52 | 3.6 | 4.1 | 4.1 | 3.9 | 3.7 | 6.2 | 4.24 | 5.68 | 5.7 | 5.3 | 6.2 | 6.1 | 3.9 | 3.7 | 4 | 4 | 4 | 6 | 8
LABORATORY NUTRIENT DATA
RAW INFLUENT | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
RAW AMMONIA (PPM) | [5 empty] | 10.92 | 10.91 | 11.31 | 11.34 | 11.34 |  |  | 14.03 | 14.82 | 14.58 | 14.22 | 14.03 |  |  | 15.63 | 13.62 | 15.73 | 14.36 | 14.97 |  |  | 15.59 | 15.17 | 15.47 | 15.46 | 15.14 |  |  | 12.2 | 13.25 | 14.02
RAW NITRATES (PPM) | [5 empty] | 0.229 | 0.277 | 0.288 | 0.249 | 0.249 |  |  | 0.264 | 0.273 | 0.281 | 0.299 | 0.317 |  |  | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 |  |  | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 |  |  | 0.02 | 0.02 | 0.02
RAW TOTAL KNEDJAHL NITRIGEN | [5 empty] | 14.36 | 15.08 | 15.26 | 14.95 | 14.95 |  |  | 18.16 | 18.11 | 18.95 | 18.53 | 17.83 |  |  | 20.88 | 18.85 | 20.65 | 19.84 | 19.98 |  |  | 20.59 | 20.65 | 20.63 | 20.71 | 20.72 |  |  | 18.39 | 19.92 | 20.35
RAW TOTAL PHOSPHORUS | [5 empty] | 1.46 | 1.6 | 1.72 | 1.72 | 1.72 |  |  | 2.16 | 2.09 | 2.2 | 2.21 | 2.3 |  |  | 2.98 | 2.23 | 2.38 | 2.39 | 2.45 |  |  | 2.4 | 2.55 | 2.35 | 2.47 | 4.05 |  |  | 2.31 | 2.64 | 2.52
EFFLUENT | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
EFFLUENT AMMONIA (PPM) | [5 empty] | 7.98 | 8.36 | 8.33 | 7.51 | 7.51 |  |  | 10.49 | 10.75 | 10.3 | 9.84 | 10 |  |  | 11.64 | 12.24 | 12.33 | 10.89 | 10.61 |  |  | 11.81 | 12.09 | 11.94 | 10.87 | 10.86 |  |  | 10.03 | 10 | 9.99
EFFLUENT NITRATES (PPM) | [5 empty] | 0.622 | 0.674 | 0.678 | 0.787 | 0.787 |  |  | 0.756 | 0.78 | 0.794 | 0.75 | 0.877 |  |  | 0.426 | 0.474 | 0.432 | 0.373 | 0.541 |  |  | 0.328 | 0.456 | 0.36 | 0.378 | 0.629 |  |  | 0.415 | 0.372 | 0.17
EFFLUENT TOTAL KNEDJAHL NITRIGEN | [5 empty] | 10.97 | 11.55 | 11.49 | 10.54 | 10.54 |  |  | 14.02 | 14.02 | 13.96 | 13.32 | 13.57 |  |  | 16.32 | 16.78 | 17.07 | 15.23 | 14.74 |  |  | 16.17 | 0 | 16.64 | 15.17 | 15.38 |  |  | 15.53 | 15.59 | 15.81
EFFLUENT TOTAL PHOSPHORUS | [5 empty] | 0.869 | 0.685 | 0.78 | 0.697 | 0.697 |  |  | 0.965 | 1.24 | 0.721 | 0.653 | 0.967 |  |  | 0.948 | 0.99 | 0.912 | 0.71 | 1.03 |  |  | 1.56 | 1.47 | 1.01 | 0.826 | 0.7 |  |  | 1.3 | 1.77 | 1.16
LABORATORY REACTOR PROCESSES DATA
| REACTOR ONE TRAIN A |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MIXED-LIQUIR SUSPENDED SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
AVERAGE SETTLABLE SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
MIXED LIQUIR VOLITLE SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
| REACTOR ONE TRAIN B |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MIXED-LIQUIR SUSPENDED SOLIDS | [5 empty] | 1500 | 1180 | 1230 | 1590 | 1910 | 1610 | 1520 | 1490 | 1500 | 1320 | 2100 | 2000 | 2100 | 1340 | 1310 | 1460 | 1390 | 1640 | 1660 | 1670 | 1640 | 1220 | 1480 | 1320 | 1380 | 2240 | 1620 | 1850 | 1000 | 820 | 1220
AVERAGE SETTLABLE SOLIDS | [5 empty] | 11 | 11 | 13 | 15 | 16 | 12 | 14 | 10 | 10 | 12 | 14 | 17 | 15 | 15 | 14 | 13 | 14 | 15 | 16 | 13 | 12 | 11 | 12 | 11 | 14 | 15 | 14 | 14 | 12 | 8 | 8
MIXED LIQUIR VOLITLE SOLIDS | [5 empty] | 1240 | 980 | 970 | 1320 | 1550 | 1360 | 1260 | 1240 | 1240 | 1100 | 1910 | 1620 | 1740 | 1120 | 1090 | 1170 | 1120 | 1360 | 1380 | 1390 | 1340 | 1010 | 1230 | 1130 | 1150 | 1860 | 1340 | 1540 | 830 | 680 | 1060
LABORATORY REACTOR PROCESSES DATA
CONTINUED
| REACTOR TWO TRAIN C |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MIXED-LIQUIR SUSPENDED SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
AVERAGE SETTLABLE SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
MIXED LIQUIR VOLITLE SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
| REACTOR TWO TRAIN D |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MIXED-LIQUIR SUSPENDED SOLIDS | [5 empty] | 1370 | 1500 | 1700 | 1810 | 1840 | 1810 | 1730 | 2270 | 1850 | 1840 | 1100 | 2940 | 2300 | 1780 | 1530 | 1710 | 1610 | 1710 | 1860 | 2180 | 1580 | 1820 | 1350 | 1460 | 1500 | 1830 | 1520 | 2350 | 1050 | 800 | 1970
AVERAGE SETTLABLE SOLIDS | [5 empty] | 11 | 12 | 14 | 17 | 17 | 15 | 16 | 13 | 14 | 14 | 15 | 19 | 16 | 16 | 14 | 14 | 14 | 15 | 16 | 14 | 13 | 11 | 12 | 12 | 16 | 14 | 14 | 14 | 12 | 9 | 9
MIXED LIQUIR VOLITLE SOLIDS | [5 empty] | 1140 | 1240 | 1390 | 1500 | 1490 | 1480 | 1520 | 1980 | 1540 | 1460 | 880 | 2610 | 1910 | 1500 | 1270 | 1410 | 1320 | 1420 | 1540 | 1810 | 1290 | 1510 | 1120 | 1250 | 1240 | 1520 | 1260 | 1950 | 870 | 660 | 1570
LABORATORY RETURN ACTIVATED SLUDGE AND WASTE SLUDGE DATA
| RETURN ACTIVATED SLUDGE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
PERCENT RETURN SLUDGE TOTAL SUSPENDED SOLIDS | [5 empty] | 0.7 | 0.77 | 0.78 | 0.74 | 0.82 | 0.7 | 0.75 | 0.62 | 0.69 | 0.88 | 1.07 | 0.79 | 0.8 | 0.74 | 0.7 | 0.66 | 0.7 | 0.7 | 0.7 | 0.8 | 0.65 | 0.7 | 0.55 | 0.66 | 0.53 | 0.7 | 0.67 | 0.61 | 0.54 | 0.43 | 0.46
PERCENT RETURN SLUDGE FIXED SUSPENDED SOLIDS | [5 empty] | 24.7 | 26 | 25.6 | 22.8 | 24.3 | 26.2 | 26.5 | 24.6 | 30.4 | 21.3 | 20 | 24.7 | 27.2 | 26.8 | 24.5 | 25 | 28.6 | 25.7 |  | 24.5 | 27.5 | 28 | 28.7 | 30.1 | 26.4 | 23 | 25 | 24.8 | 27.9 | 22.4 | 25.5
|  | WASTE SLUDGE |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
PERCENT WASTE FEED TOTAL SUSPENDED SOLDS | [5 empty] | 0.97 | 1.39 |  |  | 1.39 | 1.09 | 1.22 | 1.11 | 1.42 |  |  |  | 1.33 | 1.34 | 1.41 | 1.24 |  |  | 1.59 | 1.6 | 1.24 | 1.51 | 0.83 |  |  |  | 1.42 | 1.41 | 1.56 | 0.93
PERCENT WASTE FEED FIXED SUSPENDED SOLIDS | [5 empty] | 25.8 | 25.2 |  |  | 22.3 | 27.5 | 23.8 | 24.3 | 21.8 |  |  |  | 21.8 | 21.6 | 22 | 24.2 |  |  | 23.9 | 21.3 | 23.4 | 21.2 | 28.9 |  |  |  | 23.9 | 22.7 | 22.4 | 24.7
WASTE FEED SLUDGE pH | [5 empty] | 6.78 | 6.71 |  |  | 6.91 | 6.46 | 6.48 | 6.78 | 6.74 |  |  |  | 6.53 | 6.45 | 6.79 | 6.57 |  |  | 6.77 | 6.79 | 6.71 | 6.74 | 6.74 |  |  |  | 6.78 | 6.76 | 6.78 | 6.78
DEWATERING FILTRATE TOTAL SUSPENDED SOLIDS | [5 empty] | 0.38 | 0.2 |  |  | 0.39 | 0.21 | 0.4 | 0.31 | 0.38 |  |  |  | 0.45 | 0.46 | 0.46 | 0.34 |  |  | 0.43 | 0.33 | 0.47 | 0.31 | 0.27 |  |  |  | 0.45 | 0.36 | 0.42 | 0.16
DEWATERING FILTRATE FIXED SUSPENDED SOLIDS | [5 empty] | 39.5 | 45 |  |  | 38.46 | 61.9 | 40 | 45.2 | 42.1 |  |  |  | 37.8 | 37 | 37 | 50 |  |  | 55.8 | 48.5 | 36.2 | 48.4 | 55.5 |  |  |  | 55.6 | 47.2 | 47.6 | 81.2
DEWATERING FILTRATE pH | [5 empty] | 7.21 | 7.19 |  |  | 7.15 | 6.97 | 7.05 | 7.45 | 7.22 |  |  |  | 7.04 | 7.11 | 7.09 | 7.03 |  |  | 7.11 | 7.19 | 7.27 | 7.19 | 7.15 |  |  |  | 7.14 | 7.11 | 7.21 | 7.19
| DEWATERED CAKE SLUDGE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
PERCENT TOTAL SOLIDS PRESS CAKE | [5 empty] | 16.68 | 19.64 |  |  | 18.39 | 19.66 | 19.6 | 19.28 | 17.9 |  |  |  | 18.93 | 19.29 | 18.93 | 19.67 |  |  | 18.12 | 19.41 | 19.29 | 19.44 | 21.06 |  |  |  | 15.88 | 18.96 | 19.62 | 21
PERCENT FIXED SOLIDS PRESS CAKE | [5 empty] | 17.7 | 15.3 |  |  | 16.2 | 14.9 | 19.1 | 16 | 18 |  |  |  | 20.1 | 15.6 | 17.4 | 16.4 |  |  | 16.2 | 18 | 16.3 | 13.4 | 23 |  |  |  | 18.3 | 13.7 | 14 | 14.8
PERCENT TOTAL SOLIDS LIME CAKE
OTHER SLUDGE REMOVAL
[6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
GRIT (CU.YDS.) | [5 empty] | 9: 10; 23: 10; 31: 10
RAGS (CU.YDS.) | [5 empty] | 3: 10; 10: 10; 17: 10; 24: 10
VACUUM DEBRIS (EST. GAL) | [5 empty] | 9: 4500; 28: 4500
MONITORING WELLS LABORATORY DATA
| MONITOR WELL ONE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
UPPER LEVEL
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
MONITORING WELLS LABORATORY DATA
| MONITOR WELL TWO |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
UPPER LEVEL
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
MONITORING WELLS LABORATORY DATA
| MONITOR WELL THREE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
FUTURE
UPPER LEVEL
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
MONITORING WELLS LABORATORY DATA
| REGIONAL MONITOR WELL ONE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
UPPER LEVEL
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
OCTOBER |  | 1 |  | 3
|  | 0 |  | 0
0
0
|  | 0 |  | 0
3
[5 empty] | 1st WEEK | 1: 2nd WEEK; 2: 3rd WEEK; 3: 4th WEEK
| 1 |  | 1 |  | 1 | 1: 8; 2: 15; 3: 23
| 2 |  | 2 |  | 2 | 1: 9; 2: 16; 3: 24
| 3 |  | 3 |  | 3 | 1: 10; 2: 17; 3: 25
| 4 |  | 4 |  | 4 | 1: 11; 2: 18; 3: 26
| 5 |  | 5 |  | 5 | 1: 12; 2: 19; 3: 27
| 6 |  | 6 |  | 6 | 1: 13; 2: 20; 3: 28
| 7 |  | 7 |  | 7 | 1: 14; 2: 21; 3: 29
| 8 |  | 8 |  |  | 2: 22; 3: 30
| 9 |  | 9 |  |  | 3: 31
| 10 |  | 10
| 11 |  | 11
| 12 |  | 12
| 13 |  | 13
| 14 |  | 14
| 15 |  | 15
| 16 |  | 16
| 17 |  | 17
| 18 |  | 18
| 19 |  | 19
| 20 |  | 20
| 21 |  | 21
| 22 |  | 22
| 23 |  | 23
| 24 |  | 24
| 25 |  | 25
| 26 |  | 26
| 27 |  | 27
| 28 |  | 28
29
30
31
| APRIL | MARCH | FEBRUARY
| AUGUST | JULY | JUNE
| DECEMBER | NOVEMBER | OCTOBER
| FEBRUARY | JANUARY | DECEMBER
| JANUARY | DECEMBER | NOVEMBER
| JUNE | MAY | APRIL
| JULY | JUNE | MAY | SEPTEMBER
| MARCH | FEBRUARY | JANUARY | AUGUST
| MAY | APRIL | MARCH
| NOVEMBER | OCTOBER | SEPTEMBER
| OCTOBER | SEPTEMBER | AUGUST
| SEPTEMBER | AUGUST | JULY
| HYDROGEN PEROXIDE |  | 0.1395
| CHLORINE |  | 0.1475
| POLYMER |  | 0.61
| FPL |  | 0.055
[6 empty] | 1st WEEK |  |  | 2nd WEEK |  |  | 3rd WEEK |  |  | 4th WEEK
[7 empty] | G | H | I | J
[5 empty] | MW1 UP | 1: 311
312
313
314
315
316
317
318

## MONITOR DATA
UNDERGROUND INJECTION CONTROL SECTION
MONTHLY OPERATING REPORT DATA SUMMARY
FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT MONTH/YEAR |  |  | OCTOBER |  | 2003
I.D. NUMBER: 5006M02066 | [5 empty] | LEAD OPERATOR: |  |  |  | MIKE JUST
TELEPHONE NUMBER: (954) 523-1002
MONITORING WELL 1 DATA | [6 empty] | I.D. # 5006A11311
MW-1
PERMIT/CERTIFICATION NUMBER | [6 empty] | UO-06-279512
PERMIT EXPIRATION DATE |  | 2002-07-21
UPPER MONITORING INTERVAL | [6 empty] | 1,288' - 1,320' |  |  |  | Ft. bls.
Sample Date |  | 2003-10-07 |  | 2003-10-14 |  | 2003-10-21 |  | 2003-10-28
Submittal Date |  | 2003-10-08 |  | 2003-10-15 |  | 2003-10-22 |  | 2003-10-29
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 49.27 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 39.26 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 73 |  | 74 |  | 75 |  | 75 |  |  | degrees (F) |  | 74.25
TDS |  | 7410 |  | 7273 |  | 7366 |  | 7360 |  |  | mg/l |  | 7352.25
CHLORIDE |  | 3850 |  | 3800 |  | 3750 |  | 3800 |  |  | mg/l |  | 3800
AMMONIA-N |  | 1.11 |  | 1.13 |  | 0.433 |  | 0.545 |  |  | mg/l |  | 0.8045
TKN |  | 1.24 |  | 1.31 |  | 1.56 |  | 1.67 |  |  | mg/l |  | 1.445
pH |  | 7.75 |  | 7.9 |  | 7.92 |  | 7.93 |  |  | Std units |  | 7.875
CONDUCTIVITY |  | 12070 |  | 12050 |  | 12040 |  | 12090 |  |  | umho/cm |  | 12062.5
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.05 | < | 0.05 | < | 0.05 | < | 0.05 |  |  | mg/l |  | 0.05
SULFATE |  | 600 |  | 800 |  | 750 |  | 850 |  |  | mg/l |  | 750
C.O.D. 'S |  | 190 |  | 180 |  | 180 |  | 170 |  |  | mg/l |  | 180
IRON |  | 0.59 |  | 0.74 |  | 0.64 |  | 0.67 |  |  | mg/l |  | 0.66
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
LOWER MONITORING INTERVAL | [6 empty] | 1,449' - 1,557' |  |  |  | Ft. bls
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 42.75 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 32.54 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 73 |  | 74 |  | 74 |  | 75 |  |  | degrees (F) |  | 74
TDS |  | 9430 |  | 9188 |  | 9130 |  | 9260 |  |  | mg/l |  | 9252
CHLORIDE |  | 5200 |  | 5200 |  | 4900 |  | 5100 |  |  | mg/l |  | 5100
AMMONIA-N |  | 9.36 |  | 9.76 |  | 8.21 |  | 8.99 |  |  | mg/l |  | 9.08
TKN |  | 11.25 |  | 11.79 |  | 11.63 |  | 11.99 |  |  | mg/l |  | 11.665
pH |  | 7.08 |  | 7.24 |  | 7.28 |  | 7.31 |  |  | Std units |  | 7.2275
CONDUCTIVITY |  | 15700 |  | 15520 |  | 15530 |  | 15580 |  |  | umho/cm |  | 15582.5
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.05 | < | 0.05 | < | 0.05 | < | 0.05 |  |  | mg/l |  | 0.05
SULFATE |  | 650 |  | 650 |  | 650 |  | 700 |  |  | mg/l |  | 662.5
C.O.D. 'S |  | 280 |  | 260 |  | 280 |  | 260 |  |  | mg/l |  | 270
IRON |  | 0.03 |  | 0.02 |  | 0.04 |  | 0.02 |  |  | mg/l |  | 0.0275
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
PAGE 24
UNDERGROUND INJECTION CONTROL SECTION
MONTHLY OPERATING REPORT DATA SUMMARY
FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT MONTH/YEAR |  |  | OCTOBER |  | 2003
I.D. NUMBER: 5006M02066 | [5 empty] | LEAD OPERATOR: |  |  |  | MIKE JUST
TELEPHONE NUMBER: (954) 523-1002
MONITORING WELL 2 DATA | [6 empty] | I.D. # 5006A11308 & 309
MW-2
PERMIT/CERTIFICATION NUMBER | [6 empty] | UO-06-279401 & 508
PERMIT EXPIRATION DATE |  | 2002-07-21
UPPER MONITORING INTERVAL | [6 empty] | 1,300' - 1,344' |  |  |  | Ft. bls.
Sample Date |  | 2003-10-07 |  | 2003-10-14 |  | 2003-10-21 |  | 2003-10-28
Submittal Date |  | 2003-10-08 |  | 2003-10-15 |  | 2003-10-22 |  | 2003-10-29
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 29.71 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 23.79 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 71 |  | 72 |  | 70 |  | 73 |  |  | degrees (F) |  | 71.5
TDS |  | 7436 |  | 7014 |  | 7144 |  | 7220 |  |  | mg/l |  | 7203.5
CHLORIDE |  | 3700 |  | 3750 |  | 3550 |  | 3750 |  |  | mg/l |  | 3687.5
AMMONIA-N |  | 0.745 |  | 0.69 |  | 0.72 |  | 0.859 |  |  | mg/l |  | 0.7535
TKN |  | 1.32 |  | 1.19 |  | 1.93 |  | 1.29 |  |  | mg/l |  | 1.4325
pH |  | 7.85 |  | 7.95 |  | 8.01 |  | 8.01 |  |  | Std units |  | 7.955
CONDUCTIVITY |  | 11860 |  | 11830 |  | 11840 |  | 11820 |  |  | umho/cm |  | 11837.5
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.05 | < | 0.05 | < | 0.05 | < | 0.05 |  |  | mg/l |  | 0.05
SULFATE |  | 650 |  | 800 |  | 750 |  | 850 |  |  | mg/l |  | 762.5
C.O.D. 'S |  | 180 |  | 170 |  | 180 |  | 170 |  |  | mg/l |  | 175
IRON |  | 1.23 |  | 5 |  | 2.62 |  | 1.98 |  |  | mg/l |  | 2.7075
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
LOWER MONITORING INTERVAL | [6 empty] | 1,970' - 2,025' |  |  |  | Ft. bls
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 42.79 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 32.31 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 70 |  | 71 |  | 69 |  | 76 |  |  | degrees (F) |  | 71.5
TDS |  | 31945 |  | 31076 |  | 31361 |  | 31390 |  |  | mg/l |  | 31443
CHLORIDE |  | 18000 |  | 17800 |  | 17800 |  | 17600 |  |  | mg/l |  | 17800
AMMONIA-N |  | 1.53 |  | 1.55 |  | 0.78 |  | 1.33 |  |  | mg/l |  | 1.2975
TKN |  | 1.73 |  | 1.98 |  | 1.95 |  | 1.99 |  |  | mg/l |  | 1.9125
pH |  | 7.27 |  | 7.29 |  | 7.31 |  | 7.34 |  |  | Std units |  | 7.3025
CONDUCTIVITY |  | 47300 |  | 47200 |  | 47300 |  | 47300 |  |  | umho/cm |  | 47275
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.05 | < | 0.05 | < | 0.05 | < | 0.05 |  |  | mg/l |  | 0.05
SULFATE |  | 1900 |  | 2600 |  | 2400 |  | 2200 |  |  | mg/l |  | 2275
C.O.D. 'S |  | 860 |  | 910 |  | 870 |  | 910 |  |  | mg/l |  | 887.5
IRON |  | 0.05 |  | 0.05 |  | 0.06 |  | 0.05 |  |  | mg/l |  | 0.0525
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
PAGE 25
UNDERGROUND INJECTION CONTROL SECTION
MONTHLY OPERATING REPORT DATA SUMMARY
FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT MONTH/YEAR |  |  | OCTOBER |  | 2003
I.D. NUMBER: 5006M02066 | [5 empty] | LEAD OPERATOR: |  |  |  | MIKE JUST
TELEPHONE NUMBER: (954) 523-1002
MONITORING WELL 2 DATA | [6 empty] | I.D. # 5006A11310
MW-3
PERMIT/CERTIFICATION NUMBER | [6 empty] | UO-06-279510
PERMIT EXPIRATION DATE |  | 2002-07-21
UPPER MONITORING INTERVAL | [6 empty] | 1,300' - 1,349' |  |  |  | Ft. bls.
Sample Date |  | 2003-10-07 |  | 2003-10-14 |  | 2003-10-21 |  | 2003-10-28
Submittal Date |  | 2003-10-08 |  | 2003-10-15 |  | 2003-10-22 |  | 2003-10-29
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 32.43 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 16.91 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 71 |  | 70 |  | 70 |  | 70 |  |  | degrees (F) |  | 70.25
TDS |  | 7382 |  | 7304 |  | 7250 |  | 72566 |  |  | mg/l |  | 23625.5
CHLORIDE |  | 3900 |  | 3800 |  | 3650 |  | 3800 |  |  | mg/l |  | 3787.5
AMMONIA-N |  | 1.11 |  | 1.14 |  | 0.779 |  | 0.88 |  |  | mg/l |  | 0.97725
TKN |  | 1.37 |  | 1.28 |  | 1.63 |  | 1.46 |  |  | mg/l |  | 1.435
pH |  | 8.08 |  | 8.07 |  | 8.09 |  | 8.05 |  |  | Std units |  | 8.0725
CONDUCTIVITY |  | 12040 |  | 11950 |  | 11980 |  | 11940 |  |  | umho/cm |  | 11977.5
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.05 | < | 0.05 | < | 0.05 | < | 0.05 |  |  | mg/l |  | 0.05
SULFATE |  | 600 |  | 850 |  | 750 |  | 850 |  |  | mg/l |  | 762.5
C.O.D. 'S |  | 190 |  | 180 |  | 180 |  | 180 |  |  | mg/l |  | 182.5
IRON |  | 1.22 |  | 0.93 |  | 0.96 |  | 0.91 |  |  | mg/l |  | 1.005
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
LOWER MONITORING INTERVAL | [6 empty] | 1,970' - 2,027' |  |  |  | Ft. bls
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 46.03 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 35.66 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 70 |  | 69 |  | 69 |  | 7669 |  |  | degrees (F) |  | 1969.25
TDS |  | 29768 |  | 28564 |  | 28729 |  | 28550 |  |  | mg/l |  | 28902.75
CHLORIDE |  | 16600 |  | 16400 |  | 15200 |  | 15400 |  |  | mg/l |  | 15900
AMMONIA-N |  | 2.56 |  | 2.51 |  | 2.14 |  | 2.32 |  |  | mg/l |  | 2.3825
TKN |  | 3.09 |  | 2.97 |  | 3.2 |  | 3.25 |  |  | mg/l |  | 3.1275
pH |  | 7.29 |  | 7.26 |  | 7.29 |  | 7.3 |  |  | Std units |  | 7.285
CONDUCTIVITY |  | 43200 |  | 43500 |  | 43400 |  | 43700 |  |  | umho/cm |  | 43450
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0.05 |  |  | # col/100ml |  | 0.0125
TOTAL PHOSPHOROUS | < | 0.05 | < | 0.05 | < | 0.05 | < | 0.05 |  |  | mg/l |  | 0.05
SULFATE |  | 1800 |  | 2300 |  | 2300 |  | 2300 |  |  | mg/l |  | 2175
C.O.D. 'S |  | 830 |  | 890 |  | 890 |  | 860 |  |  | mg/l |  | 867.5
IRON |  | 0.04 |  | 0.03 |  | 0.05 |  | 0.03 |  |  | mg/l |  | 0.0375
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
PAGE 26
UNDERGROUND INJECTION CONTROL SECTION
MONTHLY OPERATING REPORT DATA SUMMARY
FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT MONTH/YEAR |  |  | OCTOBER |  | 2003
I.D. NUMBER: 5006M02066 | [5 empty] | LEAD OPERATOR: |  |  |  | MIKE JUST
TELEPHONE NUMBER: (954) 523-1002
REGIONAL MONITORING WELL DATA
RMW-1
PERMIT NUMBER | [6 empty] | UC06-249353
PERMIT EXPIRATION DATE |  | 1997-04-27
UPPER MONITORING INTERVAL | [6 empty] | 1300' - 1339' |  |  |  | Ft. bls.
Sample Date |  | 2003-10-07
Submittal Date |  | 2003-10-08
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 44.83 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 27.48 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 69 | [8 empty] | degrees (F) |  | 69
TDS |  | 5839 | [8 empty] | mg/l |  | 5839
CHLORIDE |  | 2900 | [8 empty] | mg/l |  | 2900
AMMONIA-N |  | 0.874 | [8 empty] | mg/l |  | 0.874
TKN |  | 1.07 | [8 empty] | mg/l |  | 1.07
pH |  | 7.96 | [8 empty] | Std units |  | 7.96
CONDUCTIVITY |  | 9520 | [8 empty] | umho/cm |  | 9520
FECAL COLIFORM |  | NR | [8 empty] | # col/100ml |  | #VALUE!
TOTAL PHOSPHOROUS | < | 0.05 | [8 empty] | mg/l |  | 0.05
SULFATE |  | 500 | [8 empty] | mg/l |  | 500
C.O.D. 'S |  | 140 | [8 empty] | mg/l |  | 140
IRON |  | 0.21 | [8 empty] | mg/l |  | 0.21
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
LOWER MONITORING INTERVAL | [6 empty] | 1500' - 1600' |  |  |  | Ft. bls
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 33.03 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 20.39 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 68 | [8 empty] | degrees (F) |  | 68
TDS |  | 26899 | [8 empty] | mg/l |  | 26899
CHLORIDE |  | 16200 | [8 empty] | mg/l |  | 16200
AMMONIA-N |  | 0.498 | [8 empty] | mg/l |  | 0.498
TKN |  | 0.655 | [8 empty] | mg/l |  | 0.655
pH |  | 7.35 | [8 empty] | Std units |  | 7.35
CONDUCTIVITY |  | 41000 | [8 empty] | umho/cm |  | 41000
FECAL COLIFORM |  | NR | [8 empty] | # col/100ml |  | #VALUE!
TOTAL PHOSPHOROUS | < | 0.05 | [8 empty] | mg/l |  | 0.05
SULFATE |  | 1300 | [8 empty] | mg/l |  | 1300
C.O.D. 'S |  | 710 | [8 empty] | mg/l |  | 710
IRON |  | 0.07 | [8 empty] | mg/l |  | 0.07
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
PAGE 27
Formulas:
LEAD OPERATOR: = [LEAD OPERATOR:, row above]+1

## WELL PRN DATA
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 1 |  |  | 274 | 275 | 276 | 277 | 278 | 279 | 280 | 281 | 282 | 283 | 284 | 285 | 286 | 287 | 288 | 289 | 290 | 291 | 292 | 293 | 294 | 295 | 296 | 297 | 298 | 299 | 300 | 301 | 302 | 303 | 304
274 | 14.81 | 9.51 | 12.91 | 68.13 | 52.42 | 61.38
275 | 14.21 | 9.63 | 12.45 | 65.76 | 51.51 | 59.73 |  |  | FLOW
276 | 16.32 | 8.75 | 12.38 | 73.8 | 48.93 | 59.33 | I |  | MAX | 14.81 | 14.21 | 16.32 | 14.93 | 13.22 | 13.13 | 14.67 | 12.62 | 13.2 | 12.66 | 15.03 | 12.24 | 11.78 | 11.51 | 12.31 | 11.71 | 11.62 | 11.98 | 12.74 | 11.83 | 11.91 | 12.28 | 13.14 | 12.29 | 12.16 | 13.22 | 11.5 | 13.48 | 13.52 | 12.82 | ER
277 | 14.93 | 8.84 | 11.74 | 67.76 | 49.11 | 57.13 | N |  | MIN | 9.51 | 9.63 | 8.75 | 8.84 | 7.45 | 6.87 | 6.49 | 5.73 | 5.78 | 5.4 | 5.48 | 5.41 | 5.5 | 4.6 | 5.32 | 5.27 | 5.23 | 5.89 | 5.74 | 6.06 | 4.41 | 5 | 5.09 | 4.76 | 4.51 | 5.07 | 4.33 | 4.76 | 5.82 | 6.18 | ER
278 | 13.22 | 7.45 | 11 | 61.12 | 45.79 | 54.76 | J |  | TOT | 12.91 | 12.45 | 12.38 | 11.74 | 11 | 10.7 | 10.61 | 9.99 | 9.76 | 9.73 | 9.33 | 9.2 | 9.26 | 9.13 | 9.04 | 8.93 | 9.17 | 9.05 | 8.86 | 9.23 | 9.03 | 9.09 | 9.11 | 9.17 | 8.94 | 8.69 | 8.75 | 8.81 | 10.33 | 9.54 | ER
279 | 13.13 | 6.87 | 10.7 | 61.14 | 44.47 | 54.04 | E | INJECTION WELL ONE
280 | 14.67 | 6.49 | 10.61 | 66.63 | 43.85 | 53.84 | C |  | PSI
281 | 12.62 | 5.73 | 9.99 | 60.81 | 42.36 | 52.31 | T |  | MAX | 68.13 | 65.76 | 73.8 | 67.76 | 61.12 | 61.14 | 66.63 | 60.81 | 61.74 | 59.98 | 71.3 | 58.33 | 57.43 | 56.34 | 59.23 | 57.33 | 56.95 | 57.48 | 60.02 | 57.06 | 57.78 | 58.39 | 61.45 | 58.49 | 57.6 | 61.84 | 56.89 | 62.78 | 62.85 | 60.54 | ER
282 | 13.2 | 5.78 | 9.76 | 61.74 | 42.4 | 51.6 | O |  | MIN | 52.42 | 51.51 | 48.93 | 49.11 | 45.79 | 44.47 | 43.85 | 42.36 | 42.4 | 41.56 | 41.86 | 41.5 | 41.73 | 40.29 | 41.31 | 40.83 | 41.2 | 42.45 | 42.21 | 42.66 | 39.65 | 40.93 | 40.71 | 39.91 | 39.75 | 40.38 | 39.43 | 39.81 | 41.94 | 42.65 | ER
283 | 12.66 | 5.4 | 9.73 | 59.98 | 41.56 | 51.54 | N |  | AVG | 61.38 | 59.73 | 59.33 | 57.13 | 54.76 | 54.04 | 53.84 | 52.31 | 51.6 | 51.54 | 50.76 | 50.23 | 50.38 | 50.11 | 49.71 | 49.23 | 49.99 | 49.67 | 49.23 | 50.01 | 49.63 | 49.7 | 49.76 | 49.82 | 49.11 | 48.77 | 48.87 | 49.02 | 53.03 | 50.78 | ER
284 | 15.03 | 5.48 | 9.33 | 71.3 | 41.86 | 50.76
285 | 12.24 | 5.41 | 9.2 | 58.33 | 41.5 | 50.23 | W
286 | 11.78 | 5.5 | 9.26 | 57.43 | 41.73 | 50.38 | E
287 | 11.51 | 4.6 | 9.13 | 56.34 | 40.29 | 50.11 | L
288 | 12.31 | 5.32 | 9.04 | 59.23 | 41.31 | 49.71 | L
289 | 11.71 | 5.27 | 8.93 | 57.33 | 40.83 | 49.23 | O
290 | 11.62 | 5.23 | 9.17 | 56.95 | 41.2 | 49.99 | N
291 | 11.98 | 5.89 | 9.05 | 57.48 | 42.45 | 49.67 | E
292 | 12.74 | 5.74 | 8.86 | 60.02 | 42.21 | 49.23
293 | 11.83 | 6.06 | 9.23 | 57.06 | 42.66 | 50.01 | D
294 | 11.91 | 4.41 | 9.03 | 57.78 | 39.65 | 49.63 | A
295 | 12.28 | 5 | 9.09 | 58.39 | 40.93 | 49.7 | T
296 | 13.14 | 5.09 | 9.11 | 61.45 | 40.71 | 49.76 | A
297 | 12.29 | 4.76 | 9.17 | 58.49 | 39.91 | 49.82
298 | 12.16 | 4.51 | 8.94 | 57.6 | 39.75 | 49.11
299 | 13.22 | 5.07 | 8.69 | 61.84 | 40.38 | 48.77
300 | 11.5 | 4.33 | 8.75 | 56.89 | 39.43 | 48.87
301 | 13.48 | 4.76 | 8.81 | 62.78 | 39.81 | 49.02
302 | 13.52 | 5.82 | 10.33 | 62.85 | 41.94 | 53.03
303 | 12.82 | 6.18 | 9.54 | 60.54 | 42.65 | 50.78
304 | ER | ER | ER | ER | ER | ER
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 2 |  |  | 274 | 275 | 276 | 277 | 278 | 279 | 280 | 281 | 282 | 283 | 284 | 285 | 286 | 287 | 288 | 289 | 290 | 291 | 292 | 293 | 294 | 295 | 296 | 297 | 298 | 299 | 300 | 301 | 302 | 303 | 304
274 | 15.42 | 10.15 | 13.51 | 66.9 | 51.43 | 60.26
275 | 14.91 | 10.12 | 13.06 | 64.53 | 50.52 | 58.59 |  |  | FLOW
276 | 17.11 | 9.37 | 13.01 | 72.4 | 47.99 | 58.21 | I |  | MAX | 15.42 | 14.91 | 17.11 | 15.62 | 13.84 | 13.81 | 15.14 | 13.27 | 13.95 | 13.42 | 15.68 | 12.79 | 12.39 | 12.13 | 12.92 | 12.51 | 12.29 | 12.65 | 13.49 | 12.34 | 12.54 | 12.97 | 13.83 | 13.07 | 12.86 | 13.97 | 12.19 | 14.24 | 13.9 | 13.36 | ER
277 | 15.62 | 9.38 | 12.34 | 66.58 | 48.19 | 56.06 | N |  | MIN | 10.15 | 10.12 | 9.37 | 9.38 | 8 | 7.27 | 6.93 | 6.13 | 6.13 | 5.71 | 5.83 | 5.85 | ER | 4.84 | 5.66 | 5.67 | 5.6 | 6.18 | 6.03 | 6.41 | 4.67 | 4.51 | 5.32 | 5.03 | 4.69 | 5.31 | 4.6 | ER | 6.57 | 6.94 | ER
278 | 13.84 | 8 | 11.6 | 60.05 | 44.93 | 53.74 | J |  | TOT | 13.51 | 13.06 | 13.01 | 12.34 | 11.6 | 11.3 | 11.18 | 10.58 | 10.35 | 10.32 | 9.89 | 9.73 | 8.87 | 9.66 | 9.57 | 9.47 | 9.69 | 9.57 | 9.38 | 9.78 | 9.56 | 9.63 | 9.68 | 9.75 | 9.52 | 9.26 | 9.33 | ER | 10.92 | 10.18 | ER
279 | 13.81 | 7.27 | 11.3 | 59.98 | 43.64 | 53.03 | E | INJECTION WELL TWO
280 | 15.14 | 6.93 | 11.18 | 64.93 | 43.02 | 52.8 | C |  | PSI
281 | 13.27 | 6.13 | 10.58 | 59.65 | 41.57 | 51.33 | T |  | MAX | 66.9 | 64.53 | 72.4 | 66.58 | 60.05 | 59.98 | 64.93 | 59.65 | 60.53 | 58.86 | 70.1 | 57.41 | 56.48 | 57.35 | 58.08 | 56.22 | 55.85 | 56.51 | 58.88 | 55.93 | 56.65 | 57.23 | 60.23 | 57.35 | 56.52 | 60.76 | 55.94 | 61.62 | 61.62 | 59.43 | ER
282 | 13.95 | 6.13 | 10.35 | 60.53 | 41.59 | 50.61 | I |  | MIN | 51.43 | 50.52 | 47.99 | 48.19 | 44.93 | 43.64 | 43.02 | 41.57 | 41.59 | 40.77 | 41.08 | 40.71 | 40.94 | 39.53 | 40.52 | 40.02 | 40.41 | 41.62 | 41.38 | 41.81 | 38.91 | 39.64 | 39.91 | 39.15 | 38.99 | 39.61 | 38.66 | 39.05 | 41.16 | 41.79 | ER
283 | 13.42 | 5.71 | 10.32 | 58.86 | 40.77 | 50.56 | O |  | AVG | 60.26 | 58.59 | 58.21 | 56.06 | 53.74 | 53.03 | 52.8 | 51.33 | 50.61 | 50.56 | 49.84 | 49.3 | 49.45 | 49.18 | 48.78 | 48.3 | 49.04 | 48.74 | 48.28 | 49.07 | 48.73 | 48.78 | 48.84 | 48.9 | 48.17 | 47.86 | 47.96 | 48.09 | 52.03 | 49.82 | ER
284 | 15.68 | 5.83 | 9.89 | 70.1 | 41.08 | 49.84 | N
285 | 12.79 | 5.85 | 9.73 | 57.41 | 40.71 | 49.3
286 | 12.39 | ER | 8.87 | 56.48 | 40.94 | 49.45 | W
287 | 12.13 | 4.84 | 9.66 | 55.4 | 39.53 | 49.18 | E
288 | 12.92 | 5.66 | 9.57 | 58.08 | 40.52 | 48.78 | L
289 | 12.51 | 5.67 | 9.47 | 56.22 | 40.02 | 48.3 | L
290 | 12.29 | 5.6 | 9.69 | 55.85 | 40.41 | 49.04
291 | 12.65 | 6.18 | 9.57 | 56.51 | 41.62 | 48.74 | T
292 | 13.49 | 6.03 | 9.38 | 58.88 | 41.38 | 48.28 | W
293 | 12.34 | 6.41 | 9.78 | 55.93 | 41.81 | 49.07 | O
294 | 12.54 | 4.67 | 9.56 | 56.65 | 38.91 | 48.73
295 | 12.97 | 4.51 | 9.63 | 57.23 | 39.64 | 48.78 | D
296 | 13.83 | 5.32 | 9.68 | 60.23 | 39.91 | 48.84 | A
297 | 13.07 | 5.03 | 9.75 | 57.35 | 39.15 | 48.9 | T
298 | 12.86 | 4.69 | 9.52 | 56.52 | 38.99 | 48.17 | A
299 | 13.97 | 5.31 | 9.26 | 60.76 | 39.61 | 47.86
300 | 12.19 | 4.6 | 9.33 | 55.94 | 38.66 | 47.96
301 | 14.24 | ER | ER | 61.62 | 39.05 | 48.09
302 | 13.9 | 6.57 | 10.92 | 61.62 | 41.16 | 52.03
303 | 13.36 | 6.94 | 10.18 | 59.43 | 41.79 | 49.82
304 | ER | ER | ER | ER | ER | ER
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 3 |  |  | 274 | 275 | 276 | 277 | 278 | 279 | 280 | 281 | 282 | 283 | 284 | 285 | 286 | 287 | 288 | 289 | 290 | 291 | 292 | 293 | 294 | 295 | 296 | 297 | 298 | 299 | 300 | 301 | 302 | 303 | 304
274 | 13.29 | 8.57 | 11.57 | 68.56 | 52.65 | 61.71
275 | 12.69 | 8.62 | 11.12 | 66.13 | 51.7 | 60.01 |  |  | FLOW
276 | 14.6 | 7.8 | 11.06 | 74.2 | 49.11 | 59.63 | I |  | MAX | 13.29 | 12.69 | 14.6 | 13.36 | 11.78 | 11.68 | 13.33 | 11.36 | 11.88 | 11.4 | 13.51 | 10.95 | 10.57 | 10.28 | 10.96 | 10.55 | 10.39 | 10.73 | 11.41 | 10.4 | 10.63 | 10.92 | 11.64 | 11.01 | 10.79 | 11.83 | 10.32 | 11.96 | 12.03 | 11.47 | ER
277 | 13.36 | 7.89 | 10.46 | 68.1 | 49.3 | 57.39 | N |  | MIN | 8.57 | 8.62 | 7.8 | 7.89 | 6.61 | 5.94 | 5.73 | 5.05 | 5.03 | 4.64 | 4.76 | 4.72 | ER | 3.91 | 4.6 | 4.64 | 4.53 | 5.07 | 4.92 | 5.27 | 3.76 | 4.2 | 4.37 | 4.03 | 3.75 | 4.23 | 3.67 | 3.99 | 5 | 5.41 | ER
278 | 11.78 | 6.61 | 9.8 | 61.49 | 45.95 | 55.06 | J |  | TOT | 11.57 | 11.12 | 11.06 | 10.46 | 9.8 | 9.51 | 9.43 | 8.93 | 8.73 | 8.67 | 8.33 | 8.21 | 7.97 | 8.13 | 8.04 | 7.93 | 8.14 | 8.04 | 7.86 | 8.19 | 8.02 | 8.07 | 8.09 | 8.15 | 7.93 | 7.71 | 7.78 | 7.83 | 9.21 | 8.5 | ER
279 | 11.68 | 5.94 | 9.51 | 61.46 | 44.62 | 54.25 | E | INJECTION WELL THREE
280 | 13.33 | 5.73 | 9.43 | 67.76 | 44 | 54.06 | C |  | PSI
281 | 11.36 | 5.05 | 8.93 | 61.16 | 42.5 | 52.55 | T |  | MAX | 68.56 | 66.13 | 74.2 | 68.1 | 61.49 | 61.46 | 67.76 | 61.16 | 62.08 | 60.31 | 71.8 | 58.67 | 57.74 | 56.66 | 59.57 | 57.67 | 57.22 | 57.8 | 60.36 | 57.34 | 58.08 | 58.7 | 61.77 | 58.81 | 57.91 | 62.2 | 57.2 | 63.14 | 63.2 | 60.88 | ER
282 | 11.88 | 5.03 | 8.73 | 62.08 | 42.54 | 51.85 | I |  | MIN | 52.65 | 51.7 | 49.11 | 49.3 | 45.95 | 44.62 | 44 | 42.5 | 42.54 | 41.69 | 42 | 41.63 | 41.86 | 40.4 | 41.44 | 40.96 | 41.34 | 42.61 | 42.34 | 42.8 | 39.77 | 41.04 | 40.84 | 40.02 | 39.84 | 40.51 | 39.52 | 39.92 | 42.08 | 42.78 | ER
283 | 11.4 | 4.64 | 8.67 | 60.31 | 41.69 | 51.77 | O |  | AVG | 61.71 | 60.01 | 59.63 | 57.39 | 55.06 | 54.25 | 54.06 | 52.55 | 51.85 | 51.77 | 50.99 | 50.47 | 50.6 | 50.33 | 49.94 | 49.42 | 50.19 | 49.89 | 49.44 | 50.23 | 49.81 | 49.94 | 49.96 | 50.04 | 49.32 | 48.98 | 49.09 | 49.21 | 53.29 | 51.01 | ER
284 | 13.51 | 4.76 | 8.33 | 71.8 | 42 | 50.99 | N
285 | 10.95 | 4.72 | 8.21 | 58.67 | 41.63 | 50.47
286 | 10.57 | ER | 7.97 | 57.74 | 41.86 | 50.6 | W
287 | 10.28 | 3.91 | 8.13 | 56.66 | 40.4 | 50.33 | E
288 | 10.96 | 4.6 | 8.04 | 59.57 | 41.44 | 49.94 | L
289 | 10.55 | 4.64 | 7.93 | 57.67 | 40.96 | 49.42 | L
290 | 10.39 | 4.53 | 8.14 | 57.22 | 41.34 | 50.19
291 | 10.73 | 5.07 | 8.04 | 57.8 | 42.61 | 49.89 | T
292 | 11.41 | 4.92 | 7.86 | 60.36 | 42.34 | 49.44 | H
293 | 10.4 | 5.27 | 8.19 | 57.34 | 42.8 | 50.23 | R
294 | 10.63 | 3.76 | 8.02 | 58.08 | 39.77 | 49.81 | E
295 | 10.92 | 4.2 | 8.07 | 58.7 | 41.04 | 49.94 | E
296 | 11.64 | 4.37 | 8.09 | 61.77 | 40.84 | 49.96
297 | 11.01 | 4.03 | 8.15 | 58.81 | 40.02 | 50.04 | D
298 | 10.79 | 3.75 | 7.93 | 57.91 | 39.84 | 49.32 | A
299 | 11.83 | 4.23 | 7.71 | 62.2 | 40.51 | 48.98 | T
300 | 10.32 | 3.67 | 7.78 | 57.2 | 39.52 | 49.09 | A
301 | 11.96 | 3.99 | 7.83 | 63.14 | 39.92 | 49.21
302 | 12.03 | 5 | 9.21 | 63.2 | 42.08 | 53.29
303 | 11.47 | 5.41 | 8.5 | 60.88 | 42.78 | 51.01
304 | ER | ER | ER | ER | ER | ER
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 4 |  |  | 274 | 275 | 276 | 277 | 278 | 279 | 280 | 281 | 282 | 283 | 284 | 285 | 286 | 287 | 288 | 289 | 290 | 291 | 292 | 293 | 294 | 295 | 296 | 297 | 298 | 299 | 300 | 301 | 302 | 303 | 304
274 | ER | ER | ER | 38.94 | 37.22 | 38.18
275 | ER | ER | ER | 38.67 | 37.47 | 38.13 |  |  | FLOW
276 | ER | ER | ER | 39.16 | 37.16 | 38.05 | I |  | MAX | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | 0.15 | 0.16 | 0.15 | ER
277 | ER | ER | ER | 38.7 | 37.19 | 37.86 | N |  | MIN | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | 0.13 | 0.13 | ER
278 | ER | ER | ER | 38.25 | 36.92 | 37.68 | J |  | TOT | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | 0.14 | 0.13 | ER
279 | ER | ER | ER | 38.19 | 36.68 | 37.59 | E | INJECTION WELL FOUR
280 | ER | ER | ER | 38.6 | 36.56 | 37.52 | C |  | PSI
281 | ER | ER | ER | 38.35 | 36.45 | 37.48 | T |  | MAX | 38.94 | 38.67 | 39.16 | 38.7 | 38.25 | 38.19 | 38.6 | 38.35 | 38.33 | 38.14 | 38.93 | 37.99 | 37.92 | 59.98 | 37.82 | 37.65 | 37.63 | 37.72 | 37.88 | 37.63 | 37.65 | 37.83 | 38.17 | 37.92 | 37.74 | 38.21 | 37.87 | 38.32 | 38.19 | 38.03 | ER
282 | ER | ER | ER | 38.33 | 36.4 | 37.34 | I |  | MIN | 37.22 | 37.47 | 37.16 | 37.19 | 36.92 | 36.68 | 36.56 | 36.45 | 36.4 | 36.18 | 36.09 | 36.07 | 36.08 | 29.78 | 36.06 | 35.94 | 36.02 | 36.21 | 36.19 | 36.22 | 35.9 | 35.62 | 35.97 | 35.92 | 35.78 | 35.76 | 35.64 | 35.8 | 36.24 | 36.21 | ER
283 | ER | ER | ER | 38.14 | 36.18 | 37.25 | O |  | AVG | 38.18 | 38.13 | 38.05 | 37.86 | 37.68 | 37.59 | 37.52 | 37.48 | 37.34 | 37.25 | 37.12 | 37.1 | 37.1 | 37.07 | 37 | 36.9 | 36.99 | 37.01 | 36.95 | 36.99 | 36.95 | 36.98 | 37.02 | 36.99 | 36.84 | 36.81 | 36.92 | 36.98 | 37.38 | 37.21 | ER
284 | ER | ER | ER | 38.93 | 36.09 | 37.12 | N
285 | ER | ER | ER | 37.99 | 36.07 | 37.1
286 | ER | ER | ER | 37.92 | 36.08 | 37.1 | W
287 | ER | ER | ER | 37.83 | 29.78 | 37.07 | E
288 | ER | ER | ER | 37.82 | 36.06 | 37 | L
289 | ER | ER | ER | 37.65 | 35.94 | 36.9 | L
290 | ER | ER | ER | 37.63 | 36.02 | 36.99
291 | ER | ER | ER | 37.72 | 36.21 | 37.01 | F
292 | ER | ER | ER | 37.88 | 36.19 | 36.95 | O
293 | ER | ER | ER | 37.63 | 36.22 | 36.99 | U
294 | ER | ER | ER | 37.65 | 35.9 | 36.95 | R
295 | ER | ER | ER | 37.83 | 35.62 | 36.98
296 | ER | ER | ER | 38.17 | 35.97 | 37.02 | D
297 | ER | ER | ER | 37.92 | 35.92 | 36.99 | A
298 | ER | ER | ER | 37.74 | 35.78 | 36.84 | T
299 | ER | ER | ER | 38.21 | 35.76 | 36.81 | A
300 | ER | ER | ER | 37.87 | 35.64 | 36.92
301 | 0.15 | ER | ER | 38.32 | 35.8 | 36.98
302 | 0.16 | 0.13 | 0.14 | 38.19 | 36.24 | 37.38
303 | 0.15 | 0.13 | 0.13 | 38.03 | 36.21 | 37.21
304 | ER | ER | ER | ER | ER | ER
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 5 |  |  | 274 | 275 | 276 | 277 | 278 | 279 | 280 | 281 | 282 | 283 | 284 | 285 | 286 | 287 | 288 | 289 | 290 | 291 | 292 | 293 | 294 | 295 | 296 | 297 | 298 | 299 | 300 | 301 | 302 | 303 | 304
274 | 12.99 | 8.54 | 11.36 | 67.78 | 52.25 | 61.17
275 | 12.47 | 8.63 | 10.96 | 65.54 | 51.29 | 59.51 |  |  | FLOW
276 | 14.31 | 7.33 | 10.89 | 73.7 | 48.78 | 59.07 | I |  | MAX | 12.99 | 12.47 | 14.31 | 13.08 | 11.57 | 11.51 | 12.93 | 11.14 | 11.67 | 11.23 | 13.36 | 10.8 | 10.44 | 10.23 | 10.89 | 10.48 | 10.35 | 10.61 | 11.31 | 10.39 | 10.58 | 10.82 | 11.55 | 10.89 | 10.71 | 11.68 | 10.25 | 11.89 | 11.88 | 11.38 | ER
277 | 13.08 | 7.97 | 10.35 | 67.53 | 48.92 | 56.94 | N |  | MIN | 8.54 | 8.63 | 7.33 | 7.97 | 6.84 | 6.25 | ER | 5.31 | 5.32 | 4.44 | 5.1 | 5.09 | 5.16 | 4.26 | 4.96 | 4.91 | 4.86 | 5.37 | 5.26 | 5.57 | 4.17 | ER | 4.64 | 4.44 | 4.17 | 4.64 | 4.04 | 4.34 | 5.39 | 5.74 | ER
278 | 11.57 | 6.84 | 9.74 | 60.88 | 45.61 | 54.54 | J |  | TOT | 11.36 | 10.96 | 10.89 | 10.35 | 9.74 | 9.49 | 9.07 | 8.92 | 8.73 | 8.68 | 8.38 | 8.28 | 8.32 | 8.21 | 8.12 | 8.03 | 8.23 | 8.14 | 7.98 | 8.29 | 8.14 | 7.97 | 8.16 | 8.22 | 8.02 | 7.82 | 7.88 | 7.94 | 9.2 | 8.56 | ER
279 | 11.51 | 6.25 | 9.49 | 60.99 | 44.31 | 53.8 | E | INJECTION WELL FIVE
280 | 12.93 | ER | 9.07 | 67.16 | 36.1 | 52.87 | C |  | PSI
281 | 11.14 | 5.31 | 8.92 | 60.65 | 42.25 | 52.11 | T |  | MAX | 67.78 | 65.54 | 73.7 | 67.53 | 60.88 | 60.99 | 67.16 | 60.65 | 61.66 | 59.87 | 71 | 58.03 | 57.26 | 56.18 | 59.06 | 57.21 | 56.76 | 57.35 | 59.88 | 56.92 | 57.65 | 58.37 | 61.34 | 58.39 | 57.4 | 61.65 | 56.66 | 62.68 | 62.76 | 60.38 | ER
282 | 11.67 | 5.32 | 8.73 | 61.66 | 42.29 | 51.39 | I |  | MIN | 52.25 | 51.29 | 48.78 | 48.92 | 45.61 | 44.31 | 36.1 | 42.25 | 42.29 | 41.42 | 41.71 | 41.37 | 41.6 | 40.17 | 41.2 | 40.79 | 41.1 | 42.36 | 42.1 | 42.54 | 39.55 | 35.38 | 40.67 | 39.87 | 39.61 | 40.27 | 39.32 | 39.76 | 41.79 | 42.57 | ER
283 | 11.23 | 4.44 | 8.68 | 59.87 | 41.42 | 51.29 | O |  | AVG | 61.17 | 59.51 | 59.07 | 56.94 | 54.54 | 53.8 | 52.87 | 52.11 | 51.39 | 51.29 | 50.57 | 50.06 | 50.2 | 49.91 | 49.54 | 49.01 | 49.83 | 49.51 | 49.04 | 49.83 | 49.49 | 49.35 | 49.62 | 49.68 | 48.95 | 48.62 | 48.73 | 48.89 | 52.84 | 50.56 | ER
284 | 13.36 | 5.1 | 8.38 | 71 | 41.71 | 50.57 | N
285 | 10.8 | 5.09 | 8.28 | 58.03 | 41.37 | 50.06
286 | 10.44 | 5.16 | 8.32 | 57.26 | 41.6 | 50.2 | W
287 | 10.23 | 4.26 | 8.21 | 56.18 | 40.17 | 49.91 | E
288 | 10.89 | 4.96 | 8.12 | 59.06 | 41.2 | 49.54 | L
289 | 10.48 | 4.91 | 8.03 | 57.21 | 40.79 | 49.01 | L
290 | 10.35 | 4.86 | 8.23 | 56.76 | 41.1 | 49.83
291 | 10.61 | 5.37 | 8.14 | 57.35 | 42.36 | 49.51 | F
292 | 11.31 | 5.26 | 7.98 | 59.88 | 42.1 | 49.04 | I
293 | 10.39 | 5.57 | 8.29 | 56.92 | 42.54 | 49.83 | V
294 | 10.58 | 4.17 | 8.14 | 57.65 | 39.55 | 49.49 | E
295 | 10.82 | ER | 7.97 | 58.37 | 35.38 | 49.35
296 | 11.55 | 4.64 | 8.16 | 61.34 | 40.67 | 49.62 | D
297 | 10.89 | 4.44 | 8.22 | 58.39 | 39.87 | 49.68 | A
298 | 10.71 | 4.17 | 8.02 | 57.4 | 39.61 | 48.95 | T
299 | 11.68 | 4.64 | 7.82 | 61.65 | 40.27 | 48.62 | A
300 | 10.25 | 4.04 | 7.88 | 56.66 | 39.32 | 48.73
301 | 11.89 | 4.34 | 7.94 | 62.68 | 39.76 | 48.89
302 | 11.88 | 5.39 | 9.2 | 62.76 | 41.79 | 52.84
303 | 11.38 | 5.74 | 8.56 | 60.38 | 42.57 | 50.56
304 | ER | ER | ER | ER | ER | ER

## RMW PRN DATA
julian | u-avg | u-min | u-max | l-avg | l-min | l-max
274 | 22.56 | 22.47 | 22.65 | 44.45 | 44.38 | 44.53 | R |  |  | 274 | 275 | 276 | 277 | 278 | 279 | 280 | 281 | 282 | 283 | 284 | 285 | 286 | 287 | 288 | 289 | 290 | 291 | 292 | 293 | 294 | 295 | 296 | 297 | 298 | 299 | 300 | 301 | 302 | 303 | 304
275 | 22.68 | 22.59 | 22.76 | 44.59 | 44.51 | 44.66 | E
276 | 22.72 | 22.63 | 22.8 | 44.69 | 44.63 | 44.75 | G |  | LOW
277 | 22.73 | 22.64 | 22.8 | 44.75 | 44.69 | 44.79 | I |  | MIN | 22.47 | 22.59 | 22.63 | 22.64 | 22.62 | 20.39 | 20.8 | 22.41 | 22.61 | 22.73 | 22.75 | 22.76 | 22.73 | 22.72 | 22.69 | 22.6 | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER
278 | 22.7 | 22.62 | 22.76 | 44.77 | 44.71 | 44.82 | O |  | MAX | 22.65 | 22.76 | 22.8 | 22.8 | 22.76 | 22.72 | 33.03 | 22.64 | 22.74 | 22.82 | 22.82 | 22.82 | 22.84 | 22.88 | 22.82 | 22.7 | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER
279 | 21.48 | 20.39 | 22.72 | 35.42 | 30.66 | 44.83 | N |  | AVG | 22.56 | 22.68 | 22.72 | 22.73 | 22.7 | 21.48 | 21.9 | 22.53 | 22.69 | 22.77 | 22.78 | 22.79 | 22.79 | 22.8 | 22.76 | 22.67 | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER
280 | 21.9 | 20.8 | 33.03 | 40.1 | 27.48 | 44.05 | A | RMW
281 | 22.53 | 22.41 | 22.64 | 44.15 | 44.05 | 44.24 | L |  | UP
282 | 22.69 | 22.61 | 22.74 | 44.25 | 44.18 | 44.31 |  |  | MIN | 44.38 | 44.51 | 44.63 | 44.69 | 44.71 | 30.66 | 27.48 | 44.05 | 44.18 | 44.24 | 44.23 | 44.22 | 44.21 | 44.21 | 44.15 | 44.1 | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER
283 | 22.77 | 22.73 | 22.82 | 44.29 | 44.24 | 44.34 | M |  | MAX | 44.53 | 44.66 | 44.75 | 44.79 | 44.82 | 44.83 | 44.05 | 44.24 | 44.31 | 44.34 | 44.34 | 44.33 | 44.32 | 44.34 | 44.28 | 44.18 | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER
284 | 22.78 | 22.75 | 22.82 | 44.29 | 44.23 | 44.34 | O |  | AVG | 44.45 | 44.59 | 44.69 | 44.75 | 44.77 | 35.42 | 40.1 | 44.15 | 44.25 | 44.29 | 44.29 | 44.28 | 44.27 | 44.27 | 44.23 | 44.15 | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER
285 | 22.79 | 22.76 | 22.82 | 44.28 | 44.22 | 44.33 | N
286 | 22.79 | 22.73 | 22.84 | 44.27 | 44.21 | 44.32 | I
287 | 22.8 | 22.72 | 22.88 | 44.27 | 44.21 | 44.34 | T
288 | 22.76 | 22.69 | 22.82 | 44.23 | 44.15 | 44.28 | O
289 | 22.67 | 22.6 | 22.7 | 44.15 | 44.1 | 44.18 | R
290 | ER | ER | ER | ER | ER | ER
291 | ER | ER | ER | ER | ER | ER | W
292 | ER | ER | ER | ER | ER | ER | E
293 | ER | ER | ER | ER | ER | ER | L
294 | ER | ER | ER | ER | ER | ER | L
295 | ER | ER | ER | ER | ER | ER
296 | ER | ER | ER | ER | ER | ER
297 | ER | ER | ER | ER | ER | ER | R
298 | ER | ER | ER | ER | ER | ER | M
299 | ER | ER | ER | ER | ER | ER | W
300 | ER | ER | ER | ER | ER | ER
301 | ER | ER | ER | ER | ER | ER | O
302 | ER | ER | ER | ER | ER | ER | N
303 | ER | ER | ER | ER | ER | ER | E
304 | ER | ER | ER | ER | ER | ER
274 | 42.39 | 42.23 | 42.56 | 48.91 | 48.68 | 49.06 | M |  |  | 274 | 275 | 276 | 277 | 278 | 279 | 280 | 281 | 282 | 283 | 284 | 285 | 286 | 287 | 288 | 289 | 290 | 291 | 292 | 293 | 294 | 295 | 296 | 297 | 298 | 299 | 300 | 301 | 302 | 303 | 304
275 | 42.47 | 42.39 | 42.65 | 48.97 | 48.85 | 49.17 | O
276 | 42.5 | 42.47 | 42.67 | 49.02 | 48.87 | 49.2 | N |  | LOW
277 | 42.53 | 42.49 | 42.64 | 49.02 | 48.87 | 49.19 | I |  | MIN | 42.23 | 42.39 | 42.47 | 42.49 | 42.46 | 32.54 | 32.54 | 42.26 | 42.43 | 42.52 | 42.46 | 42.42 | 36.48 | 36.38 | 42.2 | 42.13 | 42.17 | 42.27 | 42.25 | 35.14 | 35.16 | 42.06 | 42.17 | 42.1 | 42.01 | 42.06 | 36.27 | 36.25 | 42.13 | 42.11 | ER
278 | 42.53 | 42.46 | 42.64 | 48.99 | 48.82 | 49.15 | T |  | MAX | 42.56 | 42.65 | 42.67 | 42.64 | 42.64 | 42.6 | 42.31 | 42.43 | 42.66 | 42.75 | 42.61 | 42.63 | 42.49 | 42.43 | 42.41 | 42.3 | 42.35 | 42.45 | 42.51 | 42.33 | 42.19 | 42.37 | 42.53 | 42.33 | 42.26 | 42.35 | 42.44 | 42.25 | 42.39 | 42.3 | ER
279 | 35.26 | 32.54 | 42.6 | 47.35 | 46.39 | 49.07 | O |  | AVG | 42.39 | 42.47 | 42.5 | 42.53 | 42.53 | 35.26 | 39.58 | 42.39 | 42.5 | 42.55 | 42.52 | 42.48 | 38.32 | 40.56 | 42.26 | 42.17 | 42.28 | 42.38 | 42.41 | 37.5 | 40.07 | 42.28 | 42.36 | 42.15 | 42.08 | 42.27 | 39 | 40.29 | 42.21 | 42.14 | ER
280 | 39.58 | 32.54 | 42.31 | 48.33 | 45.89 | 49.27 | R | MW-1
281 | 42.39 | 42.26 | 42.43 | 48.94 | 48.75 | 49.07 |  |  | UP
282 | 42.5 | 42.43 | 42.66 | 48.97 | 48.79 | 49.08 | W |  | MIN | 48.68 | 48.85 | 48.87 | 48.87 | 48.82 | 46.39 | 45.89 | 48.75 | 48.79 | 48.85 | 48.82 | 48.78 | 44.82 | 41.83 | 48.74 | 48.61 | 48.62 | 48.69 | 48.61 | 39.26 | 39.71 | 48.61 | 48.64 | 48.5 | 48.42 | 48.38 | 44.53 | 44.8 | 48.61 | 48.47 | ER
283 | 42.55 | 42.52 | 42.75 | 48.97 | 48.85 | 49.08 | E |  | MAX | 49.06 | 49.17 | 49.2 | 49.19 | 49.15 | 49.07 | 49.27 | 49.07 | 49.08 | 49.08 | 49.04 | 49.03 | 48.93 | 49.1 | 48.94 | 48.83 | 48.87 | 48.93 | 48.88 | 48.82 | 49.09 | 49 | 49 | 48.88 | 48.77 | 48.82 | 48.93 | 49 | 48.9 | 48.78 | ER
284 | 42.52 | 42.46 | 42.61 | 48.97 | 48.82 | 49.04 | L |  | AVG | 48.91 | 48.97 | 49.02 | 49.02 | 48.99 | 47.35 | 48.33 | 48.94 | 48.97 | 48.97 | 48.97 | 48.95 | 46.4 | 47.88 | 48.92 | 48.71 | 48.86 | 48.9 | 48.79 | 42.58 | 46.22 | 48.8 | 48.85 | 48.69 | 48.56 | 48.63 | 46.54 | 47.69 | 48.73 | 48.61 | ER
285 | 42.48 | 42.42 | 42.63 | 48.95 | 48.78 | 49.03 | L
286 | 38.32 | 36.48 | 42.49 | 46.4 | 44.82 | 48.93
287 | 40.56 | 36.38 | 42.43 | 47.88 | 41.83 | 49.1 | O
288 | 42.26 | 42.2 | 42.41 | 48.92 | 48.74 | 48.94 | N
289 | 42.17 | 42.13 | 42.3 | 48.71 | 48.61 | 48.83 | E
290 | 42.28 | 42.17 | 42.35 | 48.86 | 48.62 | 48.87
291 | 42.38 | 42.27 | 42.45 | 48.9 | 48.69 | 48.93 | I
292 | 42.41 | 42.25 | 42.51 | 48.79 | 48.61 | 48.88 | N
293 | 37.5 | 35.14 | 42.33 | 42.58 | 39.26 | 48.82 | J
294 | 40.07 | 35.16 | 42.19 | 46.22 | 39.71 | 49.09 | E
295 | 42.28 | 42.06 | 42.37 | 48.8 | 48.61 | 49 | C
296 | 42.36 | 42.17 | 42.53 | 48.85 | 48.64 | 49 | T
297 | 42.15 | 42.1 | 42.33 | 48.69 | 48.5 | 48.88 | I
298 | 42.08 | 42.01 | 42.26 | 48.56 | 48.42 | 48.77 | O
299 | 42.27 | 42.06 | 42.35 | 48.63 | 48.38 | 48.82 | N
300 | 39 | 36.27 | 42.44 | 46.54 | 44.53 | 48.93
301 | 40.29 | 36.25 | 42.25 | 47.69 | 44.8 | 49 | W
302 | 42.21 | 42.13 | 42.39 | 48.73 | 48.61 | 48.9 | E
303 | 42.14 | 42.11 | 42.3 | 48.61 | 48.47 | 48.78 | L
304 | ER | ER | ER | ER | ER | ER | L
274 | 42.33 | 42.13 | 42.42 | ER | ER | ER | M |  |  | 274 | 275 | 276 | 277 | 278 | 279 | 280 | 281 | 282 | 283 | 284 | 285 | 286 | 287 | 288 | 289 | 290 | 291 | 292 | 293 | 294 | 295 | 296 | 297 | 298 | 299 | 300 | 301 | 302 | 303 | 304
275 | 42.48 | 42.38 | 42.6 | ER | ER | ER | O
276 | 42.54 | 42.5 | 42.73 | ER | ER | ER | N |  | LOW
277 | 42.66 | 42.58 | 42.77 | ER | ER | ER | I |  | MIN | 42.13 | 42.38 | 42.5 | 42.58 | 42.62 | 32.31 | 32.32 | 42.3 | 42.45 | 42.56 | 42.59 | 42.6 | 37.32 | 36.57 | 42.27 | 42.26 | 42.34 | 42.44 | 42.43 | 38.24 | 36.47 | 42.12 | 42.32 | 42.26 | 42.23 | 42.25 | 37.16 | 37.07 | 42.22 | 42.23 | ER
278 | 42.72 | 42.62 | 42.79 | ER | ER | ER | T |  | MAX | 42.42 | 42.6 | 42.73 | 42.77 | 42.79 | 42.79 | 42.37 | 42.56 | 42.64 | 42.69 | 42.68 | 42.72 | 42.67 | 42.32 | 42.38 | 42.4 | 42.5 | 42.61 | 42.6 | 42.56 | 42.18 | 42.47 | 42.54 | 42.45 | 42.4 | 42.5 | 42.59 | 42.28 | 42.39 | 42.39 | ER
279 | 35.25 | 32.31 | 42.79 | ER | ER | ER | O |  | AVG | 42.33 | 42.48 | 42.54 | 42.66 | 42.72 | 35.25 | 39.45 | 42.46 | 42.5 | 42.59 | 42.6 | 42.61 | 39.04 | 40.77 | 42.38 | 42.37 | 42.44 | 42.5 | 42.51 | 39.71 | 40.9 | 42.35 | 42.48 | 42.43 | 42.39 | 42.44 | 39.43 | 40.52 | 42.38 | 42.37 | ER
280 | 39.45 | 32.32 | 42.37 | ER | ER | ER | R | MW-2
281 | 42.46 | 42.3 | 42.56 | ER | ER | ER |  |  | UP
282 | 42.5 | 42.45 | 42.64 | ER | ER | ER | W |  | MIN | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | 23.79 | 28.34 | 28.2 | ER
283 | 42.59 | 42.56 | 42.69 | ER | ER | ER | E |  | MAX | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | 26.15 | 29.55 | 29.71 | 29.41 | ER
284 | 42.6 | 42.59 | 42.68 | ER | ER | ER | L |  | AVG | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | ER | 15.41 | 27.37 | 28.86 | 28.76 | ER
285 | 42.61 | 42.6 | 42.72 | ER | ER | ER | L
286 | 39.04 | 37.32 | 42.67 | ER | ER | ER
287 | 40.77 | 36.57 | 42.32 | ER | ER | ER | T
288 | 42.38 | 42.27 | 42.38 | ER | ER | ER | W
289 | 42.37 | 42.26 | 42.4 | ER | ER | ER | O
290 | 42.44 | 42.34 | 42.5 | ER | ER | ER
291 | 42.5 | 42.44 | 42.61 | ER | ER | ER | I
292 | 42.51 | 42.43 | 42.6 | ER | ER | ER | N
293 | 39.71 | 38.24 | 42.56 | ER | ER | ER | J
294 | 40.9 | 36.47 | 42.18 | ER | ER | ER | E
295 | 42.35 | 42.12 | 42.47 | ER | ER | ER | C
296 | 42.48 | 42.32 | 42.54 | ER | ER | ER | T
297 | 42.43 | 42.26 | 42.45 | ER | ER | ER | I
298 | 42.39 | 42.23 | 42.4 | ER | ER | ER | O
299 | 42.44 | 42.25 | 42.5 | ER | ER | ER | N
300 | 39.43 | 37.16 | 42.59 | 15.41 | ER | 26.15
301 | 40.52 | 37.07 | 42.28 | 27.37 | 23.79 | 29.55 | W
302 | 42.38 | 42.22 | 42.39 | 28.86 | 28.34 | 29.71 | E
303 | 42.37 | 42.23 | 42.39 | 28.76 | 28.2 | 29.41 | L
304 | ER | ER | ER | ER | ER | ER | L
274 | 45.46 | 45.36 | 45.63 | 31.92 | 31.71 | 32.13 | M |  |  | 274 | 275 | 276 | 277 | 278 | 279 | 280 | 281 | 282 | 283 | 284 | 285 | 286 | 287 | 288 | 289 | 290 | 291 | 292 | 293 | 294 | 295 | 296 | 297 | 298 | 299 | 300 | 301 | 302 | 303 | 304
275 | 45.83 | 45.62 | 45.84 | 32.1 | 31.99 | 32.32 | O
276 | 45.89 | 45.75 | 45.98 | 32.28 | 32.1 | 32.43 | N |  | LOW
277 | 45.94 | 45.83 | 46.01 | 32.31 | 32.14 | 32.42 | I |  | MIN | 45.36 | 45.62 | 45.75 | 45.83 | 45.86 | 40.07 | 40.07 | 45.48 | 45.64 | 45.75 | 45.78 | 45.79 | 37.19 | 37.15 | 45.36 | 45.36 | 45.47 | 45.58 | 45.58 | 35.66 | 35.67 | 45.16 | 45.39 | 45.36 | 45.34 | 45.37 | 37.45 | 37.38 | 45.3 | 45.31 | ER
278 | 45.98 | 45.86 | 46.03 | 32.25 | 32.12 | 32.38 | T |  | MAX | 45.63 | 45.84 | 45.98 | 46.01 | 46.03 | 46.01 | 45.54 | 45.74 | 45.82 | 45.88 | 45.88 | 45.89 | 45.84 | 45.38 | 45.48 | 45.51 | 45.63 | 45.77 | 45.76 | 45.7 | 45.19 | 45.53 | 45.62 | 45.53 | 45.49 | 45.62 | 45.72 | 45.32 | 45.46 | 45.48 | ER
279 | 41.73 | 40.07 | 46.01 | 25.34 | 22.6 | 32.27 | O |  | AVG | 45.46 | 45.83 | 45.89 | 45.94 | 45.98 | 41.73 | 43.88 | 45.52 | 45.8 | 45.87 | 45.88 | 45.92 | 39.79 | 42.89 | 45.45 | 45.46 | 45.5 | 45.6 | 45.61 | 38.87 | 42.38 | 45.37 | 45.49 | 45.49 | 45.47 | 45.47 | 41.02 | 42.75 | 45.41 | 45.43 | ER
280 | 43.88 | 40.07 | 45.54 | 29.12 | 22.58 | 31.94 | R | MW-3
281 | 45.52 | 45.48 | 45.74 | 31.97 | 31.81 | 32.16 |  |  | UP
282 | 45.8 | 45.64 | 45.82 | 32.08 | 31.98 | 32.25 | W |  | MIN | 31.71 | 31.99 | 32.1 | 32.14 | 32.12 | 22.6 | 22.58 | 31.81 | 31.98 | 32.1 | 32.11 | 32.1 | 17.46 | 17.34 | 31.37 | 31.38 | 31.46 | 31.58 | 31.54 | 17.3 | 17.3 | 31.17 | 31.42 | 31.39 | 31.31 | 31.31 | 17.39 | 16.91 | 31.24 | 31.24 | ER
283 | 45.87 | 45.75 | 45.88 | 32.25 | 32.1 | 32.29 | E |  | MAX | 32.13 | 32.32 | 32.43 | 32.42 | 32.38 | 32.27 | 31.94 | 32.16 | 32.25 | 32.29 | 32.29 | 32.31 | 32.23 | 31.49 | 31.61 | 31.62 | 31.74 | 31.86 | 31.83 | 31.72 | 31.27 | 31.64 | 31.74 | 31.62 | 31.57 | 31.67 | 31.79 | 31.4 | 31.57 | 31.57 | ER
284 | 45.88 | 45.78 | 45.88 | 32.24 | 32.11 | 32.29 | L |  | AVG | 31.92 | 32.1 | 32.28 | 32.31 | 32.25 | 25.34 | 29.12 | 31.97 | 32.08 | 32.25 | 32.24 | 32.21 | 21.88 | 27.14 | 31.47 | 31.48 | 31.58 | 31.68 | 31.66 | 21.88 | 27.18 | 31.4 | 31.55 | 31.51 | 31.46 | 31.46 | 23.53 | 26.88 | 31.42 | 31.43 | ER
285 | 45.92 | 45.79 | 45.89 | 32.21 | 32.1 | 32.31 | L
286 | 39.79 | 37.19 | 45.84 | 21.88 | 17.46 | 32.23
287 | 42.89 | 37.15 | 45.38 | 27.14 | 17.34 | 31.49 | T
288 | 45.45 | 45.36 | 45.48 | 31.47 | 31.37 | 31.61 | H
289 | 45.46 | 45.36 | 45.51 | 31.48 | 31.38 | 31.62 | R
290 | 45.5 | 45.47 | 45.63 | 31.58 | 31.46 | 31.74 | E
291 | 45.6 | 45.58 | 45.77 | 31.68 | 31.58 | 31.86 | E
292 | 45.61 | 45.58 | 45.76 | 31.66 | 31.54 | 31.83
293 | 38.87 | 35.66 | 45.7 | 21.88 | 17.3 | 31.72 | I
294 | 42.38 | 35.67 | 45.19 | 27.18 | 17.3 | 31.27 | N
295 | 45.37 | 45.16 | 45.53 | 31.4 | 31.17 | 31.64 | J
296 | 45.49 | 45.39 | 45.62 | 31.55 | 31.42 | 31.74 | E
297 | 45.49 | 45.36 | 45.53 | 31.51 | 31.39 | 31.62 | C
298 | 45.47 | 45.34 | 45.49 | 31.46 | 31.31 | 31.57 | T
299 | 45.47 | 45.37 | 45.62 | 31.46 | 31.31 | 31.67 | I
300 | 41.02 | 37.45 | 45.72 | 23.53 | 17.39 | 31.79 | O
301 | 42.75 | 37.38 | 45.32 | 26.88 | 16.91 | 31.4 | N
302 | 45.41 | 45.3 | 45.46 | 31.42 | 31.24 | 31.57
303 | 45.43 | 45.31 | 45.48 | 31.43 | 31.24 | 31.57 | W
304 | ER | ER | ER | ER | ER | ER | E
L
L

## SHIFT DATA
PERSONNEL LIST
|  | SHIFT CODE |  | OPERATOR NAME |  | CERTIFICATION NUMBER |  | SOCIAL SECURITY NUMBER
CHIEF OPERATORS
HOSTNICK, N. | CO# 3207-A | 3 |  | BAYLER, J. | 3 | CO# 4474-A | "A" |  | "A" | 4474 | 3207 | 2D | J. BAROFSKY | 5096-C
McGEARY, J. | CO# 4545-A | 1 |  | HOSTNICK, N. | 1 | CO# 3207-A | "A" |  | "A" | 3207 | 4545 | 5 | S. HULL | 5613-C
BAYLER, J. | CO# 4474-A | 2 |  | McGEARY, J. | 2 | CO# 4545-A | "A" |  | "A" | 4545 | 4474 | 4 | VACANT | X
POMEROY, D. | CO# 421-B | 5 |  | POMEROY, D. | 5 | CO# 421-B | "B" |  | "B" | 421 | 421 | 3 | J. TINKER | 3291-C
[12 empty] | 1 | G. SLAYTON | 2606-B
[12 empty] | 2 | H. WALKER | 4700-A
OPERATOR II' S
BENTLEY, J. | CO# 9366-C | 4 |  | BAROFSKY, J. | 4 | CO# 5096-C | [5 empty] | 5 | J. BENTLEY | X
CURMODE, S. | CO# 9379-A | 1 |  | BENTLEY, J. | 1 | CO# 9366-C | [5 empty] | 1D | S. CURMODE | X
JONES, K. | CO# 2466-B | 2 |  | CURMODE, S. | 2 | CO# 9379-A | [5 empty] | 4 | K. HENDERSON | 5087-B
BAROFSKY, J. | CO# 5096-C | 2D |  | HULL, S. | 2D | CO# 5613-C | [5 empty] | 3D | K. JONES | 2466-C
THOMAS, P. | CO# 12833 C | 3 |  | JONES, K. | 3 | CO# 2466-B | [5 empty] | 3 | G. KLEYNHANS | 7367-C
HULL, S. | CO# 5613-C | 5 |  | THOMAS, P. | 5 | CO# 12833 C | [5 empty] | 2 | A. MORROW | 9164-C
[12 empty] | 1 | J. RAINFORTH | 2718-C
OPERATOR I' S
HENDERSON, K. | CO# 5087-B | 3 |  | FREIDLAND, M. | 3 | CO# 13437-C
SANDERS, C. | CO# 13500-C | 1 |  | HENDERSON, K. | 1 | CO# 5087-B
KOKLAS, D. | CO# XXXX-X | 2 |  | KOKLAS, D. | 2 | CO# XXXX-X
FREIDLAND, M. | CO# 13437-C | 5 |  | NOBERT, B. | 5 | CO# 9661-C
VERBOSH, R. | CO# 12667-C | 4 |  | PEUGEOT, P. | 4 | CO# 12817-C
PEUGEOT, P. | CO# 12817-C | 1D |  | SANDERS, C. | 1D | CO# 13500-C
NOBERT, B. | CO# 9661-C | 3D |  | VERBOSH, R. | 3D | CO# 12667-C
|  | 4 | 1 | BERNARDI, J | 4 | CO# XXXX-X
|  | 3 | 2 | FREIDLAND, M. | 3 | CO# 13437-C
|  | 5A | 3 | FUTURE, 5A | 5A | CO# XXXX-X
|  | 1 | 4 | HENDERSON, K. | 1 | CO# 5087-B
|  | 2 | 5 | KOKLAS, D. | 2 | CO# XXXX-X
|  | 5 | 6 | NOBERT, B. | 5 | CO# 9661-C
|  | 4A | 7 | PEUGEOT, P. | 4A | CO# 12817-C
|  | 1D | 8 | SANDERS, C. | 1D | CO# 13500-C
|  | 3D | 9 | VERBOSH, R. | 3D | CO# 12667-C

## COVER PAGE
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
|  | OCTOBER |  | 2003
| OPERATOR | TITLE | CERTIFICATE # | TOTAL COST |  |  | 69057.8618
1 ST SHIFT | HOSTNICK, N. | CHIEF | CO# 3207-A | PEAK TO FLOW RATIO |  |  | 1.3154
2230-0630 | BENTLEY, J. | OP. II | CO# 9366-C
| HENDERSON, K. | OP. I | CO# 5087-B |  | TOTAL SUSPENDED SOLIDS
| SANDERS, C. | OP. I DEWAT | CO# 13500-C |  |  |  | LBS/DAY
|  |  |  | RAW INFLUENT |  |  | 28594.1606
2 ND SHIFT |  |  |  | FINAL EFFLUENT |  |  | 4480.7132
0630-1430 | McGEARY, J. | CHIEF | CO# 4545-A |  | TOTAL CBOD
| CURMODE, S. | OP. II RELIEF | CO# 9379-A |  |  |  | LBS/DAY
| HULL, S. | OP. II DEWAT | CO# 5613-C | RAW INFLUENT |  |  | 20593.7699
| KOKLAS, D. | OP. I RELIEF | CO# XXXX-X | FINAL EFFLUENT |  |  | 1392.5233
CHEMICALS
3 RD SHIFT | BAYLER, J. | CHIEF | CO# 4474-A |  |  | COST | POUNDS
1430-2230 | JONES, K. | OP. II | CO# 2466-B | HYDROGEN PEROXIDE |  | 6718.041 | 48158
| FREIDLAND, M. | OP. I | CO# 13437-C | CHLORINE |  | 4661 | 31600
| VERBOSH, R. | OP. I DEWAT | CO# 12667-C | POLYMER |  | 6064.1808 | 9941.28
SLUDGE REMOVED
4 TH SHIFT | [6 empty] | TONS
WEEKEND | BAROFSKY, J. | OP. II | CO# 5096-C | DRY TONS |  |  | 561.6377
2230-1030 | PEUGEOT, P. | OP. I | CO# 12817-C |  | ENERGY
| BERNARDI, J. | OP I | CO# XXXX-X |  |  | COST | KILOWATTS
5 TH SHIFT | POMEROY, D. | CHIEF | 0 | FPL CONSUMPTION |  | 51614.64 | 938448
WEEKEND | THOMAS, P. | OP. II | CO# 12833 C
1030-2230 | NOBERT, B. | OP. I | CO# 9661-C | POPULATION EQUIVALENCE |  |  | 121139.8231
This Monthly Operation Report prepared by: |  |  | BAYLER, J. | CO# 4474-A
State DEP Plant Classification: Class "A" Level "II"
I certify that I am familiar with the information contained in this report and that to the best of my knowledge and
belief, such information is true, complete and accurate.
Facilitiy Manager's Signature: ____________________________________ CO# __________________
Division Manager's Signature: ____________________________________ CO# __________________
Please direct all inquiries reguarding this report to the City Official Mailing Address:
Director of Public Services |  |  | Phone (954) 776-5151
City of Fort Lauderdale
P.O. Drawer 14250 |  |  | Copies mailed: Date ________________ To: DEP _____
Fort Lauderdale, Florida | [5 empty] | DNRP _____
33302
PAGE 1

## PRINT PAGES
UNDERGROUND INJECTION CONTROL SECTION
[28 empty] | MONTHLY OPERATING REPORT DATA SUMMARY | [13 empty] | DEP From # 17-801.900 (1) | [11 empty] | DEP From # 17-801.900 (1) | [19 empty] | DAILY SAMPLE RESULTS - PART B
[25 empty] | FACILITY: GEORGE T. LOHMEYER WWTP |  |  |  |  | REPORT DATE: |  | OCTOBER | 2003 | [8 empty] | Form Title:Domestic Wastewater Treatment | [11 empty] | Form Title:Domestic Wastewater Treatment
[25 empty] | I.D. NUMBER: 5006M02066 |  |  |  | CHIEF OPERATOR: |  |  | BAYLER, J. | CO# 4474-A | [8 empty] | Plant Monthly Operating Report | [11 empty] | Plant Monthly Operating Report | [15 empty] | Permit Number: |  | FLA041378 |  |  |  |  | Three-month Average Daily Flow: | [5 empty] | 37.5171
[25 empty] | TELEPHONE NUMBER: (954) 523-1002 | [16 empty] | Effective Date: July 1, 1991 | [11 empty] | Effective Date: July 1, 1991 | [15 empty] | Monitoring Period |  | From: | 2003-10-01 | To: | 2003-10-31 |  | (TMADF):/Permitted Capacity)x100: | [5 empty] | 87.25%
[19 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [8 empty] | INJECTION WELL DATA | [13 empty] | DEP Application No. __________________ | [11 empty] | DEP Application No. __________________ | [11 empty] | Department of Natural Resource Protection
[5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [13 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [6 empty] | IW-1 | IW-2 | IW-3 |  | IW-4 | IW-5 | [35 empty] | Laboratory/Licensing/Enforcement |  |  |  | Flow | Flow | Flow | Flow | Flow | Flow | CBOD5 | CBOD5 | TSS | TSS | pH | pH | TDS | NH-3 | TKN | pH | cond. | temp. | TP
[5 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [13 empty] | MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING | [5 empty] | PERMIT/CERTIFICATION NUMBER: | UO-06-279401 | UO-06-279508 | UO-06-279510 |  | UC 06-264391 | UO-06-2795112 | [19 empty] | DOMESTIC WASTEWATER TREATMENT PLANT | [11 empty] | BROWARD COUNTY DEPARTMENT OF NATURAL RESOURCE PROTECTION | [5 empty] | 218 S. W. 1st Avenue |  |  | (MGD) | (MGD) | (MGD) | (MGD) | (MGD) | (mg/l) | (mg/l) | (mg/l) | (mg/l) | (Min) | (Max) | mg/L | mg/L | mg/L | units | umho/ | F | mg/L
[5 empty] | MONTHLY OPERATIONAL REPORT | [13 empty] | MONITORING WELL ONE |  |  |  | 7/21/97 thru 7/21/02 |  | PERMIT EXPIRATION DATE: | 2002-07-27 | 2002-07-27 | 2002-07-27 |  | 2000-11-30 | 2002-07-27 | [19 empty] | MONTHLY OPERATING REPORT | [11 empty] | WASTEWATER TREATMENT PLANT | [5 empty] | Fort Lauderdale, FL 33301 | [17 empty] | cm
[5 empty] | PROCESS DATA | [11 empty] | MW-1 | I.D. #: 5066A11311 |  |  | PERMIT/CERT. #: UO-06-279512 |  |  |  | CASING DEPTH | 2799' | 2798' | 2800' |  | 2804' | 2818' | [8 empty] | DOMESTIC WASTEWATER TREATMENT PLANT |  |  |  |  | (34) | [8 empty] | MONTH: | OCTOBER |  | YEAR: | 2003 |  |  |  |  | MONTHLY SLUDGE REPORTS | [5 empty] | Tel. No. (954) 765-4804 | Code | 50050 | 50050 | 50050 | 50050 | 50050 | 50050 | 80082 | 80082 | 00530 | 00530 | 00400 | 00400
| RUN DATE | [14 empty] | RUN DATE | [8 empty] | TOTAL DEPTH | 3513' | 3518' | 3977' |  | 3305' | 3462' | [8 empty] | MONTHLY OPERATING REPORT |  |  |  |  | DAY OF | FLOW | CHLORINE | CHLORINE | CBOD5 | TSS | CBOD5 | TSS | PH |  |  | EFFLUENT NUTRIENTS (MG/L) |  |  | I. | [10 empty] | Mon. Site | INF-001 | EFF-002 | EFF-003 | EFF-004 | EFF-005 | EFF-006 | INF-002 | EFF-001 | INF-002 | EFF-001 | EFF-001 | EFF-001
| 2026-07-30 | [14 empty] | 2026-07-30 |  | UPPER MONITOR ZONE |  |  |  |  | LOWER MONITOR ZONE |  | AVERAGE DAILY FLOW: | 9.7977 | 10.3686 | 8.7137 |  | 0.135 | 8.736 | MGD | [7 empty] | Part II - General Information |  |  |  |  | THE |  | RESIDUAL | RESIDUAL | INFLUENT | INFLUENT | EFFLUENT | EFFLUENT | EFFLUENT | TKN | NH3-N | NITRATE | TOTAL | FECAL | Plant Name: | GEORGE T. LOHMEYER WASTEWATER TREATMENT FACILITY | [6 empty] | MONTH: | OCTOBER |  | 1 | 50.362 | 12.91 | 13.51 | 11.57 | ER | 11.36 | 21.2 | 4.74 | 80 | 16 | 6.8 | 6.8 | 1150 | 7.98 | 10.97 | 6.8 | 2410 | 84 | 0.869
[17 empty] | MIN | MAX | AVG |  |  | MIN | MAX | AVG | **MAX DAILY FLOW PER MO (mg): | 12.91 | 13.51 | 11.57 |  | 0.14 | 11.36 | MG | [12 empty] | MONTH | (MGD) | AFTER | AFTER DE- | [8 empty] | P | COLIFORM | II. | [7 empty] | YEAR: | 2003 |  | 2 | 48.529 | 12.45 | 13.06 | 11.12 | ER | 10.96 | 55.3 | 4.42 | 68 | 11 | 6.6 | 6.6 | 1377 | 8.36 | 11.55 | 6.7 | 2650 | 84 | 0.685
| OCTOBER | INFLUENT | HOURLY | INFLUENT | INFLUENT | RAS | PERCENT | WAS | RAIN | SPARE | [5 empty] | OCTOBER | FT HEAD | FT HEAD | FT HEAD |  |  | FT HEAD | FT HEAD | FT HEAD | ** PEAK HR FLOW (MGD) ON MAX DAY: | 13.7777 | 14.5293 | 12.2502 |  | 0.18809 | 12.2952 | MGD |  | (1) Month: |  | OCTOBER |  | Year: | 2003 |  | Parameter | Units | STORET | Value |  |  | CONTACT | CHLORINATION | MG/L | MG/L | MG/L | MG/L | [6 empty] | A) | Sludge Treatment Provided: |  |  |  |  | B) | Sludge Dewater Processes |  |  |  | 3 | 48 | 12.38 | 13.01 | 11.06 | ER | 10.89 | 40 | 4 | 98 | 11 | 6.7 | 6.8 | 1168 | 8.33 | 11.49 | 6.7 | 2660 | 84 | 0.78
| 2003 | FLOW | MAXIMUM | MAXIMUM | MINIMUM | FLOW | RAS | FLOW | INCHES | [6 empty] | 2003 | ABOVE | ABOVE | ABOVE |  |  | ABOVE | ABOVE | ABOVE | MAX SUSTAINED INJECTION PRESSURE: | 73.8 | 72.4 | 74.2 |  | 59.98 | 73.7 | PSIG |  | (2) Plant's DEP Identification Number: |  |  |  |  | 5006M02066 |  |  |  | Code |  | 1 | 50.362 | 0.8 |  | 21.2 | 80 | 4.74 | 16 | 6.8 | 10.97 | 7.98 | 0.622 | 0.869 | 0 |  |  | Aerobic Digestion | [5 empty] | Thickner |  |  | 4 | 45.967 | 11.74 | 12.34 | 10.46 | ER | 10.35 | 52 | 2.7 | 72 | 9 | 6.7 | 6.8 | 638 | 7.51 | 10.54 | 6.7 | 2560 | 84 | 0.697
|  | MGD | MGD | MGD | MGD | MGD |  | MGD | [8 empty] | NGVD | NGVD | NGVD |  |  | NGVD | NGVD | NGVD | MONTHLY AVG. INJECTION PRESSURE: | 51.7823 | 50.8117 | 52.0143 |  | 37.2463 | 51.564 | PSIG |  | (3) Plant Name: |  |  |  | George T. Lohmeyer Regional Wastewater |  |  | (16) Monthly average daily flow | mgd | 050053 | 38.2872 | 2 | 48.529 | 0.8 |  | 55.3 | 68 | 4.42 | 11 | 6.7 | 11.55 | 8.36 | 0.674 | 0.685 | 36 |  |  | Anaerobic Digestion | [5 empty] | DGA___X___Filter Press |  |  | 5 | 43.104 | 11 | 11.6 | 9.8 | ER | 9.74 | 59 | 2 | 70 | 8 | 6.6 | 6.8 | 1336 | 7.51 | 10.54 | 6.7 | 2670 | 84 | 0.697
| 1 | 50.362 | 2.196 | 60.172 | 36.461 | 12.877 | 25.57% | 0.468 | 0 |  |  | 1 |  |  |  | 1 | 48.68 | 49.06 | 49.17 |  |  | 42.23 | 42.56 | 42.39 | *** MAX INJECTION PRESSURE PERMITTED: | 99 | 99 | 99 |  | 99 | 99 | PSIG |  |  |  |  | Treatment Facility |  |  |  | (17) Permitted capacity | mgd | - | 43 | 3 | 48 | 0.8 |  | 40 | 98 | 4 | 11 | 6.7 | 11.49 | 8.33 | 0.678 | 0.78 | 9 |  |  | Other | [5 empty] | Centrifuge Drying Beds, Bed #______ |  |  | 6 | 41.423 | 10.7 | 11.3 | 9.51 | ER | 9.49 | 54.6 | 1.13 | 76 | 10 | 6.7 | 6.9 | 1292 |  |  | 6.8 | 2590 | 84
| 2 | 48.529 | 2.178 | 59.019 | 32.746 | 13.206 | 27.21% | 0.568 | 0 |  |  | 2 |  |  |  | 2 | 48.85 | 49.17 | 48.91 |  |  | 42.39 | 42.65 | 42.47 | ***NOTE: (INJECTION PRESSURE NOT TO EXCEED 66% TESTED PRESSURE | [8 empty] | (4) Plant Address: |  |  | 1765 S.E. 18th Street at |  |  |  | (18) Three-month average daily flow | mgd | - | 37.5171 | 4 | 45.967 | 0.7 |  | 52 | 72 | 2.7 | 9 | 6.7 | 10.54 | 7.51 | 0.787 | 0.697 | 0 | [8 empty] | Heat Treatment____No Treatment |  |  | 7 | 40.251 | 10.61 | 11.18 | 9.43 | ER | 9.07 | 81 | 4.1 | 96 | 10 | 6.6 | 6.8 | 1366 |  |  | 6.7 | 2640 | 84
| 3 | 48 | 2.249 | 59.5 | 0 | 13.75 | 28.65% | 0.12 | 0 |  |  | 3 |  |  |  | 3 | 48.87 | 49.2 | 49.02 |  |  | 42.47 | 42.67 | 42.5 | TESTED CASING PRESSURE DURING MIT | 150 | 150 | 150 |  | 150 | 150 | PSIG |  |  |  |  | Eisenhower Boulevard |  |  |  | (19) Percent of permitted capacity | % | - | 87.25% | 5 | 43.104 | 0.8 |  | 59 | 70 | 2 | 8 | 6.7 | 10.54 | 7.51 | 0.787 | 0.697 | 0 | [7 empty] | x | Other: | LIME STABILIZATION |  | 8 | 38.943 | 9.99 | 10.58 | 8.93 | ER | 8.92 | 51 | 3.8 | 40 | 17 | 6.7 | 6.8 | 1389 | 10.49 | 14.02 | 6.8 | 2650 | 84 | 0.965
| 4 | 45.967 | 2.159 | 59.243 | 32.329 | 12.752 | 27.74% | 0 | 0 |  |  | 4 |  |  |  | 4 | 48.87 | 49.19 | 49.02 |  |  | 42.49 | 42.64 | 42.53 | [9 empty] | (5) City: |  | Fort Lauderdale |  |  |  |  | (20) CBOD5 Effluent | mg/L | 080082 | 4.361 | 6 | 41.423 | 0.7 |  | 54.6 | 76 | 1.13 | 10 | 6.8 |  |  |  |  | 0 | [9 empty] | CLASS "AA" |  | 9 | 37.949 | 9.76 | 10.35 | 8.73 | ER | 8.73 | 65 | 5.56 | 86 | 15 | 6.7 | 6.8 | 1280 | 10.75 | 14.02 | 6.8 | 2650 | 84 | 1.24
| 5 | 43.104 | 2.044 | 57.737 | 25.504 | 12.09 | 28.05% | 0.233 | 0 |  |  | 5 |  |  |  | 5 | 48.82 | 49.15 | 48.99 |  |  | 42.46 | 42.64 | 42.53 |  |  | MONITORING WELL DATA | [6 empty] | (6) County: |  | Broward |  |  |  |  | (21) CBOD5 Effluent | lbs/day | - | 1392.5233 | 7 | 40.251 | 0.9 |  | 81 | 96 | 4.1 | 10 | 6.7 |  |  |  |  | 0 | III. | Final Sludge Disposal: | [7 empty] | RMF-Azurix (Nutri-Cycle) |  | 10 | 36.261 | 9.73 | 10.32 | 8.67 | ER | 8.68 | 57 | 2.7 | 100 | 19 | 6.7 | 6.8 | 1349 | 10.3 | 13.96 | 6.8 | NR | 82 | 0.721
| 6 | 41.423 | 1.971 | 54.212 | 22.011 | 12.488 | 30.15% | 0.599 | 0 |  |  | 6 |  |  |  | 6 | 46.39 | 49.07 | 47.35 |  |  | 32.54 | 42.6 | 35.26 |  | MW-1 | MW-2 | MW-3 |  | RMW-1 |  |  |  | (7) Phone Number: |  |  | (954) 523-1002 |  |  |  | (22) TSS Effluent | mg/L | 900201 | 14.0323 | 8 | 38.943 | 0.8 |  | 51 | 40 | 3.8 | 17 | 6.8 | 14.02 | 10.49 | 0.756 | 0.965 | 0 | A) | Liquid Sludge Disposal: | [9 empty] | 11 | 37.945 | 9.33 | 9.89 | 8.33 | ER | 8.38 | 90 | 3.1 | 94 | 14 | 6.6 | 6.7 | 1398 | 9.84 | 13.32 | 6.7 | 2740 | ER | 0.653
| 7 | 40.251 | 1.986 | 56.263 | 23.197 | 11.797 | 29.31% | 0.617 | 0 |  |  | 7 |  |  |  | 7 | 45.89 | 49.27 | 48.33 |  |  | 32.54 | 42.31 | 39.58 | PERMIT NUMBER | UO-06-279512 | UO-06-279401 | UO-06-279510 |  | UC06-249353 |  |  |  | (8) Permit Number: |  |  | FLA041378 |  |  |  | (23) TSS Effluent | lbs/day | - | 4480.7132 | 9 | 37.949 | 0.8 |  | 65 | 86 | 5.56 | 15 | 6.8 | 14.02 | 10.75 | 0.78 | 1.24 | 10 |  | WEEK OF | OCTOBER | GALLONS | % SOLIDS |  |  | HAULERS |  |  | DISPOSAL SITE | 12 | 37.11 | 9.2 | 9.73 | 8.21 | ER | 8.28 | 91.4 | 4.52 | 86 | 20 | 6.6 | 6.8 | 1331 | 10 | 13.57 | 6.7 | 2640 | 87 | 0.967
| 8 | 38.943 | 1.873 | 53.059 | 16.661 | 10.947 | 28.11% | 0.564 | 0 |  |  | 8 |  |  |  | 8 | 48.75 | 49.07 | 48.94 |  |  | 42.26 | 42.43 | 42.39 | UPPER MONITORING INTERVAL | 1288'-1320' | 1300'-1344' | 1300'-1349' |  | 1300'-1339' |  | Ft. bls. |  | (9) Plant Type: |  |  | Oxygen Activated Sludge |  |  |  | (24) Minimum pH |  | - | 6.4 | 10 | 36.261 | 0.9 |  | 57 | 100 | 2.7 | 19 | 6.8 | 13.96 | 10.3 | 0.794 | 0.721 | 0 | [11 empty] | 13 | 37.113 | 9.26 | 8.87 | 7.97 | ER | 8.32 | 75 | 3.6 | 90 | 9 | 6.5 | 6.7 | 1340 |  |  | 6.6 | 2780 | 87
| 9 | 37.949 | 1.821 | 54.693 | 19.095 | 11.681 | 30.78% | 0.444 | 0 |  |  | 9 |  |  |  | 9 | 48.79 | 49.08 | 48.97 |  |  | 42.43 | 42.66 | 42.5 | MONTHLY MAX DAILY PRESSURE | 49.27 | 29.71 | 32.43 |  | 44.83 |  | FT. HEAD |  | (10) Test Site Identification Number: |  |  |  |  | 5006X10744 |  | (25) Maximum pH |  | - | 6.9 | 11 | 37.945 | 1.2 |  | 90 | 94 | 3.1 | 14 | 6.7 | 13.32 | 9.84 | 0.75 | 0.653 | 9 |  | FIRST THRU SEVENTH | [9 empty] | 14 | 36.736 | 9.13 | 9.66 | 8.13 | ER | 8.21 | 64 | 4.1 | 106 | 11 | 6.5 | 6.7 | 1340 |  |  | 6.6 | 2720 | 87
| 10 | 36.261 | 1.941 | 53.956 | 18.518 | 10.94 | 30.17% | 0.211 | 0 |  |  | 10 |  |  |  | 10 | 48.85 | 49.08 | 48.97 |  |  | 42.52 | 42.75 | 42.55 | MONTHLY MIN DAILY PRESSURE | 39.26 | 23.79 | 16.91 |  | 27.48 |  | FT. HEAD |  | (11) Fecal Coliform Method | [6 empty] | (26) Total N | mg/L | 000600 | 14.2291 | 12 | 37.11 | 1.3 |  | 91.4 | 86 | 4.52 | 20 | 6.7 | 13.57 | 10 | 0.877 | 0.967 | 0 | [11 empty] | 15 | 36.813 | 9.04 | 9.57 | 8.04 | ER | 8.12 | 72 | 4.1 | 104 | 9 | 6.6 | 6.8 | 1290 | 11.64 | 16.32 | 6.7 | 2740 | 88 | 0.948
| 11 | 37.945 | 1.895 | 51.264 | 18.55 | 11.524 | 30.37% | 0 | 0 |  |  | 11 |  |  |  | 11 | 48.82 | 49.04 | 48.97 |  |  | 42.46 | 42.61 | 42.52 | TDS (MONTHLY AVERAGE) | 7352.25 | 7203.5 | 23625.5 |  | 5839 |  | mg/l |  |  | XX | Membrane Filter |  |  |  |  | (27) TKN | mg/L | 000625 | 13.67 | 13 | 37.113 | 1 |  | 75 | 90 | 3.6 | 9 | 6.6 |  |  |  |  | 0 |  | EIGHT THRU FORTEENTH | [9 empty] | 16 | 35.282 | 8.93 | 9.47 | 7.93 | ER | 8.03 | 63 | 3.9 | 102 | 12 | 6.7 | 6.8 | 1395 | 12.24 | 16.78 | 6.8 | 2740 | 85 | 0.99
| 12 | 37.11 | 1.892 | 51.841 | 16.724 | 11.439 | 30.82% | 0.28 | 0 |  |  | 12 |  |  |  | 12 | 48.78 | 49.03 | 48.95 |  |  | 42.42 | 42.63 | 42.48 | CHLORIDE (MONTHLY AVERAGE) | 3800 | 3687.5 | 3787.5 |  | 2900 |  | mg/l |  |  |  | Most Probable Number |  |  |  |  | (28) Ammonia (NH3 - N) | mg/L | 000610 | 10.277 | 14 | 36.736 | 0.6 |  | 64 | 106 | 4.1 | 11 | 6.6 |  |  |  |  | 0 |  | FIFTHTEENTH THRU | [9 empty] | 17 | 36.075 | 9.17 | 9.69 | 8.14 | ER | 8.23 | 81 | 3.7 | 100 | 12 | 6.7 | 6.8 | 1294 | 12.33 | 17.07 | 6.8 | 2750 | 86 | 0.912
| 13 | 37.113 | 1.787 | 50.495 | 18.454 | 10.311 | 27.78% | 0.645 | 0 |  |  | 13 |  |  |  | 13 | 44.82 | 48.93 | 46.4 |  |  | 36.48 | 42.49 | 38.32 | AMMONIA-N (MONTHLY AVERAGE) | 0.8045 | 0.7535 | 0.97725 |  | 0.874 |  | mg/l |  | (12) Type of Effluent Disposal or Reclaimed Water Reuse | [6 empty] | (29) Nitrate | mg/L | 071850 | 0.55909 | 15 | 36.813 | 0 |  | 72 | 104 | 4.1 | 9 | 6.7 | 16.32 | 11.64 | 0.426 | 0.948 | TNTC |  | TWENTY SECOND | [9 empty] | 18 | 36.448 | 9.05 | 9.57 | 8.04 | ER | 8.14 | 77 | 6.2 | 78 | 9 | 6.6 | 6.8 | 1220 | 10.89 | 15.23 | 6.7 | 2510 | 87 | 0.71
| 14 | 36.736 | 1.741 | 48.606 | 18.614 | 10.285 | 28% | 0.623 | 0.02 |  |  | 14 |  |  |  | 14 | 41.83 | 49.1 | 47.88 |  |  | 36.38 | 42.43 | 40.56 | TKN (MONTHLY AVERAGE) | 1.445 | 1.4325 | 1.435 |  | 1.07 |  | mg/l |  |  |  | Deep Well Injection |  |  |  |  | (30) Total Phosphorus | mg/L | 000665 | 0.98522 | 16 | 35.282 | 0 |  | 63 | 102 | 3.9 | 12 | 6.8 | 16.78 | 12.24 | 0.474 | 0.99 | TNTC |  | TWENTY THIRD THRU | [9 empty] | 19 | 35.154 | 8.86 | 9.38 | 7.86 | ER | 7.98 | 70.5 | 4.24 | 104 | 11 | 6.5 | 6.8 | 1525 | 10.61 | 14.74 | 6.6 | 2820 | 85 | 1.03
| 15 | 36.813 | 1.769 | 47.42 | 18.55 | 11.212 | 30.46% | 0.659 | 0 |  |  | 15 |  |  |  | 15 | 48.74 | 48.94 | 48.92 |  |  | 42.2 | 42.41 | 42.26 | pH (MONTHLY AVERAGE) | 7.875 | 7.955 | 8.0725 |  | 7.96 |  | Std units |  | (13) Limited Wet Wheather Discharge Activated | [6 empty] | (31) Minimum Chlorine Residual | mg/L | - | 0 | 17 | 36.075 | 0.2 |  | 81 | 100 | 3.7 | 12 | 6.8 | 17.07 | 12.33 | 0.432 | 0.912 | TNTC |  | THIRTY FIRST | [9 empty] | 20 | 32.326 | 9.23 | 9.78 | 8.19 | ER | 8.29 | 67.3 | 5.68 | 94 | 16 | 6.5 | 6.8 | 1453 |  |  | 6.7 | 2890 | ER
| 16 | 35.282 | 1.76 | 48.093 | 18.903 | 12.091 | 34.27% | 0.626 | 0 |  |  | 16 |  |  |  | 16 | 48.61 | 48.83 | 48.71 |  |  | 42.13 | 42.3 | 42.17 | CONDUCTIVITY (MONTHLY AVERAGE) | 12062.5 | 11837.5 | 11977.5 |  | 9520 |  | umho/cm |  |  |  | YES |  | XX | Not Applicable |  | (32) Maximum Chlorine Residual | mg/L | - | 1.3 | 18 | 36.448 | 0.9 |  | 77 | 78 | 6.2 | 9 | 6.7 | 15.23 | 10.89 | 0.373 | 0.71 | 36 | [11 empty] | 21 | 35.791 | 9.03 | 9.56 | 8.02 | ER | 8.14 | 67 | 5.7 | 104 | 18 | 6.7 | 6.8 | 1473 |  |  | 6.7 | 2890 | 86
| 17 | 36.075 | 1.829 | 48.19 | 17.845 | 12.209 | 33.84% | 0.257 | 0.24 |  |  | 17 |  |  |  | 17 | 48.62 | 48.87 | 48.86 |  |  | 42.17 | 42.35 | 42.28 | FECAL COLIFORM (MONTHLY AVERAGE) | 0 | 0 | 0 |  | #VALUE! |  | # col/100ml |  |  |  | NO |  |  |  |  | (33) Other Effluent Parameters |  |  |  | 19 | 35.154 | 0.9 |  | 70.5 | 104 | 4.24 | 11 | 6.6 | 14.74 | 10.61 | 0.541 | 1.03 | 0 | B) | Solid Sludge Hauled from Plant: | [9 empty] | 22 | 35.704 | 9.09 | 9.63 | 8.07 | ER | 7.97 | 77 | 5.3 | 94 | 14 | 6.7 | 6.8 | 1432 | 11.81 | 16.17 | 6.8 | 2880 | 86 | 1.56
| 18 | 36.448 | 1.864 | 51.489 | 19.191 | 12.052 | 33.07% | 0 | 0.02 |  |  | 18 |  |  |  | 18 | 48.69 | 48.93 | 48.9 |  |  | 42.27 | 42.45 | 42.38 | TEMPERATURE (MONTHLY AVERAGE) | 74.25 | 71.5 | 70.25 |  | 69 |  | deg. F | [12 empty] | 20 | 32.326 | 0.4 |  | 67.3 | 94 | 5.68 | 16 | 6.7 |  |  |  |  | 0 |  | WEEK OF | OCTOBER | TONS |  | % SOLIDS |  | HAULERS |  |  | DISPOSAL SITE | 23 | 36.372 | 9.11 | 9.68 | 8.09 | ER | 8.16 | 67 | 6.2 | 88 | 17 | 6.7 | 6.8 | 1555 | 12.09 | 0 | 6.7 | 3050 | 86 | 1.47
| 19 | 35.154 | 1.731 | 48.478 | 18.743 | 13.096 | 37.25% | 0.224 | 0 |  |  | 19 |  |  |  | 19 | 48.61 | 48.88 | 48.79 |  |  | 42.25 | 42.51 | 42.41 | TOTAL PHOSPHOROUS (MONTHLY AVG.) | 0.05 | 0.05 | 0.05 |  | 0.05 |  | mg/l |  | (14) Cumulative Days of Wet Wheather Discharge | [10 empty] | 21 | 35.791 | 0.2 |  | 67 | 104 | 5.7 | 18 | 6.7 |  |  |  |  | 70500 | [10 empty] | Nutri-Cylcle Inc. | 24 | 36.447 | 9.17 | 9.75 | 8.15 | ER | 8.22 | 73 | 6.1 | 100 | 27 | 6.6 | 6.7 | 1638 | 11.94 | 16.64 | 6.7 | 3111 | 86 | 1.01
| 20 | 32.326 | 1.879 | 49.343 | 18.775 | 11.035 | 34.14% | 0.474 | 0.46 |  |  | 20 |  |  |  | 20 | 39.26 | 48.82 | 42.58 |  |  | 35.14 | 42.33 | 37.5 | SULFATE (MONTHLY AVERAGE) | 750 | 762.5 | 762.5 |  | 500 |  | mg/l |  |  |  | N/A | [8 empty] | 22 | 35.704 | 0.9 |  | 77 | 94 | 5.3 | 14 | 6.8 | 16.17 | 11.81 | 0.328 | 1.56 | 63 |  | FIRST THRU SEVENTH |  | 650 |  | 18.794 |  | AZURIX |  |  | Arcadia, FL | 25 | 34.966 | 8.94 | 9.52 | 7.93 | ER | 8.02 | 55 | 3.9 | 94 | 18 | 6.5 | 6.7 | 1430 | 10.87 | 15.17 | 6.6 | 3070 | 84 | 0.826
| 21 | 35.791 | 1.785 | 42.816 | 23.328 | 11.737 | 32.79% | 0.554 | 0 |  |  | 21 |  |  |  | 21 | 39.71 | 49.09 | 46.22 |  |  | 35.16 | 42.19 | 40.07 | C.O.D. (MONTHLY AVERAGE) | 180 | 175 | 182.5 |  | 140 |  | mg/l |  | (15) Plant Staffing: | [10 empty] | 23 | 36.372 | 0.9 |  | 67 | 88 | 6.2 | 17 | 6.7 | 0 | 12.09 | 0.456 | 1.47 | 36 | [10 empty] | Nutri-Cylcle Inc. | 26 | 34.525 | 8.69 | 9.26 | 7.71 | ER | 7.82 | 64 | 3.7 | 60 | 13 | 6.5 | 6.7 | 1548 | 10.86 | 15.38 | 6.6 | 3050 | 84 | 0.7
| 22 | 35.704 | 1.77 | 50.591 | 16.405 | 12.425 | 34.8% | 0.549 | 0 |  |  | 22 |  |  |  | 22 | 48.61 | 49 | 48.8 |  |  | 42.06 | 42.37 | 42.28 | IRON (MONTHLY AVERAGE) | 0.66 | 2.7075 | 1.005 |  | 0.21 |  | mg/l | [12 empty] | 24 | 36.447 | 0.9 |  | 73 | 100 | 6.1 | 27 | 6.7 | 16.64 | 11.94 | 0.36 | 1.01 | 9 |  | EIGHT THRU FORTEENTH |  | 550 |  | 18.85 |  | AZURIX |  |  | Arcadia, FL | 27 | 34.384 | 8.75 | 9.33 | 7.78 | ER | 7.88 | 70 | 4 | 100 | 10 | 6.4 | 6.8 | 1440 |  |  | 6.6 | 3150 | 83.6
| 23 | 36.372 | 1.879 | 51.841 | 15.251 | 12.99 | 35.71% | 0.547 | 0 |  |  | 23 |  |  |  | 23 | 48.64 | 49 | 48.85 |  |  | 42.17 | 42.53 | 42.36 | SULFIDE (MONTHLY AVERAGE) | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! |  | mg/l |  |  | Day Shift Operator: |  |  | Class | "A" | Cert. No. | 4545 |  |  |  | 25 | 34.966 | 1 |  | 55 | 94 | 3.9 | 18 | 6.6 | 15.17 | 10.87 | 0.378 | 0.826 | 0 |  | FIFTHTEENTH THRU | [8 empty] | Nutri-Cylcle Inc. | 28 | 34.13 | 8.81 | ER | 7.83 | ER | 7.94 | 55 | 4 | 60 | 14 | 6.5 | 6.6 | 1605 |  |  | 6.6 | 3230 | 84
| 24 | 36.447 | 1.88 | 50.591 | 17.14 | 12.741 | 34.96% | 0.272 | 0 |  |  | 24 |  |  |  | 24 | 48.5 | 48.88 | 48.69 |  |  | 42.1 | 42.33 | 42.15 | LOWER MONITORING INTERVAL | 1449'-1557' | 1970'-2025' | 1970'-2027' |  | 1500'-1600' |  | Ft. bls | [12 empty] | 26 | 34.525 | 1 |  | 64 | 60 | 3.7 | 13 | 6.6 | 15.38 | 10.86 | 0.629 | 0.7 | 0 |  | TWENTY SECOND |  | 875 |  | 18.85 |  | AZURIX |  |  | Arcadia, FL | 29 | 40.309 | 10.33 | 10.92 | 9.21 | 0.14 | 9.2 | 91 | 4 | 94 | 16 | 6.6 | 6.6 | 1470 | 10.03 | 15.53 | 6.6 | 2930 | 83 | 1.3
| 25 | 34.966 | 1.833 | 51.392 | 16.117 | 12.2 | 34.89% | 0 | 0.06 |  |  | 25 |  |  |  | 25 | 48.42 | 48.77 | 48.56 |  |  | 42.01 | 42.26 | 42.08 | MONTHLY MAX DAILY PRESSURE | 42.75 | 42.79 | 46.03 |  | 33.03 |  | FT. HEAD |  |  | Evening Shift Operator: |  |  | Class | "A" | Cert. No. | 4474 |  |  |  | 27 | 34.384 | 0.6 |  | 70 | 100 | 4 | 10 | 6.6 |  |  |  |  | 0 |  | TWENTY THIRD THRU | [8 empty] | Nutri-Cylcle Inc. | 30 | 37.184 | 9.54 | 10.18 | 8.5 | 0.13 | 8.56 | 52 | 6 | 128 | 18 | 6.6 | 6.8 | 1383 | 10 | 15.59 | 6.7 | 2890 | 83 | 1.77
| 26 | 34.525 | 1.812 | 51.168 | 17.461 | 11.597 | 33.59% | 0.02 | 0 |  |  | 26 |  |  |  | 26 | 48.38 | 48.82 | 48.63 |  |  | 42.06 | 42.35 | 42.27 | MONTHLY MIN DAILY PRESSURE | 32.54 | 32.31 | 35.66 |  | 20.39 |  | FT. HEAD | [12 empty] | 28 | 34.13 | 0.9 |  | 55 | 60 | 4 | 14 | 6.6 |  |  |  |  | 54 |  | THIRTY FIRST |  | 900 |  | 19.304 |  | AZURIX |  |  | Arcadia, FL | 31 | 35.3 | ER | ER | ER | ER | ER | 41 | 8 | 110 | 21 | 6.7 | 6.8 | 1380 | 9.99 | 15.81 | 6.8 | 2680 | 83 | 1.16
| 27 | 34.384 | 1.711 | 49.888 | 15.892 | 10.793 | 31.39% | 0.497 | 0 |  |  | 27 |  |  |  | 27 | 44.53 | 48.93 | 46.54 |  |  | 36.27 | 42.44 | 39 | TDS (MONTHLY AVERAGE) | 9252 | 31443 | 28902.75 |  | 26899 |  | mg/l |  |  | Night Shift Operator: |  |  | Class | "A" | Cert. No. | 3207 |  |  |  | 29 | 40.309 | 0.6 |  | 91 | 94 | 4 | 16 | 6.6 | 15.53 | 10.03 | 0.415 | 1.3 | 0 | C) | Monthly quantities of solid sludge stockpiled at plant.Solid Sludge Hauled from Plant: | [9 empty] | TOT | 1186.903 | 293.93 | 300.69 | 261.41 | 0.27 | 262.08 | 1999.3 | 135.19 | 2776 | 435 | 205.1 | 209.7 | 42285 | 236.37 | 314.41 | 207.8 | 83741 | 2458.6 | 22.66
| 28 | 34.13 | 1.745 | 47.068 | 15.604 | 10.581 | 31% | 0.511 | 0 |  |  | 28 |  |  |  | 28 | 44.8 | 49 | 47.69 |  |  | 36.25 | 42.25 | 40.29 | CHLORIDE (MONTHLY AVERAGE) | 5100 | 17800 | 15900 |  | 16200 |  | mg/l | [12 empty] | 30 | 37.184 | 0.7 |  | 52 | 128 | 6 | 18 | 6.7 | 15.59 | 10 | 0.372 | 1.77 | 0 |  | 1) | Additions |  |  | Cubic Yards | [5 empty] | AVG | 38.2872 | 9.7977 | 10.3686 | 8.7137 | 0.135 | 8.736 | 64.4935 | 4.361 | 89.5484 | 14.0323 | 6.6161 | 6.7645 | 1364.0323 | 10.277 | 13.67 | 6.7032 | 2791.3667 | 84.7793 | 0.98522
| 29 | 40.309 | 1.949 | 52.482 | 20.217 | 10.91 | 27.07% | 0.52 | 1.37 |  |  | 29 |  |  |  | 29 | 48.61 | 48.9 | 48.73 |  |  | 42.13 | 42.39 | 42.21 | AMMONIA-N (MONTHLY AVERAGE) | 9.08 | 1.2975 | 2.3825 |  | 0.498 |  | mg/l |  |  | Lead Operator:_________________________________ | [9 empty] | 31 | 35.3 | 0.6 |  | 41 | 110 | 8 | 21 | 6.8 | 15.81 | 9.99 | 0.17 | 1.16 | 240 | [5 empty] | Tons | [5 empty] | MAX | 50.362 | 12.91 | 13.51 | 11.57 | 0.14 | 11.36 | 91.4 | 8 | 128 | 27 | 6.8 | 6.9 | 1638 | 12.33 | 17.07 | 6.8 | 3230 | 88 | 1.77
| 30 | 37.184 | 1.872 | 52.258 | 21.37 | 9.634 | 25.91% | 0.558 | 0.06 |  |  | 30 |  |  |  | 30 | 48.47 | 48.78 | 48.61 |  |  | 42.11 | 42.3 | 42.14 | TKN (MONTHLY AVERAGE) | 11.665 | 1.9125 | 3.1275 |  | 0.655 |  | mg/l | [5 empty] | Signature |  | Cert. No. |  |  |  |  | Lead Operator : This is to certify that I am familar with the information contained on this report and that to the best of | [14 empty] | 2) | Removals |  |  | Cubic Yards | [5 empty] | MIN | 32.326 | 8.69 | 8.87 | 7.71 | 0.13 | 7.82 | 21.2 | 1.13 | 40 | 8 | 6.4 | 6.6 | 638 | 7.51 | 0 | 6.6 | 2410 | 82 | 0.653
| 31 | 35.3 | 1.793 | 48.702 | 0 | 10.155 | 28.77% | 0.201 | 0 |  |  | 31 |  |  |  | 31 | ER | ER | ER |  |  | ER | ER | ER | pH (MONTHLY AVERAGE) | 7.2275 | 7.3025 | 7.285 |  | 7.35 |  | Std units | [12 empty] | my knowledge and belief, this information is true, complete and accuate. | [16 empty] | X |  | Tons | [6 empty] | item #1 | 13.7777 | 14.5293 | 12.2502 | 0.18809 | 12.2952 | MAX HOURLY FLOW (MG) = |  |  |  | 2.249 | ON THE | 3 | DAY OF THIS MONTH
| TOTAL | 1186.903 | 58.594 | 1611.87 | 589.656 | 363.545 |  | 11.841 | 2.23 | [6 empty] | TOTAL | 1418.21 | 1469.88 | 1447.95 |  |  | 1210.55 | 1273.83 | 1242.43 | CONDUCTIVITY (MONTHLY AVERAGE) | 15582.5 | 47275 | 43450 |  | 41000 |  | umho/cm | [33 empty] | Signature |  |  |  |  | item #2 | 51.7823 | 50.8117 | 52.0143 | 37.2463 | 51.564
| AVERAGE | 38.2872 | 1.8901 | 51.9958 | 20.333 | 11.7273 | 30.63% | 0.43856 | 0.071935 | [6 empty] | AVERAGE | 47.2737 | 48.996 | 48.265 |  |  | 40.3517 | 42.461 | 41.4143 | FECAL COLIFORM (MONTHLY AVERAGE) | 0 | 0 | 0.0125 |  | #VALUE! |  | # col/100ml | [12 empty] | Signed: ____________________________ Date: ___________________ | [20 empty] | Title |  |  |  |  | item #3 | 37.5 | 37.8 | 38 | 38.1 | 36.1
[16 empty] | MAXIMUM | 48.87 | 49.27 | 49.17 |  |  | 42.52 | 42.75 | 42.55 | TEMPERATURE (MONTHLY AVERAGE) | 74 | 71.5 | 1969.25 |  | 68 |  | deg. F | [33 empty] | Date |  |  |  | item #1 | =monthly maximum of the daily flows (MG), with peakhour flow (MGD) on the day of the month with maximum flow = | [14 empty] | 2.249 | MG/hour multiplied by
[16 empty] | MINIMUM | 39.26 | 48.77 | 42.58 |  |  | 32.54 | 42.19 | 35.26 | TOTAL PHOSPHOROUS (MONTHLY AVG.) | 0.05 | 0.05 | 0.05 |  | 0.05 |  | mg/l | [12 empty] | Name: Michael A. Just | [14 empty] | * Sludge Reports should be submitted along with the monthly operating reports to Broward County Department | [10 empty] | the % of average % of TOTAL RAW FLOW to each Injection well.
[25 empty] | SULFATE (MONTHLY AVERAGE) | 662.5 | 2275 | 2175 |  | 1300 |  | mg/l | [27 empty] | of Natural Resource Protection, 218 S. W. 1st Avenue, Fort Lauderdale, Florida 33301 | [9 empty] | item #2 | =monthly average injection well pressure at injection well (psig)
[25 empty] | C.O.D. (MONTHLY AVERAGE) | 270 | 887.5 | 867.5 |  | 710 |  | mg/l | [12 empty] | Company Name: City of Fort Lauderdale Telephone No. (954) 523-1002 | [24 empty] | item #3 | =monthly wellhead pressure with no flow (shut-in pressure,psig)
[25 empty] | IRON (MONTHLY AVERAGE) | 0.0275 | 0.0525 | 0.0375 |  | 0.07 |  | mg/l | [37 empty] | PLANT STAFFING
[5 empty] | PAGE 2 | [19 empty] | SULFIDE (MONTHLY AVERAGE) | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! |  | mg/l | [37 empty] | Day Shift Operator |  |  | Class: | "A" | Certificate No. | 4545 | Name: |  | McGEARY, J.
[70 empty] | Evening Shift Operator |  |  | Class: | "A" | Certificate No. | 4474 | Name: |  | BAYLER, J.
[20 empty] | PAGE 20 | [49 empty] | Night Shift Operator |  |  | Class: | "A" | Certificate No. | 3207 | Name: |  | HOSTNICK, N.
[70 empty] | Lead Operator |  |  | Class: | "A" | Certificate No. | 2769 | Name: |  | JUST, M.
[70 empty] | Type of Effluent Disposal or Reclaimed Water Reuse: |  |  |  |  | DEEPWELL INJECTION
[70 empty] | Permited Wet Weather Discharge Activated: |  |  |  | YES: |  | NO: |  |  | Not Applicable |  | X
If Yes, cumulative days of wet weather:
Attach additional sheets if necessary to list all certified operators. See page 1 "COVER PAGE" of supplental attachements.
DEP form 62-620.910(10), effective November 29, 1994
[19 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [46 empty] | Department of Natural Resource Protection
[5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [13 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [46 empty] | Division of Pollution Prevention and Remediation Programs
[5 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [13 empty] | MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING | [49 empty] | 218 S. W. 1st Avenue
[5 empty] | MONTHLY OPERATIONAL REPORT | [13 empty] | MONITORING WELL TWO |  |  |  | 7/21/97 thru 7/21/02 | [38 empty] | SLUDGE HAULERS MONTHLY REPORT | [6 empty] | Fort Lauderdale, FL 33301
[5 empty] | INFLUENT DATA | [11 empty] | MW-2 | I.D. #: 5066A11308 & 09 |  |  | PERMIT/CERT. #: UO-06-279401 & 508 | [40 empty] | BROWARD COUNTY CODE SECTION 27-356 (d)(4)(1) | [5 empty] | Tel. No. (954) 523-1002
| RUN DATE | [14 empty] | RUN DATE | [51 empty] | *FAX (954) 519-1245
| 2026-07-30 | [14 empty] | 2026-07-30 |  | UPPER MONITOR ZONE |  |  |  |  | LOWER MONITOR ZONE
[17 empty] | MIN | MAX | AVG |  |  | MIN | MAX | AVG | [34 empty] | Plant Name: | GEORGE T. LOHMEYER WASTEWATER TREATMENT FACILITY
| OCTOBER | RAW | RAW TSS | RAW SS | RAW | RAW | RAW | RAW | RAW | RAW | [5 empty] | OCTOBER | FT HEAD | FT HEAD | FT HEAD |  |  | FT HEAD | FT HEAD | FT HEAD | [34 empty] | Address: | 1765 S.E. 18th Street at Eisenhower Boulevard | [6 empty] | MONTH: | OCTOBER
| 2003 | CBOD | TOTAL | FIXED | COD | pH | CL_ | ALK. | H2S | TEMP.(F) | [5 empty] | 2003 | ABOVE | ABOVE | ABOVE |  |  | ABOVE | ABOVE | ABOVE | [34 empty] | Phone: | (954) 523-1002 * FAX (954) 468-1577 | [6 empty] | YEAR: | 2003
[17 empty] | NGVD | NGVD | NGVD |  |  | NGVD | NGVD | NGVD
| 1 | 21.2 | 80 | 16 | 265 | 7.2 | 750 | 198 | 3 | 82 | [5 empty] | 1 | ER | ER | ER |  |  | 42.13 | 42.42 | 42.33 | [34 empty] | a) | WEEK OF | OCTOBER |  | Type of Sludge |  |  | Disopsal Site |  |  | Cubic Yards
| 2 | 55.3 | 68 | 12 | 281 | 7.2 | 710 | 204 | 3 | 82 | [5 empty] | 2 | ER | ER | ER |  |  | 42.38 | 42.6 | 42.48
| 3 | 40 | 98 | 8 | 264 | 7.1 | 760 | 204 | 4 | 81 | [5 empty] | 3 | ER | ER | ER |  |  | 42.5 | 42.73 | 42.54 | [35 empty] | FIRST THRU SEVENTH |  |  | GRIT |  |  | Central Landfill |  |  | 0
| 4 | 52 | 72 | 12 | 250 | 7 | 750 | 198 | 4 | 81 | [5 empty] | 4 | ER | ER | ER |  |  | 42.58 | 42.77 | 42.66
| 5 | 59 | 70 | 12 | 250 | 7.1 | 750 | 192 | 5 | 81 | [5 empty] | 5 | ER | ER | ER |  |  | 42.62 | 42.79 | 42.72 | [35 empty] | EIGHT THRU FORTEENTH |  |  | GRIT |  |  | Central Landfill |  |  | 10
| 6 | 54.6 | 76 | 6 |  | 7 | 740 | 198 | 5 | 81 | [5 empty] | 6 | ER | ER | ER |  |  | 32.31 | 42.79 | 35.25 | [35 empty] | FIFTHTEENTH THRU
| 7 | 81 | 96 | 10 |  | 7.1 | 730 | 204 | 5 | 81 | [5 empty] | 7 | ER | ER | ER |  |  | 32.32 | 42.37 | 39.45 | [35 empty] | TWENTY SECOND |  |  | GRIT |  |  | Central Landfill |  |  | 0
| 8 | 51 | 40 | 8 | 240 | 7.1 | 760 | 202 | 4 | 81 | [5 empty] | 8 | ER | ER | ER |  |  | 42.3 | 42.56 | 42.46 | [35 empty] | TWENTY THIRD THRU
| 9 | 65 | 86 | 12 | 225 | 7.1 | 760 | 200 | 5 | 79.8 | [5 empty] | 9 | ER | ER | ER |  |  | 42.45 | 42.64 | 42.5 | [35 empty] | THIRTY FIRST |  |  | GRIT |  |  | Central Landfill |  |  | 20
| 10 | 57 | 100 | 10 | 230 | 7 | 720 | 202 | 5 | ER | [5 empty] | 10 | ER | ER | ER |  |  | 42.56 | 42.69 | 42.59
| 11 | 90 | 94 | 8 | 210 | 6.9 | 730 | 200 | 5 | 84 | [5 empty] | 11 | ER | ER | ER |  |  | 42.59 | 42.68 | 42.6 | [34 empty] | b) | WEEK OF | OCTOBER |  | Type of Sludge |  |  | Disopsal Site |  |  | Cubic Yards
| 12 | 91.4 | 86 | 26 | 242 | 7 | 690 | 198 | 6 | 84 | [5 empty] | 12 | ER | ER | ER |  |  | 42.6 | 42.72 | 42.61
| 13 | 75 | 90 | 14 |  | 7.1 | 680 | 196 | 7 | 84 | [5 empty] | 13 | ER | ER | ER |  |  | 37.32 | 42.67 | 39.04 | [35 empty] | FIRST THRU SEVENTH |  |  | RAGS |  |  | Central Landfill |  |  | 10
| 14 | 64 | 106 | 12 |  | 7.1 | 670 | 188 | 7 | 84 | [5 empty] | 14 | ER | ER | ER |  |  | 36.57 | 42.32 | 40.77
| 15 | 72 | 104 | 18 | 286 | 7 | 690 | 196 | 7 | 85 | [5 empty] | 15 | ER | ER | ER |  |  | 42.27 | 42.38 | 42.38 | [35 empty] | EIGHT THRU FORTEENTH |  |  | RAGS |  |  | Central Landfill |  |  | 10
| 16 | 63 | 102 | 20 | 259 | 7 | 680 | 196 | 5 | 83 | [5 empty] | 16 | ER | ER | ER |  |  | 42.26 | 42.4 | 42.37 | [35 empty] | FIFTHTEENTH THRU
| 17 | 81 | 100 | 18 | 202 | 7 | 700 | 198 | 7 | 84 | [5 empty] | 17 | ER | ER | ER |  |  | 42.34 | 42.5 | 42.44 | [35 empty] | TWENTY SECOND |  |  | RAGS |  |  | Central Landfill |  |  | 10
| 18 | 77 | 78 | 10 | 192 | 6.9 | 680 | 196 | 6 | 84 | [5 empty] | 18 | ER | ER | ER |  |  | 42.44 | 42.61 | 42.5 | [35 empty] | TWENTY THIRD THRU
| 19 | 70.5 | 104 | 18 | 206 | 7 | 680 | 198 | 5 | 83 | [5 empty] | 19 | ER | ER | ER |  |  | 42.43 | 42.6 | 42.51 | [35 empty] | THIRTY FIRST |  |  | RAGS |  |  | Central Landfill |  |  | 10
| 20 | 67.3 | 94 | 16 |  | 7.1 | 730 | 202 | 5 | ER | [5 empty] | 20 | ER | ER | ER |  |  | 38.24 | 42.56 | 39.71 | [35 empty] | BCSR = Broward County Septage Receiving
| 21 | 67 | 104 | 16 |  | 7 | 740 | 196 | 6 | 85 | [5 empty] | 21 | ER | ER | ER |  |  | 36.47 | 42.18 | 40.9 | [34 empty] | c) | WEEK OF | OCTOBER |  | Type of Sludge |  |  | Disopsal Site |  |  | Gallons
| 22 | 77 | 94 | 14 | 232 | 7.1 | 700 | 198 | 6 | 83 | [5 empty] | 22 | ER | ER | ER |  |  | 42.12 | 42.47 | 42.35
| 23 | 67 | 88 | 16 | 264 | 7.1 | 720 | 200 | 6 | 84 | [5 empty] | 23 | ER | ER | ER |  |  | 42.32 | 42.54 | 42.48 | [35 empty] | FIRST THRU SEVENTH |  |  | VAC/Plastic & Rags |  |  | BCSR |  |  | 0
| 24 | 73 | 100 | 10 | 208 | 7 | 750 | 184 | 6 | 84 | [5 empty] | 24 | ER | ER | ER |  |  | 42.26 | 42.45 | 42.43
| 25 | 55 | 94 | 14 | 241 | 7.1 | 720 | 194 | 6 | 82 | [5 empty] | 25 | ER | ER | ER |  |  | 42.23 | 42.4 | 42.39 | [35 empty] | EIGHT THRU FORTEENTH |  |  | VAC/Plastic & Rags |  |  | BCSR |  |  | 4500
| 26 | 64 | 60 | 10 | 250 | 7.1 | 700 | 198 | 5 | 81 | [5 empty] | 26 | ER | ER | ER |  |  | 42.25 | 42.5 | 42.44 | [35 empty] | FIFTHTEENTH THRU
| 27 | 70 | 100 | 20 |  | 7 | 680 | 200 | 5 | 81 | [5 empty] | 27 | ER | 26.15 | 15.41 |  |  | 37.16 | 42.59 | 39.43 | [35 empty] | TWENTY SECOND |  |  | VAC/Plastic & Rags |  |  | BSCR |  |  | 0
| 28 | 55 | 60 | 12 |  | 7 | 690 | 200 | 6 | 81 | [5 empty] | 28 | 23.79 | 29.55 | 27.37 |  |  | 37.07 | 42.28 | 40.52 | [35 empty] | TWENTY THIRD THRU
| 29 | 91 | 94 | 18 | 257 | 7 | 730 | 202 | 6 | 81 | [5 empty] | 29 | 28.34 | 29.71 | 28.86 |  |  | 42.22 | 42.39 | 42.38 | [35 empty] | THIRTY FIRST |  |  | VAC/Plastic & Rags |  |  | BSCR |  |  | 4500
| 30 | 52 | 128 | 24 | 307 | 7.1 | 710 | 202 | 6 | 81 | [5 empty] | 30 | 28.2 | 29.41 | 28.76 |  |  | 42.23 | 42.39 | 42.37 | [34 empty] | TOTALS
| 31 | 41 | 110 | 8 | 268 | 7.1 | 690 | 186 | 6 | 81 | [5 empty] | 31 | ER | ER | ER |  |  | ER | ER | ER | [35 empty] | a) | 30 | cu.yds |  | GRIT |  | Signature
| TOTAL | 1999.3 | 2776 | 428 | 5629 | 218.6 | 22190 | 6130 | 167 | 2388.8 | [5 empty] | TOTAL | 80.33 | 114.82 | 100.4 |  |  | 1219.54 | 1275.99 | 1249.6 | [35 empty] | b) | 40 | cu.yds |  | RAGS |  | Title
| AVERAGE | 64.4935 | 89.5484 | 13.8065 | 244.7391 | 7.0516 | 715.8065 | 197.7419 | 5.3871 | 82.3724 | [5 empty] | AVERAGE | 26.7767 | 28.705 | 25.1 |  |  | 40.6513 | 42.533 | 41.6533 | [35 empty] | c) | 9000 | gal. |  | VAC/Plastic & Rags |  | Date
[16 empty] | MAXIMUM | 28.34 | 29.71 | 28.86 |  |  | 42.62 | 42.79 | 42.72
[16 empty] | MINIMUM | 23.79 | 26.15 | 15.41 |  |  | 32.31 | 42.18 | 35.25 | [35 empty] | * Sludge Reports should be submitted along with the monthly operating reports to Broward County Department
of Natural Resource Protection, 218 S. W. 1st Avenue, Fort Lauderdale, Florida 33301
PAGE 3
PAGE 21
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
[5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [13 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
[5 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [13 empty] | MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
[5 empty] | MONTHLY OPERATIONAL REPORT | [13 empty] | MONITORING WELL THREE |  |  |  | 7/21/97 thru 7/21/02
[5 empty] | EFFLUENT DATA PART 1 | [11 empty] | MW-3 | I.D. #: 5066A11310 |  |  | PERMIT/CERT. #: UO-06-279510
RUN DATE
[16 empty] | 2026-07-30 |  | UPPER MONITOR ZONE |  |  |  |  | LOWER MONITOR ZONE
| RUN DATE | [15 empty] | MIN | MAX | AVG |  |  | MIN | MAX | AVG
| 2026-07-30 | [14 empty] | OCTOBER | FT HEAD | FT HEAD | FT HEAD |  |  | FT HEAD | FT HEAD | FT HEAD
[14 empty] | BOD | TSS | 2003 | ABOVE | ABOVE | ABOVE |  |  | ABOVE | ABOVE | ABOVE
| OCTOBER | EFFLUENT | EFFL. TSS | EFFL. SS | EFFLUENT | EFFL. | EFFL. | EFFL. | EFFL. | EFFL. | TDS |  |  | MONTHLY AVG OVER 30 | MONTHLY AVG OVER 30 |  | NGVD | NGVD | NGVD |  |  | NGVD | NGVD | NGVD
| 2003 | CBOD | TOTAL | FIXED | COD | CL_ | ALK. | TURB. | COND. | TEMP.(F) |  |  |  | 0 | 0 | 1 | 31.71 | 32.13 | 31.92 |  |  | 45.36 | 45.63 | 45.46
[14 empty] | WEKKLY OVER 45 | WEKKLY OVER 45 | 2 | 31.99 | 32.32 | 32.1 |  |  | 45.62 | 45.84 | 45.83
| 1 | 4.74 | 16 | 5 | 54.1 | 710 | 190 | 6.85 | 2410 | 84 | 1150 | 1 |  | 0 | 0 | 3 | 32.1 | 32.43 | 32.28 |  |  | 45.75 | 45.98 | 45.89
| 2 | 4.42 | 11 | 3 | 50.6 | 710 | 190 | 6.91 | 2650 | 84 | 1377 | 1 |  | SINGLE DAY OVER 60 | SINGLE DAY OVER 60 | 4 | 32.14 | 32.42 | 32.31 |  |  | 45.83 | 46.01 | 45.94
| 3 | 4 | 11 | 3 | 53.2 | 740 | 190 | 6.97 | 2660 | 84 | 1168 | 1 |  | 0 | 0 | 5 | 32.12 | 32.38 | 32.25 |  |  | 45.86 | 46.03 | 45.98
| 4 | 2.7 | 9 | 2 | 58.4 | 740 | 192 | 6.84 | 2560 | 84 | 638 | 1 |  | 0 | 0 | 6 | 22.6 | 32.27 | 25.34 |  |  | 40.07 | 46.01 | 41.73
| 5 | 2 | 8 | 1 | 58.4 | 740 | 192 | 4.29 | 2670 | 84 | 1336 | 1 |  |  |  | 7 | 22.58 | 31.94 | 29.12 |  |  | 40.07 | 45.54 | 43.88
| 6 | 1.13 | 10 | 1 |  | 690 | 190 | 2.98 | 2590 | 84 | 1292 | 1 |  |  |  | 8 | 31.81 | 32.16 | 31.97 |  |  | 45.48 | 45.74 | 45.52
| 7 | 4.1 | 10 | 1 |  | 720 | 192 | 5.04 | 2640 | 84 | 1366 | 1 | 3.2986 | 3.2986 | 10.7143 | 9 | 31.98 | 32.25 | 32.08 |  |  | 45.64 | 45.82 | 45.8
| 8 | 3.8 | 17 | 2 | 59.1 | 720 | 190 | 4.91 | 2650 | 84 | 1389 | 1 |  | 3.1643 | 10.8571 | 10 | 32.1 | 32.29 | 32.25 |  |  | 45.75 | 45.88 | 45.87
| 9 | 5.56 | 15 | 3 | 60.2 | 740 | 192 | 6.25 | 2650 | 84 | 1280 | 1 |  | 3.3271 | 11.4286 | 11 | 32.11 | 32.29 | 32.24 |  |  | 45.78 | 45.88 | 45.88
| 10 | 2.7 | 19 | 5 | 61.2 | 680 | 186 | 4.73 | NR | 82 | 1349 | 1 |  | 3.1414 | 12.5714 | 12 | 32.1 | 32.31 | 32.21 |  |  | 45.79 | 45.89 | 45.92
| 11 | 3.1 | 14 | 2 | 58.4 | 700 | 182 | 5.33 | 2740 | ER | 1398 | 1 |  | 3.1986 | 13.2857 | 13 | 17.46 | 32.23 | 21.88 |  |  | 37.19 | 45.84 | 39.79
| 12 | 4.52 | 20 | 7 | 54.3 | 680 | 180 | 5.99 | 2640 | 87 | 1331 | 1 |  | 3.5586 | 15 | 14 | 17.34 | 31.49 | 27.14 |  |  | 37.15 | 45.38 | 42.89
| 13 | 3.6 | 9 | 1 |  | 690 | 180 | 4.99 | 2780 | 87 | 1340 | 1 |  | 3.9114 | 14.8571 | 15 | 31.37 | 31.61 | 31.47 |  |  | 45.36 | 45.48 | 45.45
| 14 | 4.1 | 11 | 1 |  | 670 | 188 | 5.44 | 2720 | 87 | 1340 | 1 | 3.9114 | 3.9114 | 15 | 16 | 31.38 | 31.62 | 31.48 |  |  | 45.36 | 45.51 | 45.46
| 15 | 4.1 | 9 | 2 | 51.2 | 660 | 186 | 4.9 | 2740 | 88 | 1290 | 1 |  | 3.9543 | 13.8571 | 17 | 31.46 | 31.74 | 31.58 |  |  | 45.47 | 45.63 | 45.5
| 16 | 3.9 | 12 | 5 | 53.4 | 680 | 196 | 4.68 | 2740 | 85 | 1395 | 1 |  | 3.7171 | 13.4286 | 18 | 31.58 | 31.86 | 31.68 |  |  | 45.58 | 45.77 | 45.6
| 17 | 3.7 | 12 | 3 | 54.8 | 670 | 192 | 5.03 | 2750 | 86 | 1294 | 1 |  | 3.86 | 12.4286 | 19 | 31.54 | 31.83 | 31.66 |  |  | 45.58 | 45.76 | 45.61
| 18 | 6.2 | 9 | 1 | 59.6 | 680 | 186 | 5.11 | 2510 | 87 | 1220 | 1 |  | 4.3029 | 11.7143 | 20 | 17.3 | 31.72 | 21.88 |  |  | 35.66 | 45.7 | 38.87
| 19 | 4.24 | 11 | 2 | 54.2 | 760 | 186 | 5.91 | 2820 | 85 | 1525 | 1 |  | 4.2629 | 10.4286 | 21 | 17.3 | 31.27 | 27.18 |  |  | 35.67 | 45.19 | 42.38
| 20 | 5.68 | 16 | 3 |  | 830 | 190 | 6.47 | 2890 | ER | 1453 | 1 |  | 4.56 | 11.4286 | 22 | 31.17 | 31.64 | 31.4 |  |  | 45.16 | 45.53 | 45.37
| 21 | 5.7 | 18 | 6 |  | 760 | 192 | 7.4 | 2890 | 86 | 1473 | 1 | 4.7886 | 4.7886 | 12.4286 | 23 | 31.42 | 31.74 | 31.55 |  |  | 45.39 | 45.62 | 45.49
| 22 | 5.3 | 14 | 3 | 58.6 | 720 | 190 | 5.64 | 2880 | 86 | 1432 | 1 |  | 4.96 | 13.1429 | 24 | 31.39 | 31.62 | 31.51 |  |  | 45.36 | 45.53 | 45.49
| 23 | 6.2 | 17 | 5 | 51.4 | 710 | 192 | 7.72 | 3050 | 86 | 1555 | 1 |  | 5.2886 | 13.8571 | 25 | 31.31 | 31.57 | 31.46 |  |  | 45.34 | 45.49 | 45.47
| 24 | 6.1 | 27 | 11 | 60.3 | 730 | 190 | 6.49 | 3111 | 86 | 1638 | 1 |  | 5.6314 | 16 | 26 | 31.31 | 31.67 | 31.46 |  |  | 45.37 | 45.62 | 45.47
| 25 | 3.9 | 18 | 6 | 54.4 | 760 | 190 | 6.63 | 3070 | 84 | 1430 | 1 |  | 5.3029 | 17.2857 | 27 | 17.39 | 31.79 | 23.53 |  |  | 37.45 | 45.72 | 41.02
| 26 | 3.7 | 13 | 3 | 53.6 | 720 | 190 | 5.58 | 3050 | 84 | 1548 | 1 |  | 5.2257 | 17.5714 | 28 | 16.91 | 31.4 | 26.88 |  |  | 37.38 | 45.32 | 42.75
| 27 | 4 | 10 | 2 |  | 700 | 192 | 6.13 | 3150 | 83.6 | 1440 | 1 |  | 4.9857 | 16.7143 | 29 | 31.24 | 31.57 | 31.42 |  |  | 45.3 | 45.46 | 45.41
| 28 | 4 | 14 | 4 |  | 720 | 190 | 5.13 | 3230 | 84 | 1605 | 1 |  | 4.7429 | 16.1429 | 30 | 31.24 | 31.57 | 31.43 |  |  | 45.31 | 45.48 | 45.43
| 29 | 4 | 16 | 4 | 52.5 | 740 | 194 | 5.92 | 2930 | 83 | 1470 | 1 |  | 4.5571 | 16.4286 | 31 | ER | ER | ER |  |  | ER | ER | ER
| 30 | 6 | 18 | 4 | 56.9 | 720 | 192 | 5.23 | 2890 | 83 | 1383 | 1 |  | 4.5286 | 16.5714 | TOTAL | 845.45 | 957.13 | 902.66 |  |  | 1302.08 | 1370.28 | 1337.15
| 31 | 8 | 21 | 2 | 77.3 | 710 | 188 | 12.8 | 2680 | 83 | 1380 | 1 | 5.12 | 4.8 | 15.7143 | AVERAGE | 28.1817 | 31.9043 | 30.0887 |  |  | 43.4027 | 45.676 | 44.5717
| TOTAL | 135.19 | 435 | 103 | 1306.1 | 22200 | 5870 | 184.29 | 83741 | 2458.6 | 42285 |  |  |  |  | MAXIMUM | 32.14 | 32.43 | 32.31 |  |  | 45.86 | 46.03 | 45.98
| AVERAGE | 4.361 | 14.0323 | 3.3226 | 56.787 | 716.129 | 189.3548 | 5.9448 | 2791.3667 | 84.7793 | 1364.0323 |  |  | 4.2792 | 13.9543 | MINIMUM | 16.91 | 31.27 | 21.88 |  |  | 35.66 | 45.19 | 38.87
| MAXIMUM | 8 | 27
[5 empty] | PAGE 4 | [14 empty] | PAGE 22
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
[5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [13 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
[5 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [13 empty] | MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
[5 empty] | MONTHLY OPERATIONAL REPORT | [13 empty] | REGIONAL MONITORING WELL ONE
[5 empty] | EFFLUENT DATA PART 2 | [13 empty] | RMW-1
[16 empty] | RUN DATE |  |  | UC06-249353
[16 empty] | 2026-07-30 |  | UPPER MONITOR ZONE |  |  |  |  | LOWER MONITOR ZONE
RUN DATE | [16 empty] | MIN | MAX | AVG |  |  | MIN | MAX | AVG
2026-07-30 | [15 empty] | OCTOBER | FT HEAD | FT HEAD | FT HEAD |  |  | FT HEAD | FT HEAD | FT HEAD
[16 empty] | 2003 | ABOVE | ABOVE | ABOVE |  |  | ABOVE | ABOVE | ABOVE
| OCTOBER | EFF. BACT. | EFF. BACT. | FREE | TOTAL | EFFL. | EFF PH | EFF PH | EFF. SAP | AVG. | [6 empty] | NGVD | NGVD | NGVD |  |  | NGVD | NGVD | NGVD
| 2003 | TOTAL | FECAL | CL2 | CL2 | pH | MIN | MAX | TEMP.(C) | BLK. | [5 empty] | 1 | 44.38 | 44.53 | 44.45 |  |  | 22.47 | 22.65 | 22.56
[16 empty] | 2 | 44.51 | 44.66 | 44.59 |  |  | 22.59 | 22.76 | 22.68
| 1 | 8667 | 0 | 0 | 0.8 | 6.8 | 6.8 | 6.8 | 5 | 18 | [5 empty] | 3 | 44.63 | 44.75 | 44.69 |  |  | 22.63 | 22.8 | 22.72
| 2 | 36500 | 36 | 0 | 0.8 | 6.7 | 6.6 | 6.6 | 5 | 12 | [5 empty] | 4 | 44.69 | 44.79 | 44.75 |  |  | 22.64 | 22.8 | 22.73
| 3 | 4000 | 9 | 0 | 0.8 | 6.7 | 6.7 | 6.8 | 5 | 14 | [5 empty] | 5 | 44.71 | 44.82 | 44.77 |  |  | 22.62 | 22.76 | 22.7
| 4 | 839 | 0 | 0 | 0.7 | 6.7 | 6.7 | 6.8 | 0 | 20 | [5 empty] | 6 | 30.66 | 44.83 | 35.42 |  |  | 20.39 | 22.72 | 21.48
| 5 | 5100 | 0 | 0 | 0.8 | 6.7 | 6.6 | 6.8 | 5 | 19 | [5 empty] | 7 | 27.48 | 44.05 | 40.1 |  |  | 20.8 | 33.03 | 21.9
| 6 | 3500 | 0 | 0 | 0.7 | 6.8 | 6.7 | 6.9 | 4 | 20 | [5 empty] | 8 | 44.05 | 44.24 | 44.15 |  |  | 22.41 | 22.64 | 22.53
| 7 | 455 | 0 | 0 | 0.9 | 6.7 | 6.6 | 6.8 | 5 | 20 | [5 empty] | 9 | 44.18 | 44.31 | 44.25 |  |  | 22.61 | 22.74 | 22.69
| 8 | 3500 | 0 | 0 | 0.8 | 6.8 | 6.7 | 6.8 | 4 | 14 | [5 empty] | 10 | 44.24 | 44.34 | 44.29 |  |  | 22.73 | 22.82 | 22.77
| 9 | 18000 | 10 | 0 | 0.8 | 6.8 | 6.7 | 6.8 | 4 | 20 | [5 empty] | 11 | 44.23 | 44.34 | 44.29 |  |  | 22.75 | 22.82 | 22.78
| 10 | 4900 | 0 | 0 | 0.9 | 6.8 | 6.7 | 6.8 | 5 | 17 | [5 empty] | 12 | 44.22 | 44.33 | 44.28 |  |  | 22.76 | 22.82 | 22.79
| 11 | 107 | 9 | 0 | 1.2 | 6.7 | 6.6 | 6.7 | 5 | 23 | [5 empty] | 13 | 44.21 | 44.32 | 44.27 |  |  | 22.73 | 22.84 | 22.79
| 12 | 320 | 0 | 0 | 1.3 | 6.7 | 6.6 | 6.8 | 4 | 28 | [5 empty] | 14 | 44.21 | 44.34 | 44.27 |  |  | 22.72 | 22.88 | 22.8
| 13 | 3900 | 0 | 0 | 1 | 6.6 | 6.5 | 6.7 | 4 | 23 | [5 empty] | 15 | 44.15 | 44.28 | 44.23 |  |  | 22.69 | 22.82 | 22.76
| 14 | 0 | 0 | 0 | 0.6 | 6.6 | 6.5 | 6.7 | 4 | 20 | [5 empty] | 16 | 44.1 | 44.18 | 44.15 |  |  | 22.6 | 22.7 | 22.67
| 15 | TNTC | TNTC | 0 | 0 | 6.7 | 6.6 | 6.8 | 4 | 18 | [5 empty] | 17 | ER | ER | ER |  |  | ER | ER | ER
| 16 | TNTC | TNTC | 0 | 0 | 6.8 | 6.7 | 6.8 | 4 | 13 | [5 empty] | 18 | ER | ER | ER |  |  | ER | ER | ER
| 17 | TNTC | TNTC | 0 | 0.2 | 6.8 | 6.7 | 6.8 | 5 | 13 | [5 empty] | 19 | ER | ER | ER |  |  | ER | ER | ER
| 18 | 4500 | 36 | 0 | 0.9 | 6.7 | 6.6 | 6.8 | 5 | 21 | [5 empty] | 20 | ER | ER | ER |  |  | ER | ER | ER
| 19 | 610 | 0 | 0 | 0.9 | 6.6 | 6.5 | 6.8 | 3 | 20 | [5 empty] | 21 | ER | ER | ER |  |  | ER | ER | ER
| 20 | 205 | 0 | 0 | 0.4 | 6.7 | 6.5 | 6.8 | 4 | 19 | [5 empty] | 22 | ER | ER | ER |  |  | ER | ER | ER
| 21 | TNTC | 70500 | 0 | 0.2 | 6.7 | 6.7 | 6.8 | 3 | 15 | [5 empty] | 23 | ER | ER | ER |  |  | ER | ER | ER
| 22 | 44500 | 63 | 0 | 0.9 | 6.8 | 6.7 | 6.8 | 4 | 14 | [5 empty] | 24 | ER | ER | ER |  |  | ER | ER | ER
| 23 | 25500 | 36 | 0 | 0.9 | 6.7 | 6.7 | 6.8 | 4 | 11 | [5 empty] | 25 | ER | ER | ER |  |  | ER | ER | ER
| 24 | TNTC | 9 | 0 | 0.9 | 6.7 | 6.6 | 6.7 | 5 | 16 | [5 empty] | 26 | ER | ER | ER |  |  | ER | ER | ER
| 25 | 18 | 0 | 0 | 1 | 6.6 | 6.5 | 6.7 | 5 | 15 | [5 empty] | 27 | ER | ER | ER |  |  | ER | ER | ER
| 26 | 0 | 0 | 0 | 1 | 6.6 | 6.5 | 6.7 | 3 | 12 | [5 empty] | 28 | ER | ER | ER |  |  | ER | ER | ER
| 27 | 4000 | 0 | 0 | 0.6 | 6.6 | 6.4 | 6.8 | 4 | 13 | [5 empty] | 29 | ER | ER | ER |  |  | ER | ER | ER
| 28 | 4700 | 54 | 0 | 0.9 | 6.6 | 6.5 | 6.6 | 5 | 13 | [5 empty] | 30 | ER | ER | ER |  |  | ER | ER | ER
| 29 | 167 | 0 | 0 | 0.6 | 6.6 | 6.6 | 6.6 | 4 | 9 | [5 empty] | 31 | ER | ER | ER |  |  | ER | ER | ER
| 30 | 700 | 0 | 0 | 0.7 | 6.7 | 6.6 | 6.8 | 5 | 8 | [5 empty] | TOTAL | 678.65 | 711.11 | 696.95 |  |  | 358.14 | 374.6 | 361.35
| 31 | TNTC | 240 | 0 | 0.6 | 6.8 | 6.7 | 6.8 | 6 | 9 | [5 empty] | AVERAGE | 42.4156 | 44.4444 | 43.5594 |  |  | 22.3837 | 23.4125 | 22.5844
| TOTAL | 174688 | 71002 | 0 | 22.8 | 207.8 | 205.1 | 209.7 | 132 | 507 | [5 empty] | MAXIMUM | 44.71 | 44.83 | 44.77 |  |  | 22.76 | 33.03 | 22.8
| AVERAGE | 6987.52 | 2535.7857 | 0 | 0.73548 | 6.7032 | 6.6161 | 6.7645 | 4.2581 | 16.3548 | [5 empty] | MINIMUM | 27.48 | 44.05 | 35.42 |  |  | 20.39 | 22.64 | 21.48
[7 empty] | 6.4 | 6.9
[7 empty] | MIN | MAX
PAGE 5
PAGE 23
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
NUTRIENTS
RUN DATE
| 2026-07-30 |  | INFLUENT | [5 empty] | EFFLUENT
| OCTOBER | INFLUENT | INFLUENT | INFLUENT | INFLUENT |  | EFFL. | EFFL. | EFFL. | EFFL.
| 2003 | NH-3 | N03-N | TKN | TOT P |  | NH-3 | N03-N | TKN | TOT P
| 1 | 10.92 | 0.229 | 14.36 | 1.46 |  | 7.98 | 0.622 | 10.97 | 0.869
| 2 | 10.91 | 0.277 | 15.08 | 1.6 |  | 8.36 | 0.674 | 11.55 | 0.685
| 3 | 11.31 | 0.288 | 15.26 | 1.72 |  | 8.33 | 0.678 | 11.49 | 0.78
| 4 | 11.34 | 0.249 | 14.95 | 1.72 |  | 7.51 | 0.787 | 10.54 | 0.697
| 5 | 11.34 | 0.249 | 14.95 | 1.72 |  | 7.51 | 0.787 | 10.54 | 0.697
6
7
| 8 | 14.03 | 0.264 | 18.16 | 2.16 |  | 10.49 | 0.756 | 14.02 | 0.965
| 9 | 14.82 | 0.273 | 18.11 | 2.09 |  | 10.75 | 0.78 | 14.02 | 1.24
| 10 | 14.58 | 0.281 | 18.95 | 2.2 |  | 10.3 | 0.794 | 13.96 | 0.721
| 11 | 14.22 | 0.299 | 18.53 | 2.21 |  | 9.84 | 0.75 | 13.32 | 0.653
| 12 | 14.03 | 0.317 | 17.83 | 2.3 |  | 10 | 0.877 | 13.57 | 0.967
13
14
| 15 | 15.63 | 0.02 | 20.88 | 2.98 |  | 11.64 | 0.426 | 16.32 | 0.948
| 16 | 13.62 | 0.02 | 18.85 | 2.23 |  | 12.24 | 0.474 | 16.78 | 0.99
| 17 | 15.73 | 0.02 | 20.65 | 2.38 |  | 12.33 | 0.432 | 17.07 | 0.912
| 18 | 14.36 | 0.02 | 19.84 | 2.39 |  | 10.89 | 0.373 | 15.23 | 0.71
| 19 | 14.97 | 0.02 | 19.98 | 2.45 |  | 10.61 | 0.541 | 14.74 | 1.03
20
21
| 22 | 15.59 | 0.02 | 20.59 | 2.4 |  | 11.81 | 0.328 | 16.17 | 1.56
| 23 | 15.17 | 0.02 | 20.65 | 2.55 |  | 12.09 | 0.456 | 0 | 1.47
| 24 | 15.47 | 0.02 | 20.63 | 2.35 |  | 11.94 | 0.36 | 16.64 | 1.01
| 25 | 15.46 | 0.02 | 20.71 | 2.47 |  | 10.87 | 0.378 | 15.17 | 0.826
| 26 | 15.14 | 0.02 | 20.72 | 4.05 |  | 10.86 | 0.629 | 15.38 | 0.7
27
28
| 29 | 12.2 | 0.02 | 18.39 | 2.31 |  | 10.03 | 0.415 | 15.53 | 1.3
| 30 | 13.25 | 0.02 | 19.92 | 2.64 |  | 10 | 0.372 | 15.59 | 1.77
| 31 | 14.02 | 0.02 | 20.35 | 2.52 |  | 9.99 | 0.17 | 15.81 | 1.16
| TOTAL | 318.11 | 2.986 | 428.34 | 52.9 | TOT. | 236.37 | 12.859 | 314.41 | 22.66
| AVERAGE | 13.8309 | 0.12983 | 18.6235 | 2.3 | AVG. | 10.277 | 0.55909 | 13.67 | 0.98522
PAGE 6
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
REACTOR ONE PROCESS
RUN DATE
| 2026-07-30 |  | TRAIN "A" | [5 empty] | TRAIN "B"
| OCTOBER | MLSS | MLVSS | SS | SVI |  | MLSS | MLVSS | SS | SVI
| 2003 | "A" | "A" | "A" | "A" |  | "B" | "B" | "B" | "B"
| 1 | O/S | O/S | O/S |  |  | 1500 | 1240 | 11 | 73.3333
| 2 | O/S | O/S | O/S |  |  | 1180 | 980 | 11 | 93.2203
| 3 | O/S | O/S | O/S |  |  | 1230 | 970 | 13 | 105.6911
| 4 | O/S | O/S | O/S |  |  | 1590 | 1320 | 15 | 94.3396
| 5 | O/S | O/S | O/S |  |  | 1910 | 1550 | 16 | 83.7696
| 6 | O/S | O/S | O/S |  |  | 1610 | 1360 | 12 | 74.5342
| 7 | O/S | O/S | O/S |  |  | 1520 | 1260 | 14 | 92.1053
| 8 | O/S | O/S | O/S |  |  | 1490 | 1240 | 10 | 67.1141
| 9 | O/S | O/S | O/S |  |  | 1500 | 1240 | 10 | 66.6667
| 10 | O/S | O/S | O/S |  |  | 1320 | 1100 | 12 | 90.9091
| 11 | O/S | O/S | O/S |  |  | 2100 | 1910 | 14 | 66.6667
| 12 | O/S | O/S | O/S |  |  | 2000 | 1620 | 17 | 85
| 13 | O/S | O/S | O/S |  |  | 2100 | 1740 | 15 | 71.4286
| 14 | O/S | O/S | O/S |  |  | 1340 | 1120 | 15 | 111.9403
| 15 | O/S | O/S | O/S |  |  | 1310 | 1090 | 14 | 106.8702
| 16 | O/S | O/S | O/S |  |  | 1460 | 1170 | 13 | 89.0411
| 17 | O/S | O/S | O/S |  |  | 1390 | 1120 | 14 | 100.7194
| 18 | O/S | O/S | O/S |  |  | 1640 | 1360 | 15 | 91.4634
| 19 | O/S | O/S | O/S |  |  | 1660 | 1380 | 16 | 96.3855
| 20 | O/S | O/S | O/S |  |  | 1670 | 1390 | 13 | 77.8443
| 21 | O/S | O/S | O/S |  |  | 1640 | 1340 | 12 | 73.1707
| 22 | O/S | O/S | O/S |  |  | 1220 | 1010 | 11 | 90.1639
| 23 | O/S | O/S | O/S |  |  | 1480 | 1230 | 12 | 81.0811
| 24 | O/S | O/S | O/S |  |  | 1320 | 1130 | 11 | 83.3333
| 25 | O/S | O/S | O/S |  |  | 1380 | 1150 | 14 | 101.4493
| 26 | O/S | O/S | O/S |  |  | 2240 | 1860 | 15 | 66.9643
| 27 | O/S | O/S | O/S |  |  | 1620 | 1340 | 14 | 86.4198
| 28 | O/S | O/S | O/S |  |  | 1850 | 1540 | 14 | 75.6757
| 29 | O/S | O/S | O/S |  |  | 1000 | 830 | 12 | 120
| 30 | O/S | O/S | O/S |  |  | 820 | 680 | 8 | 97.561
| 31 | O/S | O/S | O/S |  |  | 1220 | 1060 | 8 | 65.5738
| TOTAL | 0 | 0 | 0 |  |  | 47310 | 39330 | 401
| AVERAGE | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1526.129 | 1268.7097 | 12.9355 | 84.7601
PAGE 7
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
REACTOR TWO PROCESS
RUN DATE
| 2026-07-30 |  | TRAIN "C" | [5 empty] | TRAIN "D"
| OCTOBER | MLSS | MLVSS | SS | SVI |  | MLSS | MLVSS | SS | SVI
| 2003 | "C" | "C" | "C" | "C" |  | "D" | "D" | "D" | "D"
| 1 | O/S | O/S | O/S |  |  | 1370 | 1140 | 11 | 80.292
| 2 | O/S | O/S | O/S |  |  | 1500 | 1240 | 12 | 80
| 3 | O/S | O/S | O/S |  |  | 1700 | 1390 | 14 | 82.3529
| 4 | O/S | O/S | O/S |  |  | 1810 | 1500 | 17 | 93.9227
| 5 | O/S | O/S | O/S |  |  | 1840 | 1490 | 17 | 92.3913
| 6 | O/S | O/S | O/S |  |  | 1810 | 1480 | 15 | 82.8729
| 7 | O/S | O/S | O/S |  |  | 1730 | 1520 | 16 | 92.4855
| 8 | O/S | O/S | O/S |  |  | 2270 | 1980 | 13 | 57.2687
| 9 | O/S | O/S | O/S |  |  | 1850 | 1540 | 14 | 75.6757
| 10 | O/S | O/S | O/S |  |  | 1840 | 1460 | 14 | 76.087
| 11 | O/S | O/S | O/S |  |  | 1100 | 880 | 15 | 136.3636
| 12 | O/S | O/S | O/S |  |  | 2940 | 2610 | 19 | 64.6259
| 13 | O/S | O/S | O/S |  |  | 2300 | 1910 | 16 | 69.5652
| 14 | O/S | O/S | O/S |  |  | 1780 | 1500 | 16 | 89.8876
| 15 | O/S | O/S | O/S |  |  | 1530 | 1270 | 14 | 91.5033
| 16 | O/S | O/S | O/S |  |  | 1710 | 1410 | 14 | 81.8713
| 17 | O/S | O/S | O/S |  |  | 1610 | 1320 | 14 | 86.9565
| 18 | O/S | O/S | O/S |  |  | 1710 | 1420 | 15 | 87.7193
| 19 | O/S | O/S | O/S |  |  | 1860 | 1540 | 16 | 86.0215
| 20 | O/S | O/S | O/S |  |  | 2180 | 1810 | 14 | 64.2202
| 21 | O/S | O/S | O/S |  |  | 1580 | 1290 | 13 | 82.2785
| 22 | O/S | O/S | O/S |  |  | 1820 | 1510 | 11 | 60.4396
| 23 | O/S | O/S | O/S |  |  | 1350 | 1120 | 12 | 88.8889
| 24 | O/S | O/S | O/S |  |  | 1460 | 1250 | 12 | 82.1918
| 25 | O/S | O/S | O/S |  |  | 1500 | 1240 | 16 | 106.6667
| 26 | O/S | O/S | O/S |  |  | 1830 | 1520 | 14 | 76.5027
| 27 | O/S | O/S | O/S |  |  | 1520 | 1260 | 14 | 92.1053
| 28 | O/S | O/S | O/S |  |  | 2350 | 1950 | 14 | 59.5745
| 29 | O/S | O/S | O/S |  |  | 1050 | 870 | 12 | 114.2857
| 30 | O/S | O/S | O/S |  |  | 800 | 660 | 9 | 112.5
| 31 | O/S | O/S | O/S |  |  | 1970 | 1570 | 9 | 45.6853
| TOTAL | 0 | 0 | 0 |  |  | 53670 | 44650 | 432
| AVERAGE | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1731.2903 | 1440.3226 | 13.9355 | 80.4919
PAGE 8
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
RAS SUMMARY
RUN DATE
2026-07-30
| OCTOBER | R-1 | R-2 | TOTAL | F/M | TOTAL | SLUDGE | % TOT | % FIX | % VOL.
| 2003 | TOT. RAS | TOT. RAS | MLVSS | RATIO | MLSS | AGE | RAS | RAS | RAS
|  | MGD | MGD
| 1 | 5.697 | 7.181 | 2380 | 0.52777 | 2870 | 0.60549 | 0.7 | 24.7 | 75.3
| 2 | 6.015 | 7.19 | 2220 | 1.4222 | 2680 | 0.69031 | 0.77 | 26 | 74
| 3 | 5.825 | 7.925 | 2360 | 0.95713 | 2930 | 0.52944 | 0.78 | 25.6 | 74.4
| 4 | 5.173 | 7.579 | 2820 | 0.9972 | 3400 | 0.87321 | 0.74 | 22.8 | 77.2
| 5 | 5.095 | 6.995 | 3040 | 0.98419 | 3750 | 1.0564 | 0.82 | 24.3 | 75.7
| 6 | 5.021 | 7.468 | 2840 | 0.93691 | 3420 | 0.9234 | 0.7 | 26.2 | 73.8
| 7 | 5.208 | 6.589 | 2780 | 1.3797 | 3250 | 0.71491 | 0.75 | 26.5 | 73.5
| 8 | 4.368 | 6.579 | 3220 | 0.72565 | 3760 | 2.0517 | 0.62 | 24.6 | 75.4
| 9 | 4.145 | 7.536 | 2780 | 1.0439 | 3350 | 0.8725 | 0.69 | 30.4 | 69.6
| 10 | 3.746 | 7.194 | 2560 | 0.94985 | 3160 | 0.74074 | 0.88 | 21.3 | 78.7
| 11 | 3.466 | 8.058 | 2790 | 1.44 | 3200 | 0.76258 | 1.07 | 20 | 80
| 12 | 3.656 | 7.782 | 4230 | 0.94336 | 4940 | 1.3157 | 0.79 | 24.7 | 75.3
| 13 | 3.754 | 6.557 | 3650 | 0.89717 | 4400 | 1.1197 | 0.8 | 27.2 | 72.8
| 14 | 3.812 | 6.473 | 2620 | 1.0557 | 3120 | 0.68104 | 0.74 | 26.8 | 73.2
| 15 | 4.556 | 6.656 | 2360 | 1.3213 | 2840 | 0.63053 | 0.7 | 24.5 | 75.5
| 16 | 5.418 | 6.674 | 2580 | 1.0136 | 3170 | 0.74873 | 0.66 | 25 | 75
| 17 | 4.898 | 7.31 | 2440 | 1.4089 | 3000 | 0.70686 | 0.7 | 28.6 | 71.4
| 18 | 4.869 | 7.183 | 2780 | 1.1877 | 3350 | 1.0016 | 0.7 | 25.7 | 74.3
| 19 | 5.593 | 7.503 | 2920 | 0.99853 | 3520 | 0.81838 | 0.7
| 20 | 5.011 | 6.024 | 3200 | 0.79983 | 3850 | 1.077 | 0.8 | 24.5 | 75.5
| 21 | 5.045 | 6.692 | 2630 | 1.0727 | 3220 | 0.73531 | 0.65 | 27.5 | 72.5
| 22 | 5.546 | 6.879 | 2520 | 1.2835 | 3040 | 0.76992 | 0.7 | 28 | 72
| 23 | 5.321 | 7.669 | 2350 | 1.22 | 2830 | 0.75155 | 0.55 | 28.7 | 71.3
| 24 | 4.753 | 7.988 | 2380 | 1.3152 | 2780 | 0.64834 | 0.66 | 30.1 | 69.9
| 25 | 4.383 | 7.817 | 2390 | 0.94666 | 2880 | 0.7448 | 0.53 | 26.4 | 73.6
| 26 | 4.2 | 7.397 | 3380 | 0.76909 | 4070 | 1.67 | 0.7 | 23 | 77
| 27 | 4.071 | 6.721 | 2600 | 1.0891 | 3140 | 0.77623 | 0.67 | 25 | 75
| 28 | 3.835 | 6.746 | 3490 | 0.63278 | 4200 | 1.7433 | 0.61 | 24.8 | 75.2
| 29 | 4.475 | 6.44 | 1700 | 2.5385 | 2050 | 0.45988 | 0.54 | 27.9 | 72.1
| 30 | 4.043 | 5.591 | 1340 | 1.6976 | 1620 | 0.28931 | 0.43 | 22.4 | 77.6
| 31 | 3.583 | 6.568 | 2630 | 0.64742 | 3190 | 0.6983 | 0.46 | 25.5 | 74.5
| TOTAL | 144.581 | 218.964 | 83980 |  | 100980 |  | 21.61 | 768.7 | 2231.3
| AVERAGE | 4.6639 | 7.0634 | 2709.0323 | 1.0724 | 3257.4194 | 0.80757 | 0.6971 | 25.6233 | 74.3767
PAGE 9
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
DEWATERING DATA
RUN DATE
| 2026-07-30 |  | FEED SLUDGE |  |  |  |  | FILTRATE RETURN
| OCTOBER | % TOT. | % FIX. | % VOL. | pH |  | % TOT. | % FIX. | % VOL. | pH
| 2003 | FEED | FEED | FEED |  |  | FILT. | FILT. | FILT.
| 1 | 0.97 | 25.8 | 74.2 | 6.78 |  | 0.38 | 39.5 | 60.5 | 7.21
| 2 | 1.39 | 25.2 | 74.8 | 6.71 |  | 0.2 | 45 | 55 | 7.19
3
4
| 5 | 1.39 | 22.3 | 77.7 | 6.91 |  | 0.39 | 38.46 | 61.54 | 7.15
| 6 | 1.09 | 27.5 | 72.5 | 6.46 |  | 0.21 | 61.9 | 38.1 | 6.97
| 7 | 1.22 | 23.8 | 76.2 | 6.48 |  | 0.4 | 40 | 60 | 7.05
| 8 | 1.11 | 24.3 | 75.7 | 6.78 |  | 0.31 | 45.2 | 54.8 | 7.45
| 9 | 1.42 | 21.8 | 78.2 | 6.74 |  | 0.38 | 42.1 | 57.9 | 7.22
10
11
12
| 13 | 1.33 | 21.8 | 78.2 | 6.53 |  | 0.45 | 37.8 | 62.2 | 7.04
| 14 | 1.34 | 21.6 | 78.4 | 6.45 |  | 0.46 | 37 | 63 | 7.11
| 15 | 1.41 | 22 | 78 | 6.79 |  | 0.46 | 37 | 63 | 7.09
| 16 | 1.24 | 24.2 | 75.8 | 6.57 |  | 0.34 | 50 | 50 | 7.03
17
18
| 19 | 1.59 | 23.9 | 76.1 | 6.77 |  | 0.43 | 55.8 | 44.2 | 7.11
| 20 | 1.6 | 21.3 | 78.7 | 6.79 |  | 0.33 | 48.5 | 51.5 | 7.19
| 21 | 1.24 | 23.4 | 76.6 | 6.71 |  | 0.47 | 36.2 | 63.8 | 7.27
| 22 | 1.51 | 21.2 | 78.8 | 6.74 |  | 0.31 | 48.4 | 51.6 | 7.19
| 23 | 0.83 | 28.9 | 71.1 | 6.74 |  | 0.27 | 55.5 | 44.5 | 7.15
24
25
26
| 27 | 1.42 | 23.9 | 76.1 | 6.78 |  | 0.45 | 55.6 | 44.4 | 7.14
| 28 | 1.41 | 22.7 | 77.3 | 6.76 |  | 0.36 | 47.2 | 52.8 | 7.11
| 29 | 1.56 | 22.4 | 77.6 | 6.78 |  | 0.42 | 47.6 | 52.4 | 7.21
| 30 | 0.93 | 24.7 | 75.3 | 6.78 |  | 0.16 | 81.2 | 18.8 | 7.19
31
| TOTAL | 26 | 472.7 | 1527.3 | 134.05 |  | 7.18 | 949.96 | 1050.04 | 143.07
| AVERAGE | 1.3 | 23.635 | 76.365 | 6.7025 |  | 0.359 | 47.498 | 52.502 | 7.1535
PAGE 10
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
SLUDGE VOLUME REMOVED
RUN DATE
2026-07-30
|  | OCTOBER | TRAILERS | TONS | DRY TONS | % LIME | % TOT. | % FIX. | % VOL.
|  | 2003 | REMOVED | SLUDGE | REMOVED | CAKE | CAKE | CAKE | CAKE
|  | 1 | 4 | 100 | 18.9301 |  | 16.68 | 17.7 | 82.3
|  | 2 | 6 | 150 | 32.923 |  | 19.64 | 15.3 | 84.7
|  | 3 | 3 | 75
|  | 4 | 0 | 0
|  | 5 | 1 | 25 | 13.5054 |  | 18.39 | 16.2 | 83.8
|  | 6 | 6 | 150 | 27.2263 |  | 19.66 | 14.9 | 85.1
|  | 7 | 6 | 150 | 31.3893 |  | 19.6 | 19.1 | 80.9
|  | 8 | 5 | 125 | 26.1059 |  | 19.28 | 16 | 84
|  | 9 | 4 | 100 | 26.291 |  | 17.9 | 18 | 82
|  | 10 | 2 | 50
|  | 11 | 0 | 0
|  | 12 | 1 | 25
|  | 13 | 5 | 125 | 35.7723 |  | 18.93 | 20.1 | 79.9
|  | 14 | 5 | 125 | 34.812 |  | 19.29 | 15.6 | 84.4
|  | 15 | 6 | 150 | 38.7472 |  | 18.93 | 17.4 | 82.6
|  | 16 | 6 | 150 | 32.3692 |  | 19.67 | 16.4 | 83.6
|  | 17 | 4 | 100
|  | 18 | 0 | 0
|  | 19 | 1 | 25 | 14.8519 |  | 18.12 | 16.2 | 83.8
|  | 20 | 6 | 150 | 31.6253 |  | 19.41 | 18 | 82
|  | 21 | 6 | 150 | 28.6462 |  | 19.29 | 16.3 | 83.7
|  | 22 | 6 | 150 | 34.5689 |  | 19.44 | 13.4 | 86.6
|  | 23 | 6 | 150 | 18.9322 |  | 21.06 | 23 | 77
|  | 24 | 4 | 100
|  | 25 | 0 | 0
|  | 26 | 0 | 0
|  | 27 | 5 | 125 | 29.4294 |  | 15.88 | 18.3 | 81.7
|  | 28 | 6 | 150 | 30.0453 |  | 18.96 | 13.7 | 86.3
|  | 29 | 6 | 150 | 33.827 |  | 19.62 | 14 | 86
|  | 30 | 6 | 150 | 21.6398 |  | 21 | 14.8 | 85.2
|  | 31 | 3 | 75
|  | TOTAL | 119 | 2975 | 561.6377 | 0 | 380.75 | 334.4 | 1665.6
|  | AVERAGE | 3.8387 | 95.9677 | 28.0819 | #DIV/0! | 19.0375 | 16.72 | 83.28
PAGE 11
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
CHEMICAL USEAGE
RUN DATE
2026-07-30
| OCTOBER | H2O2 | CL2 | POLYMER | POLYMER | LIME | GOX | O2 % | LOX | FPL
| 2003 | POUNDS | POUNDS | GALLONS | POUNDS | DELV. | TONS | PURITY | TONS | KW
| 1 | 1896 | 1000 | 17 | 141.78 | 0 | 28.2 | 100% | 101 | 19506
| 2 | 2076 | 900 | 60 | 500.4 | 0 | 22.8 | 100% | 101 | 32333
| 3 | 1577 | 960 | 4 | 33.36 | 0 | 25.7 | 100% | 101 | 29404
| 4 | 4515 | 1080 | 9 | 75.06 | 0 | 26.8 | 100% | 101 | 30876
| 5 | 1497 | 1080 | 17 | 141.78 | 0 | 28.2 | 99% | 101 | 30696
| 6 | 1647 | 1000 | 68 | 567.12 | 0 | 26.6 | 100% | 102 | 31007
| 7 | 1687 | 1080 | 60 | 500.4 | 0 | 27.1 | 100% | 104 | 30957
| 8 | 1377 | 1100 | 68 | 567.12 | 0 | 26.9 | 100% | 106 | 30821
| 9 | 1308 | 1000 | 34 | 283.56 | 0 | 30 | 97% | 106 | 30773
| 10 | 1088 | 1260 | 34 | 283.56 | 0 | 34.7 | 99% | 107 | 30603
| 11 | 1328 | 1440 | 2 | 16.68 | 0 | 37.9 | 95% | 107 | 30523
| 12 | 977 | 1440 | 24 | 200.16 | 0 | 32.6 | 100% | 106 | 30744
| 13 | 1357 | 1400 | 57 | 475.38 | 0 | 28.8 | 99% | 107 | 30762
| 14 | 1107 | 560 | 75 | 625.5 | 0 | 26.1 | 100% | 108 | 30825
| 15 | 1676 | 0 | 75 | 625.5 | 0 | 32.3 | 99% | 108 | 28715
| 16 | 958 | 220 | 55 | 458.7 | 0 | 33.2 | 99% | 109 | 30882
| 17 | 1597 | 620 | 0 | 0 | 0 | 41.5 | 96% | 109 | 30740
| 18 | 2637 | 1240 | 19 | 158.46 | 0 | 40 | 100% | 108 | 30908
| 19 | 1436 | 1400 | 47 | 391.98 | 0 | 23.3 | 100% | 108 | 30645
| 20 | 1477 | 420 | 83 | 692.22 | 0 | 21.3 | 100% | 109 | 30688
| 21 | 1068 | 560 | 62 | 517.08 | 0 | 25 | 100% | 110 | 30817
| 22 | 2016 | 1100 | 66 | 550.44 | 0 | 22.2 | 99% | 111 | 30598
| 23 | 1437 | 1100 | 47 | 391.98 | 0 | 16 | 100% | 111 | 25154
| 24 | 1008 | 1520 | 0 | 0 | 0 | 11 | 100% | 113 | 31002
| 25 | 1327 | 1320 | 0 | 0 | 0 | 12 | 100% | 113 | 31244
| 26 | 949 | 1160 | 47 | 391.98 | 0 | 11 | 100% | 112 | 31356
| 27 | 1288 | 1060 | 0 | 0 | 0 | 11 | 100% | 113 | 31172
| 28 | 818 | 1060 | 81 | 675.54 | 0 | 14.5 | 100% | 114 | 31136
| 29 | 2117 | 1280 | 44 | 366.96 | 0 | 18.9 | 99% | 114 | 31136
| 30 | 1077 | 1120 | 17 | 141.78 | 0 | 16.5 | 99% | 115 | 31217
| 31 | 1835 | 1120 | 20 | 166.8 | 0 | 20.9 | 99% | 116 | 31208
| TOTAL | 48158 | 31600 | 1192 | 9941.28 | 0 | 773 |  | 3351 | 938448
| AVERAGE | 1553.4839 | 1019.3548 | 38.4516 | 320.6865 | 0 | 24.9355 | 99.32% | 108.0968 | 30272.5161
PAGE 12
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL ONE
|  | RUN DATE |  |  | PERMIT NUMBER UO-06-279401
|  | 2026-07-30 |  |  | 7/21/97 thru 7/21/02 |  |  | I.D. #:5006A11308
|  | OCTOBER | % INFL. | MAX | MIN | WELL 1 | MAX | MIN | AVG
|  | 2003 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 25.63% | 14.81 | 9.51 | 12.91 | 68.13 | 52.42 | 61.38
|  | 2 | 25.65% | 14.21 | 9.63 | 12.45 | 65.76 | 51.51 | 59.73
|  | 3 | 25.79% | 16.32 | 8.75 | 12.38 | 73.8 | 48.93 | 59.33
|  | 4 | 25.54% | 14.93 | 8.84 | 11.74 | 67.76 | 49.11 | 57.13
|  | 5 | 25.52% | 13.22 | 7.45 | 11 | 61.12 | 45.79 | 54.76
|  | 6 | 25.83% | 13.13 | 6.87 | 10.7 | 61.14 | 44.47 | 54.04
|  | 7 | 26.36% | 14.67 | 6.49 | 10.61 | 66.63 | 43.85 | 53.84
|  | 8 | 25.65% | 12.62 | 5.73 | 9.99 | 60.81 | 42.36 | 52.31
|  | 9 | 25.72% | 13.2 | 5.78 | 9.76 | 61.74 | 42.4 | 51.6
|  | 10 | 26.83% | 12.66 | 5.4 | 9.73 | 59.98 | 41.56 | 51.54
|  | 11 | 24.59% | 15.03 | 5.48 | 9.33 | 71.3 | 41.86 | 50.76
|  | 12 | 24.79% | 12.24 | 5.41 | 9.2 | 58.33 | 41.5 | 50.23
|  | 13 | 24.95% | 11.78 | 5.5 | 9.26 | 57.43 | 41.73 | 50.38
|  | 14 | 24.85% | 11.51 | 4.6 | 9.13 | 56.34 | 40.29 | 50.11
|  | 15 | 24.56% | 12.31 | 5.32 | 9.04 | 59.23 | 41.31 | 49.71
|  | 16 | 25.31% | 11.71 | 5.27 | 8.93 | 57.33 | 40.83 | 49.23
|  | 17 | 25.42% | 11.62 | 5.23 | 9.17 | 56.95 | 41.2 | 49.99
|  | 18 | 24.83% | 11.98 | 5.89 | 9.05 | 57.48 | 42.45 | 49.67
|  | 19 | 25.2% | 12.74 | 5.74 | 8.86 | 60.02 | 42.21 | 49.23
|  | 20 | 28.55% | 11.83 | 6.06 | 9.23 | 57.06 | 42.66 | 50.01
|  | 21 | 25.23% | 11.91 | 4.41 | 9.03 | 57.78 | 39.65 | 49.63
|  | 22 | 25.46% | 12.28 | 5 | 9.09 | 58.39 | 40.93 | 49.7
|  | 23 | 25.05% | 13.14 | 5.09 | 9.11 | 61.45 | 40.71 | 49.76
|  | 24 | 25.16% | 12.29 | 4.76 | 9.17 | 58.49 | 39.91 | 49.82
|  | 25 | 25.57% | 12.16 | 4.51 | 8.94 | 57.6 | 39.75 | 49.11
|  | 26 | 25.17% | 13.22 | 5.07 | 8.69 | 61.84 | 40.38 | 48.77
|  | 27 | 25.45% | 11.5 | 4.33 | 8.75 | 56.89 | 39.43 | 48.87
|  | 28 | 25.81% | 13.48 | 4.76 | 8.81 | 62.78 | 39.81 | 49.02
|  | 29 | 25.63% | 13.52 | 5.82 | 10.33 | 62.85 | 41.94 | 53.03
|  | 30 | 25.66% | 12.82 | 6.18 | 9.54 | 60.54 | 42.65 | 50.78
|  | 31 |  | ER | ER | ER | ER | ER | ER
|  | TOTAL | 765.8% | 388.84 | 178.88 | 293.93 | 1836.95 | 1283.6 | 1553.47
|  | AVERAGE | 25.53% | 12.9613 | 5.9627 | 9.7977 | 61.2317 | 42.7867 | 51.7823
|  | MAXIMUM | 28.55% | 16.32 | 9.63 | 12.91 | 73.8 | 52.42 | 61.38
|  | MINIMUM | 24.56% | 11.5 | 4.33 | 8.69 | 56.34 | 39.43 | 48.77
PAGE 13
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL TWO
|  | RUN DATE |  |  | PERMIT NUMBER UO-06-279508
|  | 2026-07-30 |  |  | 7/21/97 thru 7/21/02 |  |  | I.D. #:5006A11309
|  | OCTOBER | % INFL. | MAX | MIN | WELL 2 | MAX | MIN | AVG
|  | 2003 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 26.83% | 15.42 | 10.15 | 13.51 | 66.9 | 51.43 | 60.26
|  | 2 | 26.91% | 14.91 | 10.12 | 13.06 | 64.53 | 50.52 | 58.59
|  | 3 | 27.1% | 17.11 | 9.37 | 13.01 | 72.4 | 47.99 | 58.21
|  | 4 | 26.85% | 15.62 | 9.38 | 12.34 | 66.58 | 48.19 | 56.06
|  | 5 | 26.91% | 13.84 | 8 | 11.6 | 60.05 | 44.93 | 53.74
|  | 6 | 27.28% | 13.81 | 7.27 | 11.3 | 59.98 | 43.64 | 53.03
|  | 7 | 27.78% | 15.14 | 6.93 | 11.18 | 64.93 | 43.02 | 52.8
|  | 8 | 27.17% | 13.27 | 6.13 | 10.58 | 59.65 | 41.57 | 51.33
|  | 9 | 27.27% | 13.95 | 6.13 | 10.35 | 60.53 | 41.59 | 50.61
|  | 10 | 28.46% | 13.42 | 5.71 | 10.32 | 58.86 | 40.77 | 50.56
|  | 11 | 26.06% | 15.68 | 5.83 | 9.89 | 70.1 | 41.08 | 49.84
|  | 12 | 26.22% | 12.79 | 5.85 | 9.73 | 57.41 | 40.71 | 49.3
|  | 13 | 23.9% | 12.39 | ER | 8.87 | 56.48 | 40.94 | 49.45
|  | 14 | 26.3% | 12.13 | 4.84 | 9.66 | 57.35 | 39.53 | 49.18
|  | 15 | 26% | 12.92 | 5.66 | 9.57 | 58.08 | 40.52 | 48.78
|  | 16 | 26.84% | 12.51 | 5.67 | 9.47 | 56.22 | 40.02 | 48.3
|  | 17 | 26.86% | 12.29 | 5.6 | 9.69 | 55.85 | 40.41 | 49.04
|  | 18 | 26.26% | 12.65 | 6.18 | 9.57 | 56.51 | 41.62 | 48.74
|  | 19 | 26.68% | 13.49 | 6.03 | 9.38 | 58.88 | 41.38 | 48.28
|  | 20 | 30.25% | 12.34 | 6.41 | 9.78 | 55.93 | 41.81 | 49.07
|  | 21 | 26.71% | 12.54 | 4.67 | 9.56 | 56.65 | 38.91 | 48.73
|  | 22 | 26.97% | 12.97 | 4.51 | 9.63 | 57.23 | 39.64 | 48.78
|  | 23 | 26.61% | 13.83 | 5.32 | 9.68 | 60.23 | 39.91 | 48.84
|  | 24 | 26.75% | 13.07 | 5.03 | 9.75 | 57.35 | 39.15 | 48.9
|  | 25 | 27.23% | 12.86 | 4.69 | 9.52 | 56.52 | 38.99 | 48.17
|  | 26 | 26.82% | 13.97 | 5.31 | 9.26 | 60.76 | 39.61 | 47.86
|  | 27 | 27.13% | 12.19 | 4.6 | 9.33 | 55.94 | 38.66 | 47.96
|  | 28 |  | 14.24 | ER | ER | 61.62 | 39.05 | 48.09
|  | 29 | 27.09% | 13.9 | 6.57 | 10.92 | 61.62 | 41.16 | 52.03
|  | 30 | 27.38% | 13.36 | 6.94 | 10.18 | 59.43 | 41.79 | 49.82
|  | 31 |  | ER | ER | ER | ER | ER | ER
|  | TOTAL | 780.6% | 408.61 | 178.9 | 300.69 | 1804.57 | 1258.54 | 1524.35
|  | AVERAGE | 26.92% | 13.6203 | 6.3893 | 10.3686 | 60.1523 | 41.9513 | 50.8117
|  | MAXIMUM | 30.25% | 17.11 | 10.15 | 13.51 | 72.4 | 51.43 | 60.26
|  | MINIMUM | 23.9% | 12.13 | 4.51 | 8.87 | 55.85 | 38.66 | 47.86
PAGE 14
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL THREE
|  | RUN DATE |  |  | PERMIT NUMBER UO-06-279510
|  | 2026-07-30 |  |  | 7/21/97 thru 7/21/02 |  |  | I.D. #:5006A11310
|  | OCTOBER | % INFL. | MAX | MIN | WELL 3 | MAX | MIN | AVG
|  | 2003 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 22.97% | 13.29 | 8.57 | 11.57 | 68.56 | 52.65 | 61.71
|  | 2 | 22.91% | 12.69 | 8.62 | 11.12 | 66.13 | 51.7 | 60.01
|  | 3 | 23.04% | 14.6 | 7.8 | 11.06 | 74.2 | 49.11 | 59.63
|  | 4 | 22.76% | 13.36 | 7.89 | 10.46 | 68.1 | 49.3 | 57.39
|  | 5 | 22.74% | 11.78 | 6.61 | 9.8 | 61.49 | 45.95 | 55.06
|  | 6 | 22.96% | 11.68 | 5.94 | 9.51 | 61.46 | 44.62 | 54.25
|  | 7 | 23.43% | 13.33 | 5.73 | 9.43 | 67.76 | 44 | 54.06
|  | 8 | 22.93% | 11.36 | 5.05 | 8.93 | 61.16 | 42.5 | 52.55
|  | 9 | 23% | 11.88 | 5.03 | 8.73 | 62.08 | 42.54 | 51.85
|  | 10 | 23.91% | 11.4 | 4.64 | 8.67 | 60.31 | 41.69 | 51.77
|  | 11 | 21.95% | 13.51 | 4.76 | 8.33 | 71.8 | 42 | 50.99
|  | 12 | 22.12% | 10.95 | 4.72 | 8.21 | 58.67 | 41.63 | 50.47
|  | 13 | 21.47% | 10.57 | ER | 7.97 | 57.74 | 41.86 | 50.6
|  | 14 | 22.13% | 10.28 | 3.91 | 8.13 | 56.66 | 40.4 | 50.33
|  | 15 | 21.84% | 10.96 | 4.6 | 8.04 | 59.57 | 41.44 | 49.94
|  | 16 | 22.48% | 10.55 | 4.64 | 7.93 | 57.67 | 40.96 | 49.42
|  | 17 | 22.56% | 10.39 | 4.53 | 8.14 | 57.22 | 41.34 | 50.19
|  | 18 | 22.06% | 10.73 | 5.07 | 8.04 | 57.8 | 42.61 | 49.89
|  | 19 | 22.36% | 11.41 | 4.92 | 7.86 | 60.36 | 42.34 | 49.44
|  | 20 | 25.34% | 10.4 | 5.27 | 8.19 | 57.34 | 42.8 | 50.23
|  | 21 | 22.41% | 10.63 | 3.76 | 8.02 | 58.08 | 39.77 | 49.81
|  | 22 | 22.6% | 10.92 | 4.2 | 8.07 | 58.7 | 41.04 | 49.94
|  | 23 | 22.24% | 11.64 | 4.37 | 8.09 | 61.77 | 40.84 | 49.96
|  | 24 | 22.36% | 11.01 | 4.03 | 8.15 | 58.81 | 40.02 | 50.04
|  | 25 | 22.68% | 10.79 | 3.75 | 7.93 | 57.91 | 39.84 | 49.32
|  | 26 | 22.33% | 11.83 | 4.23 | 7.71 | 62.2 | 40.51 | 48.98
|  | 27 | 22.63% | 10.32 | 3.67 | 7.78 | 57.2 | 39.52 | 49.09
|  | 28 | 22.94% | 11.96 | 3.99 | 7.83 | 63.14 | 39.92 | 49.21
|  | 29 | 22.85% | 12.03 | 5 | 9.21 | 63.2 | 42.08 | 53.29
|  | 30 | 22.86% | 11.47 | 5.41 | 8.5 | 60.88 | 42.78 | 51.01
|  | 31 |  | ER | ER | ER | ER | ER | ER
|  | TOTAL | 680.9% | 347.72 | 150.71 | 261.41 | 1847.97 | 1287.76 | 1560.43
|  | AVERAGE | 22.7% | 11.5907 | 5.1969 | 8.7137 | 61.599 | 42.9253 | 52.0143
|  | MAXIMUM | 25.34% | 14.6 | 8.62 | 11.57 | 74.2 | 52.65 | 61.71
|  | MINIMUM | 21.47% | 10.28 | 3.67 | 7.71 | 56.66 | 39.52 | 48.98
PAGE 15
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL FOUR
|  | RUN DATE |  |  | PERMIT NUMBER UC-06-264391 (IW-4)
2026-07-30
|  | OCTOBER | % INFL. | MAX | MIN | WELL 4 | MAX | MIN | AVG
|  | 2003 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 |  | ER | ER | ER | 38.94 | 37.22 | 38.18
|  | 2 |  | ER | ER | ER | 38.67 | 37.47 | 38.13
|  | 3 |  | ER | ER | ER | 39.16 | 37.16 | 38.05
|  | 4 |  | ER | ER | ER | 38.7 | 37.19 | 37.86
|  | 5 |  | ER | ER | ER | 38.25 | 36.92 | 37.68
|  | 6 |  | ER | ER | ER | 38.19 | 36.68 | 37.59
|  | 7 |  | ER | ER | ER | 38.6 | 36.56 | 37.52
|  | 8 |  | ER | ER | ER | 38.35 | 36.45 | 37.48
|  | 9 |  | ER | ER | ER | 38.33 | 36.4 | 37.34
|  | 10 |  | ER | ER | ER | 38.14 | 36.18 | 37.25
|  | 11 |  | ER | ER | ER | 38.93 | 36.09 | 37.12
|  | 12 |  | ER | ER | ER | 37.99 | 36.07 | 37.1
|  | 13 |  | ER | ER | ER | 37.92 | 36.08 | 37.1
|  | 14 |  | ER | ER | ER | 59.98 | 29.78 | 37.07
|  | 15 |  | ER | ER | ER | 37.82 | 36.06 | 37
|  | 16 |  | ER | ER | ER | 37.65 | 35.94 | 36.9
|  | 17 |  | ER | ER | ER | 37.63 | 36.02 | 36.99
|  | 18 |  | ER | ER | ER | 37.72 | 36.21 | 37.01
|  | 19 |  | ER | ER | ER | 37.88 | 36.19 | 36.95
|  | 20 |  | ER | ER | ER | 37.63 | 36.22 | 36.99
|  | 21 |  | ER | ER | ER | 37.65 | 35.9 | 36.95
|  | 22 |  | ER | ER | ER | 37.83 | 35.62 | 36.98
|  | 23 |  | ER | ER | ER | 38.17 | 35.97 | 37.02
|  | 24 |  | ER | ER | ER | 37.92 | 35.92 | 36.99
|  | 25 |  | ER | ER | ER | 37.74 | 35.78 | 36.84
|  | 26 |  | ER | ER | ER | 38.21 | 35.76 | 36.81
|  | 27 |  | ER | ER | ER | 37.87 | 35.64 | 36.92
|  | 28 |  | 0.15 | ER | ER | 38.32 | 35.8 | 36.98
|  | 29 | 0.3473% | 0.16 | 0.13 | 0.14 | 38.19 | 36.24 | 37.38
|  | 30 | 0.3496% | 0.15 | 0.13 | 0.13 | 38.03 | 36.21 | 37.21
|  | 31 |  | ER | ER | ER | ER | ER | ER
|  | TOTAL | 0.6969% | 0.46 | 0.26 | 0.27 | 1166.41 | 1081.73 | 1117.39
|  | AVERAGE | 0.3485% | 0.15333 | 0.13 | 0.135 | 38.8803 | 36.0577 | 37.2463
|  | MAXIMUM | 0.3496% | 0.16 | 0.13 | 0.14 | 59.98 | 37.47 | 38.18
|  | MINIMUM | 0.3473% | 0.15 | 0.13 | 0.13 | 37.63 | 29.78 | 36.81
PAGE 16
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL FIVE
|  | RUN DATE |  |  | PERMIT NUMBER UO-06-279512
|  | 2026-07-30 |  |  | 7/21/97 thru 7/21/02 |  |  | I.D. #:5006A11311
|  | OCTOBER | % INFL. | MAX | MIN | WELL 5 | MAX | MIN | AVG
|  | 2003 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 22.56% | 12.99 | 8.54 | 11.36 | 67.78 | 52.25 | 61.17
|  | 2 | 22.58% | 12.47 | 8.63 | 10.96 | 65.54 | 51.29 | 59.51
|  | 3 | 22.69% | 14.31 | 7.33 | 10.89 | 73.7 | 48.78 | 59.07
|  | 4 | 22.52% | 13.08 | 7.97 | 10.35 | 67.53 | 48.92 | 56.94
|  | 5 | 22.6% | 11.57 | 6.84 | 9.74 | 60.88 | 45.61 | 54.54
|  | 6 | 22.91% | 11.51 | 6.25 | 9.49 | 60.99 | 44.31 | 53.8
|  | 7 | 22.53% | 12.93 | ER | 9.07 | 67.16 | 36.1 | 52.87
|  | 8 | 22.91% | 11.14 | 5.31 | 8.92 | 60.65 | 42.25 | 52.11
|  | 9 | 23% | 11.67 | 5.32 | 8.73 | 61.66 | 42.29 | 51.39
|  | 10 | 23.94% | 11.23 | 4.44 | 8.68 | 59.87 | 41.42 | 51.29
|  | 11 | 22.08% | 13.36 | 5.1 | 8.38 | 71 | 41.71 | 50.57
|  | 12 | 22.31% | 10.8 | 5.09 | 8.28 | 58.03 | 41.37 | 50.06
|  | 13 | 22.42% | 10.44 | 5.16 | 8.32 | 57.26 | 41.6 | 50.2
|  | 14 | 22.35% | 10.23 | 4.26 | 8.21 | 56.18 | 40.17 | 49.91
|  | 15 | 22.06% | 10.89 | 4.96 | 8.12 | 59.06 | 41.2 | 49.54
|  | 16 | 22.76% | 10.48 | 4.91 | 8.03 | 57.21 | 40.79 | 49.01
|  | 17 | 22.81% | 10.35 | 4.86 | 8.23 | 56.76 | 41.1 | 49.83
|  | 18 | 22.33% | 10.61 | 5.37 | 8.14 | 57.35 | 42.36 | 49.51
|  | 19 | 22.7% | 11.31 | 5.26 | 7.98 | 59.88 | 42.1 | 49.04
|  | 20 | 25.64% | 10.39 | 5.57 | 8.29 | 56.92 | 42.54 | 49.83
|  | 21 | 22.74% | 10.58 | 4.17 | 8.14 | 57.65 | 39.55 | 49.49
|  | 22 | 22.32% | 10.82 | ER | 7.97 | 58.37 | 35.38 | 49.35
|  | 23 | 22.43% | 11.55 | 4.64 | 8.16 | 61.34 | 40.67 | 49.62
|  | 24 | 22.55% | 10.89 | 4.44 | 8.22 | 58.39 | 39.87 | 49.68
|  | 25 | 22.94% | 10.71 | 4.17 | 8.02 | 57.4 | 39.61 | 48.95
|  | 26 | 22.65% | 11.68 | 4.64 | 7.82 | 61.65 | 40.27 | 48.62
|  | 27 | 22.92% | 10.25 | 4.04 | 7.88 | 56.66 | 39.32 | 48.73
|  | 28 | 23.26% | 11.89 | 4.34 | 7.94 | 62.68 | 39.76 | 48.89
|  | 29 | 22.82% | 11.88 | 5.39 | 9.2 | 62.76 | 41.79 | 52.84
|  | 30 | 23.02% | 11.38 | 5.74 | 8.56 | 60.38 | 42.57 | 50.56
|  | 31 |  | ER | ER | ER | ER | ER | ER
|  | TOTAL | 683.4% | 343.39 | 152.74 | 262.08 | 1832.69 | 1266.95 | 1546.92
|  | AVERAGE | 22.78% | 11.4463 | 5.455 | 8.736 | 61.0897 | 42.2317 | 51.564
|  | MAXIMUM | 25.64% | 14.31 | 8.63 | 11.36 | 73.7 | 52.25 | 61.17
|  | MINIMUM | 22.06% | 10.23 | 4.04 | 7.82 | 56.18 | 35.38 | 48.62
PAGE 17
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
INJECTION WELL SUMMARY
RUN DATE
2026-07-30
| OCTOBER | INFLUENT | EFFLUENT | EFFLUENT | IW-1 | IW-2 | IW-3 | IW-4 | IW-5 | TOTAL
| 2003 | FLOW | FLOW | SS | LBS SS | LBS SS | LBS SS | LBS SS | LBS SS | LBS SS
|  | MGD | MGD
| 1 | 50.362 | 49.269 | 16 | 1722.7104 | 1802.7744 | 1543.9008 |  | 1515.8784 | 6585.264
| 2 | 48.529 | 47.503 | 11 | 1142.163 | 1198.1244 | 1020.1488 |  | 1005.4704 | 4365.9066
| 3 | 48 | 47.249 | 11 | 1135.7412 | 1193.5374 | 1014.6444 |  | 999.0486 | 4342.9716
| 4 | 45.967 | 44.906 | 9 | 881.2044 | 926.2404 | 785.1276 |  | 776.871 | 3369.4434
| 5 | 43.104 | 42.193 | 8 | 733.92 | 773.952 | 653.856 |  | 649.8528 | 2811.5808
| 6 | 41.423 | 40.954 | 10 | 892.38 | 942.42 | 793.134 |  | 791.466 | 3419.4
| 7 | 40.251 | 40.308 | 10 | 884.874 | 932.412 | 786.462 |  | 756.438 | 3360.186
| 8 | 38.943 | 38.485 | 17 | 1416.3822 | 1500.0324 | 1266.0954 |  | 1264.6776 | 5447.1876
| 9 | 37.949 | 37.646 | 15 | 1220.976 | 1294.785 | 1092.123 |  | 1092.123 | 4700.007
| 10 | 36.261 | 36.397 | 19 | 1541.8158 | 1635.3072 | 1373.8482 |  | 1375.4328 | 5926.404
| 11 | 37.945 | 37.376 | 14 | 1089.3708 | 1154.7564 | 972.6108 |  | 978.4488 | 4195.1868
| 12 | 37.11 | 36.554 | 20 | 1534.56 | 1622.964 | 1369.428 |  | 1381.104 | 5908.056
| 13 | 37.113 | 35.593 | 9 | 695.0556 | 665.7822 | 598.2282 |  | 624.4992 | 2583.5652
| 14 | 36.736 | 36.433 | 11 | 837.5862 | 886.2084 | 745.8462 |  | 753.1854 | 3222.8262
| 15 | 36.813 | 36.54 | 9 | 678.5424 | 718.3242 | 603.4824 |  | 609.4872 | 2609.8362
| 16 | 35.282 | 35.28 | 12 | 893.7144 | 947.7576 | 793.6344 |  | 803.6424 | 3438.7488
| 17 | 36.075 | 36.543 | 12 | 917.7336 | 969.7752 | 814.6512 |  | 823.6584 | 3525.8184
| 18 | 36.448 | 36.298 | 9 | 679.293 | 718.3242 | 603.4824 |  | 610.9884 | 2612.088
| 19 | 35.154 | 34.789 | 11 | 812.8164 | 860.5212 | 721.0764 |  | 732.0852 | 3126.4992
| 20 | 32.326 | 32.134 | 16 | 1231.6512 | 1305.0432 | 1092.8736 |  | 1106.2176 | 4735.7856
| 21 | 35.791 | 35.611 | 18 | 1355.5836 | 1435.1472 | 1203.9624 |  | 1221.9768 | 5216.67
| 22 | 35.704 | 35.863 | 14 | 1061.3484 | 1124.3988 | 942.2532 |  | 930.5772 | 4058.5776
| 23 | 36.372 | 36.218 | 17 | 1291.6158 | 1372.4304 | 1147.0002 |  | 1156.9248 | 4967.9712
| 24 | 36.447 | 36.741 | 27 | 2064.9006 | 2195.505 | 1835.217 |  | 1850.9796 | 7946.6022
| 25 | 34.966 | 34.739 | 18 | 1342.0728 | 1429.1424 | 1190.4516 |  | 1203.9624 | 5165.6292
| 26 | 34.525 | 33.721 | 13 | 942.1698 | 1003.9692 | 835.9182 |  | 847.8444 | 3629.9016
| 27 | 34.384 | 33.885 | 10 | 729.75 | 778.122 | 648.852 |  | 657.192 | 2813.916
| 28 | 34.13 | 33.982 | 14 | 1028.6556 |  | 914.2308 |  | 927.0744
| 29 | 40.309 | 39.875 | 16 | 1378.4352 | 1457.1648 | 1228.9824 | 18.6816 | 1227.648 | 5292.2304
| 30 | 37.184 | 36.983 | 18 | 1432.1448 | 1528.2216 | 1276.02 | 19.5156 | 1285.0272 | 5521.4136
| 31 | 35.3 | 35.2 | 21
| TOTAL | 1186.903 | 1175.268 | 435 | 33569.1672 | 34373.1432 | 29867.5416 | 38.1972 | 29959.782 | 124899.6732
| AVERAGE | 38.2872 | 37.9119 | 14.0323 | 1118.9722 | 1185.2808 | 995.5847 | 19.0986 | 998.6594 | 4306.8853
PAGE 18
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
| RUN DATE |  |  |  | SOLIDS REMOVAL INVENTORY DATA SHEET
2026-07-30
| OCTOBER | TONS | CAKE |  |  |  | OCTOBER | RAGS | GRIT | OTHER
| 2003 | SLUDGE | TSS |  |  |  | 2003 |  |  | (vac)
| 1st - 7th | [5 empty] | 1st - 7th
| 1 | 100 | 16.68 |  |  |  | 1
| 2 | 150 | 19.64 |  |  |  | 2
| 3 | 75 |  |  |  |  | 3 | 10
| 4 | 0 |  |  |  |  | 4
| 5 | 25 | 18.39 |  |  |  | 5
| 6 | 150 | 19.66 |  |  |  | 6
| 7 | 150 | 19.6 |  |  |  | 7
| TOTAL = | 650 | 18.794 | = AVG. |  |  | TOTAL = | 10 | 0 | 0
| 8th - 14th | [5 empty] | 8th - 14th
| 8 | 125 | 19.28 |  |  |  | 8
| 9 | 100 | 17.9 |  |  |  | 9 |  | 10 | 4500
| 10 | 50 |  |  |  |  | 10 | 10
| 11 | 0 |  |  |  |  | 11
| 12 | 25 |  |  |  |  | 12
| 13 | 125 | 18.93 |  |  |  | 13
| 14 | 125 | 19.29 |  |  |  | 14
| TOTAL = | 550 | 18.85 | = AVG. |  |  | TOTAL = | 10 | 10 | 4500
| 15th - 22nd | [5 empty] | 15th-22nd
| 15 | 150 | 18.93 |  |  |  | 15
| 16 | 150 | 19.67 |  |  |  | 16
| 17 | 100 |  |  |  |  | 17 | 10
| 18 | 0 |  |  |  |  | 18
| 19 | 25 | 18.12 |  |  |  | 19
| 20 | 150 | 19.41 |  |  |  | 20
| 21 | 150 | 19.29 |  |  |  | 21
| 22 | 150 | 19.44 |  |  |  | 22
| TOTAL = | 875 | 19.1433 | = AVG. |  |  | TOTAL = | 10 | 0 | 0
| 23rd - 31st | [5 empty] | 23rd-31st
| 23 | 150 | 21.06 |  |  |  | 23 |  | 10
| 24 | 100 |  |  |  |  | 24 | 10
| 25 | 0 |  |  |  |  | 25
| 26 | 0 |  |  |  |  | 26
| 27 | 125 | 15.88 |  |  |  | 27
| 28 | 150 | 18.96 |  |  |  | 28 |  |  | 4500
| 29 | 150 | 19.62 |  |  |  | 29
| 30 | 150 | 21 |  |  |  | 30
| 31 | 75 |  |  |  |  | 31 |  | 10
| TOTAL = | 900 | 19.304 | = AVG. |  |  | TOTAL = | 10 | 20 | 4500
RAGS & GRIT go to Central LandFill
Other(VAC) go to BCSR
PAGE 19

## INJECTION PAGES
|  |  |  | UNDERGROUND INJECTION CONTROL | [10 empty] | UNDERGROUND INJECTION CONTROL | [10 empty] | UNDERGROUND INJECTION CONTROL
[15 empty] | MONTHLY OPERATING REPORT | [10 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES |  |  |  |  | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES |  |  |  |  | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [10 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [10 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-1 | [7 empty] | Wet Well Description: |  |  | Effuent Wet Well for IW-1, IW-2, IW3, IW-4 and IW-5 | [7 empty] | Monitoring Well Decription: |  |  | UPPER ZONE OF MONITORING WELL MW-1
Permit #: |  | UO-06-279401 |  |  |  |  | Date of Issuance: |  | 1997-07-21 |  | Facility ID #: |  | 5006M02066 |  |  |  | Permit Number: |  |  | FLA041378 |  | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | UO-06-279512
[22 empty] | Monitoring Well ID #: |  |  | 5006A11311
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2002-07-21 | [7 empty] | Issue Date: |  |  | 1999-10-18 |  | As Identified in Permit: |  | Monitor Well MW-1 Upper Monitor Zone |  |  |  | Issue Date: |  |  | 1997-07-21
[22 empty] | Monitoring Well Interval: |  |  | 1288' to 1320'
Injection Well ID #: |  | 5006A11308 | [8 empty] | Wet Well ID #: |  | Well Facility U-001 |  |  |  | Expiration Date: |  |  | 2004-10-17 |  | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.3 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24 | Associated Injection Well(s):
Injection Interval: |  |  | 2799' to 3513' | [18 empty] | 500A11311 |  |  | INJECTION WELL IW-5
[11 empty] | Injection Well ID #: |  |  | Injection Well Description
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s): | [10 empty] | 5006A11308 |  |  | INJECTION WELL IW-1
[11 empty] | 5006A11309 |  |  | INJECTION WELL IW-2 | [7 empty] | REPORT MONTH / YEAR: |  | 2003-10-01 | DATE OF SAP / RECORDING: |  |  | 2003-10-07 | 2003-10-14 | 2003-10-21 | 2003-10-28
Monitoring Zone ID #: | [5 empty] | Description |  |  |  |  | 5006A11310 |  |  | INJECTION WELL IW-3
[11 empty] | N/A |  |  | INJECTION WELL IW-4 | [7 empty] | OPERATOR'S NAME: |  |  | BAYLER, J.
UO-06-279401 |  | UPPER ZONE OF MONITORING WELL MW-2 | [8 empty] | 5006A11311 |  |  | INJECTION WELL IW-5
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A
UO-06-279401 |  | LOWER ZONE OF MONITORING WELL MW-2
[11 empty] | THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [10 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [10 empty] | REPORT MONTH / YEAR: |  | 2003-10-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous |  |  | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2003-10-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous |  |  | OPERATOR'S NAME: |  |  | BAYLER, J.
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
OPERATOR'S NAME: |  |  | BAYLER, J. | [7 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A | [7 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4474-A | [7 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: |  |  |  | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 49.27 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 39.26 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: |  |  |  | PARAMETER |  |  |  | Sampling Frequency |  |  |  | VALUE |  | UNITS | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 48.265 | PSIG
[11 empty] | Nitrogen, Total as N |  |  |  |  | Daily/Monthly Average |  |  | 14.2291 |  | mg/L as N | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[11 empty] | Nitrogen, Nitrate, Total as N |  |  |  |  | Daily/Monthly Average |  |  | 0.55909 |  | mg/L as N | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7352.25 | mg/l
Total monthly flow | [7 empty] | 293.93 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 3800 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [7 empty] | Nitrogen, Total Kjeildahl as N |  |  |  |  | Daily/Monthly Average |  |  | 13.67 |  | mg/L as N | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.8045 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 16.32 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.445 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 73.8 |  | PSIG | pH |  |  |  |  | Daily/Monthly Average |  |  | 6.7032 |  | s.u. | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7.875 | Std units
Monthly average of the daily flow rates | [7 empty] | 9.7977 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 12062.5 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 13.7777 |  | MG | Phosphorus, Total as P |  |  |  |  | Daily/Monthly Average |  |  | 0.98522 |  | mg/L as P | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 2.249 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 74.25 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [10 empty] | Total Dissolved Solids (TDS) |  |  |  |  | Daily/Monthly Average |  |  | 1364.0323 |  | mg/L | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.05 | mg/l
Monthly average pressure | [7 empty] | 51.7823 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 750 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 37.5 |  | PSIG | Residue, Total filterable (TSS dried at 180 C) |  |  |  |  | Daily/Monthly Average |  |  | 14.0323 |  | mg/L | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 180 | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.66 | mg/l
[11 empty] | Specific Conductance (Temperature Compensated) |  |  |  |  | Daily/Monthly Average |  |  | 2791.3667 |  | umhos/cm | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just | [6 empty] | Temperature, Water |  |  |  |  | Daily/Monthly Average |  |  | 84.7793 |  | deg C
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [9 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just |  |  | Date: |  |  |  |  | (Signature):
Date:
(Signature):
|  |  |  | UNDERGROUND INJECTION CONTROL | [21 empty] | UNDERGROUND INJECTION CONTROL
|  |  |  | MONTHLY OPERATING REPORT | [21 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES | [15 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [21 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-2 | [18 empty] | Monitoring Well Decription: |  |  | LOWER ZONE OF MONITORING WELL MW-1
Permit #: |  | UO-06-279508 |  |  |  |  | Date of Issuance: |  | 1997-07-21 | [12 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | UO-06-279512
[22 empty] | Monitoring Well ID #: |  |  | 5006A11311
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2002-07-21 | [12 empty] | As Identified in Permit: |  | Monitor Well MW-1 Lower Monitor Zone |  |  |  | Issue Date: |  |  | 1997-07-21
[22 empty] | Monitoring Well Interval: |  |  | 1449' to 1557'
Injection Well ID #: |  | 5006A11309 | [19 empty] | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.3 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24
Injection Interval: |  |  | 2798' to 3518' | [18 empty] | 500A11311 |  |  | INJECTION WELL IW-5
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s):
[22 empty] | REPORT MONTH / YEAR: |  | 2003-10-01 | DATE OF SAP / RECORDING: |  |  | 2003-10-07 | 2003-10-14 | 2003-10-21 | 2003-10-28
Monitoring Zone ID #: | [5 empty] | Description
[22 empty] | OPERATOR'S NAME: |  |  | BAYLER, J.
UO-06-279401 |  | UPPER ZONE OF MONITORING WELL MW-2
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A
UO-06-279401 |  | LOWER ZONE OF MONITORING WELL MW-2
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [21 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2003-10-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
OPERATOR'S NAME: |  |  | BAYLER, J. | [18 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4474-A | [18 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 42.75 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 32.54 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: | [14 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 41.4143 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 9252 | mg/l
Total monthly flow | [7 empty] | 300.69 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 5100 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [18 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 9.08 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 17.11 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 11.665 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 72.4 |  | PSIG | [11 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7.2275 | Std units
Monthly average of the daily flow rates | [7 empty] | 10.3686 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 15582.5 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 14.5293 |  | MG | [11 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 2.249 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 74 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [21 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.05 | mg/l
Monthly average pressure | [7 empty] | 50.8117 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 662.5 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 37.8 |  | PSIG | [11 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 270 | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.0275 | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [21 empty] | (Signature):
Date:
|  |  |  | UNDERGROUND INJECTION CONTROL | [21 empty] | UNDERGROUND INJECTION CONTROL
|  |  |  | MONTHLY OPERATING REPORT | [21 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES | [15 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [21 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-3 | [18 empty] | Monitoring Well Decription: |  |  | UPPER ZONE OF MONITORING WELL MW-2
Permit #: |  | UO-06-279510 |  |  |  |  | Date of Issuance: |  | 1997-07-21 | [12 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | UC-06-279401 & 508
[22 empty] | Monitoring Well ID #: |  |  | 5006A11308 & 309
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2002-07-21 | [12 empty] | As Identified in Permit: |  | Monitor Well MW-2 Upper Monitor Zone |  |  |  | Issue Date: |  |  | 1997-07-21
[22 empty] | Monitoring Well Interval: |  |  | 1300' to 1344'
Injection Well ID #: |  | 5006A11310 | [19 empty] | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.3 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24
Injection Interval: |  |  | 2800' to 3977' | [18 empty] | 5006A11308 |  |  | INJECTION WELL IW-1
[22 empty] | 5006A11309 |  |  | INJECTION WELL IW-2
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s):
[22 empty] | REPORT MONTH / YEAR: |  | 2003-10-01 | DATE OF SAP / RECORDING: |  |  | 2003-10-07 | 2003-10-14 | 2003-10-21 | 2003-10-28
Monitoring Zone ID #: | [5 empty] | Description
[22 empty] | OPERATOR'S NAME: |  |  | BAYLER, J.
UO-06-279510 |  | UPPER ZONE OF MONITORING WELL MW-3
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A
UO-06-279510 |  | LOWER ZONE OF MONITORING WELL MW-3
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [21 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2003-10-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
OPERATOR'S NAME: |  |  | BAYLER, J. | [18 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4474-A | [18 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 29.71 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 23.79 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: | [14 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 25.1 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7203.5 | mg/l
Total monthly flow | [7 empty] | 261.41 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 3687.5 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [18 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.7535 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 14.6 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.4325 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 74.2 |  | PSIG | [11 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7.955 | Std units
Monthly average of the daily flow rates | [7 empty] | 8.7137 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 11837.5 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 12.2502 |  | MG | [11 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 2.249 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 71.5 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [21 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.05 | mg/l
Monthly average pressure | [7 empty] | 52.0143 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 762.5 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 38 |  | PSIG | [11 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 175 | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 2.7075 | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [21 empty] | (Signature):
Date:
|  |  |  | UNDERGROUND INJECTION CONTROL | [21 empty] | UNDERGROUND INJECTION CONTROL
|  |  |  | MONTHLY OPERATING REPORT | [21 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES | [15 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [21 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-4 | [18 empty] | Monitoring Well Decription: |  |  | LOWER ZONE OF MONITORING WELL MW-2
Permit #: |  | UC-06-264391 |  |  |  |  | Date of Issuance: |  | N/A | [12 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | UC-06-279401 & 508
[22 empty] | Monitoring Well ID #: |  |  | 5006A11308 & 309
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2000-11-30 | [12 empty] | As Identified in Permit: |  | Monitor Well MW-2 Lower Monitor Zone |  |  |  | Issue Date: |  |  | 1997-07-21
[22 empty] | Monitoring Well Interval: |  |  | 1970' to 2025'
Injection Well ID #: |  | N/A | [19 empty] | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24
Injection Interval: |  |  | 2804' to 3977' | [18 empty] | 5006A11308 |  |  | INJECTION WELL IW-1
[22 empty] | 5006A11309 |  |  | INJECTION WELL IW-2
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s):
[22 empty] | REPORT MONTH / YEAR: |  | 2003-10-01 | DATE OF SAP / RECORDING: |  |  | 2003-10-07 | 2003-10-14 | 2003-10-21 | 2003-10-28
Monitoring Zone ID #: | [5 empty] | Description
[22 empty] | OPERATOR'S NAME: |  |  | BAYLER, J.
UO-06-279510 |  | UPPER ZONE OF MONITORING WELL MW-3
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A
UO-06-279510 |  | LOWER ZONE OF MONITORING WELL MW-3
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [21 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2003-10-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
OPERATOR'S NAME: |  |  | BAYLER, J. | [18 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4474-A | [18 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 42.79 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 32.31 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: | [14 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 41.6533 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 31443 | mg/l
Total monthly flow | [7 empty] | 0.27 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 17800 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [18 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.2975 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 0.16 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.9125 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 59.98 |  | PSIG | [11 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7.3025 | Std units
Monthly average of the daily flow rates | [7 empty] | 0.135 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 47275 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 0.18809 |  | MG | [11 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 2.249 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 71.5 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [21 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.05 | mg/l
Monthly average pressure | [7 empty] | 37.2463 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 2275 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 38.1 |  | PSIG | [11 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 887.5 | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.0525 | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [21 empty] | (Signature):
Date:
|  |  |  | UNDERGROUND INJECTION CONTROL | [21 empty] | UNDERGROUND INJECTION CONTROL
|  |  |  | MONTHLY OPERATING REPORT | [21 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES | [15 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [21 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-5 | [18 empty] | Monitoring Well Decription: |  |  | UPPER ZONE OF MONITORING WELL MW-3
Permit #: |  | UO-06-279512 |  |  |  |  | Date of Issuance: |  | 1997-07-21 | [12 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | UO-06-279510
[22 empty] | Monitoring Well ID #: |  |  | 5006A11310
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2002-07-21 | [12 empty] | As Identified in Permit: |  | Monitor Well MW-3 Upper Monitor Zone |  |  |  | Issue Date: |  |  | 1997-07-21
[22 empty] | Monitoring Well Interval: |  |  | 1300' to 1349'
Injection Well ID #: |  | 5006A11311 | [19 empty] | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.3 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24
Injection Interval: |  |  | 2818' to 3462' | [18 empty] | 5006A11310 |  |  | INJECTION WELL IW-3
[22 empty] | N/A |  |  | INJECTION WELL IW-4
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s):
[22 empty] | REPORT MONTH / YEAR: |  | 2003-10-01 | DATE OF SAP / RECORDING: |  |  | 2003-10-07 | 2003-10-14 | 2003-10-21 | 2003-10-28
Monitoring Zone ID #: | [5 empty] | Description
[22 empty] | OPERATOR'S NAME: |  |  | BAYLER, J.
UO-06-279512 |  | UPPER ZONE OF MONITORING WELL MW-1
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A
UO-06-279512 |  | LOWER ZONE OF MONITORING WELL MW-1
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [21 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2003-10-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
OPERATOR'S NAME: |  |  | BAYLER, J. | [18 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4474-A | [18 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 32.43 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 16.91 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: | [14 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 30.0887 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 23625.5 | mg/l
Total monthly flow | [7 empty] | 262.08 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 3787.5 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [18 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.97725 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 14.31 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.435 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 73.7 |  | PSIG | [11 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 8.0725 | Std units
Monthly average of the daily flow rates | [7 empty] | 8.736 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 11977.5 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 12.2952 |  | MG | [11 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 2.249 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 70.25 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [21 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.05 | mg/l
Monthly average pressure | [7 empty] | 51.564 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 762.5 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 36.1 |  | PSIG | [11 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 182.5 | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.005 | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [21 empty] | (Signature):
Date:
UNDERGROUND INJECTION CONTROL
MONTHLY OPERATING REPORT
[22 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
[22 empty] | Monitoring Well Decription: |  |  | LOWER ZONE OF MONITORING WELL MW-3
[22 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | UO-06-279510
[22 empty] | Monitoring Well ID #: |  |  | 5006A11310
[22 empty] | As Identified in Permit: |  | Monitor Well MW-3 Lower Monitor Zone |  |  |  | Issue Date: |  |  | 1997-07-21
[22 empty] | Monitoring Well Interval: |  |  | 1970 to 2027'
Associated Injection Well(s):
[22 empty] | Injection Well ID #: |  |  | Injection Well Description
[22 empty] | 5006A11310 |  |  | INJECTION WELL IW-3
[22 empty] | N/A |  |  | INJECTION WELL IW-4
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
[22 empty] | REPORT MONTH / YEAR: |  | 2003-10-01 | DATE OF SAP / RECORDING: |  |  | 2003-10-07 | 2003-10-14 | 2003-10-21 | 2003-10-28
[22 empty] | OPERATOR'S NAME: |  |  | BAYLER, J.
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4474-A
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
[22 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
[22 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
[22 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 46.03 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 35.66 | PSIG
[22 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 44.5717 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
[22 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 28902.75 | mg/l
[22 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 15900 | mg/l
[22 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 2.3825 | mg/l
[22 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 3.1275 | mg/l
[22 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7.285 | Std units
[22 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 43450 | umho/cm
[22 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.0125 | # col/100ml
[22 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1969.25 | deg. F
[22 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.05 | mg/l
[22 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 2175 | mg/l
[22 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 867.5 | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.0375 | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
Date:

## DEP FORMS
Department of Environmental Protection Discharge Monitoring Report - Part A
When Completed mail this report to: Department of Environmental Protection, Wastewater Facilities Management Section, MS 3551, 2600 Blair Stone Road, Tallahassee, FL 32399-2400
PERMITEE NAME: | City of Fort Lauderdale |  |  |  |  | PERMIT NUMBER: |  | FLA041378 |  | REPORT: | Monthly
MAILING ADDRESS: | 949 NW 38th Street |  |  |  |  | LIMIT: |  | Final |  | GROUP: | Domestic
| Fort Lauderdale, FL 33309 |  |  |  |  | CLASS SIZE: |  | N/A |  | GMS TEST SITE
[6 empty] | GMS ID NO. |  | 5006M02066 |  | NO:
FACILITY: | City of Fort Lauderdale G. T. Lohmeyer WWTF |  |  |  |  | MONITORING GROUP NUMBER: |  | U-001
LOCATION: | 1765 SE 18th Street |  |  |  |  | PLANT SIZE/TREATMENT TYPE: |  | IIA
Fort Lauderdale, FL 33316
COUNTY: | Broward | [5 empty] | MONITORING PERIOD: |  |  | 2003-10-01
Parameter |  | Quantity of Loading |  | Units |  | Quality or Concentration |  | Units | No. Ex. | Frequency of Analysis | Sample Type
Flow | Sample Measurement | 13.7777 | 9.7977 | [5 empty] | 0
PARM Code 50050 1 Mon.Site No. EFF-002 | Permit Requirement | 18.3 (Peak Hour.) | Report (Mo. Avg.) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
Flow | Sample Measurement | 14.5293 | 10.3686 | [5 empty] | 0
PARM Code 50050 1 Mon.Site No. EFF-003 | Permit Requirement | 18.3 (Peak Hour.) | Report (Mo. Avg.) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
Flow | Sample Measurement | 12.2502 | 8.7137 | [5 empty] | 0
PARM Code 50050 1 Mon.Site No. EFF-004 | Permit Requirement | 18.3 (Peak Hour.) | Report (Mo. Avg.) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
Flow | Sample Measurement | 0.18809 | 0.135 | [5 empty] | 0
PARM Code 50050 1 Mon.Site No. EFF-005 | Permit Requirement | 18.0 (Peak Hour.) | Report (Mo. Avg.) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
Flow | Sample Measurement | 12.2952 | 8.736 | [5 empty] | 0
PARM Code 50050 1 Mon.Site No. EFF-006 | Permit Requirement | 18.3 (Peak Hour.) | Report (Mo. Avg.) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
I certify under penalty of law that I have personally examined and am familiar with the informantion submitted herein; and based on my inquiry of those individuals immeadiately responsible for obtaining the information, I believe the submitted
information is true, accurate and complete. I am aware that there are significant penalties for submitting false information including the possiblity of fine and imprisonment.
NAME/TITLE OF PRINCIPAL EXECUTIVE OFFICER OR AUTHORIZED AGENT |  |  |  | SIGNATURE OF PRINCIPAL EXECUTIVE OFFICER OR AUTHORIZED AGENT |  |  |  |  | TELEPHONE |  | DATE (YY/MM/DD)
954-523-1002 ext 2021
REGIONAL WASTEWATER FACILITIES MANAGER
COMMENTS AND EXPLANATION OF ANY VIOLATIONS (Reference all attachments here):
Version 8/13/99
Department of Environmental Protection Discharge Monitoring Report - Part A (Continued)
[12 empty] | PERMITEE NAME: | City of Fort Lauderdale G. T. Lohmeyer WWTF |  |  |  | PERMIT NUMBER: |  | FLA041378 | MONITORING GROUP NUMBER: U-001 |  |  | REPORT: | Monthly
[20 empty] | MONITORING PERIOD: |  |  |  | 2003-10-01
[12 empty] | Parameter |  |  | Quantity of Loading |  | Units |  | Quality or Concentration |  | Units | No. Ex. | Frequency of Analysis | Sample Type
[12 empty] | BOD, Carbonaceous 5 day, 20C |  | Sample Measurement |  |  |  | 4.3 |  |  |  | 0
[12 empty] | PARM Code 80082 Y Mon.Site No. EFF-001 |  | Permit Requirement |  |  |  | 20.0 (An.Avg.) |  |  | mg/l |  | Daily | 24-hour FPC
[12 empty] | BOD, Carbonaceous 5 day, 20C |  | Sample Measurement |  |  |  | 4.361 | 4.2792 | 8 |  | 0
[12 empty] | PARM Code 80082 1 Mon.Site No. EFF-001 |  | Permit Requirement |  |  |  | 30.0 (Mo.Avg.) | 45.0 (Week.Avg.) | 60.0 (Max.) | mg/l |  | Daily | 24-hour FPC
[12 empty] | Solids, Total Suspended |  | Sample Measurement |  |  |  | 13.3 |  |  |  | 0
[12 empty] | PARM Code 00530 Y Mon.Site No. EFF-001 |  | Permit Requirement |  |  |  | 20.0 (An.Avg.) |  |  | mg/l |  | Daily | 24-hour FPC
[12 empty] | Solids, Total Suspended |  | Sample Measurement |  |  |  | 14.0323 | 13.9543 | 27 |  | 0
[12 empty] | PARM Code 00530 1 Mon.Site No. EFF-001 |  | Permit Requirement |  |  |  | 30.0 (Mo.Avg.) | 45.0 (Week.Avg.) | 60.0 (Max.) | mg/l |  | Daily | 24-hour FPC
[12 empty] | pH |  | Sample Measurement |  |  |  | 6.4 |  |  |  | 0
[12 empty] | PARM Code 00400 1 Mon.Site No. EFF-001 |  | Permit Requirement |  |  |  | 6.0 (Min.) |  |  | s.u. |  | Continuous | Meter
[12 empty] | Flow |  | Sample Measurement | 37.5171 | 38.2872 | [5 empty] | 0
[12 empty] | PARM Code 50050 G Mon.Site No. INF-001 |  | Permit Requirement | 43.0 (3-Mo.Avg.) | Report (Mo.Avg.) | mgd | [5 empty] | Continuous | Flow meters with 24-hour recording chart
[12 empty] | BOD, Carbonaceous 5 day, 20C |  | Sample Measurement |  |  |  | 64.4935 |  |  |  | N/A
[12 empty] | PARM Code 80082 G Mon.Site No. INF-002 |  | Permit Requirement |  |  |  | Report (Mo.Avg.) |  |  | mg/l |  | Daily | 24-hour FPC
[12 empty] | Solids, Total Suspended |  | Sample Measurement |  |  |  | 89.5484 |  |  |  | N/A
[12 empty] | PARM Code 00530 G Mon.Site No. INF-002 |  | Permit Requirement |  |  |  | Report (Mo.Avg.) |  |  | mg/l |  | Daily | 24-hour FPC
Version 8/13/99

## JULIAN CONVERT
2003-10-01 | 37895 | 1999-01-01 | 1734
FROM DATE ON "DATA INPUT" PAGE | [5 empty] | 2003-10-01
1999
MONTHYY.PAR RANGE TO COMPILE (JULIAN DAY VALUES) FOR SPLIT PROGRAM ARE | [7 empty] | 274 | THROUGH | 1766
|  | 10 | OCTOBER
[5 empty] | 2003-10-01 | 2003-10-01 | 10
2003-10-01 |  |  |  |  | 1 | JANUARY |  | 1995 | 1995-01-01
[5 empty] | 2 | FEBRUARY |  | 1996 | 1996-01-01
[5 empty] | 3 | MARCH |  | 1997 | 1997-01-01
OCTOBER |  | 1 |  | 3 | 4 | APRIL |  | 1998 | 1998-01-01
|  | 0 |  | 0 | 5 | MAY |  | 1999 | 1999-01-01
|  | 0 |  |  | 6 | JUNE |  | 2000 | 2000-01-01
|  | 0 |  |  | 7 | JULY |  | 2001 | 2001-01-01
|  | 0 |  | 0 | 8 | AUGUST |  | 2002 | 2002-01-01
|  |  |  | 3 | 9 | SEPTEMBER |  | 2003 | 2003-01-01
[5 empty] | 10 | OCTOBER |  | 2004 | 2004-01-01
[5 empty] | 11 | NOVEMBER |  | 2005 | 2005-01-01
2003 |  |  |  |  | 12 | DECEMBER |  | 2006 | 2006-01-01
37895 | [6 empty] | OCTOBER | 2007 | 2007-01-01
37622 | [7 empty] | 2008 | 2008-01-01
273 | 1 |  | 1 | 274 | Wednesday
| 2 |  | 2 | 275 | Thursday
| 3 |  | 3 | 276 | Friday
| 4 |  | 4 | 277 | Saturday
| 5 |  | 5 | 278 | Sunday
| 6 |  | 6 | 279 | Monday
| 7 |  | 7 | 280 | Tuesday
| 8 |  | 8 | 281 | Wednesday
| 9 |  | 9 | 282 | Thursday
| 10 |  | 10 | 283 | Friday
| 11 |  | 11 | 284 | Saturday
| 12 |  | 12 | 285 | Sunday
| 13 |  | 13 | 286 | Monday
| 14 |  | 14 | 287 | Tuesday
| 15 |  | 15 | 288 | Wednesday
| 16 |  | 16 | 289 | Thursday
| 17 |  | 17 | 290 | Friday
| 18 |  | 18 | 291 | Saturday
| 19 |  | 19 | 292 | Sunday
| 20 |  | 20 | 293 | Monday
| 21 |  | 21 | 294 | Tuesday
| 22 |  | 22 | 295 | Wednesday
| 23 |  | 23 | 296 | Thursday
| 24 |  | 24 | 297 | Friday
| 25 |  | 25 | 298 | Saturday
| 26 |  | 26 | 299 | Sunday
| 27 |  | 27 | 300 | Monday
| 28 |  | 28 | 301 | Tuesday
| 29 |  | 29 | 302 | Wednesday
| 30 |  | 30 | 303 | Thursday
| 31 |  | 31 | 304 | Friday
31