## DATA INPUT
ENTER THE AVERAGE MONTHLY INFLUENT FLOW
INTO THE CORROSPONDING BOXES BELOW:
JUNE | 46.575 | MAY | 33.744
ENTER THE PRESENT MONTH AND YEAR IN BOX BELOW (A5) | [5 empty] | JULY
2005-07-01 | [5 empty] | 2005
IW-1 | IW-2 | IW-3 | IW-4 | IW-5
35.24 | 35.79 | 36.59 | 36.81 | 36.56 | 2005-07-14
|  | ENTER INJECTION WELL SHUT-IN PRESSURE ABOVE |  |  | ENTER DATE OF SHUT-IN READINGS
ENTER SLUDGE DISPOSAL SITE FOR EACH WEEK BELOW
| WEEK 1 | WEEK 2 | WEEK 3 | WEEK 4
1 st | Central Sanitary Landfill | Central Sanitary Landfill | Central Sanitary Landfill | Central Sanitary Landfill
2 nd | Pompano Beach, FL | Pompano Beach, FL | Pompano Beach, FL | Pompano Beach, FL
RAW DATA REPORT ENTRY CATEGORIES
GTL PLANT DAILY PROCESS SUMMARY
[6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TOTAL RAW INFLUENT FLOW (MGD) | [5 empty] | 49.948 | 49.161 | 46.028 | 43.113 | 41.832 | 39.882 | 38.595 | 37.95 | 43.366 | 45.664 | 44.078 | 42.214 | 41.078 | 38.746 | 37.233 | 36.901 | 35.84 | 35.627 | 36.04 | 36.307 | 35.846 | 35.792 | 34.863 | 34.458 | 36.143 | 36.655 | 35.382 | 34.551 | 34.272 | 34.708 | 34.844
TOTAL EFFLUENT FLOW (MGD) | [5 empty] | 49.581 | 48.851 | 46.301 | 42.618 | 41.112 | 39.364 | 38.886 | 38.774 | 42.952 | ER | 43.248 | 42.338 | 41.237 | 38.906 | 37.434 | 36.237 | 35.257 | 36.477 | 36.061 | 35.356 | 35.105 | 36.225 | 34.975 | 34.164 | 35.414 | 36.016 | 34.656 | 34.417 | 34.212 | 33.715 | 33.842
MAXIMUM HOURLY RAW INFLUENT FLOW (MGD) | [5 empty] | 2.283 | 2.399 | 2.241 | 2.093 | 1.915 | 1.953 | 1.869 | 1.926 | 2.246 | 2.054 | 2.146 | 2.088 | 1.956 | 1.891 | 1.799 | 1.791 | 1.773 | 1.809 | 1.842 | 1.76 | 1.722 | 1.815 | 1.77 | 1.681 | 1.915 | 1.693 | 1.671 | 1.694 | 1.667 | 1.849 | 1.658
MAXIMUM INSTANANEOUS PEAK RAW INFUENT FLOW (MGD) | [5 empty] | 63.665 | 61.967 | 59.051 | 57.833 | 56.391 | 52.546 | 54.501 | 55.558 | 62.576 | 61.038 | 60.813 | 57.961 | 56.295 | 54.437 | 53.988 | 56.84 | 52.033 | 49.92 | 53.219 | 53.411 | 51.232 | 50.591 | 50.623 | 50.816 | 55.654 | 49.952 | 51.649 | 50.11 | 49.247 | 50.784 | 50.143
MINIMUM INSTANANEOUS PEAK RAW INFUENT FLOW (MGD) | [5 empty] | 30.695 | 29.67 | 26.049 | 22.972 | 21.018 | 17.813 | 17.781 | 14.194 | 22.428 | 24.703 | 26.401 | 21.627 | 19.512 | 19.191 | 18.5 | 14.354 | 15.283 | 14.45 | 13.361 | 13.489 | 13.777 | 16.309 | 17.237 | 15.508 | 14.835 | 17.397 | 15.027 | 17.845 | 14.771 | 16.495 | 14.418
TOTAL RETURN ACTIVATED SLUDGE FLOW (MGD) | [5 empty] | 13.936 | 13.221 | 14.2 | 14.244 | 14.005 | 13.981 | 13.616 | 14.359 | 14.732 | 14.38 | 13.655 | 13.761 | 13.492 | 14.23 | 15.56 | 13.341 | 13.708 | 13.241 | 13.139 | 13.922 | 14.094 | 15.227 | 14.595 | 14.873 | 14.969 | 13.802 | 14.83 | 15.253 | 15.724 | 14.005 | 13.838
TOTAL WASTE FLOW TO DEWATERING PROCESS (MG) | [5 empty] | 0.32 | 0 | 0 | 0 | 0.451 | 0.549 | 0.541 | 0.23 | 0 | 0.198 | 0.436 | 0.354 | 0.427 | 0.444 | 0.037 | 0 | 0.117 | 0.253 | 0.326 | 0.38 | 0.436 | 0.182 | 0 | 0.167 | 0.385 | 0.406 | 0.371 | 0.423 | 0.135 | 0.212 | 0.158
TOTAL DAILY RAINFALL | [5 empty] | 0.2 | 1.03 | 0 | 0 | 0 | 0 | 0 | 0.02 | 3 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0 | 0 | 0 | 0.28 | 0 | 0 | 0 | 0 | 0.77 | 0
RAW INFLUENT pH | [5 empty] | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7.1 | 7 | 7 | 7 | 7 | 7.1 | 7.1 | 6.6 | 7 | 7 | 7 | 7 | 7 | 7 | 7.1
RAW INFLUENT HYDROGEN SULFIDE (PPM) | [5 empty] | 3 | 3 | 2 | 3 | 3 | 4 | 4 | 4 | 4 | 4 | 3 | 3 | 4 | 4 | 3 | 3 | 3 | 4 | 3 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
RAW INFLUENT TEMPERATURE (F ) | [5 empty] | 81 | 81 | 82 | 85 | 85 | 83 | 82 | 83 | 83 | 83 | 83 | 82 | 82 | 82 | 82 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 84 | 84 | 84 | 83 | 84 | 84 | 85 | 85 | 84
TOTAL DAILY KILOWATTS (FPL POWER CONSUMPTION) | [5 empty] | 32113 | 32417 | 32214 | 32420 | 32389 | 32275 | 32296 | 32167 | 32249 | 32046 | 32341 | 32367 | 32388 | 32186 | 31907 | 31650 | 31799 | 31832 | 31990 | 31843 | 26656 | 29089 | 32153 | 32426 | 32186 | 32253 | 32178 | 32235 | 31991 | 32219 | 32276
GTL PLANT DAILY PROCESS SUMMARY
(CONTINUED)
[6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
FINAL EFFLUENT FREE CHLORINE RESIDUAL (PPM) | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FINAL EFFLUENT TOTAL CHLORINE RESIDUAL (PPM) | [5 empty] | 0.9 | 1.2 | 1.2 | 1.2 | 1 | 1 | 1.3 | 1.2 | 0.9 | 0.8 | 1 | 1.2 | 0.9 | 1 | 1.1 | 1.2 | 1.1 | 0.9 | 0.7 | 1 | 1 | 0.9 | 1 | 1 | 1.2 | 1.1 | 1 | 1.2 | 0.09 | 0.5 | 1.1
FINAL EFFLUENT pH (daily average) | [5 empty] | 6.7 | 6.6 | 6.6 | 6.6 | 6.6 | 6.7 | 6.7 | 6.6 | 6.6 | 6.5 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.5 | 6.5 | 6.6 | 6.6 | 6.7 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.5 | 6.7
FINAL EFFLUENT pH (daily minimum) | [5 empty] | 6.6 | 6.6 | 6.6 | 6.5 | 6.6 | 6.6 | 6.5 | 6.5 | 6.5 | 6.5 | 6.6 | 6.5 | 6.5 | 6.6 | 6.6 | 6.5 | 6.5 | 6.6 | 6.5 | 6.6 | 6.5 | 6.7 | 6.5 | 6.6 | 6.5 | 6.5 | 6.6 | 6.5 | 6.5 | 6.5 | 6.5
FINAL EFFLUENT pH (daily maximum) | [5 empty] | 6.8 | 6.6 | 6.6 | 6.8 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.6 | 6.6 | 6.6 | 6.8 | 6.8 | 6.7 | 6.6 | 6.6 | 6.7 | 6.7 | 6.8 | 6.7 | 6.5 | 6.6 | 6.7 | 6.6 | 6.6 | 6.6 | 6.6 | 6.7 | 6.6 | 6.8
FINAL EFFLUENT TEMPARTURE (F ) | [5 empty] | 84 | 86 | 87 | 88 | 88 | 87 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 86 | 86 | 86 | 86 | 86 | 86.3 | 86 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 85 | 87
AVERAGE CLARIFIER BLANKET DEPTH (INCHES) | [5 empty] | 10 | 19 | 29 | 33 | 21 | 26 | 15 | 21 | 44 | 29 | 30 | 20 | 21 | 15 | 19 | 22 | 22 | 23 | 18 | 21 | 19 | 25 | 24 | 20 | 22 | 23 | 21 | 12 | 20 | 24 | 22
FINAL EFFLUENT SAMPLE TEMPARTURE (C ) | [5 empty] | 1.9 | 2.7 | 6 | 3 | 2 | 2 | 3 | 2 | 2.3 | 4 | 3 | 2 | 3 | 2 | 3.3 | 2.9 | 2 | 2 | 2 | 2 | 2 | 0.8 | 5 | 5 | 2 | 2 | 2 | 2 | 4.6 | 0 | 1
TOTAL RETURN ACTIVATED SLUDGE FLOW TO REACTOR ONE (MGD) | [5 empty] | 6.309 | 6.383 | 6.486 | 6.354 | 6.415 | 6.317 | 6.211 | 6.148 | 6.143 | 5.938 | 6.151 | 5.993 | 5.984 | 6.016 | 6.048 | 6.066 | 6.088 | 6.157 | 6.308 | 6.239 | 6.304 | 6.146 | 5.967 | 5.952 | 6.001 | 6.232 | 6.193 | 6.217 | 6.177 | 6.158 | 6.042
TOTAL RETURN ACTIVATED SLUDGE FLOW TO REACTOR TWO (MGD) | [5 empty] | 7.627 | 6.839 | 7.714 | 7.89 | 7.59 | 7.664 | 7.404 | 8.211 | 8.589 | 8.442 | 7.505 | 7.767 | 7.509 | 8.213 | 9.512 | 7.275 | 7.62 | 7.084 | 6.831 | 7.683 | 7.79 | 9.081 | 8.629 | 8.921 | 8.968 | 7.57 | 8.638 | 9.036 | 9.347 | 7.897 | 7.796
GTL PLANT DAILY PROCESS SUMMARY
CONTINUED
[6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TOTAL DAILY TRUCKING LOAD OF DEWATERED SLUDGE REMOVED | [5 empty] | 4 | 0 | 0 | 0 | 2 | 5 | 5 | 4 | 0 | 0 | 4 | 4 | 4 | 4 | 2 | 0 | 0 | 4 | 3 | 3 | 4 | 3 | 0 | 0 | 4 | 4 | 4 | 4 | 4 | 0 | 0
TOTAL DAILY HYDROGEN PEROXIDE CONSUMED (LBS) | [5 empty] | 349 | 389 | 0 | 0 | 0 | 0 | 0 | 1519 | 1317 | 1926 | 1377 | 1407 | 668 | 0 | 1158 | 240 | 0 | 0 | 0 | 698 | 1716 | 1807 | 1896 | 2096 | 1936 | 1836 | 1906 | 1916 | 1897 | 2106 | 1717
TOTAL DAILY CHLORINE CONSUMED (LBS) | [5 empty] | 1380 | 1440 | 1440 | 1480 | 1360 | 1240 | 1340 | 1500 | 1480 | 1520 | 1360 | 1140 | 1560 | 1440 | 1400 | 1680 | 1320 | 1440 | 1480 | 1480 | 1400 | 1580 | 1440 | 1440 | 1620 | 1480 | 1440 | 1400 | 1320 | 1140 | 1280
TOTAL DAILY POLYMER CONSUMED (GALS) | [5 empty] | 15 | 0 | 0 | 0 | 97 | 102 | 43 | 61 | 0 | 45 | 85 | 86 | 53 | 68 | 0 | 0 | 32 | 62 | 60 | 62 | 80 | 36 | 0 | 0 | 48 | 55 | 64 | 47 | 0 | 0 | 6
TOTAL TONS OF LIME DELIVERED DAILY | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTAL DAILY GASIOUS OXYGEN PRODUCED (TONS) | [5 empty] | 20.3 | 20.7 | 28.2 | 22.9 | 22.4 | 24.8 | 24 | 21.3 | 27.4 | 20.7 | 23 | 19 | 19 | 16.4 | 18.4 | 20.4 | 17.7 | 18.5 | 20.6 | 18.5 | 25.7 | 31.5 | 23.5 | 23.5 | 23.1 | 20.2 | 20.1 | 19.7 | 21 | 21 | 26.3
AVERAGE PERCENT OXYGEN PRODUCT PURITY | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 99 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 94 | 100 | 98 | 100 | 100 | 100 | 100 | 100 | 100 | 98 | 94
TOTAL DAILY LIQUID OXYGEN IN STORAGE (TONS) | [5 empty] | 100 | 99.3 | 99.9 | 99.6 | 100.3 | 102.2 | 102.3 | 101.3 | 101.2 | 101 | 100.9 | 104.3 | 102.7 | 104.1 | 104.5 | 103.9 | 104.8 | 109.2 | 110.1 | 106.3 | 99.7 | 91.6 | 92 | 92.2 | 96 | 96.8 | 95.8 | 95.7 | 96.6 | 94 | 94.8
MONITORING WELL PRESSURE DATA
MONITORING WELL ONE UPPER/LOWER LEVEL
| MW-1 |  | UPPER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MINIMUM | [5 empty] | 49.18 | 49.2 | 49.12 | 47.37 | 47.76 | 48.99 | 49.04 | 49.11 | ER | ER | 40.32 | 40.68 | 49.07 | 49.12 | 49.1 | 49.01 | 48.95 | 39.85 | 40.12 | 48.84 | 48.84 | 48.88 | 48.89 | ER | 47.56 | 47.74 | ER | 48.52 | 48.7 | 48.7 | 48.71
MAXIMUM | [5 empty] | 49.52 | 49.52 | 49.41 | 49.26 | 49.29 | 49.28 | 49.33 | 49.39 | ER | 49.32 | 49.32 | 49.47 | 49.3 | 49.36 | 49.35 | 49.29 | 49.31 | 49.24 | 49.49 | 49.26 | 49.27 | 49.26 | 49.25 | 49.25 | 49.25 | 49.05 | 49.1 | 49.06 | 48.97 | 48.99 | 49.02
AVERAGE | [5 empty] | 49.38 | 49.39 | 49.3 | 48.37 | 48.63 | 49.15 | 49.18 | 49.2 | ER | 30.22 | 43.11 | 46.44 | 49.19 | 49.29 | 49.23 | 49.15 | 49.14 | 42.55 | 46.23 | 49.05 | 49.08 | 49.07 | 49.02 | 48.97 | 48.23 | 48.64 | 47.27 | 48.94 | 48.92 | 48.9 | 48.89
| MW-1 |  | LOWER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MINIMUM | [5 empty] | 42.54 | 42.4 | 43.28 | 41.28 | 40.94 | 42.1 | 43.03 | 42.06 | ER | ER | 39.41 | 38.52 | 40.73 | 42.1 | 42.52 | 42.7 | 43.64 | 39.91 | 38.91 | 40.7 | 42.02 | 42.76 | 42.42 | ER | 41.36 | 41.04 | ER | 42.81 | 43.01 | 42.13 | 42.93
MAXIMUM | [5 empty] | 47.47 | 47.15 | 46.31 | 45.78 | 44.48 | 45.61 | 46.11 | 46.44 | ER | 45.08 | 44.6 | 42.37 | 44.34 | 45.69 | 46.44 | 46.39 | 46.32 | 44.25 | 42.78 | 44.99 | 45.73 | 46.53 | 47.33 | 46.82 | 46.04 | 44.92 | 45.88 | 46 | 46.34 | 46.2 | 46.93
AVERAGE | [5 empty] | 44.05 | 44.31 | 44.49 | 43.9 | 42.49 | 43.79 | 44.29 | 44.4 | ER | 27.66 | 42.93 | 40.41 | 42.47 | 43.73 | 44.37 | 44.37 | 44.69 | 42.89 | 40.81 | 42.6 | 43.74 | 44.33 | 44.39 | 44.33 | 43.24 | 42.77 | 42.44 | 43.98 | 44.23 | 43.54 | 44.76
MONITORING WELL TWO UPPER/LOWER LEVEL
| MW-2 |  | UPPER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MINIMUM | [5 empty] | 31.23 | 31.39 | 31.61 | 26.75 | 26.65 | 31.45 | 31.72 | 31.71 | ER | ER | 27.15 | 26.96 | 31.61 | 31.73 | 31.7 | 31.83 | 32.15 | 27.4 | 27.27 | 31.76 | 32.02 | 31.99 | 32.04 | ER | 27.28 | 27.31 | ER | 32.05 | 32.15 | 31.88 | 31.95
MAXIMUM | [5 empty] | 33.13 | 32.86 | 32.63 | 32.66 | 32.31 | 32.55 | 32.7 | 32.86 | 31.69 | 32.57 | 31.97 | 32.42 | 32.8 | 33.13 | 33.19 | 33.15 | 33.18 | 32.29 | 32.71 | 32.96 | 33.05 | 33.71 | 34.01 | 33.76 | 32.59 | 33.08 | 33.33 | 33.62 | 33.58 | 33.33 | 33.69
AVERAGE | [5 empty] | 31.82 | 32.02 | 32.1 | 29.66 | 30.16 | 32.06 | 32.16 | 32.33 | 24.58 | 22.38 | 29.17 | 30.45 | 32.11 | 32.34 | 32.5 | 32.36 | 32.54 | 29.31 | 30.72 | 32.3 | 32.53 | 32.71 | 32.79 | 32.78 | 29.67 | 30.88 | 32.66 | 32.71 | 32.69 | 32.45 | 32.88
| MW-2 |  | LOWER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MINIMUM | [5 empty] | 43.27 | 43.35 | 43.34 | 39.5 | 39.26 | 43.08 | 43.27 | 43.4 | ER | ER | 35.52 | 35.14 | 43.07 | 43.22 | 43.3 | 43.29 | 43.29 | 33.94 | 33.94 | 42.97 | 43.08 | 43.17 | 43.2 | ER | 35.29 | 35.18 | ER | 42.82 | 43.05 | 43.1 | 43.17
MAXIMUM | [5 empty] | 43.46 | 43.54 | 43.5 | 43.41 | 43.1 | 43.3 | 43.42 | 43.56 | ER | 43.55 | 43.55 | 43.07 | 43.28 | 43.41 | 43.46 | 43.45 | 43.5 | 43.48 | 43.02 | 43.22 | 43.29 | 43.34 | 43.38 | 43.42 | 43.42 | 43 | 43.16 | 43.21 | 43.22 | 43.26 | 43.33
AVERAGE | [5 empty] | 43.39 | 43.45 | 43.45 | 41.23 | 41.78 | 43.23 | 43.37 | 43.47 | ER | 28.05 | 37.97 | 40.6 | 43.08 | 43.37 | 43.4 | 43.4 | 43.41 | 36.71 | 40.11 | 43.01 | 43.2 | 43.26 | 43.27 | 43.3 | 38.1 | 40.45 | 41.62 | 43.06 | 43.05 | 43.12 | 43.29
MONITORING WELL THREE UPPER/LOWER LEVEL
| MW-3 |  | UPPER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MINIMUM | [5 empty] | 33.76 | 33.83 | 33.79 | 18.14 | 18 | 33.46 | 33.65 | 33.77 | ER | ER | 18.17 | 17.98 | 33.41 | 33.59 | 33.64 | 33.59 | 33.56 | 18.07 | 18.04 | 33.2 | 33.35 | 33.44 | 33.44 | ER | 22.53 | 22.35 | ER | 33.46 | 33.57 | 33.63 | 33.68
MAXIMUM | [5 empty] | 34.06 | 34.1 | 33.99 | 33.85 | 33.49 | 33.76 | 33.9 | 33.99 | ER | 34.01 | 34.01 | 33.48 | 33.71 | 33.86 | 33.88 | 33.85 | 33.89 | 33.8 | 33.33 | 33.55 | 33.67 | 33.74 | 33.76 | 33.79 | 33.8 | 33.62 | 33.82 | 33.85 | 33.86 | 33.88 | 33.95
AVERAGE | [5 empty] | 33.9 | 33.94 | 33.91 | 24.89 | 28.2 | 33.56 | 33.77 | 33.86 | ER | 23.2 | 22.81 | 28.44 | 33.54 | 33.71 | 33.74 | 33.71 | 33.73 | 22.46 | 28.35 | 33.34 | 33.44 | 33.54 | 33.58 | 33.59 | 26.2 | 29.78 | 32.67 | 33.7 | 33.72 | 33.78 | 33.84
| MW-3 |  | LOWER LEVEL |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MINIMUM | [5 empty] | 46.02 | 46.12 | 46.12 | 37.18 | 37.18 | 45.71 | 45.93 | 46.09 | ER | ER | 36.97 | 36.95 | 45.78 | 45.96 | 46.12 | 46.12 | 46.12 | 35.78 | 35.78 | 45.77 | 45.91 | 46.01 | 46.04 | ER | 40.19 | 40.14 | ER | 45.46 | 45.88 | 45.96 | 46
MAXIMUM | [5 empty] | 46.2 | 46.29 | 46.24 | 46.17 | 45.72 | 45.95 | 46.09 | 46.25 | ER | 46.29 | 46.3 | 45.78 | 46 | 46.22 | 46.29 | 46.27 | 46.33 | 46.3 | 45.79 | 45.99 | 46.08 | 46.15 | 46.18 | 46.23 | 46.24 | 45.81 | 45.98 | 46.04 | 46.07 | 46.08 | 46.16
AVERAGE | [5 empty] | 46.03 | 46.17 | 46.11 | 41.1 | 42.74 | 45.87 | 45.99 | 46.07 | ER | 29.47 | 39.73 | 42.83 | 45.91 | 46 | 46.17 | 46.17 | 46.26 | 38.77 | 42.6 | 45.89 | 45.99 | 46.01 | 46.01 | 46.03 | 42.15 | 43.8 | 44.4 | 45.96 | 46 | 46 | 46.02
MONITORING WELL RMW-1 UPPER/LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
[5 empty] | JULIAN DATE | 182 | 183 | 184 | 185 | 186 | 187 | 188 | 189 | 190 | 191 | 192 | 193 | 194 | 195 | 196 | 197 | 198 | 199 | 200 | 201 | 202 | 203 | 204 | 205 | 206 | 207 | 208 | 209 | 210 | 211 | 212
| RMW-1 |  | UPPER LEVEL
MINIMUM | [5 empty] | 45.08 | 45.1 | 45.05 | 39.05 | 38.97 | 44.48 | 44.68 | 44.81 | 44.94 | 44.95 | 44.91 | 44.89 | 44.96 | 44.99 | 44.98 | 44.93 | 44.93 | 44.93 | 44.9 | 44.93 | 44.9 | 44.92 | 44.92 | 44.96 | 44.98 | 44.98 | 44.99 | 44.97 | 44.9 | 44.88 | 44.9
MAXIMUM | [5 empty] | 45.19 | 45.2 | 45.19 | 45.09 | 44.48 | 44.68 | 44.82 | 44.99 | 45.12 | 45.08 | 45.02 | 44.97 | 45.03 | 45.07 | 45.08 | 45.05 | 45.03 | 45.05 | 45.04 | 45.03 | 45.04 | 45.03 | 45.04 | 45.04 | 45.06 | 45.04 | 45.05 | 45.05 | 44.99 | 44.98 | 44.99
AVERAGE | [5 empty] | 45.13 | 45.15 | 45.1 | 41.84 | 42.73 | 44.6 | 44.76 | 44.89 | 45.04 | 45.01 | 44.96 | 44.93 | 44.99 | 45.02 | 45.02 | 44.99 | 44.99 | 45 | 44.98 | 44.98 | 44.99 | 44.99 | 44.99 | 45 | 45.02 | 45.01 | 45.02 | 45 | 44.95 | 44.94 | 44.95
| RMW-1 |  | LOWER LEVEL
MINIMUM | [5 empty] | 23.95 | 23.95 | 23.9 | 20.52 | 20.91 | 22.58 | 22.83 | 22.97 | 23.08 | 23.07 | 23.04 | 23.02 | 23.07 | 23.08 | 23.06 | 22.98 | 22.97 | 22.98 | 22.95 | 22.98 | 22.97 | 23.01 | 23 | 23.04 | 23.04 | 23.04 | 23.01 | 22.99 | 22.92 | 22.9 | 22.92
MAXIMUM | [5 empty] | 24.07 | 24.09 | 24.04 | 23.94 | 22.59 | 22.83 | 22.98 | 23.12 | 23.19 | 23.18 | 23.15 | 23.13 | 23.15 | 23.22 | 23.2 | 23.14 | 23.14 | 23.14 | 23.11 | 23.09 | 23.1 | 23.12 | 23.12 | 23.12 | 23.15 | 23.14 | 23.15 | 23.12 | 23.05 | 23.05 | 23.05
AVERAGE | [5 empty] | 24.02 | 24.03 | 23.96 | 22.3 | 21.97 | 22.71 | 22.88 | 23.02 | 23.15 | 23.11 | 23.08 | 23.07 | 23.12 | 23.15 | 23.13 | 23.08 | 23.06 | 23.07 | 23.05 | 23.05 | 23.04 | 23.06 | 23.05 | 23.08 | 23.11 | 23.1 | 23.1 | 23.06 | 23 | 22.98 | 22.99
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
| INJECTION WELL ONE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 14.85 | 14.27 | 14.88 | 13.33 | 14.38 | 11.74 | 11.52 | 13.75 | 0 | 13.19 | 14.32 | 12.88 | 14.04 | 14.25 | 13.61 | 12.87 | 11.41 | 12.31 | 13.53 | 12.32 | 11.23 | 12.39 | 12.27 | 11.42 | 14.53 | 11.59 | 3.96 | 12.98 | 11.89 | 11.64 | 11.61
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 9.64 | 0 | 0 | 0.01 | 6.86 | 6.56 | 0.01 | 0.01 | ER | ER | 7.96 | 0.01 | 0.01 | 0.01 | 5.71 | 5.39 | 0.01 | 0.01 | 0.01 | 5.62 | 5.34 | 0.01 | 0.01 | 0 | 0.76 | 6.89 | ER | 0.01 | 0.01 | 5.53 | 5.62
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 12.93 | 3.01 | 10.56 | 8.84 | 10.6 | 10.13 | 2.15 | 8.3 | ER | 5.93 | 11.34 | 2.43 | 8.72 | 9.09 | 9.93 | 9.45 | 2 | 7.79 | 7.83 | 9.27 | 9.1 | 2.42 | 7.4 | 9.07 | 9.37 | 9.38 | ER | 7.34 | 7.41 | 8.88 | 8.8
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 70.2 | 67.93 | 69.42 | 64.78 | 67.05 | 58.62 | 56.44 | 64.52 | 41.82 | 65.44 | 69.68 | 61.45 | 65.16 | 63.39 | 62.37 | 59.72 | 57.74 | 60.03 | 64.65 | 59.76 | 57.71 | 61.27 | 59.35 | 57.38 | 66.41 | 57.79 | 44.13 | 62.62 | 58.8 | 57.97 | 58.76
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 53.94 | 35.51 | 36.36 | 35.65 | 44.95 | 44.83 | 34.87 | 34.04 | ER | ER | 48.94 | 29.99 | 36.02 | 34.82 | 40.58 | 37.99 | 35.45 | 35.77 | 35.42 | 41.37 | 41.26 | 36.01 | 35.8 | 0 | 37.5 | 45.5 | 0 | 35.74 | 35.34 | 42.07 | 42.65
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 63.39 | 43.56 | 56.67 | 52.08 | 54.81 | 53.69 | 40.35 | 51.48 | 26.05 | 30.19 | 58.28 | 41.11 | 51.5 | 51.04 | 52.64 | 51.52 | 39.74 | 48.87 | 48.56 | 50.56 | 50.85 | 40.44 | 48.3 | 50.55 | 51.88 | 51.72 | 36.62 | 48.17 | 47.92 | 50.13 | 50.18
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
| INJECTION WELL TWO |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 15.09 | 15.46 | 12.84 | 13.65 | 12.32 | 12.01 | 12.68 | 12.54 | 0 | 13.49 | 14.6 | 14.34 | 13.68 | 12.33 | 11.94 | 13.31 | 13.94 | 13.29 | 13.94 | 11.96 | 11.56 | 16.01 | 10.88 | 11.78 | 13.67 | 11.9 | 13.78 | 11.57 | 12.17 | 11.93 | 11.91
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 9.83 | 9.64 | 0.05 | 0.05 | 0.05 | 6.7 | 6.89 | 0.05 | ER | ER | 8.12 | 7.27 | 0.05 | 0.05 | 0.05 | 5.5 | 4.81 | 0.05 | 0.06 | 0.06 | 5.36 | 5.89 | 0.05 | 0 | 0.05 | 7 | ER | 0.05 | 0.05 | 0.05 | 5.57
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 13.18 | 13.53 | 0.8 | 8.54 | 8.69 | 10.36 | 10.82 | 2.38 | ER | 6.03 | 11.58 | 11.83 | 2.73 | 8.16 | 8.17 | 9.67 | 9.77 | 2.25 | 7.69 | 7.83 | 9.36 | 10.2 | 2.19 | 8.34 | 7.92 | 9.58 | 9.79 | 2.12 | 7.25 | 7.44 | 8.99
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 68.96 | 69.44 | 59.67 | 62.8 | 59.16 | 57.44 | 58.84 | 58.54 | 63.76 | 63.28 | 67.48 | 64.93 | 61.6 | 59.29 | 57.53 | 61.91 | 63.38 | 61.15 | 63.67 | 57.31 | 56.93 | 71.6 | 52.88 | 56.69 | 63.48 | 56.86 | 63.09 | 56.25 | 57.63 | 57.43 | 57.61
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 52.63 | 51.25 | 37.08 | 36.43 | 36.95 | 44.11 | 44.46 | 36.9 | ER | ER | 47.26 | 45.13 | 36.8 | 35.94 | 36.87 | 41.16 | 40.44 | 36.8 | 36.01 | 36.63 | 41.26 | 42.11 | 36.83 | 0 | 36.56 | 44.86 | 0 | 37.01 | 35.86 | 36.61 | 42.21
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 62.31 | 62.67 | 39.22 | 50.85 | 50.92 | 52.92 | 53.62 | 40.83 | 38.59 | 29.45 | 57.1 | 56.95 | 41.5 | 48.89 | 49.31 | 51.33 | 51.19 | 40.58 | 48.11 | 48.07 | 50.29 | 52.58 | 40.19 | 48.58 | 48.96 | 50.94 | 51.96 | 40.24 | 47.08 | 47.49 | 49.56
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
| INJECTION WELL THREE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 14.45 | 13.94 | 13.83 | 13.64 | 11.74 | 11.28 | 11.56 | 12.85 | 0 | 12.79 | 13.61 | 12.91 | 13.1 | 12.63 | 11.44 | 11.26 | 12.51 | 12.13 | 12.94 | 11.34 | 10.91 | 14.5 | 11.52 | 4.23 | 14.1 | 10.84 | 12.42 | 12.15 | 11.11 | 11.35 | 11.19
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 0.09 | 9.39 | 8.49 | ER | ER | ER | 6.89 | 6.84 | ER | ER | 6.28 | 7.28 | 7.97 | ER | ER | ER | 4.76 | 5.96 | ER | ER | ER | 6.03 | 6.5 | ER | ER | ER | ER | 5.59 | ER | ER | ER
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 12.23 | 12.44 | 11.36 | 2.69 | 7.95 | 8.09 | 10.07 | 10.05 | ER | 5.79 | 10.98 | 10.94 | 10.69 | 1.76 | 7.51 | 7.58 | 9.13 | 9.44 | 2.11 | 7.19 | 7.45 | 9.52 | 9.06 | 0.03 | 7.28 | 7.49 | 9 | 8.92 | 2.01 | 6.87 | 7.15
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 70.5 | 70.7 | 69.45 | 68.62 | 60.37 | 58.64 | 59.9 | 65.39 | 64.99 | 64.65 | 68.87 | 66.07 | 65.42 | 64.31 | 58.72 | 58.68 | 64.54 | 62.32 | 66.13 | 58.55 | 58.12 | 73 | 59.74 | 39.57 | 69.95 | 57.21 | 64.23 | 62.71 | 59.51 | 58.68 | 58.71
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 38.09 | 52.31 | 51.1 | 37.94 | 37.41 | 37.23 | 45.35 | 46.14 | ER | ER | 48.21 | 46.03 | 47.86 | 37.21 | 36.76 | 36.82 | 41.25 | 43.08 | 37.56 | 36.96 | 36.61 | 42.95 | 44.18 | 0 | 36.84 | 37.13 | 0 | 43.06 | 37.64 | 36.99 | 37.06
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 63.01 | 63.87 | 59.8 | 43.75 | 51.37 | 51.06 | 54.64 | 54.67 | 39.35 | 30.13 | 58.15 | 58.01 | 56.55 | 41.03 | 49.67 | 49.65 | 52.17 | 52.87 | 41.58 | 48.57 | 49.22 | 53.63 | 51.64 | 38.5 | 49.55 | 49.33 | 53 | 51.45 | 41.31 | 48.07 | 48.56
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
FUTURE
| INJECTION WELL FOUR |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 14.23 | 14.06 | 13.92 | 13.71 | 13.88 | 11.74 | 11.6 | 12.94 | 0 | 6.51 | 14.21 | 13.04 | 13.27 | 13.06 | 13.17 | 11.66 | 12.65 | 12.55 | 13.25 | 12.11 | 11.28 | 14.91 | 11.55 | 11.26 | 14.89 | 11.2 | 12.51 | 12.23 | 11.62 | 9.92 | 11.6
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | 0.04 | 0.04 | 8.62 | 7.6 | 0.05 | 0.05 | 0.05 | 6.92 | ER | ER | 0.05 | 0.05 | 8.06 | 6.56 | 0.05 | 0.05 | 0.05 | 6.13 | 6.32 | 0.05 | 0.05 | 0.05 | 6.61 | 0 | 0.05 | 0.05 | ER | 5.74 | 5.74 | 0.05 | 0.05
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 10.53 | 10.18 | 11.44 | 10.9 | 2.56 | 8 | 8.42 | 10.15 | ER | 0.07 | 8.75 | 9.09 | 10.91 | 10.27 | 2.38 | 7.45 | 7.61 | 9.59 | 9.57 | 2.11 | 7.39 | 8.06 | 9.18 | 9.1 | 2.37 | 7.36 | ER | 9.06 | 9.07 | 2.02 | 7.07
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 69.88 | 71.3 | 69.97 | 69.13 | 67.74 | 59.08 | 60.49 | 65.95 | 0 | 39.66 | 69.18 | 66.62 | 65.9 | 65.44 | 64.94 | 59.32 | 65.13 | 62.89 | 66.68 | 61.04 | 58.66 | 73.4 | 60.36 | 58.62 | 72.7 | 57.85 | 64.57 | 63.31 | 60.12 | 53.74 | 59.3
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 37.77 | 37.64 | 51.69 | 47.62 | 37.92 | 37.29 | 37.04 | 46.82 | ER | ER | 37.41 | 37.4 | 48.55 | 46.35 | 37.82 | 36.9 | 37.19 | 43.79 | 44.53 | 37.59 | 36.57 | 36.99 | 44.77 | 0 | 37.54 | 37.1 | ER | 43.76 | 43.37 | 37.8 | 37.02
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 59.57 | 59.47 | 60.37 | 57.63 | 42.91 | 50.93 | 52.53 | 55.29 | ER | ER | 53.98 | 55.11 | 57.12 | 54.75 | 42.27 | 49.59 | 50.35 | 53.53 | 53.05 | 41.16 | 49.29 | 51.85 | 52.28 | 51.58 | 41.86 | 49.31 | 51.34 | 52.11 | 51.79 | 41.06 | 48.58
GTL PLANT DAILY INJECTION WELL FLOW SUMMARY
| INJECTION WELL FIVE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
INSTANTANEOUS MAXIMUN FLOW (MGD) | [5 empty] | 12.73 | 13.19 | 13.1 | 12.87 | 12.91 | 11.02 | 10.93 | 12.18 | 0 | 12.34 | 10.71 | 12.28 | 12.33 | 12.17 | 12.24 | 12.17 | 11.9 | 10.94 | 12.33 | 11.28 | 10.25 | 11.08 | 10.92 | 10.57 | 14.47 | 10.99 | 11.8 | 11.53 | 10.87 | 11.01 | 9.33
INSTANTANEOUS MINIMUM FLOW (MGD) | [5 empty] | ER | ER | ER | 7.15 | 6.65 | ER | ER | ER | ER | ER | ER | ER | ER | 5.43 | 5.79 | ER | ER | ER | 6.07 | 5.62 | ER | ER | ER | 0 | ER | ER | ER | ER | 5.5 | 5.48 | ER
TOTAL DAILY WELL FLOW (MGD) | [5 empty] | 0.83 | 8.99 | 10.65 | 10.23 | 10.01 | 2.21 | 7.52 | 7.89 | ER | 5.58 | 0.6 | 8.1 | 8.25 | 9.58 | 9.46 | 2.11 | 6.79 | 7.42 | 8.98 | 8.91 | 1.88 | 6.11 | 7.12 | 8.55 | 8.62 | 2.17 | 8.59 | 7.01 | 8.54 | 8.56 | 1.89
INSTANTANEOUS MAXIMUM PRESSURE (PSIG) | [5 empty] | 64.89 | 70.4 | 68.94 | 68.2 | 66.71 | 57.86 | 59.47 | 64.92 | 64.6 | 64.04 | 58.38 | 65.62 | 64.97 | 63.91 | 63.9 | 62.77 | 64.19 | 59.29 | 65.75 | 60 | 55.12 | 60.62 | 59.25 | 57.4 | 71.9 | 57.74 | 63.78 | 62.32 | 59.21 | 58.11 | 51.78
INSTANTANEOUS MINIMUM PRESSURE (PSIG) | [5 empty] | 36.7 | 36.28 | 37.59 | 46.58 | 44.88 | 36.84 | 35.74 | 36.71 | ER | ER | 36.58 | 36.12 | 36.62 | 45.44 | 42.62 | 36.54 | 35.71 | 36.83 | 43.54 | 42.22 | 36.69 | 35.33 | 36.84 | 0 | 36.33 | 36.89 | 0 | 36.94 | 42.37 | 42.14 | 36.68
AVERAGE WELL PRESSURE (PSIG) | [5 empty] | 39.7 | 57.41 | 59.14 | 56.53 | 54.94 | 40.92 | 50.88 | 51.58 | 39.12 | 29.81 | 38.82 | 53.34 | 52.6 | 53.55 | 52.94 | 40.58 | 48.67 | 49.99 | 52 | 50.93 | 39.65 | 47.89 | 48.99 | 50.49 | 51.23 | 40.65 | 52.57 | 48.83 | 50.73 | 50.18 | 39.91
GTL DAILY LABORATORY ANALYSIS REPORT DATA
| RAW INFLUENT DATA |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
RAW TOTAL SUSPENDED SOLIDS | [5 empty] | 48 | 96 | 60 | 136 | 70 | 120 | 120 | 90 | 138 | 78 | 54 | 140 | 86 | 96 | 104 | 100 | 86 | 114 | 136 | 118 | 106 | 54 | 98 | 64 | 112 | 102 | 80 | 94 | 88 | 102 | 94
RAW FIXED SUSPENDED SOLIDS | [5 empty] | 0 | 28 | 0 | 10 | 0 | 18 | 12 | 22 | 14 | 18 | 0 | 24 | 22 | 8 | 12 | 10 | 10 | 24 | 16 | 30 | 0 | 8 | 18 | 0 | 20 | 11 | 2 | 0 | 6 | 4 | 4
RAW ALKILINITY | [5 empty] | 191 | 202 | 195 | 194 | 210 | 204 | 206 | 212 | 208 | 202 | 208 | 194 | 210 | 200 | 202 | 194 | 196 | 192 | 210 | 210 | 202 | 205 | 200 | 216 | 206 | 202 | 20 | 206 | 208 | 206 | 202
RAW CHLORIDES | [5 empty] | 420 | 400 | 410 | 410 | 410 | 490 | 600 | 600 | 420 | 370 | 500 | 680 | 890 | 750 | 540 | 530 | 530 | 590 | 530 | 700 | 580 | 590 | 560 | 590 | 600 | 570 | 540 | 550 | 540 | 510 | 490
RAW COD | [5 empty] | 101 | 130 | 170 | 144 | 157 | 509 | 208 | 99 | 195 | 168 | 136 | 238 | 129 | 215 | 172 | 203 | 219 | 218 | 213 | 130 | 155 | 124 | 152 | 163 | 215 | 122 | 142 | 103 | 133 | 140 | 158
RAW CBOD | [5 empty] | 69.7 | 25.2 | 99 | ER | 21.4 | ER | ER | ER | 72.7 | ER | NR | 19.1 | NR | NR | 72.75 | 63.1 | NR | 98.38 | 126.9 | 73.7 | 84.1 | 97.9 | 93.5 | 89.2 | 94.5 | 84.8 | 85 | 99 | 89 | 114 | 97
RAW SUFATES | [5 empty] | 105 | 110 | 111.25 | 103 | 104.75 | 123.5 | 134.75 | 128.75 | 104.5 | 103.25 | 104.5 | 129.75 | 162.5 | 151 | 126 | 121.75 | 124.25 | 124.5 | 125.75 | 144.25 | 139.5 | 128 | 140.25 | 135.25 | 130.25 | 134 | 124.5 | 122.75 | 119.75 | 122.25 | 112.75
| EFFLUENT DATA |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
EFFLUENT TOTAL DISSOLVED SOLIDS | [5 empty] | 975 | 953 | 951 | 908 | 902 | 989 | 1098 | 1275 | 1018 | 821 | 1005 | 1175 | 1579 | 1607 | 1112 | 1033 | 1016 | 1087 | 1278 | 1213 | 1200 | 1141 | 1237 | 1209 | 1244 | 1211 | 1112 | 1001 | 1183 | 1094 | 1030
EFFLUENT TOTAL SUSPENDED SOLIDS | [5 empty] | 15 | 24 | 10 | 7 | 2 | 17 | 15 | 16 | 18 | 16 | 19 | 12 | 13 | 23 | 12 | 21 | 5 | 40 | 27 | 18 | 14 | 9 | 23 | 8 | 20 | 8 | 3 | 11 | 13 | 10 | 18
EFFLUENT FIXED SUSPENDED SOLIDS | [5 empty] | 0 | 6 | 0 | 1 | 0 | 2 | 0 | 3 | 0 | 4 | 0 | 0 | 7 | 5 | 4 | 5 | 0 | 11 | 0 | 5 | 0 | 0 | 11 | 0 | 2 | 0 | 0 | 0 | 5 | 0 | 1
EFFLUENT ALKILINITY | [5 empty] | 184 | 182 | 184 | 188 | 192 | 186 | 196 | 190 | 194 | 178 | 188 | 200 | 196 | 192 | 184 | 188 | 190 | 190 | 188 | 194 | 190 | 189 | 190 | 182 | 190 | 182 | 186 | 184 | 186 | 184 | 190
EFFLUENT TURBIDITY | [5 empty] | 6.23 | 4.07 | 4.78 | 4.49 | 4.34 | 3.14 | 4.74 | 9.9 | 7.56 | 7.06 | 8.46 | 6.45 | 7.69 | 9.3 | 6.08 | 6.31 | 6.4 | 13.8 | 11.3 | 7.3 | 5.59 | 4.59 | 4.76 | 5.19 | 6.23 | 4.84 | 4.4 | 4.8 | 4.73 | 4.71 | 5.28
EFFLUENT CHLORIDES | [5 empty] | 420 | 410 | 410 | 410 | 450 | 480 | 570 | 630 | 480 | 400 | 510 | 590 | 840 | 820 | 550 | 530 | 530 | 580 | 620 | 620 | 600 | 520 | 590 | 600 | 600 | 570 | 540 | 550 | 540 | 530 | 500
EFFLUENT CONDUCTIVITY | [5 empty] | 1879 | 1823 | 1887 | 1947 | 1980 | 2050 | 2320 | 2660 | 2070 | 1761 | 2160 | 2450 | 3250 | 3190 | 2260 | 2210 | 2150 | 2370 | 2620 | 2570 | 2560 | 2280 | 2500 | 2580 | 2580 | 2530 | 2360 | 2250 | 2280 | 2290 | 2170
EFFLUENT TOTAL BACTERIA COUNT | [5 empty] | 634 | 0 | 9 | 134 | 196 | 18 | TNTC | 18 | 18 | TNTC | 0 | 161 | 0 | TNTC | 161 | 9 | 36 | 36 | 89 | 9 | 214 | 9 | 9 | 18 | 0 | 18 | 36 | 0 | 0 | TNTC | 9
EFFLUENT FECAL BACTERIA COUNT | [5 empty] | 0 | 0 | 0 | 0 | 9 | 9 | 23000 | 0 | 0 | TNTC | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TNTC | 0
EFFLUENT COD | [5 empty] | 41.4 | 39.9 | 36.5 | 39.5 | 43 | 65.6 | 56.6 | 49.8 | 50.2 | 39.5 | 43.1 | 47.1 | 51.3 | 48.2 | 51.6 | 48.2 | 44.6 | 45.2 | 44.3 | 44.8 | 44.7 | 44.8 | 44.2 | 42.7 | 43.2 | 43.2 | 42.6 | 41.3 | 43.8 | 43.5 | 42.5
EFFLUENT CBOD | [5 empty] | 2.08 | 3.27 | 2.93 | 2.66 | 3.53 | 3.03 | 2.43 | 3.5 | 2.4 | 2 | 4.26 | 3.95 | NR | NR | 4.62 | 2.82 | NR | 10.33 | 6.63 | 2.66 | 2.66 | NR | 3.48 | 2.4 | 2.66 | 2.51 | NR | 3 | 2 | 3 | 2
EFFLUENT SULFATES | [5 empty] | 108.5 | 104.75 | 100.25 | 103.25 | 104.75 | 111 | 113.75 | 130.25 | 109.25 | 86.75 | 109.5 | 118 | 141.75 | 149 | 112 | 110.75 | 106 | 111.25 | 114 | 120.75 | 116.5 | 138.5 | 116.5 | 118 | 115.75 | 111 | 109 | 107.5 | 113.75 | 109.5 | 105
LABORATORY NUTRIENT DATA
RAW INFLUENT | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
RAW AMMONIA (PPM) | [5 empty] | 9.3 | 8.7 | 7.5 | 5.9 | 9 | 11 | 11 | 14 | 11 | 11 | 12 | 11 | 12 | 13 | 12 | 12 | 14 | 15 | 15 | 15 | 14 | 16 | 13 | 14 | 16 | NR | NR | NR | 15 | 14 | 11
RAW NITRATES (PPM) | [5 empty] | 0.13 | 0.18 | 0.05 | 0.05 | 0.065 | 0.081 | 0.11 | 0.12 | 0.12 | 0.093 | 0.082 | 0.079 | 0.099 | 0.17 | 0.16 | 0.05 | 0.05 | 0.05 | 0.05 | 0.09 | 0.05 | 0.11 | 0.05 | 0.075 | 0.11 | NR | NR | NR | 0.026 | 0.053 | 0.05
RAW TOTAL KNEDJAHL NITRIGEN | [5 empty] | 13 | 15 | 15 | 15 | 17 | 20 | 21 | 20 | 19 | 18 | 20 | 19 | 15 | 21 | 19 | 18 | 23 | 17 | 21 | 19 | 17 | 20 | 20 | 22 | 23 | NR | NR | NR | 17 | 15 | 18
RAW TOTAL PHOSPHORUS | [5 empty] | 2 | 2.2 | 2.2 | 2 | 2.4 | 2.4 | 2.4 | 2.5 | 2.3 | 2.1 | 2 | 2.5 | 2.1 | 2.5 | 2.2 | 2.1 | 2.9 | 2.7 | 3.1 | 2.8 | 2.6 | 2.5 | 2.4 | 2.8 | 2.8 | NR | NR | NR | 3.1 | 3.7 | 2.9
EFFLUENT | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
EFFLUENT AMMONIA (PPM) | [5 empty] | 6.3 | 4.9 | 5 | 5.8 | 7.9 | 8.9 | 8.9 | 9.8 | 7.8 | 6.8 | 9.3 | 9.6 | 9.8 | 11 | 10 | 7 | 11 | 9.9 | 10 | 10 | 10 | 8.2 | 8.9 | 8.7 | 15 | NR | NR | NR | 12 | 9.5 | 9.7
EFFLUENT NITRATES (PPM) | [5 empty] | 0.44 | 0.49 | 0.37 | 0.38 | 0.38 | 0.35 | 0.29 | 0.47 | 0.24 | 0.25 | 0.31 | 0.31 | 0.31 | 0.32 | 0.37 | 0.35 | 0.35 | 0.21 | 0.23 | 0.19 | 0.3 | 0.37 | 0.34 | 0.26 | 0.32 | NR | NR | NR | 0.35 | 0.3 | 0.33
EFFLUENT TOTAL KNEDJAHL NITRIGEN | [5 empty] | 8.2 | 8.9 | 8.1 | 9.5 | 12 | 13 | 14 | 14 | 13 | 10 | 15 | 11 | 11 | 15 | 15 | 12 | 13 | 13 | 13 | 12 | 11 | 11 | 0 | 11 | 12 | NR | NR | NR | 12 | 11 | 12
EFFLUENT TOTAL PHOSPHORUS | [5 empty] | 0.99 | 0.78 | 0.65 | 0.56 | 0.56 | 0.46 | 0.99 | 0.88 | 0.8 | 0.65 | 0.99 | 0.58 | 1.1 | 1.4 | 1.3 | 1.2 | 1.3 | 1.4 | 1 | 1.4 | 1.5 | 1.3 | 1.3 | 1.2 | 0.88 | NR | NR | NR | 1.1 | 1.5 | 1.2
LABORATORY REACTOR PROCESSES DATA
| REACTOR ONE TRAIN A |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MIXED-LIQUIR SUSPENDED SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
AVERAGE SETTLABLE SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
MIXED LIQUIR VOLITLE SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
| REACTOR ONE TRAIN B |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MIXED-LIQUIR SUSPENDED SOLIDS | [5 empty] | 2430 | 1890 | 2320 | 2210 | 2080 | 2050 | 2300 | 2810 | 2660 | 2180 | 1960 | 2010 | 1570 | 1520 | 2510 | 2420 | 1440 | 2600 | 2700 | 1980 | 2610 | 3520 | 2400 | 2380 | 2230 | 2670 | 2170 | 2340 | 2480 | 2470 | 2300
AVERAGE SETTLABLE SOLIDS | [5 empty] | 12 | 16 | 20 | 24 | 22 | 20 | 20 | 22 | 21 | 20 | 14 | 17 | 20 | 15 | 19 | 23 | 20 | 16 | 19 | 19 | 19 | 20 | 27 | 24 | 26 | 20 | 21 | 21 | 23 | 26 | 18
MIXED LIQUIR VOLITLE SOLIDS | [5 empty] | 2180 | 1520 | 1950 | 1890 | ER | 1690 | 1920 | 2270 | 2180 | 1670 | 1610 | 1560 | 1200 | 1200 | 2060 | 2020 | 1210 | 2080 | 2270 | 1530 | 2230 | 2610 | 1960 | 1970 | 1750 | 2240 | 1750 | 1940 | 2060 | 2140 | 1920
LABORATORY REACTOR PROCESSES DATA
CONTINUED
| REACTOR TWO TRAIN C |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MIXED-LIQUIR SUSPENDED SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
AVERAGE SETTLABLE SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
MIXED LIQUIR VOLITLE SOLIDS | [5 empty] | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S | O/S
| REACTOR TWO TRAIN D |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
MIXED-LIQUIR SUSPENDED SOLIDS | [5 empty] | 2190 | 1590 | 2320 | 2300 | 1970 | 2090 | 2190 | 3010 | 2060 | 1860 | 1900 | 1740 | 1510 | 1930 | 2230 | 1540 | 1250 | 1730 | 1880 | 1690 | 1520 | 2880 | 2120 | 2130 | 2110 | 3360 | 2110 | 1810 | 2600 | 2420 | 1780
AVERAGE SETTLABLE SOLIDS | [5 empty] | 12 | 17 |  | 24 | 22 | 20 | 19 | 21 | 20 | 19 | 17 | 18 | 15 | 14 | 18 | 21 | 18 | 14 | 22 | 17 | 18 | 18 | 23 | 25 | 22 | 20 | 20 | 19 | 21 | 27 | 20
MIXED LIQUIR VOLITLE SOLIDS | [5 empty] | 1990 | 1290 | 1970 | 1970 | ER | 1730 | 2070 | 2400 | 1710 | 1480 | 1630 | 1430 | 1210 | 1600 | 1840 | 1310 | 1050 | 1410 | 1650 | 1350 | 1340 | 2270 | 1750 | 1740 | 1780 | 2740 | 1790 | 1550 | 2140 | 2080 | 1570
LABORATORY RETURN ACTIVATED SLUDGE AND WASTE SLUDGE DATA
| RETURN ACTIVATED SLUDGE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
PERCENT RETURN SLUDGE TOTAL SUSPENDED SOLIDS | [5 empty] | 0.66 | 0.7 | 0.84 | 0.8 | 0.66 | 0.71 | 0.68 | 0.91 | 0.9 | 0.86 | 0.73 | 0.73 | 0.62 | 0.6 | 0.51 | 0.94 | 0.54 | 0.68 | 0.69 | 0.52 | 0.64 | 0.53 | 0.61 | 0.84 | 0.79 | 0.74 | 0.7 | 0.64 | 0.44 | 0.63 | 0.58
PERCENT RETURN SLUDGE FIXED SUSPENDED SOLIDS | [5 empty] | 23.5 | 25.2 | 25.6 | 23.8 | 26.73 | 20.25 | 32.4 | 25.3 | 24.44 | 23.26 | 23.26 | 27.5 | 33.33 | 35.23 | 26.92 | 23.1 | 29.58 | 30.88 | 29.63 | 27.84 | 30.59 | 26.09 | 26.97 | 24.14 | 25.71 | 27.16 | 28.57 | 28.95 | 25.71 | 28.44 | 25.93
|  | WASTE SLUDGE |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
PERCENT WASTE FEED TOTAL SUSPENDED SOLDS | [9 empty] | 1.34 | 0.78 | 1.31 |  |  | 1.49 | 1.3 | 1.35 | 1.43 | 1.36 |  |  | 1 | 1.2 | 1.15 | 1.26 | 1.2 |  |  | 1.57 | 1.14 | 1.18 | 0.83 | 1.2 |  |  | 1.48
PERCENT WASTE FEED FIXED SUSPENDED SOLIDS | [9 empty] | 21.64 | 25.64 | 22.9 |  |  | 20.8 | 23.1 | 23.7 | 25.87 | 29.41 |  |  | 24 | 23.33 | 24.35 | 24.6 | 25.83 |  |  | 20.38 | 23.68 | 22.88 | 26.51 | 23.33 |  |  | 19.59
WASTE FEED SLUDGE pH | [9 empty] | 6.14 | 6.5 | 6.24 |  |  | 5.67 | 5.7 | 5.98 | 6.01 | 5.78 |  |  | 5.97 | 5.77 | 6.1 | 6.11 | 6.09 |  |  | 6.09 | 6 | 6.12 | 6.24 | 6.16 |  |  | 6.12
DEWATERING FILTRATE TOTAL SUSPENDED SOLIDS | [9 empty] | 0.15 | 0.23 | 0.18 |  |  | 0.13 | 0.15 | 0.19 | 0.22 | 0.23 |  |  | 0.17 | 0.19 | 0.19 | 0.22 | 0.22 |  |  | 0.19 | 0.21 | 0.2 | 0.16 | 0.21 |  |  | 0.17
DEWATERING FILTRATE FIXED SUSPENDED SOLIDS | [9 empty] | 66.7 | 47.83 | 83.3 |  |  | 92.37 | 80 | 73.68 | 77.27 | 73.91 |  |  | 88.24 | 68.42 | 78.95 | 68.18 | 72.73 |  |  | 63.16 | 66.67 | 70 | 68.75 | 57.14 |  |  | 70.59
DEWATERING FILTRATE pH | [9 empty] | 6.29 | 6.9 | 6.9 |  |  | 6.67 | 6.66 | 6.76 | 6.77 | 6.69 |  |  | 6.63 | 6.6 | 6.72 | 6.83 | 6.65 |  |  | 6.85 | 6.8 | 6.71 | 6.8 | 6.73 |  |  | 6.76
| DEWATERED CAKE SLUDGE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
PERCENT TOTAL SOLIDS PRESS CAKE | [9 empty] | 17.15 | 17.73 | 18.42 |  |  | 18.01 | 17.78 | 18.39 | 20.55 | 20.37 |  |  | 17.12 | 18.13 | 18.68 | 18.81 | 18.76 |  |  | 17.22 | 18.2 | 18.47 | 17.91 | 17.8 |  |  | 17.01
PERCENT FIXED SOLIDS PRESS CAKE | [9 empty] | 14.56 | 16.41 | 16.7 |  |  | 16.88 | 19.12 | 18.92 | 20.68 | 19.64 |  |  | 15.42 | 15.19 | 18.79 | 18.61 | 19.24 |  |  | 15.74 | 18.35 | 15.65 | 17.91 | 14.21 |  |  | 15.52
PERCENT TOTAL SOLIDS LIME CAKE
OTHER SLUDGE REMOVAL
[6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
GRIT (CU.YDS.) | [5 empty] | 1: 10; 8: 10; 15: 10; 25: 10; 28: 10
RAGS (CU.YDS.) | [5 empty] | 1: 10
VACUUM DEBRIS (EST. GAL)
MONITORING WELLS LABORATORY DATA
| MONITOR WELL ONE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
UPPER LEVEL
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
MONITORING WELLS LABORATORY DATA
| MONITOR WELL TWO |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
UPPER LEVEL
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
MONITORING WELLS LABORATORY DATA
| MONITOR WELL THREE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
FUTURE
UPPER LEVEL
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
MONITORING WELLS LABORATORY DATA
| REGIONAL MONITOR WELL ONE |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
UPPER LEVEL
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
LOWER LEVEL | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
TDS
CHLORIDES
AMMONIA-N
TKN
CONDUCTIVITY @ 25' C
FECAL COLIFORM
TOTAL PHOSPHORUS
SULFATE
JULY |  | 1 |  | 3
|  | 0 |  | 0
0
0
|  | 0 |  | 0
3
[5 empty] | 1st WEEK | 1: 2nd WEEK; 2: 3rd WEEK; 3: 4th WEEK
| 1 |  | 1 |  | 1 | 1: 8; 2: 15; 3: 23
| 2 |  | 2 |  | 2 | 1: 9; 2: 16; 3: 24
| 3 |  | 3 |  | 3 | 1: 10; 2: 17; 3: 25
| 4 |  | 4 |  | 4 | 1: 11; 2: 18; 3: 26
| 5 |  | 5 |  | 5 | 1: 12; 2: 19; 3: 27
| 6 |  | 6 |  | 6 | 1: 13; 2: 20; 3: 28
| 7 |  | 7 |  | 7 | 1: 14; 2: 21; 3: 29
| 8 |  | 8 |  |  | 2: 22; 3: 30
| 9 |  | 9 |  |  | 3: 31
| 10 |  | 10
| 11 |  | 11
| 12 |  | 12
| 13 |  | 13
| 14 |  | 14
| 15 |  | 15
| 16 |  | 16
| 17 |  | 17
| 18 |  | 18
| 19 |  | 19
| 20 |  | 20
| 21 |  | 21
| 22 |  | 22
| 23 |  | 23
| 24 |  | 24
| 25 |  | 25
| 26 |  | 26
| 27 |  | 27
| 28 |  | 28
29
30
31
| APRIL | MARCH | FEBRUARY
| AUGUST | JULY | JUNE
| DECEMBER | NOVEMBER | OCTOBER
| FEBRUARY | JANUARY | DECEMBER
| JANUARY | DECEMBER | NOVEMBER
| JUNE | MAY | APRIL
| JULY | JUNE | MAY | JUNE
| MARCH | FEBRUARY | JANUARY | MAY
| MAY | APRIL | MARCH
| NOVEMBER | OCTOBER | SEPTEMBER
| OCTOBER | SEPTEMBER | AUGUST
| SEPTEMBER | AUGUST | JULY
| HYDROGEN PEROXIDE |  | 0.1465
| CHLORINE |  | 0.295
| POLYMER |  | 0.61
| FPL |  | 0.055
[6 empty] | 1st WEEK |  |  | 2nd WEEK |  |  | 3rd WEEK |  |  | 4th WEEK
[7 empty] | G | H | I | J
[5 empty] | MW1 UP | 1: 311
312
313
314
315
316
317
318

## MONITOR DATA
UNDERGROUND INJECTION CONTROL SECTION
MONTHLY OPERATING REPORT DATA SUMMARY
FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT MONTH/YEAR |  |  | JULY |  | 2005
I.D. NUMBER: 5006M02066 | [5 empty] | LEAD OPERATOR: |  |  |  | MIKE JUST
TELEPHONE NUMBER: (954) 523-1002
MONITORING WELL 1 DATA | [6 empty] | I.D. # 5006A11311
MW-1
PERMIT/CERTIFICATION NUMBER | [6 empty] | 0054569-142-UO
PERMIT EXPIRATION DATE |  | 2009-01-06
UPPER MONITORING INTERVAL | [6 empty] | 1,288' - 1,320' |  |  |  | Ft. bls.
Sample Date |  | 2005-07-05 |  | 2005-07-12 |  | 2005-07-19 |  | 2005-07-26
Submittal Date |  | 2005-07-06 |  | 2005-07-13 |  | 2005-07-20 |  | 2005-07-27
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 49.52 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 39.85 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 77 |  | 76 |  | 74 |  | 77 |  |  | degrees (F) |  | 76
TDS |  | 7509 |  | 7702 |  | 7516 |  | 7882 |  |  | mg/l |  | 7652.25
CHLORIDE |  | 3750 |  | 3750 |  | 3750 |  | 3650 |  |  | mg/l |  | 3725
AMMONIA-N |  | 0.78 |  | 0.94 |  | 0.99 |  | 0.89 |  |  | mg/l |  | 0.9
TKN |  | 1 |  | 1.1 |  | 1 |  | 0.93 |  |  | mg/l |  | 1.0075
pH |  | 7.32 |  | 7.48 |  | 7.95 |  | 8.02 |  |  | Std units |  | 7.6925
CONDUCTIVITY |  | 15640 |  | 12040 |  | 12200 |  | 12140 |  |  | umho/cm |  | 13005
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.008 | < | 0.01 | < | 0.01 | < | 0.01 |  |  | mg/l |  | 0.0095
SULFATE |  | 955 |  | 983 |  | 868 |  | 943 |  |  | mg/l |  | 937.25
C.O.D. 'S | [10 empty] | mg/l |  | #DIV/0!
IRON | [10 empty] | mg/l |  | #DIV/0!
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
LOWER MONITORING INTERVAL | [6 empty] | 1,449' - 1,557' |  |  |  | Ft. bls
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 47.47 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 38.52 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 76 |  | 77 |  | 78 |  | 76 |  |  | degrees (F) |  | 76.75
TDS |  | 9664 |  | 9803 |  | 9760 |  | 10044 |  |  | mg/l |  | 9817.75
CHLORIDE |  | 5000 |  | 5100 |  | 5100 |  | 4700 |  |  | mg/l |  | 4975
AMMONIA-N |  | 7.1 |  | 9.4 |  | 8.6 |  | 7.8 |  |  | mg/l |  | 8.225
TKN |  | 9.2 |  | 11 |  | 9.2 |  | 10 |  |  | mg/l |  | 9.85
pH |  | 7.59 |  | 7.32 |  | 7.38 |  | 7.4 |  |  | Std units |  | 7.4225
CONDUCTIVITY |  | 12130 |  | 15480 |  | 15520 |  | 15660 |  |  | umho/cm |  | 14697.5
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.008 | < | 0.01 | < | 0.01 | < | 0.01 |  |  | mg/l |  | 0.0095
SULFATE |  | 940 |  | 805 |  | 743 |  | 863 |  |  | mg/l |  | 837.75
C.O.D. 'S | [10 empty] | mg/l |  | #DIV/0!
IRON | [10 empty] | mg/l |  | #DIV/0!
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
PAGE 24
UNDERGROUND INJECTION CONTROL SECTION
MONTHLY OPERATING REPORT DATA SUMMARY
FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT MONTH/YEAR |  |  | JULY |  | 2005
I.D. NUMBER: 5006M02066 | [5 empty] | LEAD OPERATOR: |  |  |  | MIKE JUST
TELEPHONE NUMBER: (954) 523-1002
MONITORING WELL 2 DATA | [6 empty] | I.D. # 5006A11308 & 309
MW-2
PERMIT/CERTIFICATION NUMBER | [6 empty] | 0054569-142-UO
PERMIT EXPIRATION DATE |  | 2009-01-06
UPPER MONITORING INTERVAL | [6 empty] | 1,300' - 1,344' |  |  |  | Ft. bls.
Sample Date |  | 2005-07-05 |  | 2005-07-12 |  | 2005-07-19 |  | 2005-07-26
Submittal Date |  | 2005-07-06 |  | 2005-07-13 |  | 2005-07-20 |  | 2005-07-27
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 34.01 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 26.65 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 76 |  | 74 |  | 74 |  | 74 |  |  | degrees (F) |  | 74.5
TDS |  | 7381 |  | 7686 |  | 7393 |  | 7289 |  |  | mg/l |  | 7437.25
CHLORIDE |  | 3800 |  | 3650 |  | 3750 |  | 3550 |  |  | mg/l |  | 3687.5
AMMONIA-N |  | 0.75 |  | 0.95 |  | 1 |  | 0.82 |  |  | mg/l |  | 0.88
TKN |  | 1 |  | 1.2 |  | 1.2 |  | 1.1 |  |  | mg/l |  | 1.125
pH |  | 7.84 |  | 7.89 |  | 8.12 |  | 8.08 |  |  | Std units |  | 7.9825
CONDUCTIVITY |  | 12320 |  | 11780 |  | 11780 |  | 11790 |  |  | umho/cm |  | 11917.5
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.01 | < | 0.01 | < | 0.01 | < | 0.01 |  |  | mg/l |  | 0.01
SULFATE |  | 913 |  | 770 |  | 935 |  | 908 |  |  | mg/l |  | 881.5
C.O.D. 'S | [10 empty] | mg/l |  | #DIV/0!
IRON | [10 empty] | mg/l |  | #DIV/0!
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
LOWER MONITORING INTERVAL | [6 empty] | 1,970' - 2,025' |  |  |  | Ft. bls
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 43.56 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 33.94 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 76 |  | 74 |  | 74 |  | 74 |  |  | degrees (F) |  | 74.5
TDS |  | 33343 |  | 32950 |  | 32819 |  | 32438 |  |  | mg/l |  | 32887.5
CHLORIDE |  | 18200 |  | 18000 |  | 18400 |  | 16400 |  |  | mg/l |  | 17750
AMMONIA-N |  | 1.2 |  | 1.5 |  | 1.5 |  | 1.2 |  |  | mg/l |  | 1.35
TKN |  | 1.6 |  | 2.2 |  | 1.6 |  | 1.5 |  |  | mg/l |  | 1.725
pH |  | 7.52 |  | 7.43 |  | 7.56 |  | 7.49 |  |  | Std units |  | 7.5
CONDUCTIVITY |  | 46400 |  | 46000 |  | 46500 |  | 46600 |  |  | umho/cm |  | 46375
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.01 | < | 0.01 | < | 0.01 | < | 0.01 |  |  | mg/l |  | 0.01
SULFATE |  | 3410 |  | 2760 |  | 3010 |  | 3010 |  |  | mg/l |  | 3047.5
C.O.D. 'S | [10 empty] | mg/l |  | #DIV/0!
IRON | [10 empty] | mg/l |  | #DIV/0!
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
PAGE 25
UNDERGROUND INJECTION CONTROL SECTION
MONTHLY OPERATING REPORT DATA SUMMARY
FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT MONTH/YEAR |  |  | JULY |  | 2005
I.D. NUMBER: 5006M02066 | [5 empty] | LEAD OPERATOR: |  |  |  | MIKE JUST
TELEPHONE NUMBER: (954) 523-1002
MONITORING WELL 2 DATA | [6 empty] | I.D. # 5006A11310
MW-3
PERMIT/CERTIFICATION NUMBER | [6 empty] | 0054569-142-UO
PERMIT EXPIRATION DATE |  | 2009-01-06
UPPER MONITORING INTERVAL | [6 empty] | 1,300' - 1,349' |  |  |  | Ft. bls.
Sample Date |  | 2005-07-05 |  | 2005-07-12 |  | 2005-07-19 |  | 2005-07-26
Submittal Date |  | 2005-07-06 |  | 2005-07-13 |  | 2005-07-20 |  | 2005-07-27
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 34.1 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 17.98 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 72 |  | 72 |  | 72 |  | 73 |  |  | degrees (F) |  | 72.25
TDS |  | 7413 |  | 7796 |  | 7856 |  | 8608 |  |  | mg/l |  | 7918.25
CHLORIDE |  | 3650 |  | 3750 |  | 3700 |  | 3650 |  |  | mg/l |  | 3687.5
AMMONIA-N |  | 0.8 |  | 0.95 |  | 0.99 |  | 0.81 |  |  | mg/l |  | 0.8875
TKN |  | 0.97 |  | 1.3 |  | 2.4 |  | 1 |  |  | mg/l |  | 1.4175
pH |  | 8.15 |  | 8.16 |  | 8.31 |  | 8.23 |  |  | Std units |  | 8.2125
CONDUCTIVITY |  | 12070 |  | 11860 |  | 11960 |  | 12070 |  |  | umho/cm |  | 11990
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS |  | 0.01 | < | 0.01 | < | 0.01 | < | 0.01 |  |  | mg/l |  | 0.01
SULFATE |  | 978 |  | 943 |  | 878 |  | 905 |  |  | mg/l |  | 926
C.O.D. 'S | [10 empty] | mg/l |  | #DIV/0!
IRON | [10 empty] | mg/l |  | #DIV/0!
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
LOWER MONITORING INTERVAL | [6 empty] | 1,970' - 2,027' |  |  |  | Ft. bls
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 46.33 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 35.78 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 72 |  | 72 |  | 72 |  | 72 |  |  | degrees (F) |  | 72
TDS |  | 30602 |  | 30782 |  | 30575 |  | 29846 |  |  | mg/l |  | 30451.25
CHLORIDE |  | 16400 |  | 17200 |  | 16800 |  | 14600 |  |  | mg/l |  | 16250
AMMONIA-N |  | 2.1 |  | 2.5 |  | 2.4 |  | 2.4 |  |  | mg/l |  | 2.35
TKN |  | 2.4 |  | 2.4 |  | 1 |  | 2.2 |  |  | mg/l |  | 2
pH |  | 7.55 |  | 7.4 |  | 7.54 |  | 7.52 |  |  | Std units |  | 7.5025
CONDUCTIVITY |  | 42700 |  | 42600 |  | 42700 |  | 42400 |  |  | umho/cm |  | 42600
FECAL COLIFORM |  | 0 |  | 0 |  | 0 |  | 0 |  |  | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.01 |  | 0.012 | < | 0.01 | < | 0.01 |  |  | mg/l |  | 0.0105
SULFATE |  | 2960 |  | 2660 |  | 2730 |  | 2850 |  |  | mg/l |  | 2800
C.O.D. 'S | [10 empty] | mg/l |  | #DIV/0!
IRON | [10 empty] | mg/l |  | #DIV/0!
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
PAGE 26
UNDERGROUND INJECTION CONTROL SECTION
MONTHLY OPERATING REPORT DATA SUMMARY
FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT MONTH/YEAR |  |  | JULY |  | 2005
I.D. NUMBER: 5006M02066 | [5 empty] | LEAD OPERATOR: |  |  |  | MIKE JUST
TELEPHONE NUMBER: (954) 523-1002
REGIONAL MONITORING WELL DATA
RMW-1
PERMIT NUMBER | [6 empty] | 0054569-142-UO
PERMIT EXPIRATION DATE |  | 2009-01-06
UPPER MONITORING INTERVAL | [6 empty] | 1300' - 1339' |  |  |  | Ft. bls.
Sample Date |  | 2005-07-05
Submittal Date |  | 2005-07-06
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 45.2 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 38.97 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 72 | [8 empty] | degrees (F) |  | 72
TDS |  | 5602 | [8 empty] | mg/l |  | 5602
CHLORIDE |  | 2700 | [8 empty] | mg/l |  | 2700
AMMONIA-N |  | 0.61 | [8 empty] | mg/l |  | 0.61
TKN |  | 1 | [8 empty] | mg/l |  | 1
pH |  | 8.29 | [8 empty] | Std units |  | 8.29
CONDUCTIVITY |  | 95700 | [8 empty] | umho/cm |  | 95700
FECAL COLIFORM |  | 0 | [8 empty] | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.01 | [8 empty] | mg/l |  | 0.01
SULFATE |  | 848 | [8 empty] | mg/l |  | 848
C.O.D. 'S | [10 empty] | mg/l |  | #DIV/0!
IRON | [10 empty] | mg/l |  | #DIV/0!
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
LOWER MONITORING INTERVAL | [6 empty] | 1500' - 1600' |  |  |  | Ft. bls
MONTHLY MAX DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 24.09 |  | FT. HEAD | Rel NGVD
MONTHLY MIN DAILY PRESSURE ( PSIG or FT. HEAD : Rel to NGVD) | [8 empty] | 20.52 |  | FT. HEAD | Rel NGVD
TEMPERATURE (F) |  | 72 | [8 empty] | degrees (F) |  | 72
TDS |  | 53859 | [8 empty] | mg/l |  | 53859
CHLORIDE |  | 16000 | [8 empty] | mg/l |  | 16000
AMMONIA-N |  | 0.28 | [8 empty] | mg/l |  | 0.28
TKN |  | 0.24 | [8 empty] | mg/l |  | 0.24
pH |  | 7.59 | [8 empty] | Std units |  | 7.59
CONDUCTIVITY |  | 40800 | [8 empty] | umho/cm |  | 40800
FECAL COLIFORM |  | 0 | [8 empty] | # col/100ml |  | 0
TOTAL PHOSPHOROUS | < | 0.01 | [8 empty] | mg/l |  | 0.01
SULFATE |  | 2090 | [8 empty] | mg/l |  | 2090
C.O.D. 'S | [10 empty] | mg/l |  | #DIV/0!
IRON | [10 empty] | mg/l |  | #DIV/0!
SULFIDE | [10 empty] | mg/l |  | #DIV/0!
PAGE 27
Formulas:
LEAD OPERATOR: = [LEAD OPERATOR:, row above]+1

## WELL PRN DATA
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 1 |  |  | 182 | 183 | 184 | 185 | 186 | 187 | 188 | 189 | 190 | 191 | 192 | 193 | 194 | 195 | 196 | 197 | 198 | 199 | 200 | 201 | 202 | 203 | 204 | 205 | 206 | 207 | 208 | 209 | 210 | 211 | 212
182 | 14.85 | 9.64 | 12.93 | 70.2 | 53.94 | 63.39
183 | 14.27 | 0 | 3.01 | 67.93 | 35.51 | 43.56 |  |  | FLOW
184 | 14.88 | 0 | 10.56 | 69.42 | 36.36 | 56.67 | I |  | MAX | 14.85 | 14.27 | 14.88 | 13.33 | 14.38 | 11.74 | 11.52 | 13.75 | 0 | 13.19 | 14.32 | 12.88 | 14.04 | 14.25 | 13.61 | 12.87 | 11.41 | 12.31 | 13.53 | 12.32 | 11.23 | 12.39 | 12.27 | 11.42 | 14.53 | 11.59 | 3.96 | 12.98 | 11.89 | 11.64 | 11.61
185 | 13.33 | 0.01 | 8.84 | 64.78 | 35.65 | 52.08 | N |  | MIN | 9.64 | 0 | 0 | 0.01 | 6.86 | 6.56 | 0.01 | 0.01 | ER | ER | 7.96 | 0.01 | 0.01 | 0.01 | 5.71 | 5.39 | 0.01 | 0.01 | 0.01 | 5.62 | 5.34 | 0.01 | 0.01 | 0 | 0.76 | 6.89 | ER | 0.01 | 0.01 | 5.53 | 5.62
186 | 14.38 | 6.86 | 10.6 | 67.05 | 44.95 | 54.81 | J |  | TOT | 12.93 | 3.01 | 10.56 | 8.84 | 10.6 | 10.13 | 2.15 | 8.3 | ER | 5.93 | 11.34 | 2.43 | 8.72 | 9.09 | 9.93 | 9.45 | 2 | 7.79 | 7.83 | 9.27 | 9.1 | 2.42 | 7.4 | 9.07 | 9.37 | 9.38 | ER | 7.34 | 7.41 | 8.88 | 8.8
187 | 11.74 | 6.56 | 10.13 | 58.62 | 44.83 | 53.69 | E | INJECTION WELL ONE
188 | 11.52 | 0.01 | 2.15 | 56.44 | 34.87 | 40.35 | C |  | PSI
189 | 13.75 | 0.01 | 8.3 | 64.52 | 34.04 | 51.48 | T |  | MAX | 70.2 | 67.93 | 69.42 | 64.78 | 67.05 | 58.62 | 56.44 | 64.52 | 41.82 | 65.44 | 69.68 | 61.45 | 65.16 | 63.39 | 62.37 | 59.72 | 57.74 | 60.03 | 64.65 | 59.76 | 57.71 | 61.27 | 59.35 | 57.38 | 66.41 | 57.79 | 44.13 | 62.62 | 58.8 | 57.97 | 58.76
190 | 0 | ER | ER | 41.82 | ER | 26.05 | O |  | MIN | 53.94 | 35.51 | 36.36 | 35.65 | 44.95 | 44.83 | 34.87 | 34.04 | ER | ER | 48.94 | 29.99 | 36.02 | 34.82 | 40.58 | 37.99 | 35.45 | 35.77 | 35.42 | 41.37 | 41.26 | 36.01 | 35.8 | 0 | 37.5 | 45.5 | 0 | 35.74 | 35.34 | 42.07 | 42.65
191 | 13.19 | ER | 5.93 | 65.44 | ER | 30.19 | N |  | AVG | 63.39 | 43.56 | 56.67 | 52.08 | 54.81 | 53.69 | 40.35 | 51.48 | 26.05 | 30.19 | 58.28 | 41.11 | 51.5 | 51.04 | 52.64 | 51.52 | 39.74 | 48.87 | 48.56 | 50.56 | 50.85 | 40.44 | 48.3 | 50.55 | 51.88 | 51.72 | 36.62 | 48.17 | 47.92 | 50.13 | 50.18
192 | 14.32 | 7.96 | 11.34 | 69.68 | 48.94 | 58.28
193 | 12.88 | 0.01 | 2.43 | 61.45 | 29.99 | 41.11 | W
194 | 14.04 | 0.01 | 8.72 | 65.16 | 36.02 | 51.5 | E
195 | 14.25 | 0.01 | 9.09 | 63.39 | 34.82 | 51.04 | L
196 | 13.61 | 5.71 | 9.93 | 62.37 | 40.58 | 52.64 | L
197 | 12.87 | 5.39 | 9.45 | 59.72 | 37.99 | 51.52 | O
198 | 11.41 | 0.01 | 2 | 57.74 | 35.45 | 39.74 | N
199 | 12.31 | 0.01 | 7.79 | 60.03 | 35.77 | 48.87 | E
200 | 13.53 | 0.01 | 7.83 | 64.65 | 35.42 | 48.56
201 | 12.32 | 5.62 | 9.27 | 59.76 | 41.37 | 50.56 | D
202 | 11.23 | 5.34 | 9.1 | 57.71 | 41.26 | 50.85 | A
203 | 12.39 | 0.01 | 2.42 | 61.27 | 36.01 | 40.44 | T
204 | 12.27 | 0.01 | 7.4 | 59.35 | 35.8 | 48.3 | A
205 | 11.42 | 0 | 9.07 | 57.38 | 0 | 50.55
206 | 14.53 | 0.76 | 9.37 | 66.41 | 37.5 | 51.88
207 | 11.59 | 6.89 | 9.38 | 57.79 | 45.5 | 51.72
208 | 3.96 | ER | ER | 44.13 | 0 | 36.62
209 | 12.98 | 0.01 | 7.34 | 62.62 | 35.74 | 48.17
210 | 11.89 | 0.01 | 7.41 | 58.8 | 35.34 | 47.92
211 | 11.64 | 5.53 | 8.88 | 57.97 | 42.07 | 50.13
212 | 11.61 | 5.62 | 8.8 | 58.76 | 42.65 | 50.18
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 2 |  |  | 182 | 183 | 184 | 185 | 186 | 187 | 188 | 189 | 190 | 191 | 192 | 193 | 194 | 195 | 196 | 197 | 198 | 199 | 200 | 201 | 202 | 203 | 204 | 205 | 206 | 207 | 208 | 209 | 210 | 211 | 212
182 | 15.09 | 9.83 | 13.18 | 68.96 | 52.63 | 62.31
183 | 15.46 | 9.64 | 13.53 | 69.44 | 51.25 | 62.67 |  |  | FLOW
184 | 12.84 | 0.05 | 0.8 | 59.67 | 37.08 | 39.22 | I |  | MAX | 15.09 | 15.46 | 12.84 | 13.65 | 12.32 | 12.01 | 12.68 | 12.54 | 0 | 13.49 | 14.6 | 14.34 | 13.68 | 12.33 | 11.94 | 13.31 | 13.94 | 13.29 | 13.94 | 11.96 | 11.56 | 16.01 | 10.88 | 11.78 | 13.67 | 11.9 | 13.78 | 11.57 | 12.17 | 11.93 | 11.91
185 | 13.65 | 0.05 | 8.54 | 62.8 | 36.43 | 50.85 | N |  | MIN | 9.83 | 9.64 | 0.05 | 0.05 | 0.05 | 6.7 | 6.89 | 0.05 | ER | ER | 8.12 | 7.27 | 0.05 | 0.05 | 0.05 | 5.5 | 4.81 | 0.05 | 0.06 | 0.06 | 5.36 | 5.89 | 0.05 | 0 | 0.05 | 7 | ER | 0.05 | 0.05 | 0.05 | 5.57
186 | 12.32 | 0.05 | 8.69 | 59.16 | 36.95 | 50.92 | J |  | TOT | 13.18 | 13.53 | 0.8 | 8.54 | 8.69 | 10.36 | 10.82 | 2.38 | ER | 6.03 | 11.58 | 11.83 | 2.73 | 8.16 | 8.17 | 9.67 | 9.77 | 2.25 | 7.69 | 7.83 | 9.36 | 10.2 | 2.19 | 8.34 | 7.92 | 9.58 | 9.79 | 2.12 | 7.25 | 7.44 | 8.99
187 | 12.01 | 6.7 | 10.36 | 57.44 | 44.11 | 52.92 | E | INJECTION WELL TWO
188 | 12.68 | 6.89 | 10.82 | 58.84 | 44.46 | 53.62 | C |  | PSI
189 | 12.54 | 0.05 | 2.38 | 58.54 | 36.9 | 40.83 | T |  | MAX | 68.96 | 69.44 | 59.67 | 62.8 | 59.16 | 57.44 | 58.84 | 58.54 | 63.76 | 63.28 | 67.48 | 64.93 | 61.6 | 59.29 | 57.53 | 61.91 | 63.38 | 61.15 | 63.67 | 57.31 | 56.93 | 71.6 | 52.88 | 56.69 | 63.48 | 56.86 | 63.09 | 56.25 | 57.63 | 57.43 | 57.61
190 | 0 | ER | ER | 63.76 | ER | 38.59 | I |  | MIN | 52.63 | 51.25 | 37.08 | 36.43 | 36.95 | 44.11 | 44.46 | 36.9 | ER | ER | 47.26 | 45.13 | 36.8 | 35.94 | 36.87 | 41.16 | 40.44 | 36.8 | 36.01 | 36.63 | 41.26 | 42.11 | 36.83 | 0 | 36.56 | 44.86 | 0 | 37.01 | 35.86 | 36.61 | 42.21
191 | 13.49 | ER | 6.03 | 63.28 | ER | 29.45 | O |  | AVG | 62.31 | 62.67 | 39.22 | 50.85 | 50.92 | 52.92 | 53.62 | 40.83 | 38.59 | 29.45 | 57.1 | 56.95 | 41.5 | 48.89 | 49.31 | 51.33 | 51.19 | 40.58 | 48.11 | 48.07 | 50.29 | 52.58 | 40.19 | 48.58 | 48.96 | 50.94 | 51.96 | 40.24 | 47.08 | 47.49 | 49.56
192 | 14.6 | 8.12 | 11.58 | 67.48 | 47.26 | 57.1 | N
193 | 14.34 | 7.27 | 11.83 | 64.93 | 45.13 | 56.95
194 | 13.68 | 0.05 | 2.73 | 61.6 | 36.8 | 41.5 | W
195 | 12.33 | 0.05 | 8.16 | 57.52 | 35.94 | 48.89 | E
196 | 11.94 | 0.05 | 8.17 | 57.53 | 36.87 | 49.31 | L
197 | 13.31 | 5.5 | 9.67 | 61.91 | 41.16 | 51.33 | L
198 | 13.94 | 4.81 | 9.77 | 63.38 | 40.44 | 51.19
199 | 13.29 | 0.05 | 2.25 | 61.15 | 36.8 | 40.58 | T
200 | 13.94 | 0.06 | 7.69 | 63.67 | 36.01 | 48.11 | W
201 | 11.96 | 0.06 | 7.83 | 57.31 | 36.63 | 48.07 | O
202 | 11.56 | 5.36 | 9.36 | 56.93 | 41.26 | 50.29
203 | 16.01 | 5.89 | 10.2 | 71.6 | 42.11 | 52.58 | D
204 | 10.88 | 0.05 | 2.19 | 52.88 | 36.83 | 40.19 | A
205 | 11.78 | 0 | 8.34 | 56.69 | 0 | 48.58 | T
206 | 13.67 | 0.05 | 7.92 | 63.48 | 36.56 | 48.96 | A
207 | 11.9 | 7 | 9.58 | 56.86 | 44.86 | 50.94
208 | 13.78 | ER | 9.79 | 63.09 | 0 | 51.96
209 | 11.57 | 0.05 | 2.12 | 56.25 | 37.01 | 40.24
210 | 12.17 | 0.05 | 7.25 | 57.63 | 35.86 | 47.08
211 | 11.93 | 0.05 | 7.44 | 57.43 | 36.61 | 47.49
212 | 11.91 | 5.57 | 8.99 | 57.61 | 42.21 | 49.56
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 3 |  |  | 182 | 183 | 184 | 185 | 186 | 187 | 188 | 189 | 190 | 191 | 192 | 193 | 194 | 195 | 196 | 197 | 198 | 199 | 200 | 201 | 202 | 203 | 204 | 205 | 206 | 207 | 208 | 209 | 210 | 211 | 212
182 | 14.45 | 0.09 | 12.23 | 70.5 | 38.09 | 63.01
183 | 13.94 | 9.39 | 12.44 | 70.7 | 52.31 | 63.87 |  |  | FLOW
184 | 13.83 | 8.49 | 11.36 | 69.45 | 51.1 | 59.8 | I |  | MAX | 14.45 | 13.94 | 13.83 | 13.64 | 11.74 | 11.28 | 11.56 | 12.85 | 0 | 12.79 | 13.61 | 12.91 | 13.1 | 12.63 | 11.44 | 11.26 | 12.51 | 12.13 | 12.94 | 11.34 | 10.91 | 14.5 | 11.52 | 4.23 | 14.1 | 10.84 | 12.42 | 12.15 | 11.11 | 11.35 | 11.19
185 | 13.64 | ER | 2.69 | 68.62 | 37.94 | 43.75 | N |  | MIN | 0.09 | 9.39 | 8.49 | ER | ER | ER | 6.89 | 6.84 | ER | ER | 6.28 | 7.28 | 7.97 | ER | ER | ER | 4.76 | 5.96 | ER | ER | ER | 6.03 | 6.5 | ER | ER | ER | ER | 5.59 | ER | ER | ER
186 | 11.74 | ER | 7.95 | 60.37 | 37.41 | 51.37 | J |  | TOT | 12.23 | 12.44 | 11.36 | 2.69 | 7.95 | 8.09 | 10.07 | 10.05 | ER | 5.79 | 10.98 | 10.94 | 10.69 | 1.76 | 7.51 | 7.58 | 9.13 | 9.44 | 2.11 | 7.19 | 7.45 | 9.52 | 9.06 | 0.03 | 7.28 | 7.49 | 9 | 8.92 | 2.01 | 6.87 | 7.15
187 | 11.28 | ER | 8.09 | 58.64 | 37.23 | 51.06 | E | INJECTION WELL THREE
188 | 11.56 | 6.89 | 10.07 | 59.9 | 45.35 | 54.64 | C |  | PSI
189 | 12.85 | 6.84 | 10.05 | 65.39 | 46.14 | 54.67 | T |  | MAX | 70.5 | 70.7 | 69.45 | 68.62 | 60.37 | 58.64 | 59.9 | 65.39 | 64.99 | 64.65 | 68.87 | 66.07 | 65.42 | 64.31 | 58.72 | 58.68 | 64.54 | 62.32 | 66.13 | 58.55 | 58.12 | 73 | 59.74 | 39.57 | 69.95 | 57.21 | 64.23 | 62.71 | 59.51 | 58.68 | 58.71
190 | 0 | ER | ER | 64.99 | ER | 39.35 | I |  | MIN | 38.09 | 52.31 | 51.1 | 37.94 | 37.41 | 37.23 | 45.35 | 46.14 | ER | ER | 48.21 | 46.03 | 47.86 | 37.21 | 36.76 | 36.82 | 41.25 | 43.08 | 37.56 | 36.96 | 36.61 | 42.95 | 44.18 | 0 | 36.84 | 37.13 | 0 | 43.06 | 37.64 | 36.99 | 37.06
191 | 12.79 | ER | 5.79 | 64.65 | ER | 30.13 | O |  | AVG | 63.01 | 63.87 | 59.8 | 43.75 | 51.37 | 51.06 | 54.64 | 54.67 | 39.35 | 30.13 | 58.15 | 58.01 | 56.55 | 41.03 | 49.67 | 49.65 | 52.17 | 52.87 | 41.58 | 48.57 | 49.22 | 53.63 | 51.64 | 38.5 | 49.55 | 49.33 | 53 | 51.45 | 41.31 | 48.07 | 48.56
192 | 13.61 | 6.28 | 10.98 | 68.87 | 48.21 | 58.15 | N
193 | 12.91 | 7.28 | 10.94 | 66.07 | 46.03 | 58.01
194 | 13.1 | 7.97 | 10.69 | 65.42 | 47.86 | 56.55 | W
195 | 12.63 | ER | 1.76 | 64.31 | 37.21 | 41.03 | E
196 | 11.44 | ER | 7.51 | 58.72 | 36.76 | 49.67 | L
197 | 11.26 | ER | 7.58 | 58.68 | 36.82 | 49.65 | L
198 | 12.51 | 4.76 | 9.13 | 64.54 | 41.25 | 52.17
199 | 12.13 | 5.96 | 9.44 | 62.32 | 43.08 | 52.87 | T
200 | 12.94 | ER | 2.11 | 66.13 | 37.56 | 41.58 | H
201 | 11.34 | ER | 7.19 | 58.55 | 36.96 | 48.57 | R
202 | 10.91 | ER | 7.45 | 58.12 | 36.61 | 49.22 | E
203 | 14.5 | 6.03 | 9.52 | 73 | 42.95 | 53.63 | E
204 | 11.52 | 6.5 | 9.06 | 59.74 | 44.18 | 51.64
205 | 4.23 | ER | 0.03 | 39.57 | 0 | 38.5 | D
206 | 14.1 | ER | 7.28 | 69.95 | 36.84 | 49.55 | A
207 | 10.84 | ER | 7.49 | 57.21 | 37.13 | 49.33 | T
208 | 12.42 | ER | 9 | 64.23 | 0 | 53 | A
209 | 12.15 | 5.59 | 8.92 | 62.71 | 43.06 | 51.45
210 | 11.11 | ER | 2.01 | 59.51 | 37.64 | 41.31
211 | 11.35 | ER | 6.87 | 58.68 | 36.99 | 48.07
212 | 11.19 | ER | 7.15 | 58.71 | 37.06 | 48.56
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 4 |  |  | 182 | 183 | 184 | 185 | 186 | 187 | 188 | 189 | 190 | 191 | 192 | 193 | 194 | 195 | 196 | 197 | 198 | 199 | 200 | 201 | 202 | 203 | 204 | 205 | 206 | 207 | 208 | 209 | 210 | 211 | 212
182 | 14.23 | 0.04 | 10.53 | 69.88 | 37.77 | 59.57
183 | 14.06 | 0.04 | 10.18 | 71.3 | 37.64 | 59.47 |  |  | FLOW
184 | 13.92 | 8.62 | 11.44 | 69.97 | 51.69 | 60.37 | I |  | MAX | 14.23 | 14.06 | 13.92 | 13.71 | 13.88 | 11.74 | 11.6 | 12.94 | 0 | 6.51 | 14.21 | 13.04 | 13.27 | 13.06 | 13.17 | 11.66 | 12.65 | 12.55 | 13.25 | 12.11 | 11.28 | 14.91 | 11.55 | 11.26 | 14.89 | 11.2 | 12.51 | 12.23 | 11.62 | 9.92 | 11.6
185 | 13.71 | 7.6 | 10.9 | 69.13 | 47.62 | 57.63 | N |  | MIN | 0.04 | 0.04 | 8.62 | 7.6 | 0.05 | 0.05 | 0.05 | 6.92 | ER | ER | 0.05 | 0.05 | 8.06 | 6.56 | 0.05 | 0.05 | 0.05 | 6.13 | 6.32 | 0.05 | 0.05 | 0.05 | 6.61 | 0 | 0.05 | 0.05 | ER | 5.74 | 5.74 | 0.05 | 0.05
186 | 13.88 | 0.05 | 2.56 | 67.74 | 37.92 | 42.91 | J |  | TOT | 10.53 | 10.18 | 11.44 | 10.9 | 2.56 | 8 | 8.42 | 10.15 | ER | 0.07 | 8.75 | 9.09 | 10.91 | 10.27 | 2.38 | 7.45 | 7.61 | 9.59 | 9.57 | 2.11 | 7.39 | 8.06 | 9.18 | 9.1 | 2.37 | 7.36 | ER | 9.06 | 9.07 | 2.02 | 7.07
187 | 11.74 | 0.05 | 8 | 59.08 | 37.29 | 50.93 | E | INJECTION WELL FOUR
188 | 11.6 | 0.05 | 8.42 | 60.49 | 37.04 | 52.53 | C |  | PSI
189 | 12.94 | 6.92 | 10.15 | 65.95 | 46.82 | 55.29 | T |  | MAX | 69.88 | 71.3 | 69.97 | 69.13 | 67.74 | 59.08 | 60.49 | 65.95 | 0 | 39.66 | 69.18 | 66.62 | 65.9 | 65.44 | 64.94 | 59.32 | 65.13 | 62.89 | 66.68 | 61.04 | 58.66 | 73.4 | 60.36 | 58.62 | 72.7 | 57.85 | 64.57 | 63.31 | 60.12 | 53.74 | 59.3
190 | 0 | ER | ER | 0 | ER | ER | I |  | MIN | 37.77 | 37.64 | 51.69 | 47.62 | 37.92 | 37.29 | 37.04 | 46.82 | ER | ER | 37.41 | 37.4 | 48.55 | 46.35 | 37.82 | 36.9 | 37.19 | 43.79 | 44.53 | 37.59 | 36.57 | 36.99 | 44.77 | 0 | 37.54 | 37.1 | ER | 43.76 | 43.37 | 37.8 | 37.02
191 | 6.51 | ER | 0.07 | 39.66 | ER | ER | O |  | AVG | 59.57 | 59.47 | 60.37 | 57.63 | 42.91 | 50.93 | 52.53 | 55.29 | ER | ER | 53.98 | 55.11 | 57.12 | 54.75 | 42.27 | 49.59 | 50.35 | 53.53 | 53.05 | 41.16 | 49.29 | 51.85 | 52.28 | 51.58 | 41.86 | 49.31 | 51.34 | 52.11 | 51.79 | 41.06 | 48.58
192 | 14.21 | 0.05 | 8.75 | 69.18 | 37.41 | 53.98 | N
193 | 13.04 | 0.05 | 9.09 | 66.62 | 37.4 | 55.11
194 | 13.27 | 8.06 | 10.91 | 65.9 | 48.55 | 57.12 | W
195 | 13.06 | 6.56 | 10.27 | 64.88 | 46.35 | 54.75 | E
196 | 13.17 | 0.05 | 2.38 | 64.94 | 37.82 | 42.27 | L
197 | 11.66 | 0.05 | 7.45 | 59.32 | 36.9 | 49.59 | L
198 | 12.65 | 0.05 | 7.61 | 65.13 | 37.19 | 50.35
199 | 12.55 | 6.13 | 9.59 | 62.89 | 43.79 | 53.53 | F
200 | 13.25 | 6.32 | 9.57 | 66.68 | 44.53 | 53.05 | O
201 | 12.11 | 0.05 | 2.11 | 61.04 | 37.59 | 41.16 | U
202 | 11.28 | 0.05 | 7.39 | 58.66 | 36.57 | 49.29 | R
203 | 14.91 | 0.05 | 8.06 | 73.4 | 36.99 | 51.85
204 | 11.55 | 6.61 | 9.18 | 60.36 | 44.77 | 52.28 | D
205 | 11.26 | 0 | 9.1 | 58.62 | 0 | 51.58 | A
206 | 14.89 | 0.05 | 2.37 | 72.7 | 37.54 | 41.86 | T
207 | 11.2 | 0.05 | 7.36 | 57.85 | 37.1 | 49.31 | A
208 | 12.51 | ER | ER | 64.57 | ER | 51.34
209 | 12.23 | 5.74 | 9.06 | 63.31 | 43.76 | 52.11
210 | 11.62 | 5.74 | 9.07 | 60.12 | 43.37 | 51.79
211 | 9.92 | 0.05 | 2.02 | 53.74 | 37.8 | 41.06
212 | 11.6 | 0.05 | 7.07 | 59.3 | 37.02 | 48.58
Julian Day | Max Flow | Min Flow | Tot Flow | Max PSI | Min PSI | Avg PSI | 5 |  |  | 182 | 183 | 184 | 185 | 186 | 187 | 188 | 189 | 190 | 191 | 192 | 193 | 194 | 195 | 196 | 197 | 198 | 199 | 200 | 201 | 202 | 203 | 204 | 205 | 206 | 207 | 208 | 209 | 210 | 211 | 212
182 | 12.73 | ER | 0.83 | 64.89 | 36.7 | 39.7
183 | 13.19 | ER | 8.99 | 70.4 | 36.28 | 57.41 |  |  | FLOW
184 | 13.1 | ER | 10.65 | 68.94 | 37.59 | 59.14 | I |  | MAX | 12.73 | 13.19 | 13.1 | 12.87 | 12.91 | 11.02 | 10.93 | 12.18 | 0 | 12.34 | 10.71 | 12.28 | 12.33 | 12.17 | 12.24 | 12.17 | 11.9 | 10.94 | 12.33 | 11.28 | 10.25 | 11.08 | 10.92 | 10.57 | 14.47 | 10.99 | 11.8 | 11.53 | 10.87 | 11.01 | 9.33
185 | 12.87 | 7.15 | 10.23 | 68.2 | 46.58 | 56.53 | N |  | MIN | ER | ER | ER | 7.15 | 6.65 | ER | ER | ER | ER | ER | ER | ER | ER | 5.43 | 5.79 | ER | ER | ER | 6.07 | 5.62 | ER | ER | ER | 0 | ER | ER | ER | ER | 5.5 | 5.48 | ER
186 | 12.91 | 6.65 | 10.01 | 66.71 | 44.88 | 54.94 | J |  | TOT | 0.83 | 8.99 | 10.65 | 10.23 | 10.01 | 2.21 | 7.52 | 7.89 | ER | 5.58 | 0.6 | 8.1 | 8.25 | 9.58 | 9.46 | 2.11 | 6.79 | 7.42 | 8.98 | 8.91 | 1.88 | 6.11 | 7.12 | 8.55 | 8.62 | 2.17 | 8.59 | 7.01 | 8.54 | 8.56 | 1.89
187 | 11.02 | ER | 2.21 | 57.86 | 36.84 | 40.92 | E | INJECTION WELL FIVE
188 | 10.93 | ER | 7.52 | 59.47 | 35.74 | 50.88 | C |  | PSI
189 | 12.18 | ER | 7.89 | 64.92 | 36.71 | 51.58 | T |  | MAX | 64.89 | 70.4 | 68.94 | 68.2 | 66.71 | 57.86 | 59.47 | 64.92 | 64.6 | 64.04 | 58.38 | 65.62 | 64.97 | 63.91 | 63.9 | 62.77 | 64.19 | 59.29 | 65.75 | 60 | 55.12 | 60.62 | 59.25 | 57.4 | 71.9 | 57.74 | 63.78 | 62.32 | 59.21 | 58.11 | 51.78
190 | 0 | ER | ER | 64.6 | ER | 39.12 | I |  | MIN | 36.7 | 36.28 | 37.59 | 46.58 | 44.88 | 36.84 | 35.74 | 36.71 | ER | ER | 36.58 | 36.12 | 36.62 | 45.44 | 42.62 | 36.54 | 35.71 | 36.83 | 43.54 | 42.22 | 36.69 | 35.33 | 36.84 | 0 | 36.33 | 36.89 | 0 | 36.94 | 42.37 | 42.14 | 36.68
191 | 12.34 | ER | 5.58 | 64.04 | ER | 29.81 | O |  | AVG | 39.7 | 57.41 | 59.14 | 56.53 | 54.94 | 40.92 | 50.88 | 51.58 | 39.12 | 29.81 | 38.82 | 53.34 | 52.6 | 53.55 | 52.94 | 40.58 | 48.67 | 49.99 | 52 | 50.93 | 39.65 | 47.89 | 48.99 | 50.49 | 51.23 | 40.65 | 52.57 | 48.83 | 50.73 | 50.18 | 39.91
192 | 10.71 | ER | 0.6 | 58.38 | 36.58 | 38.82 | N
193 | 12.28 | ER | 8.1 | 65.62 | 36.12 | 53.34
194 | 12.33 | ER | 8.25 | 64.97 | 36.62 | 52.6 | W
195 | 12.17 | 5.43 | 9.58 | 63.91 | 45.44 | 53.55 | E
196 | 12.24 | 5.79 | 9.46 | 63.9 | 42.62 | 52.94 | L
197 | 12.17 | ER | 2.11 | 62.77 | 36.54 | 40.58 | L
198 | 11.9 | ER | 6.79 | 64.19 | 35.71 | 48.67
199 | 10.94 | ER | 7.42 | 59.29 | 36.83 | 49.99 | F
200 | 12.33 | 6.07 | 8.98 | 65.75 | 43.54 | 52 | I
201 | 11.28 | 5.62 | 8.91 | 60 | 42.22 | 50.93 | V
202 | 10.25 | ER | 1.88 | 55.12 | 36.69 | 39.65 | E
203 | 11.08 | ER | 6.11 | 60.62 | 35.33 | 47.89
204 | 10.92 | ER | 7.12 | 59.25 | 36.84 | 48.99 | D
205 | 10.57 | 0 | 8.55 | 57.4 | 0 | 50.49 | A
206 | 14.47 | ER | 8.62 | 71.9 | 36.33 | 51.23 | T
207 | 10.99 | ER | 2.17 | 57.74 | 36.89 | 40.65 | A
208 | 11.8 | ER | 8.59 | 63.78 | 0 | 52.57
209 | 11.53 | ER | 7.01 | 62.32 | 36.94 | 48.83
210 | 10.87 | 5.5 | 8.54 | 59.21 | 42.37 | 50.73
211 | 11.01 | 5.48 | 8.56 | 58.11 | 42.14 | 50.18
212 | 9.33 | ER | 1.89 | 51.78 | 36.68 | 39.91

## RMW PRN DATA
julian | u-avg | u-min | u-max | l-avg | l-min | l-max
182 | 24.02 | 23.95 | 24.07 | 45.13 | 45.08 | 45.19 | R |  |  | 182 | 183 | 184 | 185 | 186 | 187 | 188 | 189 | 190 | 191 | 192 | 193 | 194 | 195 | 196 | 197 | 198 | 199 | 200 | 201 | 202 | 203 | 204 | 205 | 206 | 207 | 208 | 209 | 210 | 211 | 212
183 | 24.03 | 23.95 | 24.09 | 45.15 | 45.1 | 45.2 | E
184 | 23.96 | 23.9 | 24.04 | 45.1 | 45.05 | 45.19 | G |  | LOW
185 | 22.3 | 20.52 | 23.94 | 41.84 | 39.05 | 45.09 | I |  | MIN | 23.95 | 23.95 | 23.9 | 20.52 | 20.91 | 22.58 | 22.83 | 22.97 | 23.08 | 23.07 | 23.04 | 23.02 | 23.07 | 23.08 | 23.06 | 22.98 | 22.97 | 22.98 | 22.95 | 22.98 | 22.97 | 23.01 | 23 | 23.04 | 23.04 | 23.04 | 23.01 | 22.99 | 22.92 | 22.9 | 22.92
186 | 21.97 | 20.91 | 22.59 | 42.73 | 38.97 | 44.48 | O |  | MAX | 24.07 | 24.09 | 24.04 | 23.94 | 22.59 | 22.83 | 22.98 | 23.12 | 23.19 | 23.18 | 23.15 | 23.13 | 23.15 | 23.22 | 23.2 | 23.14 | 23.14 | 23.14 | 23.11 | 23.09 | 23.1 | 23.12 | 23.12 | 23.12 | 23.15 | 23.14 | 23.15 | 23.12 | 23.05 | 23.05 | 23.05
187 | 22.71 | 22.58 | 22.83 | 44.6 | 44.48 | 44.68 | N |  | AVG | 24.02 | 24.03 | 23.96 | 22.3 | 21.97 | 22.71 | 22.88 | 23.02 | 23.15 | 23.11 | 23.08 | 23.07 | 23.12 | 23.15 | 23.13 | 23.08 | 23.06 | 23.07 | 23.05 | 23.05 | 23.04 | 23.06 | 23.05 | 23.08 | 23.11 | 23.1 | 23.1 | 23.06 | 23 | 22.98 | 22.99
188 | 22.88 | 22.83 | 22.98 | 44.76 | 44.68 | 44.82 | A | RMW
189 | 23.02 | 22.97 | 23.12 | 44.89 | 44.81 | 44.99 | L |  | UP
190 | 23.15 | 23.08 | 23.19 | 45.04 | 44.94 | 45.12 |  |  | MIN | 45.08 | 45.1 | 45.05 | 39.05 | 38.97 | 44.48 | 44.68 | 44.81 | 44.94 | 44.95 | 44.91 | 44.89 | 44.96 | 44.99 | 44.98 | 44.93 | 44.93 | 44.93 | 44.9 | 44.93 | 44.9 | 44.92 | 44.92 | 44.96 | 44.98 | 44.98 | 44.99 | 44.97 | 44.9 | 44.88 | 44.9
191 | 23.11 | 23.07 | 23.18 | 45.01 | 44.95 | 45.08 | M |  | MAX | 45.19 | 45.2 | 45.19 | 45.09 | 44.48 | 44.68 | 44.82 | 44.99 | 45.12 | 45.08 | 45.02 | 44.97 | 45.03 | 45.07 | 45.08 | 45.05 | 45.03 | 45.05 | 45.04 | 45.03 | 45.04 | 45.03 | 45.04 | 45.04 | 45.06 | 45.04 | 45.05 | 45.05 | 44.99 | 44.98 | 44.99
192 | 23.08 | 23.04 | 23.15 | 44.96 | 44.91 | 45.02 | O |  | AVG | 45.13 | 45.15 | 45.1 | 41.84 | 42.73 | 44.6 | 44.76 | 44.89 | 45.04 | 45.01 | 44.96 | 44.93 | 44.99 | 45.02 | 45.02 | 44.99 | 44.99 | 45 | 44.98 | 44.98 | 44.99 | 44.99 | 44.99 | 45 | 45.02 | 45.01 | 45.02 | 45 | 44.95 | 44.94 | 44.95
193 | 23.07 | 23.02 | 23.13 | 44.93 | 44.89 | 44.97 | N
194 | 23.12 | 23.07 | 23.15 | 44.99 | 44.96 | 45.03 | I
195 | 23.15 | 23.08 | 23.22 | 45.02 | 44.99 | 45.07 | T
196 | 23.13 | 23.06 | 23.2 | 45.02 | 44.98 | 45.08 | O
197 | 23.08 | 22.98 | 23.14 | 44.99 | 44.93 | 45.05 | R
198 | 23.06 | 22.97 | 23.14 | 44.99 | 44.93 | 45.03
199 | 23.07 | 22.98 | 23.14 | 45 | 44.93 | 45.05 | W
200 | 23.05 | 22.95 | 23.11 | 44.98 | 44.9 | 45.04 | E
201 | 23.05 | 22.98 | 23.09 | 44.98 | 44.93 | 45.03 | L
202 | 23.04 | 22.97 | 23.1 | 44.99 | 44.9 | 45.04 | L
203 | 23.06 | 23.01 | 23.12 | 44.99 | 44.92 | 45.03
204 | 23.05 | 23 | 23.12 | 44.99 | 44.92 | 45.04
205 | 23.08 | 23.04 | 23.12 | 45 | 44.96 | 45.04 | R
206 | 23.11 | 23.04 | 23.15 | 45.02 | 44.98 | 45.06 | M
207 | 23.1 | 23.04 | 23.14 | 45.01 | 44.98 | 45.04 | W
208 | 23.1 | 23.01 | 23.15 | 45.02 | 44.99 | 45.05
209 | 23.06 | 22.99 | 23.12 | 45 | 44.97 | 45.05 | O
210 | 23 | 22.92 | 23.05 | 44.95 | 44.9 | 44.99 | N
211 | 22.98 | 22.9 | 23.05 | 44.94 | 44.88 | 44.98 | E
212 | 22.99 | 22.92 | 23.05 | 44.95 | 44.9 | 44.99
182 | 44.05 | 42.54 | 47.47 | 49.38 | 49.18 | 49.52 | M |  |  | 182 | 183 | 184 | 185 | 186 | 187 | 188 | 189 | 190 | 191 | 192 | 193 | 194 | 195 | 196 | 197 | 198 | 199 | 200 | 201 | 202 | 203 | 204 | 205 | 206 | 207 | 208 | 209 | 210 | 211 | 212
183 | 44.31 | 42.4 | 47.15 | 49.39 | 49.2 | 49.52 | O
184 | 44.49 | 43.28 | 46.31 | 49.3 | 49.12 | 49.41 | N |  | LOW
185 | 43.9 | 41.28 | 45.78 | 48.37 | 47.37 | 49.26 | I |  | MIN | 42.54 | 42.4 | 43.28 | 41.28 | 40.94 | 42.1 | 43.03 | 42.06 | ER | ER | 39.41 | 38.52 | 40.73 | 42.1 | 42.52 | 42.7 | 43.64 | 39.91 | 38.91 | 40.7 | 42.02 | 42.76 | 42.42 | ER | 41.36 | 41.04 | ER | 42.81 | 43.01 | 42.13 | 42.93
186 | 42.49 | 40.94 | 44.48 | 48.63 | 47.76 | 49.29 | T |  | MAX | 47.47 | 47.15 | 46.31 | 45.78 | 44.48 | 45.61 | 46.11 | 46.44 | ER | 45.08 | 44.6 | 42.37 | 44.34 | 45.69 | 46.44 | 46.39 | 46.32 | 44.25 | 42.78 | 44.99 | 45.73 | 46.53 | 47.33 | 46.82 | 46.04 | 44.92 | 45.88 | 46 | 46.34 | 46.2 | 46.93
187 | 43.79 | 42.1 | 45.61 | 49.15 | 48.99 | 49.28 | O |  | AVG | 44.05 | 44.31 | 44.49 | 43.9 | 42.49 | 43.79 | 44.29 | 44.4 | ER | 27.66 | 42.93 | 40.41 | 42.47 | 43.73 | 44.37 | 44.37 | 44.69 | 42.89 | 40.81 | 42.6 | 43.74 | 44.33 | 44.39 | 44.33 | 43.24 | 42.77 | 42.44 | 43.98 | 44.23 | 43.54 | 44.76
188 | 44.29 | 43.03 | 46.11 | 49.18 | 49.04 | 49.33 | R | MW-1
189 | 44.4 | 42.06 | 46.44 | 49.2 | 49.11 | 49.39 |  |  | UP
190 | ER | ER | ER | ER | ER | ER | W |  | MIN | 49.18 | 49.2 | 49.12 | 47.37 | 47.76 | 48.99 | 49.04 | 49.11 | ER | ER | 40.32 | 40.68 | 49.07 | 49.12 | 49.1 | 49.01 | 48.95 | 39.85 | 40.12 | 48.84 | 48.84 | 48.88 | 48.89 | ER | 47.56 | 47.74 | ER | 48.52 | 48.7 | 48.7 | 48.71
191 | 27.66 | ER | 45.08 | 30.22 | ER | 49.32 | E |  | MAX | 49.52 | 49.52 | 49.41 | 49.26 | 49.29 | 49.28 | 49.33 | 49.39 | ER | 49.32 | 49.32 | 49.47 | 49.3 | 49.36 | 49.35 | 49.29 | 49.31 | 49.24 | 49.49 | 49.26 | 49.27 | 49.26 | 49.25 | 49.25 | 49.25 | 49.05 | 49.1 | 49.06 | 48.97 | 48.99 | 49.02
192 | 42.93 | 39.41 | 44.6 | 43.11 | 40.32 | 49.32 | L |  | AVG | 49.38 | 49.39 | 49.3 | 48.37 | 48.63 | 49.15 | 49.18 | 49.2 | ER | 30.22 | 43.11 | 46.44 | 49.19 | 49.29 | 49.23 | 49.15 | 49.14 | 42.55 | 46.23 | 49.05 | 49.08 | 49.07 | 49.02 | 48.97 | 48.23 | 48.64 | 47.27 | 48.94 | 48.92 | 48.9 | 48.89
193 | 40.41 | 38.52 | 42.37 | 46.44 | 40.68 | 49.47 | L
194 | 42.47 | 40.73 | 44.34 | 49.19 | 49.07 | 49.3
195 | 43.73 | 42.1 | 45.69 | 49.29 | 49.12 | 49.36 | O
196 | 44.37 | 42.52 | 46.44 | 49.23 | 49.1 | 49.35 | N
197 | 44.37 | 42.7 | 46.39 | 49.15 | 49.01 | 49.29 | E
198 | 44.69 | 43.64 | 46.32 | 49.14 | 48.95 | 49.31
199 | 42.89 | 39.91 | 44.25 | 42.55 | 39.85 | 49.24 | I
200 | 40.81 | 38.91 | 42.78 | 46.23 | 40.12 | 49.49 | N
201 | 42.6 | 40.7 | 44.99 | 49.05 | 48.84 | 49.26 | J
202 | 43.74 | 42.02 | 45.73 | 49.08 | 48.84 | 49.27 | E
203 | 44.33 | 42.76 | 46.53 | 49.07 | 48.88 | 49.26 | C
204 | 44.39 | 42.42 | 47.33 | 49.02 | 48.89 | 49.25 | T
205 | 44.33 | ER | 46.82 | 48.97 | ER | 49.25 | I
206 | 43.24 | 41.36 | 46.04 | 48.23 | 47.56 | 49.25 | O
207 | 42.77 | 41.04 | 44.92 | 48.64 | 47.74 | 49.05 | N
208 | 42.44 | ER | 45.88 | 47.27 | ER | 49.1
209 | 43.98 | 42.81 | 46 | 48.94 | 48.52 | 49.06 | W
210 | 44.23 | 43.01 | 46.34 | 48.92 | 48.7 | 48.97 | E
211 | 43.54 | 42.13 | 46.2 | 48.9 | 48.7 | 48.99 | L
212 | 44.76 | 42.93 | 46.93 | 48.89 | 48.71 | 49.02 | L
182 | 43.39 | 43.27 | 43.46 | 31.82 | 31.23 | 33.13 | M |  |  | 182 | 183 | 184 | 185 | 186 | 187 | 188 | 189 | 190 | 191 | 192 | 193 | 194 | 195 | 196 | 197 | 198 | 199 | 200 | 201 | 202 | 203 | 204 | 205 | 206 | 207 | 208 | 209 | 210 | 211 | 212
183 | 43.45 | 43.35 | 43.54 | 32.02 | 31.39 | 32.86 | O
184 | 43.45 | 43.34 | 43.5 | 32.1 | 31.61 | 32.63 | N |  | LOW
185 | 41.23 | 39.5 | 43.41 | 29.66 | 26.75 | 32.66 | I |  | MIN | 43.27 | 43.35 | 43.34 | 39.5 | 39.26 | 43.08 | 43.27 | 43.4 | ER | ER | 35.52 | 35.14 | 43.07 | 43.22 | 43.3 | 43.29 | 43.29 | 33.94 | 33.94 | 42.97 | 43.08 | 43.17 | 43.2 | ER | 35.29 | 35.18 | ER | 42.82 | 43.05 | 43.1 | 43.17
186 | 41.78 | 39.26 | 43.1 | 30.16 | 26.65 | 32.31 | T |  | MAX | 43.46 | 43.54 | 43.5 | 43.41 | 43.1 | 43.3 | 43.42 | 43.56 | ER | 43.55 | 43.55 | 43.07 | 43.28 | 43.41 | 43.46 | 43.45 | 43.5 | 43.48 | 43.02 | 43.22 | 43.29 | 43.34 | 43.38 | 43.42 | 43.42 | 43 | 43.16 | 43.21 | 43.22 | 43.26 | 43.33
187 | 43.23 | 43.08 | 43.3 | 32.06 | 31.45 | 32.55 | O |  | AVG | 43.39 | 43.45 | 43.45 | 41.23 | 41.78 | 43.23 | 43.37 | 43.47 | ER | 28.05 | 37.97 | 40.6 | 43.08 | 43.37 | 43.4 | 43.4 | 43.41 | 36.71 | 40.11 | 43.01 | 43.2 | 43.26 | 43.27 | 43.3 | 38.1 | 40.45 | 41.62 | 43.06 | 43.05 | 43.12 | 43.29
188 | 43.37 | 43.27 | 43.42 | 32.16 | 31.72 | 32.7 | R | MW-2
189 | 43.47 | 43.4 | 43.56 | 32.33 | 31.71 | 32.86 |  |  | UP
190 | ER | ER | ER | 24.58 | ER | 31.69 | W |  | MIN | 31.23 | 31.39 | 31.61 | 26.75 | 26.65 | 31.45 | 31.72 | 31.71 | ER | ER | 27.15 | 26.96 | 31.61 | 31.73 | 31.7 | 31.83 | 32.15 | 27.4 | 27.27 | 31.76 | 32.02 | 31.99 | 32.04 | ER | 27.28 | 27.31 | ER | 32.05 | 32.15 | 31.88 | 31.95
191 | 28.05 | ER | 43.55 | 22.38 | ER | 32.57 | E |  | MAX | 33.13 | 32.86 | 32.63 | 32.66 | 32.31 | 32.55 | 32.7 | 32.86 | 31.69 | 32.57 | 31.97 | 32.42 | 32.8 | 33.13 | 33.19 | 33.15 | 33.18 | 32.29 | 32.71 | 32.96 | 33.05 | 33.71 | 34.01 | 33.76 | 32.59 | 33.08 | 33.33 | 33.62 | 33.58 | 33.33 | 33.69
192 | 37.97 | 35.52 | 43.55 | 29.17 | 27.15 | 31.97 | L |  | AVG | 31.82 | 32.02 | 32.1 | 29.66 | 30.16 | 32.06 | 32.16 | 32.33 | 24.58 | 22.38 | 29.17 | 30.45 | 32.11 | 32.34 | 32.5 | 32.36 | 32.54 | 29.31 | 30.72 | 32.3 | 32.53 | 32.71 | 32.79 | 32.78 | 29.67 | 30.88 | 32.66 | 32.71 | 32.69 | 32.45 | 32.88
193 | 40.6 | 35.14 | 43.07 | 30.45 | 26.96 | 32.42 | L
194 | 43.08 | 43.07 | 43.28 | 32.11 | 31.61 | 32.8
195 | 43.37 | 43.22 | 43.41 | 32.34 | 31.73 | 33.13 | T
196 | 43.4 | 43.3 | 43.46 | 32.5 | 31.7 | 33.19 | W
197 | 43.4 | 43.29 | 43.45 | 32.36 | 31.83 | 33.15 | O
198 | 43.41 | 43.29 | 43.5 | 32.54 | 32.15 | 33.18
199 | 36.71 | 33.94 | 43.48 | 29.31 | 27.4 | 32.29 | I
200 | 40.11 | 33.94 | 43.02 | 30.72 | 27.27 | 32.71 | N
201 | 43.01 | 42.97 | 43.22 | 32.3 | 31.76 | 32.96 | J
202 | 43.2 | 43.08 | 43.29 | 32.53 | 32.02 | 33.05 | E
203 | 43.26 | 43.17 | 43.34 | 32.71 | 31.99 | 33.71 | C
204 | 43.27 | 43.2 | 43.38 | 32.79 | 32.04 | 34.01 | T
205 | 43.3 | ER | 43.42 | 32.78 | ER | 33.76 | I
206 | 38.1 | 35.29 | 43.42 | 29.67 | 27.28 | 32.59 | O
207 | 40.45 | 35.18 | 43 | 30.88 | 27.31 | 33.08 | N
208 | 41.62 | ER | 43.16 | 32.66 | ER | 33.33
209 | 43.06 | 42.82 | 43.21 | 32.71 | 32.05 | 33.62 | W
210 | 43.05 | 43.05 | 43.22 | 32.69 | 32.15 | 33.58 | E
211 | 43.12 | 43.1 | 43.26 | 32.45 | 31.88 | 33.33 | L
212 | 43.29 | 43.17 | 43.33 | 32.88 | 31.95 | 33.69 | L
182 | 46.03 | 46.02 | 46.2 | 33.9 | 33.76 | 34.06 | M |  |  | 182 | 183 | 184 | 185 | 186 | 187 | 188 | 189 | 190 | 191 | 192 | 193 | 194 | 195 | 196 | 197 | 198 | 199 | 200 | 201 | 202 | 203 | 204 | 205 | 206 | 207 | 208 | 209 | 210 | 211 | 212
183 | 46.17 | 46.12 | 46.29 | 33.94 | 33.83 | 34.1 | O
184 | 46.11 | 46.12 | 46.24 | 33.91 | 33.79 | 33.99 | N |  | LOW
185 | 41.1 | 37.18 | 46.17 | 24.89 | 18.14 | 33.85 | I |  | MIN | 46.02 | 46.12 | 46.12 | 37.18 | 37.18 | 45.71 | 45.93 | 46.09 | ER | ER | 36.97 | 36.95 | 45.78 | 45.96 | 46.12 | 46.12 | 46.12 | 35.78 | 35.78 | 45.77 | 45.91 | 46.01 | 46.04 | ER | 40.19 | 40.14 | ER | 45.46 | 45.88 | 45.96 | 46
186 | 42.74 | 37.18 | 45.72 | 28.2 | 18 | 33.49 | T |  | MAX | 46.2 | 46.29 | 46.24 | 46.17 | 45.72 | 45.95 | 46.09 | 46.25 | ER | 46.29 | 46.3 | 45.78 | 46 | 46.22 | 46.29 | 46.27 | 46.33 | 46.3 | 45.79 | 45.99 | 46.08 | 46.15 | 46.18 | 46.23 | 46.24 | 45.81 | 45.98 | 46.04 | 46.07 | 46.08 | 46.16
187 | 45.87 | 45.71 | 45.95 | 33.56 | 33.46 | 33.76 | O |  | AVG | 46.03 | 46.17 | 46.11 | 41.1 | 42.74 | 45.87 | 45.99 | 46.07 | ER | 29.47 | 39.73 | 42.83 | 45.91 | 46 | 46.17 | 46.17 | 46.26 | 38.77 | 42.6 | 45.89 | 45.99 | 46.01 | 46.01 | 46.03 | 42.15 | 43.8 | 44.4 | 45.96 | 46 | 46 | 46.02
188 | 45.99 | 45.93 | 46.09 | 33.77 | 33.65 | 33.9 | R | MW-3
189 | 46.07 | 46.09 | 46.25 | 33.86 | 33.77 | 33.99 |  |  | UP
190 | ER | ER | ER | ER | ER | ER | W |  | MIN | 33.76 | 33.83 | 33.79 | 18.14 | 18 | 33.46 | 33.65 | 33.77 | ER | ER | 18.17 | 17.98 | 33.41 | 33.59 | 33.64 | 33.59 | 33.56 | 18.07 | 18.04 | 33.2 | 33.35 | 33.44 | 33.44 | ER | 22.53 | 22.35 | ER | 33.46 | 33.57 | 33.63 | 33.68
191 | 29.47 | ER | 46.29 | 23.2 | ER | 34.01 | E |  | MAX | 34.06 | 34.1 | 33.99 | 33.85 | 33.49 | 33.76 | 33.9 | 33.99 | ER | 34.01 | 34.01 | 33.48 | 33.71 | 33.86 | 33.88 | 33.85 | 33.89 | 33.8 | 33.33 | 33.55 | 33.67 | 33.74 | 33.76 | 33.79 | 33.8 | 33.62 | 33.82 | 33.85 | 33.86 | 33.88 | 33.95
192 | 39.73 | 36.97 | 46.3 | 22.81 | 18.17 | 34.01 | L |  | AVG | 33.9 | 33.94 | 33.91 | 24.89 | 28.2 | 33.56 | 33.77 | 33.86 | ER | 23.2 | 22.81 | 28.44 | 33.54 | 33.71 | 33.74 | 33.71 | 33.73 | 22.46 | 28.35 | 33.34 | 33.44 | 33.54 | 33.58 | 33.59 | 26.2 | 29.78 | 32.67 | 33.7 | 33.72 | 33.78 | 33.84
193 | 42.83 | 36.95 | 45.78 | 28.44 | 17.98 | 33.48 | L
194 | 45.91 | 45.78 | 46 | 33.54 | 33.41 | 33.71
195 | 46 | 45.96 | 46.22 | 33.71 | 33.59 | 33.86 | T
196 | 46.17 | 46.12 | 46.29 | 33.74 | 33.64 | 33.88 | H
197 | 46.17 | 46.12 | 46.27 | 33.71 | 33.59 | 33.85 | R
198 | 46.26 | 46.12 | 46.33 | 33.73 | 33.56 | 33.89 | E
199 | 38.77 | 35.78 | 46.3 | 22.46 | 18.07 | 33.8 | E
200 | 42.6 | 35.78 | 45.79 | 28.35 | 18.04 | 33.33
201 | 45.89 | 45.77 | 45.99 | 33.34 | 33.2 | 33.55 | I
202 | 45.99 | 45.91 | 46.08 | 33.44 | 33.35 | 33.67 | N
203 | 46.01 | 46.01 | 46.15 | 33.54 | 33.44 | 33.74 | J
204 | 46.01 | 46.04 | 46.18 | 33.58 | 33.44 | 33.76 | E
205 | 46.03 | ER | 46.23 | 33.59 | ER | 33.79 | C
206 | 42.15 | 40.19 | 46.24 | 26.2 | 22.53 | 33.8 | T
207 | 43.8 | 40.14 | 45.81 | 29.78 | 22.35 | 33.62 | I
208 | 44.4 | ER | 45.98 | 32.67 | ER | 33.82 | O
209 | 45.96 | 45.46 | 46.04 | 33.7 | 33.46 | 33.85 | N
210 | 46 | 45.88 | 46.07 | 33.72 | 33.57 | 33.86
211 | 46 | 45.96 | 46.08 | 33.78 | 33.63 | 33.88 | W
212 | 46.02 | 46 | 46.16 | 33.84 | 33.68 | 33.95 | E
L
L

## SHIFT DATA
PERSONNEL LIST
[6 empty] | CERTIFICATION NUMBER |  | SOCIAL SECURITY NUMBER
CHIEF OPERATORS
McGEARY, J. | CO# 4545-A | [5 empty] | "A" |  | 2D | J. BAROFSKY | 5096-C
BAYLER, J. | CO# 4474-A | [5 empty] | "A" |  | 5 | S. HULL | 5613-C
[9 empty] | 4 | VACANT | X
[9 empty] | 3 | J. TINKER | 3291-C
[9 empty] | 1 | G. SLAYTON | 2606-B
[9 empty] | 2 | H. WALKER | 4700-A
OPERATOR II' S
BAROFSKY, J. | CO# 5096-C | 1 |  | BAROFSKY, J. | 1 | CO# 5096-C | "C" |  | 5 | J. BENTLEY | X
JVACANT | CO# XXXX-X | 4 |  | BENTLEY, J. | 4 | CO# 9366-C |  |  | 1D | S. CURMODE | X
THOMAS, P. | CO# 12833 B | 5 |  | CURMODE, S. | 5 | CO# 9379-A |  |  | 4 | K. HENDERSON | 5087-B
BENTLEY, J. | CO# 9366-C | 2D |  | HULL, S. | 2D | CO# 5613-C |  |  | 3D | K. JONES | 2466-C
CURMODE, S. | CO# 9379-A | 2 |  | JVACANT | 2 | CO# XXXX-X |  |  | 3 | G. KLEYNHANS | 7367-C
HULL, S. | CO# 5613-C | 3 |  | THOMAS, P. | 3 | CO# 12833 B |  |  | 2 | A. MORROW | 9164-C
[9 empty] | 1 | J. RAINFORTH | 2718-C
OPERATOR I' S
PEUGEOT, P. | CO# 12817-C | 5A |  | DESHIELDS, D | 5A | CO# XXXXX-X | 5A | DESHIELDS, D
PEUGEOT, P. | CO# 12817-C | 2 |  | FVACACNT | 2 | CO# XXXXX-X | 2 | FVACACNT
ROUSE, Y | CO# XXXXX-X | 4 |  | HENDERSON, K. | 4 | CO# 5087-B | 4 | HENDERSON, K.
FVACACNT | CO# XXXXX-X | 4A |  | KOKLAS, D. | 4A | CO# 13506-C | 4A | KOKLAS, D.
NOBERT, B. | CO# 9661-C | 3 |  | NOBERT, B. | 3 | CO# 9661-C | 3 | NOBERT, B.
SANDERS, C. | CO# 13500-B | 1 |  | PEUGEOT, P. | 1 | CO# 12817-C | 1 | PEUGEOT, P.
HENDERSON, K. | CO# 5087-B | 1D |  | ROUSE, Y | 1D | CO# XXXXX-X | 1D | ROUSE, Y
1 | #N/A | 3D |  | SANDERS, C. | 3D | CO# 13500-B | 3D | SANDERS, C.
KOKLAS, D. | CO# 13506-C | 5 |  | VERBOSH, R. | 5 | CO# 12667-C | 5 | VERBOSH, R.
|  | 4 | 1 | BERNARDI, J | 4 | CO# XXXX-X
|  | 3 | 2 | FREIDLAND, M. | 3 | CO# 13437-C
|  | 5A | 3 | FUTURE, 5A | 5A | CO# XXXX-X
|  | 1 | 4 | HENDERSON, K. | 1 | CO# 5087-B
|  | 2 | 5 | KOKLAS, D. | 2 | CO# 13506-C
|  | 5 | 6 | NOBERT, B. | 5 | CO# 9661-C
|  | 4A | 7 | PEUGEOT, P. | 4A | CO# 12817-C
|  | 1D | 8 | SANDERS, C. | 1D | CO# 13500-C
|  | 3D | 9 | VERBOSH, R. | 3D | CO# 12667-C

## COVER PAGE
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
|  | JULY |  | 2005
| OPERATOR | TITLE | CERTIFICATE # | TOTAL COST |  |  | 78166.6773
1 ST SHIFT |  |  |  | PEAK TO FLOW RATIO |  |  | 1.2827
2230-0630 | BAROFSKY, J. | OP. II | CO# 5096-C
| PEUGEOT, P. | OP. I | CO# 12817-C |  | TOTAL SUSPENDED SOLIDS
| ROUSE, Y | OP. I DEWAT | N/A |  |  |  | LBS/DAY
|  |  |  | RAW INFLUENT |  |  | 31260.1349
2 ND SHIFT |  |  |  | FINAL EFFLUENT |  |  | 4892.253
0630-1430 | McGEARY, J. | CHIEF | CO# 4545-A |  | TOTAL CBOD
| JVACANT | OP. II RELIEF | CO# XXXX-X |  |  |  | LBS/DAY
| HULL, S. | OP. II DEWAT | CO# 5613-C | RAW INFLUENT |  |  | 26126.8549
| FVACACNT | OP. I RELIEF | CO# XXXXX-X | FINAL EFFLUENT |  |  | 1084.3017
CHEMICALS
3 RD SHIFT | BAYLER, J. | CHIEF | CO# 4474-A |  |  | COST | POUNDS
1430-2230 | THOMAS, P. | OP. II | CO# 12833 B | HYDROGEN PEROXIDE |  | 4669.9805 | 31877
| NOBERT, B. | OP. I | CO# 9661-C | CHLORINE |  | 12985.9 | 44020
| SANDERS, C. | OP. I DEWAT | CO# 13500-B | POLYMER |  | 6140.4918 | 10066.38
SLUDGE REMOVED
4 TH SHIFT | [6 empty] | TONS
WEEKEND | BENTLEY, J. | OP. II | CO# 9366-C | DRY TONS |  |  | 347.0474
2230-1030 | HENDERSON, K. | OP. I | CO# 5087-B |  | ENERGY
| KOKLAS, D. | OPI | CO# 13506-C |  |  | COST | KILOWATTS
5 TH SHIFT |  |  |  | FPL CONSUMPTION |  | 54370.305 | 988551
WEEKEND | CURMODE, S. | OP. II | CO# 9379-A
1030-2230 | VERBOSH, R. | OP. I | CO# 12667-C | POPULATION EQUIVALENCE |  |  | 153687.3815
| DESHIELDS, D | OP. I | N/A
This Monthly Operation Report prepared by: |  |  | BAYLER, J. | CO# 4474-A
State DEP Plant Classification: Class "A" Level "II"
I certify that I am familiar with the information contained in this report and that to the best of my knowledge and
belief, such information is true, complete and accurate.
Facilitiy Manager's Signature: ____________________________________ CO# __________________
Division Manager's Signature: ____________________________________ CO# __________________
Please direct all inquiries reguarding this report to the City Official Mailing Address:
Director of Public Services |  |  | Phone (954) 776-5151
City of Fort Lauderdale
P.O. Drawer 14250 |  |  | Copies mailed: Date ________________ To: DEP _____
Fort Lauderdale, Florida | [5 empty] | DNRP _____
33302
PAGE 1

## PRINT PAGES
UNDERGROUND INJECTION CONTROL SECTION
[29 empty] | MONTHLY OPERATING REPORT DATA SUMMARY | [13 empty] | DEP From # 17-801.900 (1) | [11 empty] | DEP From # 17-801.900 (1) | [19 empty] | DAILY SAMPLE RESULTS - PART B
[25 empty] | FACILITY: GEORGE T. LOHMEYER WWTP | [5 empty] | REPORT DATE: |  | JULY | 2005 | [8 empty] | Form Title:Domestic Wastewater Treatment | [11 empty] | Form Title:Domestic Wastewater Treatment
[25 empty] | I.D. NUMBER: 5006M02066 |  |  |  |  | CHIEF OPERATOR: |  |  | McGEARY, J. | CO# 4545-A | [8 empty] | Plant Monthly Operating Report | [11 empty] | Plant Monthly Operating Report | [15 empty] | Permit Number: |  | FLA041378 |  |  |  |  | Three-month Average Daily Flow: | [5 empty] | 39.7528
[25 empty] | TELEPHONE NUMBER: (954) 523-1002 | [17 empty] | Effective Date: July 1, 1991 | [11 empty] | Effective Date: July 1, 1991 | [15 empty] | Monitoring Period |  | From: | 2005-07-01 | To: | 2005-07-31 |  | (TMADF):/Permitted Capacity)x100: | [5 empty] | 71.37%
[19 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [9 empty] | INJECTION WELL DATA | [13 empty] | DEP Application No. __________________ | [11 empty] | DEP Application No. __________________ | [11 empty] | Department of Natural Resource Protection
[5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [13 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [6 empty] | IW-1 | IW-2 |  | IW-3 |  | IW-4 | IW-5 | [35 empty] | Laboratory/Licensing/Enforcement |  |  |  | Flow | Flow | Flow | Flow | Flow | Flow | CBOD5 | CBOD5 | TSS | TSS | pH | pH | TDS | NH-3 | TKN | pH | cond. | temp. | TP
[5 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [13 empty] | MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING | [5 empty] | PERMIT/CERTIFICATION NUMBER: | 0054569-142-UO | 0054569-142-UO |  | 0054569-142-UO |  | 0054569-142-UO | 0054569-142-UO | [19 empty] | DOMESTIC WASTEWATER TREATMENT PLANT | [11 empty] | BROWARD COUNTY DEPARTMENT OF NATURAL RESOURCE PROTECTION | [5 empty] | 218 S. W. 1st Avenue |  |  | (MGD) | (MGD) | (MGD) | (MGD) | (MGD) | (mg/l) | (mg/l) | (mg/l) | (mg/l) | (Min) | (Max) | mg/L | mg/L | mg/L | units | umho/ | F | mg/L
[5 empty] | MONTHLY OPERATIONAL REPORT | [13 empty] | MONITORING WELL ONE |  |  |  | 1/07/04 thru 1/06/09 |  | PERMIT EXPIRATION DATE: | 2009-01-06 | 2009-01-06 |  | 2009-01-06 |  | 2009-01-06 | 2009-01-06 | [19 empty] | MONTHLY OPERATING REPORT | [11 empty] | WASTEWATER TREATMENT PLANT | [5 empty] | Fort Lauderdale, FL 33301 | [17 empty] | cm
[5 empty] | PROCESS DATA | [11 empty] | MW-1 | I.D. #: 5066A11311 |  |  | PERMIT # 0054569-142-UO |  |  |  | CASING DEPTH | 2799' | 2798' |  | 2800' |  | 2804' | 2818' | [8 empty] | DOMESTIC WASTEWATER TREATMENT PLANT |  |  |  |  | (34) | [8 empty] | MONTH: | JULY |  | YEAR: | 2005 |  |  |  |  | MONTHLY SLUDGE REPORTS | [5 empty] | Tel. No. (954) 765-4804 | Code | 50050 | 50050 | 50050 | 50050 | 50050 | 50050 | 80082 | 80082 | 00530 | 00530 | 00400 | 00400
| RUN DATE | [14 empty] | RUN DATE | [8 empty] | TOTAL DEPTH | 3513' | 3518' |  | 3977' |  | 3305' | 3462' | [8 empty] | MONTHLY OPERATING REPORT |  |  |  |  | DAY OF | FLOW | CHLORINE | CHLORINE | CBOD5 | TSS | CBOD5 | TSS | PH |  |  | EFFLUENT NUTRIENTS (MG/L) |  |  | I. | [10 empty] | Mon. Site | INF-001 | EFF-003 | EFF-004 | EFF-005 | EFF-006 | EFF-007 | INF-002 | EFF-001 | INF-002 | EFF-002 | EFF-002 | EFF-002
| 2026-07-30 | [14 empty] | 2026-07-30 |  | UPPER MONITOR ZONE |  |  |  |  | LOWER MONITOR ZONE |  | AVERAGE DAILY FLOW: | 7.9128 | 7.9063 |  | 7.7593 |  | 7.609 | 6.7717 | MGD | [7 empty] | Part II - General Information |  |  |  |  | THE |  | RESIDUAL | RESIDUAL | INFLUENT | INFLUENT | EFFLUENT | EFFLUENT | EFFLUENT | TKN | NH3-N | NITRATE | TOTAL | FECAL | Plant Name: | GEORGE T. LOHMEYER WASTEWATER TREATMENT FACILITY | [6 empty] | MONTH: | JULY |  | 1 | 49.948 | 12.93 | 13.18 | 12.23 | 10.53 | 0.83 | 69.7 | 2.08 | 48 | 15 | 6.7 | 6.7 | 975 | 6.3 | 8.2 | 6.7 | 1879 | 84 | 0.99
[17 empty] | MIN | MAX | AVG |  |  | MIN | MAX | AVG | **MAX DAILY FLOW PER MO (mg): | 12.93 | 13.53 |  | 12.44 |  | 11.44 | 10.65 | MG | [12 empty] | MONTH | (MGD) | AFTER | AFTER DE- | [8 empty] | P | COLIFORM | II. | [7 empty] | YEAR: | 2005 |  | 2 | 49.161 | 3.01 | 13.53 | 12.44 | 10.18 | 8.99 | 25.2 | 3.27 | 96 | 24 | 6.6 | 6.6 | 953 | 4.9 | 8.9 | 6.6 | 1823 | 86 | 0.78
| JULY | INFLUENT | HOURLY | INFLUENT | INFLUENT | RAS | PERCENT | WAS | RAIN | Sufates | [5 empty] | JULY | FT HEAD | FT HEAD | FT HEAD |  |  | FT HEAD | FT HEAD | FT HEAD | ** PEAK HR FLOW (MGD) ON MAX DAY: | 11.8069 | 11.7395 |  | 11.4471 |  | 11.3102 | 10.1984 | MGD |  | (1) Month: |  | JULY |  | Year: | 2005 |  | Parameter | Units | STORET | Value |  |  | CONTACT | CHLORINATION | MG/L | MG/L | MG/L | MG/L | [6 empty] | A) | Sludge Treatment Provided: |  |  |  |  | B) | Sludge Dewater Processes |  |  |  | 3 | 46.028 | 10.56 | 0.8 | 11.36 | 11.44 | 10.65 | 99 | 2.93 | 60 | 10 | 6.6 | 6.6 | 951 | 5 | 8.1 | 6.6 | 1887 | 87 | 0.65
| 2005 | FLOW | MAXIMUM | MAXIMUM | MINIMUM | FLOW | RAS | FLOW | INCHES | [6 empty] | 2005 | ABOVE | ABOVE | ABOVE |  |  | ABOVE | ABOVE | ABOVE | MAX SUSTAINED INJECTION PRESSURE: | 70.2 | 71.6 |  | 73 |  | 73.4 | 71.9 | PSIG |  | (2) Plant's DEP Identification Number: |  |  |  |  | 5006M02066 |  |  |  | Code |  | 1 | 49.948 | 0.9 |  | 69.7 | 48 | 2.08 | 15 | 6.7 | 8.2 | 6.3 | 0.44 | 0.99 | 0 |  |  | Aerobic Digestion | [5 empty] | Thickner |  |  | 4 | 43.113 | 8.84 | 8.54 | 2.69 | 10.9 | 10.23 | ER | 2.66 | 136 | 7 | 6.5 | 6.8 | 908 | 5.8 | 9.5 | 6.6 | 1947 | 88 | 0.56
|  | MGD | MGD | MGD | MGD | MGD |  | MGD | [8 empty] | NGVD | NGVD | NGVD |  |  | NGVD | NGVD | NGVD | MONTHLY AVG. INJECTION PRESSURE: | 48.1565 | 48.4606 |  | 50.1342 |  | 51.4021 | 48.2119 | PSIG |  | (3) Plant Name: |  |  |  | George T. Lohmeyer Regional Wastewater |  |  | (16) Monthly average daily flow | mgd | 050053 | 38.9393 | 2 | 49.161 | 1.2 |  | 25.2 | 96 | 3.27 | 24 | 6.6 | 8.9 | 4.9 | 0.49 | 0.78 | 0 |  |  | Anaerobic Digestion | [5 empty] | DGA___X___Filter Press |  |  | 5 | 41.832 | 10.6 | 8.69 | 7.95 | 2.56 | 10.01 | 21.4 | 3.53 | 70 | 2 | 6.6 | 6.7 | 902 | 7.9 | 12 | 6.6 | 1980 | 88 | 0.56
| 1 | 49.948 | 2.283 | 63.665 | 30.695 | 13.936 | 27.9% | 0.32 | 0.2 | 105 |  | 1 |  |  |  | 1 | 49.18 | 49.52 | 49.52 |  |  | 42.54 | 47.47 | 44.05 | *** MAX INJECTION PRESSURE PERMITTED: | 99 | 99 |  | 99 |  | 99 | 99 | PSIG |  |  |  |  | Treatment Facility |  |  |  | (17) Permitted capacity | mgd | - | 55.7 | 3 | 46.028 | 1.2 |  | 99 | 60 | 2.93 | 10 | 6.6 | 8.1 | 5 | 0.37 | 0.65 | 0 |  |  | Other | [5 empty] | Centrifuge Drying Beds, Bed #______ |  |  | 6 | 39.882 | 10.13 | 10.36 | 8.09 | 8 | 2.21 | ER | 3.03 | 120 | 17 | 6.6 | 6.7 | 989 | 8.9 | 13 | 6.7 | 2050 | 87 | 0.46
| 2 | 49.161 | 2.399 | 61.967 | 29.67 | 13.221 | 26.89% | 0 | 1.03 | 110 |  | 2 |  |  |  | 2 | 49.2 | 49.52 | 49.38 |  |  | 42.4 | 47.15 | 44.31 | ***NOTE: (INJECTION PRESSURE NOT TO EXCEED 66% TESTED PRESSURE | [9 empty] | (4) Plant Address: |  |  | 1765 S.E. 18th Street at |  |  |  | (18) Three-month average daily flow | mgd | - | 39.7528 | 4 | 43.113 | 1.2 |  | ER | 136 | 2.66 | 7 | 6.6 | 9.5 | 5.8 | 0.38 | 0.56 | 0 | [8 empty] | Heat Treatment____No Treatment |  |  | 7 | 38.595 | 2.15 | 10.82 | 10.07 | 8.42 | 7.52 | ER | 2.43 | 120 | 15 | 6.5 | 6.7 | 1098 | 8.9 | 14 | 6.7 | 2320 | 85 | 0.99
| 3 | 46.028 | 2.241 | 59.051 | 26.049 | 14.2 | 30.85% | 0 | 0 | 111.25 |  | 3 |  |  |  | 3 | 49.12 | 49.41 | 49.3 |  |  | 43.28 | 46.31 | 44.49 | TESTED CASING PRESSURE DURING MIT | 150 | 150 |  | 150 |  | 150 | 150 | PSIG |  |  |  |  | Eisenhower Boulevard |  |  |  | (19) Percent of permitted capacity | % | - | 71.37% | 5 | 41.832 | 1 |  | 21.4 | 70 | 3.53 | 2 | 6.6 | 12 | 7.9 | 0.38 | 0.56 | 9 | [7 empty] | x | Other: | Press Dewatered |  | 8 | 37.95 | 8.3 | 2.38 | 10.05 | 10.15 | 7.89 | ER | 3.5 | 90 | 16 | 6.5 | 6.7 | 1275 | 9.8 | 14 | 6.6 | 2660 | 85 | 0.88
| 4 | 43.113 | 2.093 | 57.833 | 22.972 | 14.244 | 33.04% | 0 | 0 | 103 |  | 4 |  |  |  | 4 | 47.37 | 49.26 | 48.37 |  |  | 41.28 | 45.78 | 43.9 | [10 empty] | (5) City: |  | Fort Lauderdale |  |  |  |  | (20) CBOD5 Effluent | mg/L | 080082 | 3.3388 | 6 | 39.882 | 1 |  | ER | 120 | 3.03 | 17 | 6.7 | 13 | 8.9 | 0.35 | 0.46 | 9 | [9 empty] | To Landfill |  | 9 | 43.366 | ER | ER | ER | ER | ER | 72.7 | 2.4 | 138 | 18 | 6.5 | 6.7 | 1018 | 7.8 | 13 | 6.6 | 2070 | 85 | 0.8
| 5 | 41.832 | 1.915 | 56.391 | 21.018 | 14.005 | 33.48% | 0.451 | 0 | 104.75 |  | 5 |  |  |  | 5 | 47.76 | 49.29 | 48.63 |  |  | 40.94 | 44.48 | 42.49 |  |  | MONITORING WELL DATA | [7 empty] | (6) County: |  | Broward |  |  |  |  | (21) CBOD5 Effluent | lbs/day | - | 1084.3017 | 7 | 38.595 | 1.3 |  | ER | 120 | 2.43 | 15 | 6.7 | 14 | 8.9 | 0.29 | 0.99 | 23000 | III. | Final Sludge Disposal: | [9 empty] | 10 | 45.664 | 5.93 | 6.03 | 5.79 | 0.07 | 5.58 | ER | 2 | 78 | 16 | 6.5 | 6.6 | 821 | 6.8 | 10 | 6.5 | 1761 | 85 | 0.65
| 6 | 39.882 | 1.953 | 52.546 | 17.813 | 13.981 | 35.06% | 0.549 | 0 | 123.5 |  | 6 |  |  |  | 6 | 48.99 | 49.28 | 49.15 |  |  | 42.1 | 45.61 | 43.79 |  | MW-1 | MW-2 |  | MW-3 |  | RMW-1 |  |  |  | (7) Phone Number: |  |  | (954) 523-1002 |  |  |  | (22) TSS Effluent | mg/L | 900201 | 15.0645 | 8 | 37.95 | 1.2 |  | ER | 90 | 3.5 | 16 | 6.6 | 14 | 9.8 | 0.47 | 0.88 | 0 | A) | Liquid Sludge Disposal: | [9 empty] | 11 | 44.078 | 11.34 | 11.58 | 10.98 | 8.75 | 0.6 | NR | 4.26 | 54 | 19 | 6.6 | 6.6 | 1005 | 9.3 | 15 | 6.6 | 2160 | 85 | 0.99
| 7 | 38.595 | 1.869 | 54.501 | 17.781 | 13.616 | 35.28% | 0.541 | 0 | 134.75 |  | 7 |  |  |  | 7 | 49.04 | 49.33 | 49.18 |  |  | 43.03 | 46.11 | 44.29 | PERMIT NUMBER | 0054569-142-UO | 0054569-142-UO |  | 0054569-142-UO |  | 0054569-142-UO |  |  |  | (8) Permit Number: |  |  | FLA041378 |  |  |  | (23) TSS Effluent | lbs/day | - | 4892.253 | 9 | 43.366 | 0.9 |  | 72.7 | 138 | 2.4 | 18 | 6.6 | 13 | 7.8 | 0.24 | 0.8 | 0 |  | WEEK OF | JULY | GALLONS | % SOLIDS |  |  | HAULERS |  |  | DISPOSAL SITE | 12 | 42.214 | 2.43 | 11.83 | 10.94 | 9.09 | 8.1 | 19.1 | 3.95 | 140 | 12 | 6.5 | 6.6 | 1175 | 9.6 | 11 | 6.6 | 2450 | 85 | 0.58
| 8 | 37.95 | 1.926 | 55.558 | 14.194 | 14.359 | 37.84% | 0.23 | 0.02 | 128.75 |  | 8 |  |  |  | 8 | 49.11 | 49.39 | 49.2 |  |  | 42.06 | 46.44 | 44.4 | UPPER MONITORING INTERVAL | 1288'-1320' | 1300'-1344' |  | 1300'-1349' |  | 1300'-1339' |  | Ft. bls. |  | (9) Plant Type: |  |  | Oxygen Activated Sludge |  |  |  | (24) Minimum pH |  | - | 6.5 | 10 | 45.664 | 0.8 |  | ER | 78 | 2 | 16 | 6.5 | 10 | 6.8 | 0.25 | 0.65 | TNTC | [11 empty] | 13 | 41.078 | 8.72 | 2.73 | 10.69 | 10.91 | 8.25 | NR | NR | 86 | 13 | 6.5 | 6.8 | 1579 | 9.8 | 11 | 6.6 | 3250 | 85 | 1.1
| 9 | 43.366 | 2.246 | 62.576 | 22.428 | 14.732 | 33.97% | 0 | 3 | 104.5 |  | 9 |  |  |  | 9 | ER | ER | ER |  |  | ER | ER | ER | MONTHLY MAX DAILY PRESSURE | 49.52 | 34.01 |  | 34.1 |  | 45.2 |  | FT. HEAD |  | (10) Test Site Identification Number: |  |  |  |  | 5006X10744 |  | (25) Maximum pH |  | - | 6.8 | 11 | 44.078 | 1 |  | NR | 54 | 4.26 | 19 | 6.6 | 15 | 9.3 | 0.31 | 0.99 | 0 |  | FIRST THRU SEVENTH | [9 empty] | 14 | 38.746 | 9.09 | 8.16 | 1.76 | 10.27 | 9.58 | NR | NR | 96 | 23 | 6.6 | 6.8 | 1579 | 11 | 15 | 6.6 | 3190 | 85 | 1.4
| 10 | 45.664 | 2.054 | 61.038 | 24.703 | 14.38 | 31.49% | 0.198 | 0.7 | 103.25 |  | 10 |  |  |  | 10 | ER | 49.32 | 30.22 |  |  | ER | 45.08 | 27.66 | MONTHLY MIN DAILY PRESSURE | 39.85 | 26.65 |  | 17.98 |  | 38.97 |  | FT. HEAD |  | (11) Fecal Coliform Method | [6 empty] | (26) Total N | mg/L | 000600 | 11.7814 | 12 | 42.214 | 1.2 |  | 19.1 | 140 | 3.95 | 12 | 6.6 | 11 | 9.6 | 0.31 | 0.58 | 0 | [11 empty] | 15 | 37.233 | 9.93 | 8.17 | 7.51 | 2.38 | 9.46 | 72.75 | 4.62 | 104 | 12 | 6.6 | 6.7 | 1112 | 10 | 15 | 6.6 | 2260 | 86 | 1.3
| 11 | 44.078 | 2.146 | 60.813 | 26.401 | 13.655 | 30.98% | 0.436 | 0 | 104.5 |  | 11 |  |  |  | 11 | 40.32 | 49.32 | 43.11 |  |  | 39.41 | 44.6 | 42.93 | TDS (MONTHLY AVERAGE) | 7652.25 | 7437.25 |  | 7918.25 |  | 5602 |  | mg/l |  |  | XX | Membrane Filter |  |  |  |  | (27) TKN | mg/L | 000625 | 11.4536 | 13 | 41.078 | 0.9 |  | NR | 86 | NR | 13 | 6.6 | 11 | 9.8 | 0.31 | 1.1 | 0 |  | EIGHT THRU FORTEENTH | [9 empty] | 16 | 36.901 | 9.45 | 9.67 | 7.58 | 7.45 | 2.11 | 63.1 | 2.82 | 100 | 21 | 6.5 | 6.6 | 1033 | 7 | 12 | 6.5 | 2210 | 86 | 1.2
| 12 | 42.214 | 2.088 | 57.961 | 21.627 | 13.761 | 32.6% | 0.354 | 0 | 129.75 |  | 12 |  |  |  | 12 | 40.68 | 49.47 | 46.44 |  |  | 38.52 | 42.37 | 40.41 | CHLORIDE (MONTHLY AVERAGE) | 3725 | 3687.5 |  | 3687.5 |  | 2700 |  | mg/l |  |  |  | Most Probable Number |  |  |  |  | (28) Ammonia (NH3 - N) | mg/L | 000610 | 8.9893 | 14 | 38.746 | 1 |  | NR | 96 | NR | 23 | 6.6 | 15 | 11 | 0.32 | 1.4 | 250 |  | FIFTHTEENTH THRU | [9 empty] | 17 | 35.84 | 2 | 9.77 | 9.13 | 7.61 | 6.79 | NR | NR | 86 | 5 | 6.5 | 6.6 | 1016 | 11 | 13 | 6.5 | 2150 | 86 | 1.3
| 13 | 41.078 | 1.956 | 56.295 | 19.512 | 13.492 | 32.84% | 0.427 | 0 | 162.5 |  | 13 |  |  |  | 13 | 49.07 | 49.3 | 49.19 |  |  | 40.73 | 44.34 | 42.47 | AMMONIA-N (MONTHLY AVERAGE) | 0.9 | 0.88 |  | 0.8875 |  | 0.61 |  | mg/l |  | (12) Type of Effluent Disposal or Reclaimed Water Reuse | [6 empty] | (29) Nitrate | mg/L | 071850 | 0.32786 | 15 | 37.233 | 1.1 |  | 72.75 | 104 | 4.62 | 12 | 6.6 | 15 | 10 | 0.37 | 1.3 | 0 |  | TWENTY SECOND | [9 empty] | 18 | 35.627 | 7.79 | 2.25 | 9.44 | 9.59 | 7.42 | 98.38 | 10.33 | 114 | 40 | 6.6 | 6.7 | 1087 | 9.9 | 13 | 6.6 | 2370 | 86 | 1.4
| 14 | 38.746 | 1.891 | 54.437 | 19.191 | 14.23 | 36.73% | 0.444 | 0 | 151 |  | 14 |  |  |  | 14 | 49.12 | 49.36 | 49.29 |  |  | 42.1 | 45.69 | 43.73 | TKN (MONTHLY AVERAGE) | 1.0075 | 1.125 |  | 1.4175 |  | 1 |  | mg/l |  |  |  | Deep Well Injection |  |  |  |  | (30) Total Phosphorus | mg/L | 000665 | 1.0346 | 16 | 36.901 | 1.2 |  | 63.1 | 100 | 2.82 | 21 | 6.5 | 12 | 7 | 0.35 | 1.2 | 0 |  | TWENTY THIRD THRU | [9 empty] | 19 | 36.04 | 7.83 | 7.69 | 2.11 | 9.57 | 8.98 | 126.9 | 6.63 | 136 | 27 | 6.5 | 6.7 | 1278 | 10 | 13 | 6.6 | 2620 | 86 | 1
| 15 | 37.233 | 1.799 | 53.988 | 18.5 | 15.56 | 41.79% | 0.037 | 0 | 126 |  | 15 |  |  |  | 15 | 49.1 | 49.35 | 49.23 |  |  | 42.52 | 46.44 | 44.37 | pH (MONTHLY AVERAGE) | 7.6925 | 7.9825 |  | 8.2125 |  | 8.29 |  | Std units |  | (13) Limited Wet Wheather Discharge Activated | [6 empty] | (31) Minimum Chlorine Residual | mg/L | - | 0.09 | 17 | 35.84 | 1.1 |  | NR | 86 | NR | 5 | 6.5 | 13 | 11 | 0.35 | 1.3 | 0 |  | THIRTY FIRST | [9 empty] | 20 | 36.307 | 9.27 | 7.83 | 7.19 | 2.11 | 8.91 | 73.7 | 2.66 | 118 | 18 | 6.6 | 6.8 | 1213 | 10 | 12 | 6.7 | 2570 | 86.3 | 1.4
| 16 | 36.901 | 1.791 | 56.84 | 14.354 | 13.341 | 36.15% | 0 | 0 | 121.75 |  | 16 |  |  |  | 16 | 49.01 | 49.29 | 49.15 |  |  | 42.7 | 46.39 | 44.37 | CONDUCTIVITY (MONTHLY AVERAGE) | 13005 | 11917.5 |  | 11990 |  | 95700 |  | umho/cm |  |  |  | YES |  | XX | Not Applicable |  | (32) Maximum Chlorine Residual | mg/L | - | 1.3 | 18 | 35.627 | 0.9 |  | 98.38 | 114 | 10.33 | 40 | 6.6 | 13 | 9.9 | 0.21 | 1.4 | 0 | [11 empty] | 21 | 35.846 | 9.1 | 9.36 | 7.45 | 7.39 | 1.88 | 84.1 | 2.66 | 106 | 14 | 6.5 | 6.7 | 1200 | 10 | 11 | 6.6 | 2560 | 86 | 1.5
| 17 | 35.84 | 1.773 | 52.033 | 15.283 | 13.708 | 38.25% | 0.117 | 0 | 124.25 |  | 17 |  |  |  | 17 | 48.95 | 49.31 | 49.14 |  |  | 43.64 | 46.32 | 44.69 | FECAL COLIFORM (MONTHLY AVERAGE) | 0 | 0 |  | 0 |  | 0 |  | # col/100ml |  |  |  | NO |  |  |  |  | (33) Other Effluent Parameters |  |  |  | 19 | 36.04 | 0.7 |  | 126.9 | 136 | 6.63 | 27 | 6.6 | 13 | 10 | 0.23 | 1 | 0 | B) | Solid Sludge Hauled from Plant: | [9 empty] | 22 | 35.792 | 2.42 | 10.2 | 9.52 | 8.06 | 6.11 | 97.9 | NR | 54 | 9 | 6.7 | 6.5 | 1141 | 8.2 | 11 | 6.6 | 2280 | 87 | 1.3
| 18 | 35.627 | 1.809 | 49.92 | 14.45 | 13.241 | 37.17% | 0.253 | 0 | 124.5 |  | 18 |  |  |  | 18 | 39.85 | 49.24 | 42.55 |  |  | 39.91 | 44.25 | 42.89 | TEMPERATURE (MONTHLY AVERAGE) | 76 | 74.5 |  | 72.25 |  | 72 |  | deg. F | [12 empty] | 20 | 36.307 | 1 |  | 73.7 | 118 | 2.66 | 18 | 6.7 | 12 | 10 | 0.19 | 1.4 | 0 |  | WEEK OF | JULY | TONS |  | % SOLIDS |  | HAULERS |  |  | DISPOSAL SITE | 23 | 34.863 | 7.4 | 2.19 | 9.06 | 9.18 | 7.12 | 93.5 | 3.48 | 98 | 23 | 6.5 | 6.6 | 1237 | 8.9 | 0 | 6.6 | 2500 | 87 | 1.3
| 19 | 36.04 | 1.842 | 53.219 | 13.361 | 13.139 | 36.46% | 0.326 | 0 | 125.75 |  | 19 |  |  |  | 19 | 40.12 | 49.49 | 46.23 |  |  | 38.91 | 42.78 | 40.81 | TOTAL PHOSPHOROUS (MONTHLY AVG.) | 0.0095 | 0.01 |  | 0.01 |  | 0.01 |  | mg/l |  | (14) Cumulative Days of Wet Wheather Discharge | [10 empty] | 21 | 35.846 | 1 |  | 84.1 | 106 | 2.66 | 14 | 6.6 | 11 | 10 | 0.3 | 1.5 | 0 | [10 empty] | Central Sanitary Landfill | 24 | 34.458 | 9.07 | 8.34 | 0.03 | 9.1 | 8.55 | 89.2 | 2.4 | 64 | 8 | 6.6 | 6.7 | 1209 | 8.7 | 11 | 6.6 | 2580 | 87 | 1.2
| 20 | 36.307 | 1.76 | 53.411 | 13.489 | 13.922 | 38.35% | 0.38 | 0 | 144.25 |  | 20 |  |  |  | 20 | 48.84 | 49.26 | 49.05 |  |  | 40.7 | 44.99 | 42.6 | SULFATE (MONTHLY AVERAGE) | 937.25 | 881.5 |  | 926 |  | 848 |  | mg/l |  |  |  | N/A | [8 empty] | 22 | 35.792 | 0.9 |  | 97.9 | 54 | NR | 9 | 6.6 | 11 | 8.2 | 0.37 | 1.3 | 0 |  | FIRST THRU SEVENTH |  | 352 |  | 17.7667 |  | SYNAGRO |  |  | Pompano Beach, FL | 25 | 36.143 | 9.37 | 7.92 | 7.28 | 2.37 | 8.62 | 94.5 | 2.66 | 112 | 20 | 6.5 | 6.6 | 1244 | 15 | 12 | 6.6 | 2580 | 87 | 0.88
| 21 | 35.846 | 1.722 | 51.232 | 13.777 | 14.094 | 39.32% | 0.436 | 0.15 | 139.5 |  | 21 |  |  |  | 21 | 48.84 | 49.27 | 49.08 |  |  | 42.02 | 45.73 | 43.74 | C.O.D. (MONTHLY AVERAGE) | #DIV/0! | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | mg/l |  | (15) Plant Staffing: | [10 empty] | 23 | 34.863 | 1 |  | 93.5 | 98 | 3.48 | 23 | 6.6 | 0 | 8.9 | 0.34 | 1.3 | 0 | [10 empty] | Central Sanitary Landfill | 26 | 36.655 | 9.38 | 9.58 | 7.49 | 7.36 | 2.17 | 84.8 | 2.51 | 102 | 8 | 6.5 | 6.6 | 1211 | NR | NR | 6.6 | 2530 | 87 | NR
| 22 | 35.792 | 1.815 | 50.591 | 16.309 | 15.227 | 42.54% | 0.182 | 0 | 128 |  | 22 |  |  |  | 22 | 48.88 | 49.26 | 49.07 |  |  | 42.76 | 46.53 | 44.33 | IRON (MONTHLY AVERAGE) | #DIV/0! | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | mg/l | [12 empty] | 24 | 34.458 | 1 |  | 89.2 | 64 | 2.4 | 8 | 6.6 | 11 | 8.7 | 0.26 | 1.2 | 0 |  | EIGHT THRU FORTEENTH |  | 440 |  | 19.02 |  | SYNAGRO |  |  | Pompano Beach, FL | 27 | 35.382 | ER | 9.79 | 9 | ER | 8.59 | 85 | NR | 80 | 3 | 6.6 | 6.6 | 1112 | NR | NR | 6.6 | 2360 | 87 | NR
| 23 | 34.863 | 1.77 | 50.623 | 17.237 | 14.595 | 41.86% | 0 | 0 | 140.25 |  | 23 |  |  |  | 23 | 48.89 | 49.25 | 49.02 |  |  | 42.42 | 47.33 | 44.39 | SULFIDE (MONTHLY AVERAGE) | #DIV/0! | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | mg/l |  |  | Day Shift Operator: |  |  | Class | "A" | Cert. No. | CO# 4545-A |  |  |  | 25 | 36.143 | 1.2 |  | 94.5 | 112 | 2.66 | 20 | 6.6 | 12 | 15 | 0.32 | 0.88 | 0 |  | FIFTHTEENTH THRU | [8 empty] | Central Sanitary Landfill | 28 | 34.551 | 7.34 | 2.12 | 8.92 | 9.06 | 7.01 | 99 | 3 | 94 | 11 | 6.5 | 6.6 | 1001 | NR | NR | 6.6 | 2250 | 87 | NR
| 24 | 34.458 | 1.681 | 50.816 | 15.508 | 14.873 | 43.16% | 0.167 | 0 | 135.25 |  | 24 |  |  |  | 24 | ER | 49.25 | 48.97 |  |  | ER | 46.82 | 44.33 | LOWER MONITORING INTERVAL | 1449'-1557' | 1970'-2025' |  | 1970'-2027' |  | 1500'-1600' |  | Ft. bls | [12 empty] | 26 | 36.655 | 1.1 |  | 84.8 | 102 | 2.51 | 8 | 6.6 | NR | NR | NR | NR | 0 |  | TWENTY SECOND |  | 427 |  | 19.02 |  | SYNAGRO |  |  | Pompano Beach, FL | 29 | 34.272 | 7.41 | 7.25 | 2.01 | 9.07 | 8.54 | 89 | 2 | 88 | 13 | 6.5 | 6.7 | 1183 | 12 | 12 | 6.6 | 2280 | 87 | 1.1
| 25 | 36.143 | 1.915 | 55.654 | 14.835 | 14.969 | 41.42% | 0.385 | 0.28 | 130.25 |  | 25 |  |  |  | 25 | 47.56 | 49.25 | 48.23 |  |  | 41.36 | 46.04 | 43.24 | MONTHLY MAX DAILY PRESSURE | 47.47 | 43.56 |  | 46.33 |  | 24.09 |  | FT. HEAD |  |  | Evening Shift Operator: |  |  | Class | "A" | Cert. No. | CO# 4474-A |  |  |  | 27 | 35.382 | 1 |  | 85 | 80 | NR | 3 | 6.6 | NR | NR | NR | NR | 0 |  | TWENTY THIRD THRU | [8 empty] | Central Sanitary Landfill | 30 | 34.708 | 8.88 | 7.44 | 6.87 | 2.02 | 8.56 | 114 | 3 | 102 | 10 | 6.5 | 6.6 | 1094 | 9.5 | 11 | 6.5 | 2290 | 85 | 1.5
| 26 | 36.655 | 1.693 | 49.952 | 17.397 | 13.802 | 37.65% | 0.406 | 0 | 134 |  | 26 |  |  |  | 26 | 47.74 | 49.05 | 48.64 |  |  | 41.04 | 44.92 | 42.77 | MONTHLY MIN DAILY PRESSURE | 38.52 | 33.94 |  | 35.78 |  | 20.52 |  | FT. HEAD | [12 empty] | 28 | 34.551 | 1.2 |  | 99 | 94 | 3 | 11 | 6.6 | NR | NR | NR | NR | 0 |  | THIRTY FIRST |  | 440 |  | 17.7683 |  | SYNAGRO |  |  | Pompano Beach, FL | 31 | 34.844 | 8.8 | 8.99 | 7.15 | 7.07 | 1.89 | 97 | 2 | 94 | 18 | 6.5 | 6.8 | 1030 | 9.7 | 12 | 6.7 | 2170 | 87 | 1.2
| 27 | 35.382 | 1.671 | 51.649 | 15.027 | 14.83 | 41.91% | 0.371 | 0 | 124.5 |  | 27 |  |  |  | 27 | ER | 49.1 | 47.27 |  |  | ER | 45.88 | 42.44 | TDS (MONTHLY AVERAGE) | 9817.75 | 32887.5 |  | 30451.25 |  | 53859 |  | mg/l |  |  | Night Shift Operator: |  |  | Class | "C" | Cert. No. | CO# 5096-C |  |  |  | 29 | 34.272 | 0.09 |  | 89 | 88 | 2 | 13 | 6.6 | 12 | 12 | 0.35 | 1.1 | 0 | C) | Monthly quantities of solid sludge stockpiled at plant.Solid Sludge Hauled from Plant: | [9 empty] | TOT | 1207.117 | 229.47 | 237.19 | 232.78 | 220.66 | 203.15 | 1769.93 | 86.81 | 2984 | 467 | 203 | 206.7 | 34629 | 251.7 | 320.7 | 204.7 | 71987 | 2670.3 | 28.97
| 28 | 34.551 | 1.694 | 50.11 | 17.845 | 15.253 | 44.15% | 0.423 | 0 | 122.75 |  | 28 |  |  |  | 28 | 48.52 | 49.06 | 48.94 |  |  | 42.81 | 46 | 43.98 | CHLORIDE (MONTHLY AVERAGE) | 4975 | 17750 |  | 16250 |  | 16000 |  | mg/l | [12 empty] | 30 | 34.708 | 0.5 |  | 114 | 102 | 3 | 10 | 6.5 | 11 | 9.5 | 0.3 | 1.5 | TNTC |  | 1) | Additions |  |  | Cubic Yards | [5 empty] | AVG | 38.9393 | 7.9128 | 7.9063 | 7.7593 | 7.609 | 6.7717 | 80.4514 | 3.3388 | 96.2581 | 15.0645 | 6.5484 | 6.6677 | 1117.0645 | 8.9893 | 11.4536 | 6.6032 | 2322.1613 | 86.1387 | 1.0346
| 29 | 34.272 | 1.667 | 49.247 | 14.771 | 15.724 | 45.88% | 0.135 | 0 | 119.75 |  | 29 |  |  |  | 29 | 48.7 | 48.97 | 48.92 |  |  | 43.01 | 46.34 | 44.23 | AMMONIA-N (MONTHLY AVERAGE) | 8.225 | 1.35 |  | 2.35 |  | 0.28 |  | mg/l |  |  | Lead Operator:_________________________________ | [9 empty] | 31 | 34.844 | 1.1 |  | 97 | 94 | 2 | 18 | 6.7 | 12 | 9.7 | 0.33 | 1.2 | 0 | [5 empty] | Tons | [5 empty] | MAX | 49.948 | 12.93 | 13.53 | 12.44 | 11.44 | 10.65 | 126.9 | 10.33 | 140 | 40 | 6.7 | 6.8 | 1579 | 15 | 15 | 6.7 | 3250 | 88 | 1.5
| 30 | 34.708 | 1.849 | 50.784 | 16.495 | 14.005 | 40.35% | 0.212 | 0.77 | 122.25 |  | 30 |  |  |  | 30 | 48.7 | 48.99 | 48.9 |  |  | 42.13 | 46.2 | 43.54 | TKN (MONTHLY AVERAGE) | 9.85 | 1.725 |  | 2 |  | 0.24 |  | mg/l | [5 empty] | Signature |  | Cert. No. |  |  |  |  | Lead Operator : This is to certify that I am familar with the information contained on this report and that to the best of | [14 empty] | 2) | Removals |  |  | Cubic Yards | [5 empty] | MIN | 34.272 | 2 | 0.8 | 0.03 | 0.07 | 0.6 | 19.1 | 2 | 48 | 2 | 6.5 | 6.5 | 821 | 4.9 | 0 | 6.5 | 1761 | 84 | 0.46
| 31 | 34.844 | 1.658 | 50.143 | 14.418 | 13.838 | 39.71% | 0.158 | 0 | 112.75 |  | 31 |  |  |  | 31 | 48.71 | 49.02 | 48.89 |  |  | 42.93 | 46.93 | 44.76 | pH (MONTHLY AVERAGE) | 7.4225 | 7.5 |  | 7.5025 |  | 7.59 |  | Std units | [12 empty] | my knowledge and belief, this information is true, complete and accuate. | [16 empty] | X |  | Tons | [6 empty] | item #1 | 11.8069 | 11.7395 | 11.4471 | 11.3102 | 10.1984 | MAX HOURLY FLOW (MG) = |  |  |  | 2.399 | ON THE | 2 | DAY OF THIS MONTH
| TOTAL | 1207.117 | 58.969 | 1694.844 | 577.11 | 439.933 |  | 7.938 | 6.15 | 3852.25 | [5 empty] | TOTAL | 1281.37 | 1478.18 | 1432.26 |  |  | 1127.25 | 1371.32 | 1290.4 | CONDUCTIVITY (MONTHLY AVERAGE) | 14697.5 | 46375 |  | 42600 |  | 40800 |  | umho/cm | [33 empty] | Signature |  |  |  |  | item #2 | 48.1565 | 48.4606 | 50.1342 | 51.4021 | 48.2119
| AVERAGE | 38.9393 | 1.9022 | 54.6724 | 18.6165 | 14.1914 | 36.44% | 0.31752 | 0.19839 | 124.2661 | [5 empty] | AVERAGE | 47.4581 | 49.2727 | 47.742 |  |  | 41.75 | 45.7107 | 43.0133 | FECAL COLIFORM (MONTHLY AVERAGE) | 0 | 0 |  | 0 |  | 0 |  | # col/100ml | [12 empty] | Signed: ____________________________ Date: ___________________ | [20 empty] | Title |  |  |  |  | item #3 | 35.24 | 35.79 | 36.59 | 36.81 | 36.56
[16 empty] | MAXIMUM | 49.2 | 49.52 | 49.52 |  |  | 43.64 | 47.47 | 44.76 | TEMPERATURE (MONTHLY AVERAGE) | 76.75 | 74.5 |  | 72 |  | 72 |  | deg. F | [33 empty] | Date |  |  |  | item #1 | =monthly maximum of the daily flows (MG), with peakhour flow (MGD) on the day of the month with maximum flow = | [14 empty] | 2.399 | MG/hour multiplied by
[16 empty] | MINIMUM | 39.85 | 48.97 | 30.22 |  |  | 38.52 | 42.37 | 27.66 | TOTAL PHOSPHOROUS (MONTHLY AVG.) | 0.0095 | 0.01 |  | 0.0105 |  | 0.01 |  | mg/l | [12 empty] | Name: Michael A. Just | [14 empty] | * Sludge Reports should be submitted along with the monthly operating reports to Broward County Department | [10 empty] | the % of average % of TOTAL RAW FLOW to each Injection well.
[25 empty] | SULFATE (MONTHLY AVERAGE) | 837.75 | 3047.5 |  | 2800 |  | 2090 |  | mg/l | [27 empty] | of Natural Resource Protection, 218 S. W. 1st Avenue, Fort Lauderdale, Florida 33301 | [9 empty] | item #2 | =monthly average injection well pressure at injection well (psig)
[25 empty] | C.O.D. (MONTHLY AVERAGE) | #DIV/0! | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | mg/l | [12 empty] | Company Name: City of Fort Lauderdale Telephone No. (954) 523-1002 | [24 empty] | item #3 | =monthly wellhead pressure with no flow (shut-in pressure,psig)
[25 empty] | IRON (MONTHLY AVERAGE) | #DIV/0! | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | mg/l | [37 empty] | PLANT STAFFING
[5 empty] | PAGE 2 | [19 empty] | SULFIDE (MONTHLY AVERAGE) | #DIV/0! | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | mg/l | [37 empty] | Day Shift Operator |  |  | Class: | "A" | Certificate No. | CO# 4545-A | Name: |  | McGEARY, J.
[71 empty] | Evening Shift Operator |  |  | Class: | "A" | Certificate No. | CO# 4474-A | Name: |  | BAYLER, J.
[20 empty] | PAGE 20 | [50 empty] | Night Shift Operator |  |  | Class: | "C" | Certificate No. | CO# 5096-C | Name: |  | BAROFSKY, J.
[71 empty] | Lead Operator |  |  | Class: | "A" | Certificate No. | 2769 | Name: |  | JUST, M.
[71 empty] | Type of Effluent Disposal or Reclaimed Water Reuse: |  |  |  |  | DEEPWELL INJECTION
[71 empty] | Permited Wet Weather Discharge Activated: |  |  |  | YES: |  | NO: |  |  | Not Applicable |  | X
[28 empty] | Page 28 | [42 empty] | If Yes, cumulative days of wet weather:
Attach additional sheets if necessary to list all certified operators. See page 1 "COVER PAGE" of supplental attachements.
DEP form 62-620.910(10), effective November 29, 1994
[19 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [47 empty] | Department of Natural Resource Protection
[5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [13 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [47 empty] | Division of Pollution Prevention and Remediation Programs
[5 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [13 empty] | MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING | [50 empty] | 218 S. W. 1st Avenue
[5 empty] | MONTHLY OPERATIONAL REPORT | [13 empty] | MONITORING WELL TWO |  |  |  | 1/07/04 thru 1/06/09 | [39 empty] | SLUDGE HAULERS MONTHLY REPORT | [6 empty] | Fort Lauderdale, FL 33301
[5 empty] | INFLUENT DATA | [11 empty] | MW-2 | I.D. #: 5066A11308 & 09 |  |  | PERMIT # 0054569-142-UO | [41 empty] | BROWARD COUNTY CODE SECTION 27-356 (d)(4)(1) | [5 empty] | Tel. No. (954) 523-1002
| RUN DATE | [14 empty] | RUN DATE | [52 empty] | *FAX (954) 519-1245
| 2026-07-30 | [14 empty] | 2026-07-30 |  | UPPER MONITOR ZONE |  |  |  |  | LOWER MONITOR ZONE
[17 empty] | MIN | MAX | AVG |  |  | MIN | MAX | AVG | [35 empty] | Plant Name: | GEORGE T. LOHMEYER WASTEWATER TREATMENT FACILITY
| JULY | RAW | RAW TSS | RAW SS | RAW | RAW | RAW | RAW | RAW | RAW | [5 empty] | JULY | FT HEAD | FT HEAD | FT HEAD |  |  | FT HEAD | FT HEAD | FT HEAD | [35 empty] | Address: | 1765 S.E. 18th Street at Eisenhower Boulevard | [6 empty] | MONTH: | JULY
| 2005 | CBOD | TOTAL | FIXED | COD | pH | CL_ | ALK. | H2S | TEMP.(F) | [5 empty] | 2005 | ABOVE | ABOVE | ABOVE |  |  | ABOVE | ABOVE | ABOVE | [35 empty] | Phone: | (954) 523-1002 * FAX (954) 468-1577 | [6 empty] | YEAR: | 2005
[17 empty] | NGVD | NGVD | NGVD |  |  | NGVD | NGVD | NGVD
| 1 | 69.7 | 48 | 0 | 101 | 7 | 420 | 191 | 3 | 81 | [5 empty] | 1 | 31.23 | 33.13 | 31.82 |  |  | 43.27 | 43.46 | 43.39 | [35 empty] | a) | WEEK OF | JULY |  | Type of Sludge |  |  | Disopsal Site |  |  | Cubic Yards
| 2 | 25.2 | 96 | 28 | 130 | 7 | 400 | 202 | 3 | 81 | [5 empty] | 2 | 31.39 | 32.86 | 32.02 |  |  | 43.35 | 43.54 | 43.45
| 3 | 99 | 60 | 0 | 170 | 7 | 410 | 195 | 2 | 82 | [5 empty] | 3 | 31.61 | 32.63 | 32.1 |  |  | 43.34 | 43.5 | 43.45 | [36 empty] | FIRST THRU SEVENTH |  |  | GRIT |  |  | Central Landfill |  |  | 10
| 4 | ER | 136 | 10 | 144 | 7 | 410 | 194 | 3 | 85 | [5 empty] | 4 | 26.75 | 32.66 | 29.66 |  |  | 39.5 | 43.41 | 41.23
| 5 | 21.4 | 70 | 0 | 157 | 7 | 410 | 210 | 3 | 85 | [5 empty] | 5 | 26.65 | 32.31 | 30.16 |  |  | 39.26 | 43.1 | 41.78 | [36 empty] | EIGHT THRU FORTEENTH |  |  | GRIT |  |  | Central Landfill |  |  | 10
| 6 | ER | 120 | 18 | 509 | 7 | 490 | 204 | 4 | 83 | [5 empty] | 6 | 31.45 | 32.55 | 32.06 |  |  | 43.08 | 43.3 | 43.23 | [36 empty] | FIFTHTEENTH THRU
| 7 | ER | 120 | 12 | 208 | 7 | 600 | 206 | 4 | 82 | [5 empty] | 7 | 31.72 | 32.7 | 32.16 |  |  | 43.27 | 43.42 | 43.37 | [36 empty] | TWENTY SECOND |  |  | GRIT |  |  | Central Landfill |  |  | 10
| 8 | ER | 90 | 22 | 99 | 7 | 600 | 212 | 4 | 83 | [5 empty] | 8 | 31.71 | 32.86 | 32.33 |  |  | 43.4 | 43.56 | 43.47 | [36 empty] | TWENTY THIRD THRU
| 9 | 72.7 | 138 | 14 | 195 | 7 | 420 | 208 | 4 | 83 | [5 empty] | 9 | ER | 31.69 | 24.58 |  |  | ER | ER | ER | [36 empty] | THIRTY FIRST |  |  | GRIT |  |  | Central Landfill |  |  | 20
| 10 | ER | 78 | 18 | 168 | 7 | 370 | 202 | 4 | 83 | [5 empty] | 10 | ER | 32.57 | 22.38 |  |  | ER | 43.55 | 28.05
| 11 | NR | 54 | 0 | 136 | 7 | 500 | 208 | 3 | 83 | [5 empty] | 11 | 27.15 | 31.97 | 29.17 |  |  | 35.52 | 43.55 | 37.97 | [35 empty] | b) | WEEK OF | JULY |  | Type of Sludge |  |  | Disopsal Site |  |  | Cubic Yards
| 12 | 19.1 | 140 | 24 | 238 | 7 | 680 | 194 | 3 | 82 | [5 empty] | 12 | 26.96 | 32.42 | 30.45 |  |  | 35.14 | 43.07 | 40.6
| 13 | NR | 86 | 22 | 129 | 7 | 890 | 210 | 4 | 82 | [5 empty] | 13 | 31.61 | 32.8 | 32.11 |  |  | 43.07 | 43.28 | 43.08 | [36 empty] | FIRST THRU SEVENTH |  |  | RAGS |  |  | Central Landfill |  |  | 10
| 14 | NR | 96 | 8 | 215 | 7 | 750 | 200 | 4 | 82 | [5 empty] | 14 | 31.73 | 33.13 | 32.34 |  |  | 43.22 | 43.41 | 43.37
| 15 | 72.75 | 104 | 12 | 172 | 7 | 540 | 202 | 3 | 82 | [5 empty] | 15 | 31.7 | 33.19 | 32.5 |  |  | 43.3 | 43.46 | 43.4 | [36 empty] | EIGHT THRU FORTEENTH |  |  | RAGS |  |  | Central Landfill |  |  | 0
| 16 | 63.1 | 100 | 10 | 203 | 7 | 530 | 194 | 3 | 83 | [5 empty] | 16 | 31.83 | 33.15 | 32.36 |  |  | 43.29 | 43.45 | 43.4 | [36 empty] | FIFTHTEENTH THRU
| 17 | NR | 86 | 10 | 219 | 7.1 | 530 | 196 | 3 | 83 | [5 empty] | 17 | 32.15 | 33.18 | 32.54 |  |  | 43.29 | 43.5 | 43.41 | [36 empty] | TWENTY SECOND |  |  | RAGS |  |  | Central Landfill |  |  | 0
| 18 | 98.38 | 114 | 24 | 218 | 7 | 590 | 192 | 4 | 83 | [5 empty] | 18 | 27.4 | 32.29 | 29.31 |  |  | 33.94 | 43.48 | 36.71 | [36 empty] | TWENTY THIRD THRU
| 19 | 126.9 | 136 | 16 | 213 | 7 | 530 | 210 | 3 | 83 | [5 empty] | 19 | 27.27 | 32.71 | 30.72 |  |  | 33.94 | 43.02 | 40.11 | [36 empty] | THIRTY FIRST |  |  | RAGS |  |  | Central Landfill |  |  | 0
| 20 | 73.7 | 118 | 30 | 130 | 7 | 700 | 210 | 4 | 83 | [5 empty] | 20 | 31.76 | 32.96 | 32.3 |  |  | 42.97 | 43.22 | 43.01 | [36 empty] | BCSR = Broward County Septage Receiving
| 21 | 84.1 | 106 | 0 | 155 | 7 | 580 | 202 | 4 | 83 | [5 empty] | 21 | 32.02 | 33.05 | 32.53 |  |  | 43.08 | 43.29 | 43.2 | [35 empty] | c) | WEEK OF | JULY |  | Type of Sludge |  |  | Disopsal Site |  |  | Gallons
| 22 | 97.9 | 54 | 8 | 124 | 7.1 | 590 | 205 | 4 | 83 | [5 empty] | 22 | 31.99 | 33.71 | 32.71 |  |  | 43.17 | 43.34 | 43.26
| 23 | 93.5 | 98 | 18 | 152 | 7.1 | 560 | 200 | 4 | 84 | [5 empty] | 23 | 32.04 | 34.01 | 32.79 |  |  | 43.2 | 43.38 | 43.27 | [36 empty] | FIRST THRU SEVENTH |  |  | VAC/Plastic & Rags |  |  | BCSR |  |  | 0
| 24 | 89.2 | 64 | 0 | 163 | 6.6 | 590 | 216 | 4 | 84 | [5 empty] | 24 | ER | 33.76 | 32.78 |  |  | ER | 43.42 | 43.3
| 25 | 94.5 | 112 | 20 | 215 | 7 | 600 | 206 | 4 | 84 | [5 empty] | 25 | 27.28 | 32.59 | 29.67 |  |  | 35.29 | 43.42 | 38.1 | [36 empty] | EIGHT THRU FORTEENTH |  |  | VAC/Plastic & Rags |  |  | BCSR |  |  | 0
| 26 | 84.8 | 102 | 11 | 122 | 7 | 570 | 202 | 4 | 83 | [5 empty] | 26 | 27.31 | 33.08 | 30.88 |  |  | 35.18 | 43 | 40.45 | [36 empty] | FIFTHTEENTH THRU
| 27 | 85 | 80 | 2 | 142 | 7 | 540 | 20 | 4 | 84 | [5 empty] | 27 | ER | 33.33 | 32.66 |  |  | ER | 43.16 | 41.62 | [36 empty] | TWENTY SECOND |  |  | VAC/Plastic & Rags |  |  | BSCR |  |  | 0
| 28 | 99 | 94 | 0 | 103 | 7 | 550 | 206 | 4 | 84 | [5 empty] | 28 | 32.05 | 33.62 | 32.71 |  |  | 42.82 | 43.21 | 43.06 | [36 empty] | TWENTY THIRD THRU
| 29 | 89 | 88 | 6 | 133 | 7 | 540 | 208 | 4 | 85 | [5 empty] | 29 | 32.15 | 33.58 | 32.69 |  |  | 43.05 | 43.22 | 43.05 | [36 empty] | THIRTY FIRST |  |  | VAC/Plastic & Rags |  |  | BSCR |  |  | 0
| 30 | 114 | 102 | 4 | 140 | 7 | 510 | 206 | 4 | 85 | [5 empty] | 30 | 31.88 | 33.33 | 32.45 |  |  | 43.1 | 43.26 | 43.12 | [35 empty] | TOTALS
| 31 | 97 | 94 | 4 | 158 | 7.1 | 490 | 202 | 4 | 84 | [5 empty] | 31 | 31.95 | 33.69 | 32.88 |  |  | 43.17 | 43.33 | 43.29 | [36 empty] | a) | 50 | cu.yds |  | GRIT |  | Signature
| TOTAL | 1769.93 | 2984 | 351 | 5361 | 217 | 16890 | 6113 | 112 | 2577 | [5 empty] | TOTAL | 820.74 | 1021.51 | 967.82 |  |  | 1108.21 | 1300.31 | 1252.2 | [36 empty] | b) | 10 | cu.yds |  | RAGS |  | Title
| AVERAGE | 80.4514 | 96.2581 | 14.625 | 172.9355 | 7 | 544.8387 | 197.1935 | 3.6129 | 83.129 | [5 empty] | AVERAGE | 30.3978 | 32.9519 | 31.22 |  |  | 41.0448 | 43.3437 | 41.74 | [36 empty] | c) | 0 | gal. |  | VAC/Plastic & Rags |  | Date
[16 empty] | MAXIMUM | 32.15 | 34.01 | 32.88 |  |  | 43.4 | 43.56 | 43.47
[16 empty] | MINIMUM | 26.65 | 31.69 | 22.38 |  |  | 33.94 | 43 | 28.05 | [36 empty] | * Sludge Reports should be submitted along with the monthly operating reports to Broward County Department
of Natural Resource Protection, 218 S. W. 1st Avenue, Fort Lauderdale, Florida 33301
PAGE 3
PAGE 21
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
[5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [13 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
[5 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [13 empty] | MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
[5 empty] | MONTHLY OPERATIONAL REPORT | [13 empty] | MONITORING WELL THREE |  |  |  | 1/07/04 thru 1/06/09
[5 empty] | EFFLUENT DATA PART 1 | [11 empty] | MW-3 | I.D. #: 5066A11310 |  |  | PERMIT # 0054569-142-UO
RUN DATE
[16 empty] | 2026-07-30 |  | UPPER MONITOR ZONE |  |  |  |  | LOWER MONITOR ZONE
| RUN DATE | [15 empty] | MIN | MAX | AVG |  |  | MIN | MAX | AVG
| 2026-07-30 | [14 empty] | JULY | FT HEAD | FT HEAD | FT HEAD |  |  | FT HEAD | FT HEAD | FT HEAD
[14 empty] | BOD | TSS | 2005 | ABOVE | ABOVE | ABOVE |  |  | ABOVE | ABOVE | ABOVE
| JULY | EFFLUENT | EFFL. TSS | EFFL. SS | EFFLUENT | EFFL. | EFFL. | EFFL. | EFFL. | EFFL. | TDS |  |  | MONTHLY AVG OVER 30 | MONTHLY AVG OVER 30 |  | NGVD | NGVD | NGVD |  |  | NGVD | NGVD | NGVD
| 2005 | CBOD | TOTAL | FIXED | COD | CL_ | ALK. | TURB. | COND. | TEMP.(F) |  |  |  | 0 | 0 | 1 | 33.76 | 34.06 | 33.9 |  |  | 46.02 | 46.2 | 46.03
[14 empty] | WEKKLY OVER 45 | WEKKLY OVER 45 | 2 | 33.83 | 34.1 | 33.94 |  |  | 46.12 | 46.29 | 46.17
| 1 | 2.08 | 15 | 0 | 41.4 | 420 | 184 | 6.23 | 1879 | 84 | 975 | 1 |  | 0 | 0 | 3 | 33.79 | 33.99 | 33.91 |  |  | 46.12 | 46.24 | 46.11
| 2 | 3.27 | 24 | 6 | 39.9 | 410 | 182 | 4.07 | 1823 | 86 | 953 | 1 |  | SINGLE DAY OVER 60 | SINGLE DAY OVER 60 | 4 | 18.14 | 33.85 | 24.89 |  |  | 37.18 | 46.17 | 41.1
| 3 | 2.93 | 10 | 0 | 36.5 | 410 | 184 | 4.78 | 1887 | 87 | 951 | 1 |  | 0 | 0 | 5 | 18 | 33.49 | 28.2 |  |  | 37.18 | 45.72 | 42.74
| 4 | 2.66 | 7 | 1 | 39.5 | 410 | 188 | 4.49 | 1947 | 88 | 908 | 1 |  | 0 | 0 | 6 | 33.46 | 33.76 | 33.56 |  |  | 45.71 | 45.95 | 45.87
| 5 | 3.53 | 2 | 0 | 43 | 450 | 192 | 4.34 | 1980 | 88 | 902 | 1 |  |  |  | 7 | 33.65 | 33.9 | 33.77 |  |  | 45.93 | 46.09 | 45.99
| 6 | 3.03 | 17 | 2 | 65.6 | 480 | 186 | 3.14 | 2050 | 87 | 989 | 1 |  |  |  | 8 | 33.77 | 33.99 | 33.86 |  |  | 46.09 | 46.25 | 46.07
| 7 | 2.43 | 15 | 0 | 56.6 | 570 | 196 | 4.74 | 2320 | 85 | 1098 | 1 | 2.8471 | 2.8471 | 12.8571 | 9 | ER | ER | ER |  |  | ER | ER | ER
| 8 | 3.5 | 16 | 3 | 49.8 | 630 | 190 | 9.9 | 2660 | 85 | 1275 | 1 |  | 3.05 | 13 | 10 | ER | 34.01 | 23.2 |  |  | ER | 46.29 | 29.47
| 9 | 2.4 | 18 | 0 | 50.2 | 480 | 194 | 7.56 | 2070 | 85 | 1018 | 1 |  | 2.9257 | 12.1429 | 11 | 18.17 | 34.01 | 22.81 |  |  | 36.97 | 46.3 | 39.73
| 10 | 2 | 16 | 4 | 39.5 | 400 | 178 | 7.06 | 1761 | 85 | 821 | 1 |  | 2.7929 | 13 | 12 | 17.98 | 33.48 | 28.44 |  |  | 36.95 | 45.78 | 42.83
| 11 | 4.26 | 19 | 0 | 43.1 | 510 | 188 | 8.46 | 2160 | 85 | 1005 | 1 |  | 3.0214 | 14.7143 | 13 | 33.41 | 33.71 | 33.54 |  |  | 45.78 | 46 | 45.91
| 12 | 3.95 | 12 | 0 | 47.1 | 590 | 200 | 6.45 | 2450 | 85 | 1175 | 1 |  | 3.0814 | 16.1429 | 14 | 33.59 | 33.86 | 33.71 |  |  | 45.96 | 46.22 | 46
| 13 | NR | 13 | 7 | 51.3 | 840 | 196 | 7.69 | 3250 | 85 | 1579 | 0 |  | 3.09 | 15.5714 | 15 | 33.64 | 33.88 | 33.74 |  |  | 46.12 | 46.29 | 46.17
| 14 | NR | 23 | 5 | 48.2 | 820 | 192 | 9.3 | 3190 | 85 | 1579 | 0 | 3.222 | 3.222 | 16.7143 | 16 | 33.59 | 33.85 | 33.71 |  |  | 46.12 | 46.27 | 46.17
| 15 | 4.62 | 12 | 4 | 51.6 | 550 | 184 | 6.08 | 2260 | 86 | 1112 | 1 |  | 3.446 | 16.1429 | 17 | 33.56 | 33.89 | 33.73 |  |  | 46.12 | 46.33 | 46.26
| 16 | 2.82 | 21 | 5 | 48.2 | 530 | 188 | 6.31 | 2210 | 86 | 1033 | 1 |  | 3.53 | 16.5714 | 18 | 18.07 | 33.8 | 22.46 |  |  | 35.78 | 46.3 | 38.77
| 17 | NR | 5 | 0 | 44.6 | 530 | 190 | 6.4 | 2150 | 86 | 1016 | 0 |  | 3.9125 | 15 | 19 | 18.04 | 33.33 | 28.35 |  |  | 35.78 | 45.79 | 42.6
| 18 | 10.33 | 40 | 11 | 45.2 | 580 | 190 | 13.8 | 2370 | 86 | 1087 | 1 |  | 5.43 | 18 | 20 | 33.2 | 33.55 | 33.34 |  |  | 45.77 | 45.99 | 45.89
| 19 | 6.63 | 27 | 0 | 44.3 | 620 | 188 | 11.3 | 2620 | 86 | 1278 | 1 |  | 6.1 | 20.1429 | 21 | 33.35 | 33.67 | 33.44 |  |  | 45.91 | 46.08 | 45.99
| 20 | 2.66 | 18 | 5 | 44.8 | 620 | 194 | 7.3 | 2570 | 86.3 | 1213 | 1 |  | 5.412 | 20.8571 | 22 | 33.44 | 33.74 | 33.54 |  |  | 46.01 | 46.15 | 46.01
| 21 | 2.66 | 14 | 0 | 44.7 | 600 | 190 | 5.59 | 2560 | 86 | 1200 | 1 | 4.9533 | 4.9533 | 19.5714 | 23 | 33.44 | 33.76 | 33.58 |  |  | 46.04 | 46.18 | 46.01
| 22 | NR | 9 | 0 | 44.8 | 520 | 189 | 4.59 | 2280 | 87 | 1141 | 0 |  | 5.02 | 19.1429 | 24 | ER | 33.79 | 33.59 |  |  | ER | 46.23 | 46.03
| 23 | 3.48 | 23 | 11 | 44.2 | 590 | 190 | 4.76 | 2500 | 87 | 1237 | 1 |  | 5.152 | 19.4286 | 25 | 22.53 | 33.8 | 26.2 |  |  | 40.19 | 46.24 | 42.15
| 24 | 2.4 | 8 | 0 | 42.7 | 600 | 182 | 5.19 | 2580 | 87 | 1209 | 1 |  | 4.6933 | 19.8571 | 26 | 22.35 | 33.62 | 29.78 |  |  | 40.14 | 45.81 | 43.8
| 25 | 2.66 | 20 | 2 | 43.2 | 600 | 190 | 6.23 | 2580 | 87 | 1244 | 1 |  | 3.415 | 17 | 27 | ER | 33.82 | 32.67 |  |  | ER | 45.98 | 44.4
| 26 | 2.51 | 8 | 0 | 43.2 | 570 | 182 | 4.84 | 2530 | 87 | 1211 | 1 |  | 2.7283 | 14.2857 | 28 | 33.46 | 33.85 | 33.7 |  |  | 45.46 | 46.04 | 45.96
| 27 | NR | 3 | 0 | 42.6 | 540 | 186 | 4.4 | 2360 | 87 | 1112 | 0 |  | 2.742 | 12.1429 | 29 | 33.57 | 33.86 | 33.72 |  |  | 45.88 | 46.07 | 46
| 28 | 3 | 11 | 0 | 41.3 | 550 | 184 | 4.8 | 2250 | 87 | 1001 | 1 |  | 2.81 | 11.7143 | 30 | 33.63 | 33.88 | 33.78 |  |  | 45.96 | 46.08 | 46
| 29 | 2 | 13 | 5 | 43.8 | 540 | 186 | 4.73 | 2280 | 87 | 1183 | 1 |  | 2.675 | 12.2857 | 31 | 33.68 | 33.95 | 33.84 |  |  | 46 | 46.16 | 46.02
| 30 | 3 | 10 | 0 | 43.5 | 530 | 184 | 4.71 | 2290 | 85 | 1094 | 1 |  | 2.595 | 10.4286 | TOTAL | 791.1 | 1014.25 | 940.9 |  |  | 1173.29 | 1383.49 | 1328.25
| 31 | 2 | 18 | 1 | 42.5 | 500 | 190 | 5.28 | 2170 | 87 | 1030 | 1 | 2.6313 | 2.5283 | 11.8571 | AVERAGE | 29.3 | 33.8083 | 31.3633 |  |  | 43.4552 | 46.1163 | 44.275
| TOTAL | 86.81 | 467 | 72 | 1406.9 | 16990 | 5837 | 194.52 | 71987 | 2670.3 | 34629 |  |  |  |  | MAXIMUM | 33.83 | 34.1 | 33.94 |  |  | 46.12 | 46.33 | 46.26
| AVERAGE | 3.3388 | 15.0645 | 4.8 | 45.3839 | 548.0645 | 188.2903 | 6.2748 | 2322.1613 | 86.1387 | 1117.0645 |  |  | 3.6469 | 15.5429 | MINIMUM | 17.98 | 33.33 | 22.46 |  |  | 35.78 | 45.72 | 29.47
| MAXIMUM | 10.33 | 40
[5 empty] | PAGE 4 | [14 empty] | PAGE 22
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
[5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT | [13 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
[5 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY | [13 empty] | MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
[5 empty] | MONTHLY OPERATIONAL REPORT | [13 empty] | REGIONAL MONITORING WELL ONE
[5 empty] | EFFLUENT DATA PART 2 | [13 empty] | RMW-1 |  |  |  | 1/07/04 thru 1/06/09
[16 empty] | RUN DATE |  |  |  |  | PERMIT # 0054569-142-UO
[16 empty] | 2026-07-30 |  | UPPER MONITOR ZONE |  |  |  |  | LOWER MONITOR ZONE
RUN DATE | [16 empty] | MIN | MAX | AVG |  |  | MIN | MAX | AVG
2026-07-30 | [15 empty] | JULY | FT HEAD | FT HEAD | FT HEAD |  |  | FT HEAD | FT HEAD | FT HEAD
[16 empty] | 2005 | ABOVE | ABOVE | ABOVE |  |  | ABOVE | ABOVE | ABOVE
| JULY | EFF. BACT. | EFF. BACT. | FREE | TOTAL | EFFL. | EFF PH | EFF PH | EFF. SAP | AVG. | Sufates | [5 empty] | NGVD | NGVD | NGVD |  |  | NGVD | NGVD | NGVD
| 2005 | TOTAL | FECAL | CL2 | CL2 | pH | MIN | MAX | TEMP.(C) | BLK. | [5 empty] | 1 | 45.08 | 45.19 | 45.13 |  |  | 23.95 | 24.07 | 24.02
[16 empty] | 2 | 45.1 | 45.2 | 45.15 |  |  | 23.95 | 24.09 | 24.03
| 1 | 634 | 0 | 0 | 0.9 | 6.7 | 6.7 | 6.7 | 1.9 | 10 | 108.5 |  |  |  |  | 3 | 45.05 | 45.19 | 45.1 |  |  | 23.9 | 24.04 | 23.96
| 2 | 0 | 0 | 0 | 1.2 | 6.6 | 6.6 | 6.6 | 2.7 | 19 | 104.75 |  |  |  |  | 4 | 39.05 | 45.09 | 41.84 |  |  | 20.52 | 23.94 | 22.3
| 3 | 9 | 0 | 0 | 1.2 | 6.6 | 6.6 | 6.6 | 6 | 29 | 100.25 |  |  |  |  | 5 | 38.97 | 44.48 | 42.73 |  |  | 20.91 | 22.59 | 21.97
| 4 | 134 | 0 | 0 | 1.2 | 6.6 | 6.5 | 6.8 | 3 | 33 | 103.25 |  |  |  |  | 6 | 44.48 | 44.68 | 44.6 |  |  | 22.58 | 22.83 | 22.71
| 5 | 196 | 9 | 0 | 1 | 6.6 | 6.6 | 6.7 | 2 | 21 | 104.75 |  |  |  |  | 7 | 44.68 | 44.82 | 44.76 |  |  | 22.83 | 22.98 | 22.88
| 6 | 18 | 9 | 0 | 1 | 6.7 | 6.6 | 6.7 | 2 | 26 | 111 |  |  |  |  | 8 | 44.81 | 44.99 | 44.89 |  |  | 22.97 | 23.12 | 23.02
| 7 | TNTC | 23000 | 0 | 1.3 | 6.7 | 6.5 | 6.7 | 3 | 15 | 113.75 |  |  |  |  | 9 | 44.94 | 45.12 | 45.04 |  |  | 23.08 | 23.19 | 23.15
| 8 | 18 | 0 | 0 | 1.2 | 6.6 | 6.5 | 6.7 | 2 | 21 | 130.25 |  |  |  |  | 10 | 44.95 | 45.08 | 45.01 |  |  | 23.07 | 23.18 | 23.11
| 9 | 18 | 0 | 0 | 0.9 | 6.6 | 6.5 | 6.7 | 2.3 | 44 | 109.25 |  |  |  |  | 11 | 44.91 | 45.02 | 44.96 |  |  | 23.04 | 23.15 | 23.08
| 10 | TNTC | TNTC | 0 | 0.8 | 6.5 | 6.5 | 6.6 | 4 | 29 | 86.75 |  |  |  |  | 12 | 44.89 | 44.97 | 44.93 |  |  | 23.02 | 23.13 | 23.07
| 11 | 0 | 0 | 0 | 1 | 6.6 | 6.6 | 6.6 | 3 | 30 | 109.5 |  |  |  |  | 13 | 44.96 | 45.03 | 44.99 |  |  | 23.07 | 23.15 | 23.12
| 12 | 161 | 0 | 0 | 1.2 | 6.6 | 6.5 | 6.6 | 2 | 20 | 118 |  |  |  |  | 14 | 44.99 | 45.07 | 45.02 |  |  | 23.08 | 23.22 | 23.15
| 13 | 0 | 0 | 0 | 0.9 | 6.6 | 6.5 | 6.8 | 3 | 21 | 141.75 |  |  |  |  | 15 | 44.98 | 45.08 | 45.02 |  |  | 23.06 | 23.2 | 23.13
| 14 | TNTC | 250 | 0 | 1 | 6.6 | 6.6 | 6.8 | 2 | 15 | 149 |  |  |  |  | 16 | 44.93 | 45.05 | 44.99 |  |  | 22.98 | 23.14 | 23.08
| 15 | 161 | 0 | 0 | 1.1 | 6.6 | 6.6 | 6.7 | 3.3 | 19 | 112 |  |  |  |  | 17 | 44.93 | 45.03 | 44.99 |  |  | 22.97 | 23.14 | 23.06
| 16 | 9 | 0 | 0 | 1.2 | 6.5 | 6.5 | 6.6 | 2.9 | 22 | 110.75 |  |  |  |  | 18 | 44.93 | 45.05 | 45 |  |  | 22.98 | 23.14 | 23.07
| 17 | 36 | 0 | 0 | 1.1 | 6.5 | 6.5 | 6.6 | 2 | 22 | 106 |  |  |  |  | 19 | 44.9 | 45.04 | 44.98 |  |  | 22.95 | 23.11 | 23.05
| 18 | 36 | 0 | 0 | 0.9 | 6.6 | 6.6 | 6.7 | 2 | 23 | 111.25 |  |  |  |  | 20 | 44.93 | 45.03 | 44.98 |  |  | 22.98 | 23.09 | 23.05
| 19 | 89 | 0 | 0 | 0.7 | 6.6 | 6.5 | 6.7 | 2 | 18 | 114 |  |  |  |  | 21 | 44.9 | 45.04 | 44.99 |  |  | 22.97 | 23.1 | 23.04
| 20 | 9 | 0 | 0 | 1 | 6.7 | 6.6 | 6.8 | 2 | 21 | 120.75 |  |  |  |  | 22 | 44.92 | 45.03 | 44.99 |  |  | 23.01 | 23.12 | 23.06
| 21 | 214 | 0 | 0 | 1 | 6.6 | 6.5 | 6.7 | 2 | 19 | 116.5 |  |  |  |  | 23 | 44.92 | 45.04 | 44.99 |  |  | 23 | 23.12 | 23.05
| 22 | 9 | 0 | 0 | 0.9 | 6.6 | 6.7 | 6.5 | 0.8 | 25 | 138.5 |  |  |  |  | 24 | 44.96 | 45.04 | 45 |  |  | 23.04 | 23.12 | 23.08
| 23 | 9 | 0 | 0 | 1 | 6.6 | 6.5 | 6.6 | 5 | 24 | 116.5 |  |  |  |  | 25 | 44.98 | 45.06 | 45.02 |  |  | 23.04 | 23.15 | 23.11
| 24 | 18 | 0 | 0 | 1 | 6.6 | 6.6 | 6.7 | 5 | 20 | 118 |  |  |  |  | 26 | 44.98 | 45.04 | 45.01 |  |  | 23.04 | 23.14 | 23.1
| 25 | 0 | 0 | 0 | 1.2 | 6.6 | 6.5 | 6.6 | 2 | 22 | 115.75 |  |  |  |  | 27 | 44.99 | 45.05 | 45.02 |  |  | 23.01 | 23.15 | 23.1
| 26 | 18 | 0 | 0 | 1.1 | 6.6 | 6.5 | 6.6 | 2 | 23 | 111 |  |  |  |  | 28 | 44.97 | 45.05 | 45 |  |  | 22.99 | 23.12 | 23.06
| 27 | 36 | 0 | 0 | 1 | 6.6 | 6.6 | 6.6 | 2 | 21 | 109 |  |  |  |  | 29 | 44.9 | 44.99 | 44.95 |  |  | 22.92 | 23.05 | 23
| 28 | 0 | 0 | 0 | 1.2 | 6.6 | 6.5 | 6.6 | 2 | 12 | 107.5 |  |  |  |  | 30 | 44.88 | 44.98 | 44.94 |  |  | 22.9 | 23.05 | 22.98
| 29 | 0 | 0 | 0 | 0.09 | 6.6 | 6.5 | 6.7 | 4.6 | 20 | 113.75 |  |  |  |  | 31 | 44.9 | 44.99 | 44.95 |  |  | 22.92 | 23.05 | 22.99
| 30 | TNTC | TNTC | 0 | 0.5 | 6.5 | 6.5 | 6.6 | 0 | 24 | 109.5 |  |  |  |  | TOTAL | 1380.76 | 1395.52 | 1388.97 |  |  | 710.73 | 719.67 | 715.58
| 31 | 9 | 0 | 0 | 1.1 | 6.7 | 6.5 | 6.8 | 1 | 22 | 105 |  |  |  |  | AVERAGE | 44.5406 | 45.0168 | 44.8055 |  |  | 22.9268 | 23.2152 | 23.0832
| TOTAL | 1841 | 23268 | 0 | 30.89 | 204.7 | 203 | 206.7 | 79.5 | 690 | 3526.5 |  |  |  |  | MAXIMUM | 45.1 | 45.2 | 45.15 |  |  | 23.95 | 24.09 | 24.03
| AVERAGE | 68.1852 | 802.3448 | 0 | 0.99645 | 6.6032 | 6.5484 | 6.6677 | 2.5645 | 22.2581 | 113.7581 |  |  |  |  | MINIMUM | 38.97 | 44.48 | 41.84 |  |  | 20.52 | 22.59 | 21.97
[7 empty] | 6.5 | 6.8
[7 empty] | MIN | MAX
PAGE 5
PAGE 23
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
NUTRIENTS
RUN DATE
| 2026-07-30 |  | INFLUENT | [5 empty] | EFFLUENT
| JULY | INFLUENT | INFLUENT | INFLUENT | INFLUENT |  | EFFL. | EFFL. | EFFL. | EFFL.
| 2005 | NH-3 | N03-N | TKN | TOT P |  | NH-3 | N03-N | TKN | TOT P
| 1 | 9.3 | 0.13 | 13 | 2 |  | 6.3 | 0.44 | 8.2 | 0.99
| 2 | 8.7 | 0.18 | 15 | 2.2 |  | 4.9 | 0.49 | 8.9 | 0.78
| 3 | 7.5 | 0.05 | 15 | 2.2 |  | 5 | 0.37 | 8.1 | 0.65
| 4 | 5.9 | 0.05 | 15 | 2 |  | 5.8 | 0.38 | 9.5 | 0.56
| 5 | 9 | 0.065 | 17 | 2.4 |  | 7.9 | 0.38 | 12 | 0.56
| 6 | 11 | 0.081 | 20 | 2.4 |  | 8.9 | 0.35 | 13 | 0.46
| 7 | 11 | 0.11 | 21 | 2.4 |  | 8.9 | 0.29 | 14 | 0.99
| 8 | 14 | 0.12 | 20 | 2.5 |  | 9.8 | 0.47 | 14 | 0.88
| 9 | 11 | 0.12 | 19 | 2.3 |  | 7.8 | 0.24 | 13 | 0.8
| 10 | 11 | 0.093 | 18 | 2.1 |  | 6.8 | 0.25 | 10 | 0.65
| 11 | 12 | 0.082 | 20 | 2 |  | 9.3 | 0.31 | 15 | 0.99
| 12 | 11 | 0.079 | 19 | 2.5 |  | 9.6 | 0.31 | 11 | 0.58
| 13 | 12 | 0.099 | 15 | 2.1 |  | 9.8 | 0.31 | 11 | 1.1
| 14 | 13 | 0.17 | 21 | 2.5 |  | 11 | 0.32 | 15 | 1.4
| 15 | 12 | 0.16 | 19 | 2.2 |  | 10 | 0.37 | 15 | 1.3
| 16 | 12 | 0.05 | 18 | 2.1 |  | 7 | 0.35 | 12 | 1.2
| 17 | 14 | 0.05 | 23 | 2.9 |  | 11 | 0.35 | 13 | 1.3
| 18 | 15 | 0.05 | 17 | 2.7 |  | 9.9 | 0.21 | 13 | 1.4
| 19 | 15 | 0.05 | 21 | 3.1 |  | 10 | 0.23 | 13 | 1
| 20 | 15 | 0.09 | 19 | 2.8 |  | 10 | 0.19 | 12 | 1.4
| 21 | 14 | 0.05 | 17 | 2.6 |  | 10 | 0.3 | 11 | 1.5
| 22 | 16 | 0.11 | 20 | 2.5 |  | 8.2 | 0.37 | 11 | 1.3
| 23 | 13 | 0.05 | 20 | 2.4 |  | 8.9 | 0.34 | 0 | 1.3
| 24 | 14 | 0.075 | 22 | 2.8 |  | 8.7 | 0.26 | 11 | 1.2
| 25 | 16 | 0.11 | 23 | 2.8 |  | 15 | 0.32 | 12 | 0.88
| 26 | NR | NR | NR | NR |  | NR | NR | NR | NR
| 27 | NR | NR | NR | NR |  | NR | NR | NR | NR
| 28 | NR | NR | NR | NR |  | NR | NR | NR | NR
| 29 | 15 | 0.026 | 17 | 3.1 |  | 12 | 0.35 | 12 | 1.1
| 30 | 14 | 0.053 | 15 | 3.7 |  | 9.5 | 0.3 | 11 | 1.5
| 31 | 11 | 0.05 | 18 | 2.9 |  | 9.7 | 0.33 | 12 | 1.2
| TOTAL | 342.4 | 2.403 | 517 | 70.2 | TOT. | 251.7 | 9.18 | 320.7 | 28.97
| AVERAGE | 12.2286 | 0.085821 | 18.4643 | 2.5071 | AVG. | 8.9893 | 0.32786 | 11.4536 | 1.0346
PAGE 6
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
REACTOR ONE PROCESS
RUN DATE
| 2026-07-30 |  | TRAIN "A" | [5 empty] | TRAIN "B"
| JULY | MLSS | MLVSS | SS | SVI |  | MLSS | MLVSS | SS | SVI
| 2005 | "A" | "A" | "A" | "A" |  | "B" | "B" | "B" | "B"
| 1 | O/S | O/S | O/S |  |  | 2430 | 2180 | 12 | 49.3827
| 2 | O/S | O/S | O/S |  |  | 1890 | 1520 | 16 | 84.6561
| 3 | O/S | O/S | O/S |  |  | 2320 | 1950 | 20 | 86.2069
| 4 | O/S | O/S | O/S |  |  | 2210 | 1890 | 24 | 108.5973
| 5 | O/S | O/S | O/S |  |  | 2080 | ER | 22 | 105.7692
| 6 | O/S | O/S | O/S |  |  | 2050 | 1690 | 20 | 97.561
| 7 | O/S | O/S | O/S |  |  | 2300 | 1920 | 20 | 86.9565
| 8 | O/S | O/S | O/S |  |  | 2810 | 2270 | 22 | 78.2918
| 9 | O/S | O/S | O/S |  |  | 2660 | 2180 | 21 | 78.9474
| 10 | O/S | O/S | O/S |  |  | 2180 | 1670 | 20 | 91.7431
| 11 | O/S | O/S | O/S |  |  | 1960 | 1610 | 14 | 71.4286
| 12 | O/S | O/S | O/S |  |  | 2010 | 1560 | 17 | 84.5771
| 13 | O/S | O/S | O/S |  |  | 1570 | 1200 | 20 | 127.3885
| 14 | O/S | O/S | O/S |  |  | 1520 | 1200 | 15 | 98.6842
| 15 | O/S | O/S | O/S |  |  | 2510 | 2060 | 19 | 75.6972
| 16 | O/S | O/S | O/S |  |  | 2420 | 2020 | 23 | 95.0413
| 17 | O/S | O/S | O/S |  |  | 1440 | 1210 | 20 | 138.8889
| 18 | O/S | O/S | O/S |  |  | 2600 | 2080 | 16 | 61.5385
| 19 | O/S | O/S | O/S |  |  | 2700 | 2270 | 19 | 70.3704
| 20 | O/S | O/S | O/S |  |  | 1980 | 1530 | 19 | 95.9596
| 21 | O/S | O/S | O/S |  |  | 2610 | 2230 | 19 | 72.7969
| 22 | O/S | O/S | O/S |  |  | 3520 | 2610 | 20 | 56.8182
| 23 | O/S | O/S | O/S |  |  | 2400 | 1960 | 27 | 112.5
| 24 | O/S | O/S | O/S |  |  | 2380 | 1970 | 24 | 100.8403
| 25 | O/S | O/S | O/S |  |  | 2230 | 1750 | 26 | 116.5919
| 26 | O/S | O/S | O/S |  |  | 2670 | 2240 | 20 | 74.9064
| 27 | O/S | O/S | O/S |  |  | 2170 | 1750 | 21 | 96.7742
| 28 | O/S | O/S | O/S |  |  | 2340 | 1940 | 21 | 89.7436
| 29 | O/S | O/S | O/S |  |  | 2480 | 2060 | 23 | 92.7419
| 30 | O/S | O/S | O/S |  |  | 2470 | 2140 | 26 | 105.2632
| 31 | O/S | O/S | O/S |  |  | 2300 | 1920 | 18 | 78.2609
| TOTAL | 0 | 0 | 0 |  |  | 71210 | 56580 | 624
| AVERAGE | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 2297.0968 | 1886 | 20.129 | 87.6281
PAGE 7
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
REACTOR TWO PROCESS
RUN DATE
| 2026-07-30 |  | TRAIN "C" | [5 empty] | TRAIN "D"
| JULY | MLSS | MLVSS | SS | SVI |  | MLSS | MLVSS | SS | SVI
| 2005 | "C" | "C" | "C" | "C" |  | "D" | "D" | "D" | "D"
| 1 | O/S | O/S | O/S |  |  | 2190 | 1990 | 12 | 54.7945
| 2 | O/S | O/S | O/S |  |  | 1590 | 1290 | 17 | 106.9182
| 3 | O/S | O/S | O/S |  |  | 2320 | 1970
| 4 | O/S | O/S | O/S |  |  | 2300 | 1970 | 24 | 104.3478
| 5 | O/S | O/S | O/S |  |  | 1970 | ER | 22 | 111.6751
| 6 | O/S | O/S | O/S |  |  | 2090 | 1730 | 20 | 95.6938
| 7 | O/S | O/S | O/S |  |  | 2190 | 2070 | 19 | 86.758
| 8 | O/S | O/S | O/S |  |  | 3010 | 2400 | 21 | 69.7674
| 9 | O/S | O/S | O/S |  |  | 2060 | 1710 | 20 | 97.0874
| 10 | O/S | O/S | O/S |  |  | 1860 | 1480 | 19 | 102.1505
| 11 | O/S | O/S | O/S |  |  | 1900 | 1630 | 17 | 89.4737
| 12 | O/S | O/S | O/S |  |  | 1740 | 1430 | 18 | 103.4483
| 13 | O/S | O/S | O/S |  |  | 1510 | 1210 | 15 | 99.3377
| 14 | O/S | O/S | O/S |  |  | 1930 | 1600 | 14 | 72.5389
| 15 | O/S | O/S | O/S |  |  | 2230 | 1840 | 18 | 80.7175
| 16 | O/S | O/S | O/S |  |  | 1540 | 1310 | 21 | 136.3636
| 17 | O/S | O/S | O/S |  |  | 1250 | 1050 | 18 | 144
| 18 | O/S | O/S | O/S |  |  | 1730 | 1410 | 14 | 80.9249
| 19 | O/S | O/S | O/S |  |  | 1880 | 1650 | 22 | 117.0213
| 20 | O/S | O/S | O/S |  |  | 1690 | 1350 | 17 | 100.5917
| 21 | O/S | O/S | O/S |  |  | 1520 | 1340 | 18 | 118.4211
| 22 | O/S | O/S | O/S |  |  | 2880 | 2270 | 18 | 62.5
| 23 | O/S | O/S | O/S |  |  | 2120 | 1750 | 23 | 108.4906
| 24 | O/S | O/S | O/S |  |  | 2130 | 1740 | 25 | 117.3709
| 25 | O/S | O/S | O/S |  |  | 2110 | 1780 | 22 | 104.2654
| 26 | O/S | O/S | O/S |  |  | 3360 | 2740 | 20 | 59.5238
| 27 | O/S | O/S | O/S |  |  | 2110 | 1790 | 20 | 94.7867
| 28 | O/S | O/S | O/S |  |  | 1810 | 1550 | 19 | 104.9724
| 29 | O/S | O/S | O/S |  |  | 2600 | 2140 | 21 | 80.7692
| 30 | O/S | O/S | O/S |  |  | 2420 | 2080 | 27 | 111.5702
| 31 | O/S | O/S | O/S |  |  | 1780 | 1570 | 20 | 112.3596
| TOTAL | 0 | 0 | 0 |  |  | 63820 | 51840 | 581
| AVERAGE | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 2058.7097 | 1728 | 19.3667 | 94.0719
PAGE 8
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
RAS SUMMARY
RUN DATE
2026-07-30
| JULY | R-1 | R-2 | TOTAL | F/M | TOTAL | SLUDGE | % TOT | % FIX | % VOL.
| 2005 | TOT. RAS | TOT. RAS | MLVSS | RATIO | MLSS | AGE | RAS | RAS | RAS
|  | MGD | MGD
| 1 | 6.309 | 7.627 | 4170 | 0.98219 | 4620 | 1.638 | 0.66 | 23.5 | 76.5
| 2 | 6.383 | 6.839 | 2810 | 0.51868 | 3480 | 0.62677 | 0.7 | 25.2 | 74.8
| 3 | 6.486 | 7.714 | 3920 | 1.3676 | 4640 | 1.4281 | 0.84 | 25.6 | 74.4
| 4 | 6.354 | 7.89 | 3860 |  | 4510 | 0.65381 | 0.8 | 23.8 | 76.2
| 5 | 6.415 | 7.59 |  |  | 4050 | 1.1756 | 0.66 | 26.73 | 73.27
| 6 | 6.317 | 7.664 | 3420 |  | 4140 | 0.73529 | 0.71 | 20.25 | 79.75
| 7 | 6.211 | 7.404 | 3990 |  | 4490 | 0.82405 | 0.68 | 32.4 | 67.6
| 8 | 6.148 | 8.211 | 4670 |  | 5820 | 1.4484 | 0.91 | 25.3 | 74.7
| 9 | 6.143 | 8.589 | 3890 | 0.95349 | 4720 | 0.6704 | 0.9 | 24.44 | 75.56
| 10 | 5.938 | 8.442 | 3150 |  | 4040 | 0.96412 | 0.86 | 23.26 | 76.74
| 11 | 6.151 | 7.505 | 3240 |  | 3860 | 1.3784 | 0.73 | 23.26 | 76.74
| 12 | 5.993 | 7.767 | 2990 | 0.31725 | 3750 | 0.53934 | 0.73 | 27.5 | 72.5
| 13 | 5.984 | 7.509 | 2410 |  | 3080 | 0.74107 | 0.62 | 33.33 | 66.67
| 14 | 6.016 | 8.213 | 2800 |  | 3450 | 0.78839 | 0.6 | 35.23 | 64.77
| 15 | 6.048 | 9.512 | 3900 | 0.8171 | 4740 | 1.0405 | 0.51 | 26.92 | 73.08
| 16 | 6.066 | 7.275 | 3330 | 0.82263 | 3960 | 0.91217 | 0.94 | 23.1 | 76.9
| 17 | 6.088 | 7.62 | 2260 |  | 2690 | 0.74183 | 0.54 | 29.58 | 70.42
| 18 | 6.157 | 7.084 | 3490 | 1.1815 | 4330 | 0.9062 | 0.68 | 30.88 | 69.12
| 19 | 6.308 | 6.831 | 3920 | 1.3726 | 4580 | 0.79426 | 0.69 | 29.63 | 70.37
| 20 | 6.239 | 7.683 | 2880 | 1.0931 | 3670 | 0.72814 | 0.52 | 27.84 | 72.16
| 21 | 6.304 | 7.79 | 3570 | 0.99346 | 4130 | 0.92389 | 0.64 | 30.59 | 69.41
| 22 | 6.146 | 9.081 | 4880 | 0.84475 | 6400 | 2.8146 | 0.53 | 26.09 | 73.91
| 23 | 5.967 | 8.629 | 3710 | 1.0337 | 4520 | 1.1245 | 0.61 | 26.97 | 73.03
| 24 | 5.952 | 8.921 | 3710 | 0.97468 | 4510 | 1.7383 | 0.84 | 24.14 | 75.86
| 25 | 6.001 | 8.968 | 3530 | 1.1383 | 4340 | 0.91131 | 0.79 | 25.71 | 74.29
| 26 | 6.232 | 7.57 | 4980 | 0.73431 | 6030 | 1.3709 | 0.74 | 27.16 | 72.84
| 27 | 6.193 | 8.638 | 3540 | 0.99949 | 4280 | 1.2853 | 0.7 | 28.57 | 71.43
| 28 | 6.217 | 9.036 | 3490 | 1.1531 | 4150 | 1.0861 | 0.64 | 28.95 | 71.05
| 29 | 6.177 | 9.347 | 4200 | 0.8544 | 5080 | 1.4317 | 0.44 | 25.71 | 74.29
| 30 | 6.158 | 7.897 | 4220 | 1.1031 | 4890 | 1.1741 | 0.63 | 28.44 | 71.56
| 31 | 6.042 | 7.796 | 3490 | 1.1393 | 4080 | 1.0588 | 0.58 | 25.93 | 74.07
| TOTAL | 191.143 | 248.642 | 108420 |  | 135030 |  | 21.42 | 836.01 | 2263.99
| AVERAGE | 6.1659 | 8.0207 | 3614 | 1.0198 | 4355.8065 | 0.98779 | 0.69097 | 26.9681 | 73.0319
PAGE 9
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
DEWATERING DATA
RUN DATE
| 2026-07-30 |  | FEED SLUDGE |  |  |  |  | FILTRATE RETURN
| JULY | % TOT. | % FIX. | % VOL. | pH |  | % TOT. | % FIX. | % VOL. | pH
| 2005 | FEED | FEED | FEED |  |  | FILT. | FILT. | FILT.
1
2
3
4
| 5 | 1.34 | 21.64 | 78.36 | 6.14 |  | 0.15 | 66.7 | 33.3 | 6.29
| 6 | 0.78 | 25.64 | 74.36 | 6.5 |  | 0.23 | 47.83 | 52.17 | 6.9
| 7 | 1.31 | 22.9 | 77.1 | 6.24 |  | 0.18 | 83.3 | 16.7 | 6.9
8
9
| 10 | 1.49 | 20.8 | 79.2 | 5.67 |  | 0.13 | 92.37 | 7.63 | 6.67
| 11 | 1.3 | 23.1 | 76.9 | 5.7 |  | 0.15 | 80 | 20 | 6.66
| 12 | 1.35 | 23.7 | 76.3 | 5.98 |  | 0.19 | 73.68 | 26.32 | 6.76
| 13 | 1.43 | 25.87 | 74.13 | 6.01 |  | 0.22 | 77.27 | 22.73 | 6.77
| 14 | 1.36 | 29.41 | 70.59 | 5.78 |  | 0.23 | 73.91 | 26.09 | 6.69
15
16
| 17 | 1 | 24 | 76 | 5.97 |  | 0.17 | 88.24 | 11.76 | 6.63
| 18 | 1.2 | 23.33 | 76.67 | 5.77 |  | 0.19 | 68.42 | 31.58 | 6.6
| 19 | 1.15 | 24.35 | 75.65 | 6.1 |  | 0.19 | 78.95 | 21.05 | 6.72
| 20 | 1.26 | 24.6 | 75.4 | 6.11 |  | 0.22 | 68.18 | 31.82 | 6.83
| 21 | 1.2 | 25.83 | 74.17 | 6.09 |  | 0.22 | 72.73 | 27.27 | 6.65
22
23
| 24 | 1.57 | 20.38 | 79.62 | 6.09 |  | 0.19 | 63.16 | 36.84 | 6.85
| 25 | 1.14 | 23.68 | 76.32 | 6 |  | 0.21 | 66.67 | 33.33 | 6.8
| 26 | 1.18 | 22.88 | 77.12 | 6.12 |  | 0.2 | 70 | 30 | 6.71
| 27 | 0.83 | 26.51 | 73.49 | 6.24 |  | 0.16 | 68.75 | 31.25 | 6.8
| 28 | 1.2 | 23.33 | 76.67 | 6.16 |  | 0.21 | 57.14 | 42.86 | 6.73
29
30
| 31 | 1.48 | 19.59 | 80.41 | 6.12 |  | 0.17 | 70.59 | 29.41 | 6.76
| TOTAL | 23.57 | 451.54 | 1448.46 | 114.79 |  | 3.61 | 1367.89 | 532.11 | 127.72
| AVERAGE | 1.2405 | 23.7653 | 76.2347 | 6.0416 |  | 0.19 | 71.9942 | 28.0058 | 6.7221
PAGE 10
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
SLUDGE VOLUME REMOVED
RUN DATE
2026-07-30
|  | JULY | TRAILERS | TONS | DRY TONS | % LIME | % TOT. | % FIX. | % VOL.
|  | 2005 | REMOVED | SLUDGE | REMOVED | CAKE | CAKE | CAKE | CAKE
|  | 1 | 4 | 88
|  | 2 | 0 | 0
|  | 3 | 0 | 0
|  | 4 | 0 | 0
|  | 5 | 2 | 44 | 25.201 |  | 17.15 | 14.56 | 85.44
|  | 6 | 5 | 110 | 17.8568 |  | 17.73 | 16.41 | 83.59
|  | 7 | 5 | 110 | 29.5532 |  | 18.42 | 16.7 | 83.3
|  | 8 | 4 | 88
|  | 9 | 0 | 0
|  | 10 | 0 | 0 | 12.3023 |  | 18.01 | 16.88 | 83.12
|  | 11 | 4 | 88 | 23.6356 |  | 17.78 | 19.12 | 80.88
|  | 12 | 4 | 88 | 19.9284 |  | 18.39 | 18.92 | 81.08
|  | 13 | 4 | 88 | 25.4624 |  | 20.55 | 20.68 | 79.32
|  | 14 | 4 | 88 | 25.1801 |  | 20.37 | 19.64 | 80.36
|  | 15 | 2 | 44
|  | 16 | 0 | 0
|  | 17 | 0 | 0 | 4.8789 |  | 17.12 | 15.42 | 84.58
|  | 18 | 4 | 88 | 12.6601 |  | 18.13 | 15.19 | 84.81
|  | 19 | 3 | 66 | 15.6333 |  | 18.68 | 18.79 | 81.21
|  | 20 | 3 | 75 | 19.966 |  | 18.81 | 18.61 | 81.39
|  | 21 | 4 | 88 | 21.8174 |  | 18.76 | 19.24 | 80.76
|  | 22 | 3 | 66
|  | 23 | 0 | 0
|  | 24 | 0 | 0 | 10.9333 |  | 17.22 | 15.74 | 84.26
|  | 25 | 4 | 88 | 18.3021 |  | 18.2 | 18.35 | 81.65
|  | 26 | 4 | 88 | 19.9776 |  | 18.47 | 15.65 | 84.35
|  | 27 | 4 | 88 | 12.8407 |  | 17.91 | 17.91 | 82.09
|  | 28 | 4 | 88 | 21.1669 |  | 17.8 | 14.21 | 85.79
|  | 29 | 4 | 88
|  | 30 | 0 | 0
|  | 31 | 0 | 0 | 9.7511 |  | 17.01 | 15.52 | 84.48
|  | TOTAL | 75 | 1659 | 347.0474 | 0 | 346.51 | 327.54 | 1572.46
|  | AVERAGE | 2.4194 | 53.5161 | 18.2657 | #DIV/0! | 18.2374 | 17.2389 | 82.7611
PAGE 11
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
CHEMICAL USEAGE
RUN DATE
2026-07-30
| JULY | H2O2 | CL2 | POLYMER | POLYMER | LIME | GOX | O2 % | LOX | FPL
| 2005 | POUNDS | POUNDS | GALLONS | POUNDS | DELV. | TONS | PURITY | TONS | KW
| 1 | 349 | 1380 | 15 | 125.1 | 0 | 20.3 | 100% | 100 | 32113
| 2 | 389 | 1440 | 0 | 0 | 0 | 20.7 | 100% | 99.3 | 32417
| 3 | 0 | 1440 | 0 | 0 | 0 | 28.2 | 100% | 99.9 | 32214
| 4 | 0 | 1480 | 0 | 0 | 0 | 22.9 | 100% | 99.6 | 32420
| 5 | 0 | 1360 | 97 | 808.98 | 0 | 22.4 | 100% | 100.3 | 32389
| 6 | 0 | 1240 | 102 | 850.68 | 0 | 24.8 | 100% | 102.2 | 32275
| 7 | 0 | 1340 | 43 | 358.62 | 0 | 24 | 100% | 102.3 | 32296
| 8 | 1519 | 1500 | 61 | 508.74 | 0 | 21.3 | 100% | 101.3 | 32167
| 9 | 1317 | 1480 | 0 | 0 | 0 | 27.4 | 100% | 101.2 | 32249
| 10 | 1926 | 1520 | 45 | 375.3 | 0 | 20.7 | 99% | 101 | 32046
| 11 | 1377 | 1360 | 85 | 708.9 | 0 | 23 | 100% | 100.9 | 32341
| 12 | 1407 | 1140 | 86 | 717.24 | 0 | 19 | 100% | 104.3 | 32367
| 13 | 668 | 1560 | 53 | 442.02 | 0 | 19 | 100% | 102.7 | 32388
| 14 | 0 | 1440 | 68 | 567.12 | 0 | 16.4 | 100% | 104.1 | 32186
| 15 | 1158 | 1400 | 0 | 0 | 0 | 18.4 | 100% | 104.5 | 31907
| 16 | 240 | 1680 | 0 | 0 | 0 | 20.4 | 100% | 103.9 | 31650
| 17 | 0 | 1320 | 32 | 266.88 | 0 | 17.7 | 100% | 104.8 | 31799
| 18 | 0 | 1440 | 62 | 517.08 | 0 | 18.5 | 100% | 109.2 | 31832
| 19 | 0 | 1480 | 60 | 500.4 | 0 | 20.6 | 100% | 110.1 | 31990
| 20 | 698 | 1480 | 62 | 517.08 | 0 | 18.5 | 100% | 106.3 | 31843
| 21 | 1716 | 1400 | 80 | 667.2 | 0 | 25.7 | 94% | 99.7 | 26656
| 22 | 1807 | 1580 | 36 | 300.24 | 0 | 31.5 | 100% | 91.6 | 29089
| 23 | 1896 | 1440 | 0 | 0 | 0 | 23.5 | 98% | 92 | 32153
| 24 | 2096 | 1440 | 0 | 0 | 0 | 23.5 | 100% | 92.2 | 32426
| 25 | 1936 | 1620 | 48 | 400.32 | 0 | 23.1 | 100% | 96 | 32186
| 26 | 1836 | 1480 | 55 | 458.7 | 0 | 20.2 | 100% | 96.8 | 32253
| 27 | 1906 | 1440 | 64 | 533.76 | 0 | 20.1 | 100% | 95.8 | 32178
| 28 | 1916 | 1400 | 47 | 391.98 | 0 | 19.7 | 100% | 95.7 | 32235
| 29 | 1897 | 1320 | 0 | 0 | 0 | 21 | 100% | 96.6 | 31991
| 30 | 2106 | 1140 | 0 | 0 | 0 | 21 | 98% | 94 | 32219
| 31 | 1717 | 1280 | 6 | 50.04 | 0 | 26.3 | 94% | 94.8 | 32276
| TOTAL | 31877 | 44020 | 1207 | 10066.38 | 0 | 679.8 |  | 3103.1 | 988551
| AVERAGE | 1028.2903 | 1420 | 38.9355 | 324.7219 | 0 | 21.929 | 99.45% | 100.1 | 31888.7419
PAGE 12
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL ONE
|  | RUN DATE |  |  | PERMIT NUMBER 0054569-142-UO
|  | 2026-07-30 |  |  | 1/07/04 thru 1/06/09 |  |  | I.D. #:5006A11308
|  | JULY | % INFL. | MAX | MIN | WELL 1 | MAX | MIN | AVG
|  | 2005 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 25.89% | 14.85 | 9.64 | 12.93 | 70.2 | 53.94 | 63.39
|  | 2 | 6.123% | 14.27 | 0 | 3.01 | 67.93 | 35.51 | 43.56
|  | 3 | 22.94% | 14.88 | 0 | 10.56 | 69.42 | 36.36 | 56.67
|  | 4 | 20.5% | 13.33 | 0.01 | 8.84 | 64.78 | 35.65 | 52.08
|  | 5 | 25.34% | 14.38 | 6.86 | 10.6 | 67.05 | 44.95 | 54.81
|  | 6 | 25.4% | 11.74 | 6.56 | 10.13 | 58.62 | 44.83 | 53.69
|  | 7 | 5.571% | 11.52 | 0.01 | 2.15 | 56.44 | 34.87 | 40.35
|  | 8 | 21.87% | 13.75 | 0.01 | 8.3 | 64.52 | 34.04 | 51.48
|  | 9 |  | 0 | ER | ER | 41.82 | ER | 26.05
|  | 10 | 12.99% | 13.19 | ER | 5.93 | 65.44 | ER | 30.19
|  | 11 | 25.73% | 14.32 | 7.96 | 11.34 | 69.68 | 48.94 | 58.28
|  | 12 | 5.756% | 12.88 | 0.01 | 2.43 | 61.45 | 29.99 | 41.11
|  | 13 | 21.23% | 14.04 | 0.01 | 8.72 | 65.16 | 36.02 | 51.5
|  | 14 | 23.46% | 14.25 | 0.01 | 9.09 | 63.39 | 34.82 | 51.04
|  | 15 | 26.67% | 13.61 | 5.71 | 9.93 | 62.37 | 40.58 | 52.64
|  | 16 | 25.61% | 12.87 | 5.39 | 9.45 | 59.72 | 37.99 | 51.52
|  | 17 | 5.58% | 11.41 | 0.01 | 2 | 57.74 | 35.45 | 39.74
|  | 18 | 21.87% | 12.31 | 0.01 | 7.79 | 60.03 | 35.77 | 48.87
|  | 19 | 21.73% | 13.53 | 0.01 | 7.83 | 64.65 | 35.42 | 48.56
|  | 20 | 25.53% | 12.32 | 5.62 | 9.27 | 59.76 | 41.37 | 50.56
|  | 21 | 25.39% | 11.23 | 5.34 | 9.1 | 57.71 | 41.26 | 50.85
|  | 22 | 6.761% | 12.39 | 0.01 | 2.42 | 61.27 | 36.01 | 40.44
|  | 23 | 21.23% | 12.27 | 0.01 | 7.4 | 59.35 | 35.8 | 48.3
|  | 24 | 26.32% | 11.42 | 0 | 9.07 | 57.38 | 0 | 50.55
|  | 25 | 25.92% | 14.53 | 0.76 | 9.37 | 66.41 | 37.5 | 51.88
|  | 26 | 25.59% | 11.59 | 6.89 | 9.38 | 57.79 | 45.5 | 51.72
|  | 27 |  | 3.96 | ER | ER | 44.13 | 0 | 36.62
|  | 28 | 21.24% | 12.98 | 0.01 | 7.34 | 62.62 | 35.74 | 48.17
|  | 29 | 21.62% | 11.89 | 0.01 | 7.41 | 58.8 | 35.34 | 47.92
|  | 30 | 25.58% | 11.64 | 5.53 | 8.88 | 57.97 | 42.07 | 50.13
|  | 31 | 25.26% | 11.61 | 5.62 | 8.8 | 58.76 | 42.65 | 50.18
|  | TOTAL | 594.7% | 378.96 | 72.01 | 229.47 | 1892.36 | 1048.37 | 1492.85
|  | AVERAGE | 20.51% | 12.2245 | 2.5718 | 7.9128 | 61.0439 | 36.1507 | 48.1565
|  | MAXIMUM | 26.67% | 14.88 | 9.64 | 12.93 | 70.2 | 53.94 | 63.39
|  | MINIMUM | 5.571% | 0 | 0 | 2 | 41.82 | 0 | 26.05
PAGE 13
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL TWO
|  | RUN DATE |  |  | PERMIT NUMBER 0054569-142-UO
|  | 2026-07-30 |  |  | 1/07/04 thru 1/06/09 |  |  | I.D. #:5006A11309
|  | JULY | % INFL. | MAX | MIN | WELL 2 | MAX | MIN | AVG
|  | 2005 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 26.39% | 15.09 | 9.83 | 13.18 | 68.96 | 52.63 | 62.31
|  | 2 | 27.52% | 15.46 | 9.64 | 13.53 | 69.44 | 51.25 | 62.67
|  | 3 | 1.738% | 12.84 | 0.05 | 0.8 | 59.67 | 37.08 | 39.22
|  | 4 | 19.81% | 13.65 | 0.05 | 8.54 | 62.8 | 36.43 | 50.85
|  | 5 | 20.77% | 12.32 | 0.05 | 8.69 | 59.16 | 36.95 | 50.92
|  | 6 | 25.98% | 12.01 | 6.7 | 10.36 | 57.44 | 44.11 | 52.92
|  | 7 | 28.03% | 12.68 | 6.89 | 10.82 | 58.84 | 44.46 | 53.62
|  | 8 | 6.271% | 12.54 | 0.05 | 2.38 | 58.54 | 36.9 | 40.83
|  | 9 |  | 0 | ER | ER | 63.76 | ER | 38.59
|  | 10 | 13.21% | 13.49 | ER | 6.03 | 63.28 | ER | 29.45
|  | 11 | 26.27% | 14.6 | 8.12 | 11.58 | 67.48 | 47.26 | 57.1
|  | 12 | 28.02% | 14.34 | 7.27 | 11.83 | 64.93 | 45.13 | 56.95
|  | 13 | 6.646% | 13.68 | 0.05 | 2.73 | 61.6 | 36.8 | 41.5
|  | 14 | 21.06% | 12.33 | 0.05 | 8.16 | 59.29 | 35.94 | 48.89
|  | 15 | 21.94% | 11.94 | 0.05 | 8.17 | 57.53 | 36.87 | 49.31
|  | 16 | 26.21% | 13.31 | 5.5 | 9.67 | 61.91 | 41.16 | 51.33
|  | 17 | 27.26% | 13.94 | 4.81 | 9.77 | 63.38 | 40.44 | 51.19
|  | 18 | 6.315% | 13.29 | 0.05 | 2.25 | 61.15 | 36.8 | 40.58
|  | 19 | 21.34% | 13.94 | 0.06 | 7.69 | 63.67 | 36.01 | 48.11
|  | 20 | 21.57% | 11.96 | 0.06 | 7.83 | 57.31 | 36.63 | 48.07
|  | 21 | 26.11% | 11.56 | 5.36 | 9.36 | 56.93 | 41.26 | 50.29
|  | 22 | 28.5% | 16.01 | 5.89 | 10.2 | 71.6 | 42.11 | 52.58
|  | 23 | 6.282% | 10.88 | 0.05 | 2.19 | 52.88 | 36.83 | 40.19
|  | 24 | 24.2% | 11.78 | 0 | 8.34 | 56.69 | 0 | 48.58
|  | 25 | 21.91% | 13.67 | 0.05 | 7.92 | 63.48 | 36.56 | 48.96
|  | 26 | 26.14% | 11.9 | 7 | 9.58 | 56.86 | 44.86 | 50.94
|  | 27 | 27.67% | 13.78 | ER | 9.79 | 63.09 | 0 | 51.96
|  | 28 | 6.136% | 11.57 | 0.05 | 2.12 | 56.25 | 37.01 | 40.24
|  | 29 | 21.15% | 12.17 | 0.05 | 7.25 | 57.63 | 35.86 | 47.08
|  | 30 | 21.44% | 11.93 | 0.05 | 7.44 | 57.43 | 36.61 | 47.49
|  | 31 | 25.8% | 11.91 | 5.57 | 8.99 | 57.61 | 42.21 | 49.56
|  | TOTAL | 611.7% | 390.57 | 83.35 | 237.19 | 1890.59 | 1086.16 | 1502.28
|  | AVERAGE | 20.39% | 12.599 | 2.9768 | 7.9063 | 60.9868 | 37.4538 | 48.4606
|  | MAXIMUM | 28.5% | 16.01 | 9.83 | 13.53 | 71.6 | 52.63 | 62.67
|  | MINIMUM | 1.738% | 0 | 0 | 0.8 | 52.88 | 0 | 29.45
PAGE 14
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL THREE
|  | RUN DATE |  |  | PERMIT NUMBER 0054569-142-UO
|  | 2026-07-30 |  |  | 1/07/04 thru 1/06/09 |  |  | I.D. #:5006A11310
|  | JULY | % INFL. | MAX | MIN | WELL 3 | MAX | MIN | AVG
|  | 2005 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 24.49% | 14.45 | 0.09 | 12.23 | 70.5 | 38.09 | 63.01
|  | 2 | 25.3% | 13.94 | 9.39 | 12.44 | 70.7 | 52.31 | 63.87
|  | 3 | 24.68% | 13.83 | 8.49 | 11.36 | 69.45 | 51.1 | 59.8
|  | 4 | 6.239% | 13.64 | ER | 2.69 | 68.62 | 37.94 | 43.75
|  | 5 | 19% | 11.74 | ER | 7.95 | 60.37 | 37.41 | 51.37
|  | 6 | 20.28% | 11.28 | ER | 8.09 | 58.64 | 37.23 | 51.06
|  | 7 | 26.09% | 11.56 | 6.89 | 10.07 | 59.9 | 45.35 | 54.64
|  | 8 | 26.48% | 12.85 | 6.84 | 10.05 | 65.39 | 46.14 | 54.67
|  | 9 |  | 0 | ER | ER | 64.99 | ER | 39.35
|  | 10 | 12.68% | 12.79 | ER | 5.79 | 64.65 | ER | 30.13
|  | 11 | 24.91% | 13.61 | 6.28 | 10.98 | 68.87 | 48.21 | 58.15
|  | 12 | 25.92% | 12.91 | 7.28 | 10.94 | 66.07 | 46.03 | 58.01
|  | 13 | 26.02% | 13.1 | 7.97 | 10.69 | 65.42 | 47.86 | 56.55
|  | 14 | 4.542% | 12.63 | ER | 1.76 | 64.31 | 37.21 | 41.03
|  | 15 | 20.17% | 11.44 | ER | 7.51 | 58.72 | 36.76 | 49.67
|  | 16 | 20.54% | 11.26 | ER | 7.58 | 58.68 | 36.82 | 49.65
|  | 17 | 25.47% | 12.51 | 4.76 | 9.13 | 64.54 | 41.25 | 52.17
|  | 18 | 26.5% | 12.13 | 5.96 | 9.44 | 62.32 | 43.08 | 52.87
|  | 19 | 5.855% | 12.94 | ER | 2.11 | 66.13 | 37.56 | 41.58
|  | 20 | 19.8% | 11.34 | ER | 7.19 | 58.55 | 36.96 | 48.57
|  | 21 | 20.78% | 10.91 | ER | 7.45 | 58.12 | 36.61 | 49.22
|  | 22 | 26.6% | 14.5 | 6.03 | 9.52 | 73 | 42.95 | 53.63
|  | 23 | 25.99% | 11.52 | 6.5 | 9.06 | 59.74 | 44.18 | 51.64
|  | 24 | 0.08706% | 4.23 | ER | 0.03 | 39.57 | 0 | 38.5
|  | 25 | 20.14% | 14.1 | ER | 7.28 | 69.95 | 36.84 | 49.55
|  | 26 | 20.43% | 10.84 | ER | 7.49 | 57.21 | 37.13 | 49.33
|  | 27 | 25.44% | 12.42 | ER | 9 | 64.23 | 0 | 53
|  | 28 | 25.82% | 12.15 | 5.59 | 8.92 | 62.71 | 43.06 | 51.45
|  | 29 | 5.865% | 11.11 | ER | 2.01 | 59.51 | 37.64 | 41.31
|  | 30 | 19.79% | 11.35 | ER | 6.87 | 58.68 | 36.99 | 48.07
|  | 31 | 20.52% | 11.19 | ER | 7.15 | 58.71 | 37.06 | 48.56
|  | TOTAL | 596.4% | 364.27 | 82.07 | 232.78 | 1948.25 | 1109.77 | 1554.16
|  | AVERAGE | 19.88% | 11.7506 | 6.3131 | 7.7593 | 62.8468 | 38.2679 | 50.1342
|  | MAXIMUM | 26.6% | 14.5 | 9.39 | 12.44 | 73 | 52.31 | 63.87
|  | MINIMUM | 0.08706% | 0 | 0.09 | 0.03 | 39.57 | 0 | 30.13
PAGE 15
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL FOUR
|  | RUN DATE |  |  | PERMIT NUMBER 0054569-142-UO
|  | 2026-07-30 |  |  | 1/07/04 thru 1/06/09
|  | JULY | % INFL. | MAX | MIN | WELL 4 | MAX | MIN | AVG
|  | 2005 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 21.08% | 14.23 | 0.04 | 10.53 | 69.88 | 37.77 | 59.57
|  | 2 | 20.71% | 14.06 | 0.04 | 10.18 | 71.3 | 37.64 | 59.47
|  | 3 | 24.85% | 13.92 | 8.62 | 11.44 | 69.97 | 51.69 | 60.37
|  | 4 | 25.28% | 13.71 | 7.6 | 10.9 | 69.13 | 47.62 | 57.63
|  | 5 | 6.12% | 13.88 | 0.05 | 2.56 | 67.74 | 37.92 | 42.91
|  | 6 | 20.06% | 11.74 | 0.05 | 8 | 59.08 | 37.29 | 50.93
|  | 7 | 21.82% | 11.6 | 0.05 | 8.42 | 60.49 | 37.04 | 52.53
|  | 8 | 26.75% | 12.94 | 6.92 | 10.15 | 65.95 | 46.82 | 55.29
|  | 9 |  | 0 | ER | ER | 0 | ER | ER
|  | 10 | 0.1533% | 6.51 | ER | 0.07 | 39.66 | ER | ER
|  | 11 | 19.85% | 14.21 | 0.05 | 8.75 | 69.18 | 37.41 | 53.98
|  | 12 | 21.53% | 13.04 | 0.05 | 9.09 | 66.62 | 37.4 | 55.11
|  | 13 | 26.56% | 13.27 | 8.06 | 10.91 | 65.9 | 48.55 | 57.12
|  | 14 | 26.51% | 13.06 | 6.56 | 10.27 | 65.44 | 46.35 | 54.75
|  | 15 | 6.392% | 13.17 | 0.05 | 2.38 | 64.94 | 37.82 | 42.27
|  | 16 | 20.19% | 11.66 | 0.05 | 7.45 | 59.32 | 36.9 | 49.59
|  | 17 | 21.23% | 12.65 | 0.05 | 7.61 | 65.13 | 37.19 | 50.35
|  | 18 | 26.92% | 12.55 | 6.13 | 9.59 | 62.89 | 43.79 | 53.53
|  | 19 | 26.55% | 13.25 | 6.32 | 9.57 | 66.68 | 44.53 | 53.05
|  | 20 | 5.812% | 12.11 | 0.05 | 2.11 | 61.04 | 37.59 | 41.16
|  | 21 | 20.62% | 11.28 | 0.05 | 7.39 | 58.66 | 36.57 | 49.29
|  | 22 | 22.52% | 14.91 | 0.05 | 8.06 | 73.4 | 36.99 | 51.85
|  | 23 | 26.33% | 11.55 | 6.61 | 9.18 | 60.36 | 44.77 | 52.28
|  | 24 | 26.41% | 11.26 | 0 | 9.1 | 58.62 | 0 | 51.58
|  | 25 | 6.557% | 14.89 | 0.05 | 2.37 | 72.7 | 37.54 | 41.86
|  | 26 | 20.08% | 11.2 | 0.05 | 7.36 | 57.85 | 37.1 | 49.31
|  | 27 |  | 12.51 | ER | ER | 64.57 | ER | 51.34
|  | 28 | 26.22% | 12.23 | 5.74 | 9.06 | 63.31 | 43.76 | 52.11
|  | 29 | 26.46% | 11.62 | 5.74 | 9.07 | 60.12 | 43.37 | 51.79
|  | 30 | 5.82% | 9.92 | 0.05 | 2.02 | 53.74 | 37.8 | 41.06
|  | 31 | 20.29% | 11.6 | 0.05 | 7.07 | 59.3 | 37.02 | 48.58
|  | TOTAL | 569.7% | 374.53 | 69.13 | 220.66 | 1902.97 | 1096.24 | 1490.66
|  | AVERAGE | 19.64% | 12.0816 | 2.4689 | 7.609 | 61.3861 | 39.1514 | 51.4021
|  | MAXIMUM | 26.92% | 14.91 | 8.62 | 11.44 | 73.4 | 51.69 | 60.37
|  | MINIMUM | 0.1533% | 0 | 0 | 0.07 | 0 | 0 | 41.06
PAGE 16
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT INJECTION WELL MONITORING
WELL FIVE
|  | RUN DATE |  |  | PERMIT NUMBER 0054569-142-UO
|  | 2026-07-30 |  |  | 1/07/04 thru 1/06/09 |  |  | I.D. #:5006A11311
|  | JULY | % INFL. | MAX | MIN | WELL 5 | MAX | MIN | AVG
|  | 2005 | FLOW | FLOW | FLOW | FLOW | PSI | PSI | PSI
|  |  |  | MGD | MGD | MGD
|  | 1 | 1.662% | 12.73 | ER | 0.83 | 64.89 | 36.7 | 39.7
|  | 2 | 18.29% | 13.19 | ER | 8.99 | 70.4 | 36.28 | 57.41
|  | 3 | 23.14% | 13.1 | ER | 10.65 | 68.94 | 37.59 | 59.14
|  | 4 | 23.73% | 12.87 | 7.15 | 10.23 | 68.2 | 46.58 | 56.53
|  | 5 | 23.93% | 12.91 | 6.65 | 10.01 | 66.71 | 44.88 | 54.94
|  | 6 | 5.541% | 11.02 | ER | 2.21 | 57.86 | 36.84 | 40.92
|  | 7 | 19.48% | 10.93 | ER | 7.52 | 59.47 | 35.74 | 50.88
|  | 8 | 20.79% | 12.18 | ER | 7.89 | 64.92 | 36.71 | 51.58
|  | 9 |  | 0 | ER | ER | 64.6 | ER | 39.12
|  | 10 | 12.22% | 12.34 | ER | 5.58 | 64.04 | ER | 29.81
|  | 11 | 1.361% | 10.71 | ER | 0.6 | 58.38 | 36.58 | 38.82
|  | 12 | 19.19% | 12.28 | ER | 8.1 | 65.62 | 36.12 | 53.34
|  | 13 | 20.08% | 12.33 | ER | 8.25 | 64.97 | 36.62 | 52.6
|  | 14 | 24.73% | 12.17 | 5.43 | 9.58 | 63.91 | 45.44 | 53.55
|  | 15 | 25.41% | 12.24 | 5.79 | 9.46 | 63.9 | 42.62 | 52.94
|  | 16 | 5.718% | 12.17 | ER | 2.11 | 62.77 | 36.54 | 40.58
|  | 17 | 18.95% | 11.9 | ER | 6.79 | 64.19 | 35.71 | 48.67
|  | 18 | 20.83% | 10.94 | ER | 7.42 | 59.29 | 36.83 | 49.99
|  | 19 | 24.92% | 12.33 | 6.07 | 8.98 | 65.75 | 43.54 | 52
|  | 20 | 24.54% | 11.28 | 5.62 | 8.91 | 60 | 42.22 | 50.93
|  | 21 | 5.245% | 10.25 | ER | 1.88 | 55.12 | 36.69 | 39.65
|  | 22 | 17.07% | 11.08 | ER | 6.11 | 60.62 | 35.33 | 47.89
|  | 23 | 20.42% | 10.92 | ER | 7.12 | 59.25 | 36.84 | 48.99
|  | 24 | 24.81% | 10.57 | 0 | 8.55 | 57.4 | 0 | 50.49
|  | 25 | 23.85% | 14.47 | ER | 8.62 | 71.9 | 36.33 | 51.23
|  | 26 | 5.92% | 10.99 | ER | 2.17 | 57.74 | 36.89 | 40.65
|  | 27 | 24.28% | 11.8 | ER | 8.59 | 63.78 | 0 | 52.57
|  | 28 | 20.29% | 11.53 | ER | 7.01 | 62.32 | 36.94 | 48.83
|  | 29 | 24.92% | 10.87 | 5.5 | 8.54 | 59.21 | 42.37 | 50.73
|  | 30 | 24.66% | 11.01 | 5.48 | 8.56 | 58.11 | 42.14 | 50.18
|  | 31 | 5.424% | 9.33 | ER | 1.89 | 51.78 | 36.68 | 39.91
|  | TOTAL | 531.4% | 352.44 | 47.69 | 203.15 | 1936.04 | 1043.75 | 1494.57
|  | AVERAGE | 17.71% | 11.369 | 5.2989 | 6.7717 | 62.4529 | 35.9914 | 48.2119
|  | MAXIMUM | 25.41% | 14.47 | 7.15 | 10.65 | 71.9 | 46.58 | 59.14
|  | MINIMUM | 1.361% | 0 | 0 | 0.6 | 51.78 | 0 | 29.81
PAGE 17
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
INJECTION WELL SUMMARY
RUN DATE
2026-07-30
| JULY | INFLUENT | EFFLUENT | EFFLUENT | IW-1 | IW-2 | IW-3 | IW-4 | IW-5 | TOTAL
| 2005 | FLOW | FLOW | SS | LBS SS | LBS SS | LBS SS | LBS SS | LBS SS | LBS SS
|  | MGD | MGD
| 1 | 49.948 | 49.581 | 15 | 1617.543 | 1648.818 | 1529.973 | 1317.303 | 103.833 | 4900.167
| 2 | 49.161 | 48.851 | 24 | 602.4816 | 2708.1648 | 2489.9904 | 2037.6288 | 1799.4384 | 7600.0752
| 3 | 46.028 | 46.301 | 10 | 880.704 | 66.72 | 947.424 | 954.096 | 888.21 | 2783.058
| 4 | 43.113 | 42.618 | 7 | 516.0792 | 498.5652 | 157.0422 | 636.342 | 597.2274 | 1768.914
| 5 | 41.832 | 41.112 | 2 | 176.808 | 144.9492 | 132.606 | 42.7008 | 166.9668 | 621.33
| 6 | 39.882 | 39.364 | 17 | 1436.2314 | 1468.8408 | 1147.0002 | 1134.24 | 313.3338 | 4365.4062
| 7 | 38.595 | 38.886 | 15 | 268.965 | 1353.582 | 1259.757 | 1053.342 | 940.752 | 3823.056
| 8 | 37.95 | 38.774 | 16 | 1107.552 | 317.5872 | 1341.072 | 1354.416 | 1052.8416 | 3819.0528
| 9 | 43.366 | 42.952 | 18
| 10 | 45.664 | ER | 16 | 791.2992 | 804.6432 | 772.6176 | 9.3408 | 744.5952 | 3113.1552
| 11 | 44.078 | 43.248 | 19 | 1796.9364 | 1834.9668 | 1739.8908 | 1386.525 | 95.076 | 5466.87
| 12 | 42.214 | 42.338 | 12 | 243.1944 | 1183.9464 | 1094.8752 | 909.7272 | 810.648 | 3332.664
| 13 | 41.078 | 41.237 | 13 | 945.4224 | 295.9866 | 1159.0098 | 1182.8622 | 894.465 | 3294.8838
| 14 | 38.746 | 38.906 | 23 | 1743.6438 | 1565.2512 | 337.6032 | 1969.9914 | 1837.6356 | 5484.1338
| 15 | 37.233 | 37.434 | 12 | 993.7944 | 817.6536 | 751.6008 | 238.1904 | 946.7568 | 3509.8056
| 16 | 36.901 | 36.237 | 21 | 1655.073 | 1693.6038 | 1327.5612 | 1304.793 | 369.5454 | 5045.7834
| 17 | 35.84 | 35.257 | 5 | 83.4 | 407.409 | 380.721 | 317.337 | 283.143 | 1154.673
| 18 | 35.627 | 36.477 | 40 | 2598.744 | 750.6 | 3149.184 | 3199.224 | 2475.312 | 8973.84
| 19 | 36.04 | 36.061 | 27 | 1763.1594 | 1731.6342 | 475.1298 | 2154.9726 | 2022.1164 | 5992.0398
| 20 | 36.307 | 35.356 | 18 | 1391.6124 | 1175.4396 | 1079.3628 | 316.7532 | 1337.5692 | 4983.984
| 21 | 35.846 | 35.105 | 14 | 1062.516 | 1092.8736 | 869.862 | 862.8564 | 219.5088 | 3244.7604
| 22 | 35.792 | 36.225 | 9 | 181.6452 | 765.612 | 714.5712 | 604.9836 | 458.6166 | 2120.445
| 23 | 34.863 | 34.975 | 23 | 1419.468 | 420.0858 | 1737.8892 | 1760.9076 | 1365.7584 | 4943.2014
| 24 | 34.458 | 34.164 | 8 | 605.1504 | 556.4448 | 2.0016 | 607.152 | 570.456 | 1734.0528
| 25 | 36.143 | 35.414 | 20 | 1562.916 | 1321.056 | 1214.304 | 395.316 | 1437.816 | 5536.092
| 26 | 36.655 | 36.016 | 8 | 625.8336 | 639.1776 | 499.7328 | 491.0592 | 144.7824 | 1909.5264
| 27 | 35.382 | 34.656 | 3 |  | 244.9458 | 225.18 |  | 214.9218
| 28 | 34.551 | 34.417 | 11 | 673.3716 | 194.4888 | 818.3208 | 831.1644 | 643.0974 | 2329.2786
| 29 | 34.272 | 34.212 | 13 | 803.3922 | 786.045 | 217.9242 | 983.3694 | 925.9068 | 2733.2682
| 30 | 34.708 | 33.715 | 10 | 740.592 | 620.496 | 572.958 | 168.468 | 713.904 | 2647.95
| 31 | 34.844 | 33.842 | 18 | 1321.056 | 1349.5788 | 1073.358 | 1061.3484 | 283.7268 | 4027.7196
| TOTAL | 1207.117 | 1153.731 | 467 | 29608.5846 | 28459.1658 | 29218.5228 | 29286.4104 | 24657.9606 | 111259.1862
| AVERAGE | 38.9393 | 38.4577 | 15.0645 | 1020.9857 | 948.6389 | 973.9508 | 1009.8762 | 821.932 | 3836.5237
PAGE 18
CITY OF FORT LAUDERDALE PUBLIC SERVICES DEPARTMENT
GEORGE T. LOHMEYER REGIONAL WASTEWATER TREATMENT FACILITY
MONTHLY OPERATIONAL REPORT
| RUN DATE |  |  |  | SOLIDS REMOVAL INVENTORY DATA SHEET
2026-07-30
| JULY | TONS | CAKE |  |  |  | JULY | RAGS | GRIT | OTHER
| 2005 | SLUDGE | TSS |  |  |  | 2005 |  |  | (vac)
| 1st - 7th | [5 empty] | 1st - 7th
| 1 | 88 |  |  |  |  | 1 | 10 | 10
| 2 | 0 |  |  |  |  | 2
| 3 | 0 |  |  |  |  | 3
| 4 | 0 |  |  |  |  | 4
| 5 | 44 | 17.15 |  |  |  | 5
| 6 | 110 | 17.73 |  |  |  | 6
| 7 | 110 | 18.42 |  |  |  | 7
| TOTAL = | 352 | 17.7667 | = AVG. |  |  | TOTAL = | 10 | 10 | 0
| 8th - 14th | [5 empty] | 8th - 14th
| 8 | 88 |  |  |  |  | 8 |  | 10
| 9 | 0 |  |  |  |  | 9
| 10 | 0 | 18.01 |  |  |  | 10
| 11 | 88 | 17.78 |  |  |  | 11
| 12 | 88 | 18.39 |  |  |  | 12
| 13 | 88 | 20.55 |  |  |  | 13
| 14 | 88 | 20.37 |  |  |  | 14
| TOTAL = | 440 | 19.02 | = AVG. |  |  | TOTAL = | 0 | 10 | 0
| 15th - 22nd | [5 empty] | 15th-22nd
| 15 | 44 |  |  |  |  | 15 |  | 10
| 16 | 0 |  |  |  |  | 16
| 17 | 0 | 17.12 |  |  |  | 17
| 18 | 88 | 18.13 |  |  |  | 18
| 19 | 66 | 18.68 |  |  |  | 19
| 20 | 75 | 18.81 |  |  |  | 20
| 21 | 88 | 18.76 |  |  |  | 21
| 22 | 66 |  |  |  |  | 22
| TOTAL = | 427 | 18.3 | = AVG. |  |  | TOTAL = | 0 | 10 | 0
| 23rd - 31st | [5 empty] | 23rd-31st
| 23 | 0 |  |  |  |  | 23
| 24 | 0 | 17.22 |  |  |  | 24
| 25 | 88 | 18.2 |  |  |  | 25 |  | 10
| 26 | 88 | 18.47 |  |  |  | 26
| 27 | 88 | 17.91 |  |  |  | 27
| 28 | 88 | 17.8 |  |  |  | 28 |  | 10
| 29 | 88 |  |  |  |  | 29
| 30 | 0 |  |  |  |  | 30
| 31 | 0 | 17.01 |  |  |  | 31
| TOTAL = | 440 | 17.7683 | = AVG. |  |  | TOTAL = | 0 | 20 | 0
RAGS & GRIT go to Central LandFill
Other(VAC) go to BCSR
PAGE 19

## INJECTION PAGES
|  |  |  | UNDERGROUND INJECTION CONTROL | [10 empty] | UNDERGROUND INJECTION CONTROL | [10 empty] | UNDERGROUND INJECTION CONTROL
[15 empty] | MONTHLY OPERATING REPORT | [10 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES |  |  |  |  | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES |  |  |  |  | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [10 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [10 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-1 | [7 empty] | Wet Well Description: |  |  | Effuent Wet Well for IW-1, IW-2, IW3, IW-4 and IW-5 | [7 empty] | Monitoring Well Decription: |  |  | UPPER ZONE OF MONITORING WELL MW-1
Permit #: |  | 0054569-142-UO |  |  |  |  | Date of Issuance: |  | 2004-01-07 |  | Facility ID #: |  | 5006M02066 |  |  |  | Permit Number: |  |  | FLA041378 |  | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | 0054569-142-UO
[22 empty] | Monitoring Well ID #: |  |  | 5006A11311
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2009-01-06 | [7 empty] | Issue Date: |  |  | 1999-10-18 |  | As Identified in Permit: |  | Monitor Well MW-1 Upper Monitor Zone |  |  |  | Issue Date: |  |  | 2004-01-07
[22 empty] | Monitoring Well Interval: |  |  | 1288' to 1320'
Injection Well ID #: |  | 5006A11308 | [8 empty] | Wet Well ID #: |  | Well Facility U-001 |  |  |  | Expiration Date: |  |  | 2004-10-17 |  | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.7 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24 | Associated Injection Well(s):
Injection Interval: |  |  | 2799' to 3513' | [18 empty] | 500A11311 |  |  | INJECTION WELL IW-5
[11 empty] | Injection Well ID #: |  |  | Injection Well Description
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s): | [10 empty] | 5006A11308 |  |  | INJECTION WELL IW-1
[11 empty] | 5006A11309 |  |  | INJECTION WELL IW-2 | [7 empty] | REPORT MONTH / YEAR: |  | 2005-07-01 | DATE OF SAP / RECORDING: |  |  | 2005-07-05 | 2005-07-12 | 2005-07-19 | 2005-07-26
Monitoring Zone ID #: | [5 empty] | Description |  |  |  |  | 5006A11310 |  |  | INJECTION WELL IW-3
[11 empty] | N/A |  |  | INJECTION WELL IW-4 | [7 empty] | OPERATOR'S NAME: |  |  | McGEARY, J.
UO-06-279401 |  | UPPER ZONE OF MONITORING WELL MW-2 | [8 empty] | 5006A11311 |  |  | INJECTION WELL IW-5
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4545-A
UO-06-279401 |  | LOWER ZONE OF MONITORING WELL MW-2
[11 empty] | THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [10 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [10 empty] | REPORT MONTH / YEAR: |  | 2005-07-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous |  |  | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2005-07-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous |  |  | OPERATOR'S NAME: |  |  | McGEARY, J.
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
OPERATOR'S NAME: |  |  | McGEARY, J. | [7 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4545-A | [7 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4545-A | [7 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: |  |  |  | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 49.52 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 39.85 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: |  |  |  | PARAMETER |  |  |  | Sampling Frequency |  |  |  | VALUE |  | UNITS | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 47.742 | PSIG
[11 empty] | Nitrogen, Total as N |  |  |  |  | Daily/Monthly Average |  |  | 11.7814 |  | mg/L as N | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[11 empty] | Nitrogen, Nitrate, Total as N |  |  |  |  | Daily/Monthly Average |  |  | 0.32786 |  | mg/L as N | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7652.25 | mg/l
Total monthly flow | [7 empty] | 229.47 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 3725 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [7 empty] | Nitrogen, Total Kjeildahl as N |  |  |  |  | Daily/Monthly Average |  |  | 11.4536 |  | mg/L as N | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.9 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 14.88 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.0075 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 70.2 |  | PSIG | pH |  |  |  |  | Daily/Monthly Average |  |  | 6.6032 |  | s.u. | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7.6925 | Std units
Monthly average of the daily flow rates | [7 empty] | 7.9128 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 13005 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 11.8069 |  | MG | Phosphorus, Total as P |  |  |  |  | Daily/Monthly Average |  |  | 1.0346 |  | mg/L as P | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 2.399 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 76 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [10 empty] | Total Dissolved Solids (TDS) |  |  |  |  | Daily/Monthly Average |  |  | 1117.0645 |  | mg/L | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.0095 | mg/l
Monthly average pressure | [7 empty] | 48.1565 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 937.25 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 35.24 |  | PSIG | Residue, Total filterable (TSS dried at 180 C) |  |  |  |  | Daily/Monthly Average |  |  | 15.0645 |  | mg/L | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[11 empty] | Specific Conductance (Temperature Compensated) |  |  |  |  | Daily/Monthly Average |  |  | 2322.1613 |  | umhos/cm | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just | [6 empty] | Temperature, Water |  |  |  |  | Daily/Monthly Average |  |  | 86.1387 |  | deg C
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [9 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just |  |  | Date: |  |  |  |  | (Signature):
[12 empty] | (Signature): | [10 empty] | Date:
|  |  |  | UNDERGROUND INJECTION CONTROL | [21 empty] | UNDERGROUND INJECTION CONTROL
|  |  |  | MONTHLY OPERATING REPORT | [21 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES | [15 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [21 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-2 | [18 empty] | Monitoring Well Decription: |  |  | LOWER ZONE OF MONITORING WELL MW-1
Permit #: |  | 0054569-142-UO |  |  |  |  | Date of Issuance: |  | 2004-01-07 | [12 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | 0054569-142-UO
[22 empty] | Monitoring Well ID #: |  |  | 5006A11311
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2009-01-06 | [12 empty] | As Identified in Permit: |  | Monitor Well MW-1 Lower Monitor Zone |  |  |  | Issue Date: |  |  | 2004-01-07
[22 empty] | Monitoring Well Interval: |  |  | 1449' to 1557'
Injection Well ID #: |  | 5006A11309 | [19 empty] | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.7 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24
Injection Interval: |  |  | 2798' to 3518' | [18 empty] | 500A11311 |  |  | INJECTION WELL IW-5
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s):
[22 empty] | REPORT MONTH / YEAR: |  | 2005-07-01 | DATE OF SAP / RECORDING: |  |  | 2005-07-05 | 2005-07-12 | 2005-07-19 | 2005-07-26
Monitoring Zone ID #: | [5 empty] | Description
[22 empty] | OPERATOR'S NAME: |  |  | McGEARY, J.
UO-06-279401 |  | UPPER ZONE OF MONITORING WELL MW-2
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4545-A
UO-06-279401 |  | LOWER ZONE OF MONITORING WELL MW-2
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [21 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2005-07-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
OPERATOR'S NAME: |  |  | McGEARY, J. | [18 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 20 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4545-A | [18 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 47.47 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 38.52 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: | [14 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 43.0133 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 9817.75 | mg/l
Total monthly flow | [7 empty] | 237.19 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 4975 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [18 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 8.225 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 16.01 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 9.85 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 71.6 |  | PSIG | [11 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7.4225 | Std units
Monthly average of the daily flow rates | [7 empty] | 7.9063 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 14697.5 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 11.7395 |  | MG | [11 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 2.399 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 76.75 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [21 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.0095 | mg/l
Monthly average pressure | [7 empty] | 48.4606 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 837.75 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 35.79 |  | PSIG | [11 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [21 empty] | (Signature):
Date:
|  |  |  | UNDERGROUND INJECTION CONTROL | [21 empty] | UNDERGROUND INJECTION CONTROL
|  |  |  | MONTHLY OPERATING REPORT | [21 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES | [15 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [21 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-3 | [18 empty] | Monitoring Well Decription: |  |  | UPPER ZONE OF MONITORING WELL MW-2
Permit #: |  | 0054569-142-UO |  |  |  |  | Date of Issuance: |  | 2004-01-07 | [12 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | 0054569-142-UO
[22 empty] | Monitoring Well ID #: |  |  | 5006A11308 & 309
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2009-01-06 | [12 empty] | As Identified in Permit: |  | Monitor Well MW-2 Upper Monitor Zone |  |  |  | Issue Date: |  |  | 2004-01-07
[22 empty] | Monitoring Well Interval: |  |  | 1300' to 1344'
Injection Well ID #: |  | 5006A11310 | [19 empty] | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.7 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24
Injection Interval: |  |  | 2800' to 3977' | [18 empty] | 5006A11308 |  |  | INJECTION WELL IW-1
[22 empty] | 5006A11309 |  |  | INJECTION WELL IW-2
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s):
[22 empty] | REPORT MONTH / YEAR: |  | 2005-07-01 | DATE OF SAP / RECORDING: |  |  | 2005-07-05 | 2005-07-12 | 2005-07-19 | 2005-07-26
Monitoring Zone ID #: | [5 empty] | Description
[22 empty] | OPERATOR'S NAME: |  |  | McGEARY, J.
UO-06-279510 |  | UPPER ZONE OF MONITORING WELL MW-3
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4545-A
UO-06-279510 |  | LOWER ZONE OF MONITORING WELL MW-3
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [21 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2005-07-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
OPERATOR'S NAME: |  |  | McGEARY, J. | [18 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4545-A | [18 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 34.01 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 26.65 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: | [14 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 31.22 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7437.25 | mg/l
Total monthly flow | [7 empty] | 232.78 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 3687.5 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [18 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.88 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 14.5 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.125 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 73 |  | PSIG | [11 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7.9825 | Std units
Monthly average of the daily flow rates | [7 empty] | 7.7593 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 11917.5 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 11.4471 |  | MG | [11 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 2.399 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 74.5 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [21 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.01 | mg/l
Monthly average pressure | [7 empty] | 50.1342 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 881.5 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 36.59 |  | PSIG | [11 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [21 empty] | (Signature):
Date:
|  |  |  | UNDERGROUND INJECTION CONTROL | [21 empty] | UNDERGROUND INJECTION CONTROL
|  |  |  | MONTHLY OPERATING REPORT | [21 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES | [15 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [21 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-4 | [18 empty] | Monitoring Well Decription: |  |  | LOWER ZONE OF MONITORING WELL MW-2
Permit #: |  | 0054569-142-UO |  |  |  |  | Date of Issuance: |  | 2004-01-07 | [12 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | 0054569-142-UO
[22 empty] | Monitoring Well ID #: |  |  | 5006A11308 & 309
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2009-01-06 | [12 empty] | As Identified in Permit: |  | Monitor Well MW-2 Lower Monitor Zone |  |  |  | Issue Date: |  |  | 2004-01-07
[22 empty] | Monitoring Well Interval: |  |  | 1970' to 2025'
Injection Well ID #: |  | N/A | [19 empty] | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.7 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24
Injection Interval: |  |  | 2804' to 3977' | [18 empty] | 5006A11308 |  |  | INJECTION WELL IW-1
[22 empty] | 5006A11309 |  |  | INJECTION WELL IW-2
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s):
[22 empty] | REPORT MONTH / YEAR: |  | 2005-07-01 | DATE OF SAP / RECORDING: |  |  | 2005-07-05 | 2005-07-12 | 2005-07-19 | 2005-07-26
Monitoring Zone ID #: | [5 empty] | Description
[22 empty] | OPERATOR'S NAME: |  |  | McGEARY, J.
UO-06-279510 |  | UPPER ZONE OF MONITORING WELL MW-3
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4545-A
UO-06-279510 |  | LOWER ZONE OF MONITORING WELL MW-3
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [21 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2005-07-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
OPERATOR'S NAME: |  |  | McGEARY, J. | [18 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 21 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4545-A | [18 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 43.56 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 33.94 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: | [14 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 41.74 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 32887.5 | mg/l
Total monthly flow | [7 empty] | 220.66 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 17750 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [18 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.35 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 14.91 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.725 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 73.4 |  | PSIG | [11 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7.5 | Std units
Monthly average of the daily flow rates | [7 empty] | 7.609 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 46375 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 11.3102 |  | MG | [11 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 2.399 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 74.5 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [21 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.01 | mg/l
Monthly average pressure | [7 empty] | 51.4021 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 3047.5 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 36.81 |  | PSIG | [11 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [21 empty] | (Signature):
Date:
|  |  |  | UNDERGROUND INJECTION CONTROL | [21 empty] | UNDERGROUND INJECTION CONTROL
|  |  |  | MONTHLY OPERATING REPORT | [21 empty] | MONTHLY OPERATING REPORT
Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES | [15 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
[6 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY | [21 empty] | GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
Injection Well Description: |  |  | INJECTION WELL IW-5 | [18 empty] | Monitoring Well Decription: |  |  | UPPER ZONE OF MONITORING WELL MW-3
Permit #: |  | 0054569-142-UO |  |  |  |  | Date of Issuance: |  | 2004-01-07 | [12 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | 0054569-142-UO
[22 empty] | Monitoring Well ID #: |  |  | 5006A11310
Facility ID #: |  | 5006M02066 |  |  |  |  | Expiration Date: |  | 2009-01-06 | [12 empty] | As Identified in Permit: |  | Monitor Well MW-3 Upper Monitor Zone |  |  |  | Issue Date: |  |  | 2004-01-07
[22 empty] | Monitoring Well Interval: |  |  | 1300' to 1349'
Injection Well ID #: |  | 5006A11311 | [19 empty] | Associated Injection Well(s):
Permitted Peak Hourly Flow Rate, MGD: |  |  |  | 18.7 |  | MAX Permitted Inj Pressure, PSIG: |  |  |  | 99 | [11 empty] | Injection Well ID #: |  |  | Injection Well Description
[6 empty] | Casing Diameter , Inches: |  |  |  | 24
Injection Interval: |  |  | 2818' to 3462' | [18 empty] | 5006A11310 |  |  | INJECTION WELL IW-3
[22 empty] | N/A |  |  | INJECTION WELL IW-4
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
Associated Monitoring Zone(s):
[22 empty] | REPORT MONTH / YEAR: |  | 2005-07-01 | DATE OF SAP / RECORDING: |  |  | 2005-07-05 | 2005-07-12 | 2005-07-19 | 2005-07-26
Monitoring Zone ID #: | [5 empty] | Description
[22 empty] | OPERATOR'S NAME: |  |  | McGEARY, J.
UO-06-279512 |  | UPPER ZONE OF MONITORING WELL MW-1
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4545-A
UO-06-279512 |  | LOWER ZONE OF MONITORING WELL MW-1
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE: | [21 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
REPORT MONTH / YEAR: |  | 2005-07-01 |  | SAMPLING / RECORDING: |  |  |  | Continuous
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
OPERATOR'S NAME: |  |  | McGEARY, J. | [18 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
OPERATOR'S LICENSE NO: |  |  | CO# 4545-A | [18 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 34.1 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 17.98 | PSIG
OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL: | [14 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 31.3633 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
PARAMETER | [7 empty] | VALUE |  | UNITS | [11 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7918.25 | mg/l
Total monthly flow | [7 empty] | 203.15 |  | MG | [11 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 3687.5 | mg/l
Daily flow rate |  |  | (See page "Daily Sample Results - Part B, DEP form 62-620.910(10) | [18 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0.8875 | mg/l
Daily maximum sustained flow rate (max of month) | [7 empty] | 14.47 |  | MGD | [11 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 1.4175 | mg/l
Daily maximum sustained pressure (psig max of month) | [7 empty] | 71.9 |  | PSIG | [11 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 8.2125 | Std units
Monthly average of the daily flow rates | [7 empty] | 6.7717 |  | MGD | [11 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 11990 | umho/cm
Monthly maximum of daily flow rates (MG), with peak hour flow (MGD) | [7 empty] | 10.1984 |  | MG | [11 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
of the month with the maximum flow = |  |  |  | 2.399 | MG/hour multiplied by | [16 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 72.25 | deg. F
the % of average % of TOTAL RAW FLOW to each Injection well. | [21 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.01 | mg/l
Monthly average pressure | [7 empty] | 48.2119 |  | PSIG | [11 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 926 | mg/l
Monthly Well-Head Pressure with No Flow (Sustained) | [7 empty] | 36.56 |  | PSIG | [11 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
| Date: | [21 empty] | (Signature):
Date:
UNDERGROUND INJECTION CONTROL
MONTHLY OPERATING REPORT
[22 empty] | Facility name: | [5 empty] | CITY OF FORT LAUDERDALE PUBLIC SERVICES
GEORGE T. LOHMEYER REGIONAL WASTEWATER FACILITY
[22 empty] | Monitoring Well Decription: |  |  | LOWER ZONE OF MONITORING WELL MW-3
[22 empty] | Facility ID #: |  |  | 5006M02066 |  |  | Permit Number: |  |  | 0054569-142-UO
[22 empty] | Monitoring Well ID #: |  |  | 5006A11310
[22 empty] | As Identified in Permit: |  | Monitor Well MW-3 Lower Monitor Zone |  |  |  | Issue Date: |  |  | 2004-01-07
[22 empty] | Monitoring Well Interval: |  |  | 1970 to 2027'
Associated Injection Well(s):
[22 empty] | Injection Well ID #: |  |  | Injection Well Description
[22 empty] | 5006A11310 |  |  | INJECTION WELL IW-3
[22 empty] | N/A |  |  | INJECTION WELL IW-4
THE FOLLOWING IS TO BE COMPLETED BY THE PERMITEE:
[22 empty] | REPORT MONTH / YEAR: |  | 2005-07-01 | DATE OF SAP / RECORDING: |  |  | 2005-07-05 | 2005-07-12 | 2005-07-19 | 2005-07-26
[22 empty] | OPERATOR'S NAME: |  |  | McGEARY, J.
[22 empty] | OPERATOR'S LICENSE NO: |  |  | CO# 4545-A
[22 empty] | OPERATOR'S PHONE: |  | (954) 523-1002 |  | FAX: | (954) 468-1577 |  | E-MAIL:
[22 empty] | Physical Characteristics |  |  |  | Recording |  |  | Reporting
[22 empty] | Parameter |  |  |  | Frequency |  |  | Requirements |  | VALUE | UNITS
[22 empty] | Daily maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
[22 empty] | Daily minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
[22 empty] | Daily average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | SEE PAGE 22 of MOR
[22 empty] | Monthly maximum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 46.33 | PSIG
[22 empty] | Monthly minimum sustained pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 35.78 | PSIG
[22 empty] | Monthly average pressure |  |  |  | Continuous |  |  | Daily AVG/Monthly AVG of Daily |  | 44.275 | PSIG
[22 empty] | Chemical Characteristics |  |  |  |  | Recording |  | Reporting
[22 empty] | Parameters |  |  |  |  | Frequency |  | Requirements |  | VALUE | UNITS
[22 empty] | TDS (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 30451.25 | mg/l
[22 empty] | CHLORIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 16250 | mg/l
[22 empty] | AMMONIA-N (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 2.35 | mg/l
[22 empty] | TKN (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 2 | mg/l
[22 empty] | pH (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 7.5025 | Std units
[22 empty] | CONDUCTIVITY (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 42600 | umho/cm
[22 empty] | FECAL COLIFORM (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 0 | # col/100ml
[22 empty] | TEMPERATURE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 72 | deg. F
[22 empty] | TOTAL PHOSPHOROUS (MONTHLY AVG.) |  |  |  |  | Weekly |  | Monthly |  | 0.0105 | mg/l
[22 empty] | SULFATE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | 2800 | mg/l
[22 empty] | C.O.D. (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | IRON (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  | #DIV/0! | mg/l
[22 empty] | SULFIDE (MONTHLY AVERAGE) |  |  |  |  | Weekly |  | Monthly |  |  | mg/l
[22 empty] | LEAD PLANT OPERATOR (Name:) |  |  |  | Mike Just
(Signature):
Date:

## DEP PART-A FORMS
31 | [5 empty] | Department of Environmental Protection Discharge Monitoring Report - Part A
When Completed mail this report to: Department of Environmental Protection, Southeast District, 400 North Congress Avenue, Suite 200 West Palm Beach, FL, 33401
| PERMITEE NAME: | City of Fort Lauderdale |  |  |  |  | PERMIT NUMBER: |  | FLA041378 |  | REPORT: | Monthly
| MAILING ADDRESS: | 949 NW 38th Street |  |  |  |  | LIMIT: |  | Final |  | GROUP: | Domestic
|  | Fort Lauderdale, FL 33309 |  |  |  |  | CLASS SIZE: |  | N/A |  | GMS TEST SITE
[7 empty] | MONITORING GROUP NUMBER: |  | U-001 |  | NO:
| FACILITY: | City of Fort Lauderdale G. T. Lohmeyer WWTF |  |  |  |  | MONITORING GROUP DESC: |  | Effluent Disposal including Influent
| LOCATION: | 1765 SE 18th Street |  |  |  |  | NO DISCHARGE FROM SITE:
Fort Lauderdale, FL 33316
| COUNTY: | Broward |  |  |  |  | MONITORING PERIOD: | From: | 2005-07-01 |  | To: | 2005-07-31
| Parameter |  | Quantity of Loading |  | Units |  | Quality or Concentration |  | Units | No. Ex. | Frequency of Analysis | Sample Type
| Flow | Sample Measurement | 6.7717 | 10.1984 | [5 empty] | 0
| PARM Code 50050 1 Mon.Site No. EFF-007 | Permit Requirement | Report (Mo. Avg.) | Report (Peak Hour) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
| Flow | Sample Measurement | 7.609 | 11.3102 | [5 empty] | 0
| PARM Code 50050 P Mon.Site No. EFF-006 | Permit Requirement | Report (Mo. Avg.) | Report (Peak Hour) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
| Flow | Sample Measurement | 7.7593 | 11.4471 | [5 empty] | 0
| PARM Code 50050 Q Mon.Site No. EFF-005 | Permit Requirement | Report (Mo. Avg.) | Report (Peak Hour) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
| Flow | Sample Measurement | 7.9063 | 11.7395 | [5 empty] | 0
| PARM Code 50050 R Mon.Site No. EFF-004 | Permit Requirement | Report (Mo. Avg.) | Report (Peak Hour) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
| Flow | Sample Measurement | 7.9128 | 11.8069 | [5 empty] | 0
| PARM Code 50050 S Mon.Site No. EFF-003 | Permit Requirement | Report (Mo. Avg.) | Report (Peak Hour) | mgd | [5 empty] | Continuous | Flow Meters with 24 hour Data Logger
| BOD, Carbonaceous 5 day, 20C | Sample Measurement |  |  |  | 4.6 |  |  |  | 0
| PARM Code 80082 Y Mon.Site No. EFF-002 | Permit Requirement |  |  |  | 20.0 (An.Avg.) |  |  | mg/l |  | Daily | 24-hour FPC
I certify under penalty of law that I have personally examined and am familiar with the informantion submitted herein; and based on my inquiry of those individuals immeadiately responsible for obtaining the information, I believe the submitted
information is true, accurate and complete. I am aware that there are significant penalties for submitting false information including the possiblity of fine and imprisonment.
| NAME/TITLE OF PRINCIPAL EXECUTIVE OFFICER OR AUTHORIZED AGENT |  |  |  | SIGNATURE OF PRINCIPAL EXECUTIVE OFFICER OR AUTHORIZED AGENT |  |  |  |  | TELEPHONE |  | DATE (YY/MM/DD)
954-523-1002 ext 2021
REGIONAL WASTEWATER FACILITIES MANAGER
COMMENTS AND EXPLANATION OF ANY VIOLATIONS (Reference all attachments here):
Version 3/30/05
Discharge Monitoring Report - Part A (Continued)
[13 empty] | FACILITY: | City of Fort Lauderdale G. T. Lohmeyer WWTF | [5 empty] | MONITORING GROUP NUMBER: U-001 |  |  | PERMIT NUMBER: |  | FLA041378
[20 empty] | MONITORING PERIOD: |  | From: | 2005-07-01 | To: | 2005-07-31
[13 empty] | Parameter |  |  | Quantity of Loading |  | Units |  | Quality or Concentration |  | Units | No. Ex. | Frequency of Analysis | Sample Type
[13 empty] | BOD, Carbonaceous 5 day, 20C |  | Sample Measurement |  |  |  | 3.3388 | 3.6469 | 10.33 |  | 0
[13 empty] | PARM Code 80082 1 Mon.Site No. EFF-002 |  | Permit Requirement |  |  |  | 30.0 (Mo.Avg.) | 45.0 (Week.Avg.) | 60.0 (Max.) | mg/l |  | Daily | 24-hour FPC
[13 empty] | Solids, Total Suspended |  | Sample Measurement |  |  |  | 17.2 |  |  |  | 0
[13 empty] | PARM Code 00530 Y Mon.Site No. EFF-002 |  | Permit Requirement |  |  |  | 20.0 (An.Avg.) |  |  | mg/l |  | Daily | 24-hour FPC
[13 empty] | Solids, Total Suspended |  | Sample Measurement |  |  |  | 15.0645 | 15.5429 | 40 |  | 0
[13 empty] | PARM Code 00530 1 Mon.Site No. EFF-002 |  | Permit Requirement |  |  |  | 30.0 (Mo.Avg.) | 45.0 (Week.Avg.) | 60.0 (Max.) | mg/l |  | Daily | 24-hour FPC
[13 empty] | pH |  | Sample Measurement |  |  |  | 6.5 |  |  |  | 0
[13 empty] | PARM Code 00400 1 Mon.Site No. EFF-002 |  | Permit Requirement |  |  |  | 6.0 (Min.) |  |  | s.u. |  | Continuous | Meter
[13 empty] | Flow |  | Sample Measurement | 37.1 | [6 empty] | N/A
[13 empty] | PARM Code 50050 G Mon.Site No. INF-001 |  | Permit Requirement | Report (An.Avg.) |  | mgd | [5 empty] | Continuous | Flow meters and totalizers
[13 empty] | Flow |  | Sample Measurement | 38.9393 | 39.7528 | [5 empty] | 0
[13 empty] | PARM Code 50050 T Mon.Site No. INF-001 |  | Permit Requirement | Report (Mo.Avg.) | 55.7 (3-Mo.Avg.) | mgd | [5 empty] | Continuous | Flow meters and totalizers
[13 empty] | BOD, Carbonaceous 5 day, 20C |  | Sample Measurement |  |  |  | 80.4514 |  |  |  | N/A
[13 empty] | PARM Code 80082 G Mon.Site No. INF-002 |  | Permit Requirement |  |  |  | Report (Mo.Avg.) |  |  | mg/l |  | Daily | 24-hour FPC
[13 empty] | Solids, Total Suspended |  | Sample Measurement |  |  |  | 96.2581 |  |  |  | N/A
[13 empty] | PARM Code 00530 G Mon.Site No. INF-002 |  | Permit Requirement |  |  |  | Report (Mo.Avg.) |  |  | mg/l |  | Daily | 24-hour FPC
[13 empty] | Percent Capacity, (TMADF/Permitted Capacity) x 100 |  | Sample Measurement |  |  |  | 71.37% |  |  |  | 0
[13 empty] | PARM Code 00530 G Mon.Site No. INF-002 |  | Permit Requirement |  |  |  | Report (Mo.Total) |  |  | mg/l |  | PERCENT | Calculated
Version 03/30/05
Formulas:
Monthly = ([FLA041378]-1)+A2

## DEP PART-B FORMS
DAILY SAMPLE RESULTS - B
| Permit Number |  | FLA041378 |  |  | Facility: | City of Fort Lauderdale G. T. Lohmeyer WWTF
| Monitoring Period: |  | From: | 2005-07-01 |  | To: | 2005-07-31
|  | CBOD5 (mg/L | pH (Max) | pH (Min) | TSS (mg/L | Flow (mgd) | Flow (mgd) | Flow (mgd) | Flow (mgd) | Flow (mgd)
Code |  | 80082 | 00400 | 00400 | 00530 | 50050 | 50050 | 50050 | 50050 | 50050
Mon. Site |  | EFF-002 | EFF-002 | EFF-002 | EFF-002 | EFF-003 | EFF-004 | EFF-005 | EFF-006 | EFF-007
1 |  | 2.08 | 6.7 | 6.7 | 15 | 12.93 | 13.18 | 12.23 | 10.53 | 0.83
2 |  | 3.27 | 6.6 | 6.6 | 24 | 3.01 | 13.53 | 12.44 | 10.18 | 8.99
3 |  | 2.93 | 6.6 | 6.6 | 10 | 10.56 | 0.8 | 11.36 | 11.44 | 10.65
4 |  | 2.66 | 6.8 | 6.5 | 7 | 8.84 | 8.54 | 2.69 | 10.9 | 10.23
5 |  | 3.53 | 6.7 | 6.6 | 2 | 10.6 | 8.69 | 7.95 | 2.56 | 10.01
6 |  | 3.03 | 6.7 | 6.6 | 17 | 10.13 | 10.36 | 8.09 | 8 | 2.21
7 |  | 2.43 | 6.7 | 6.5 | 15 | 2.15 | 10.82 | 10.07 | 8.42 | 7.52
8 |  | 3.5 | 6.7 | 6.5 | 16 | 8.3 | 2.38 | 10.05 | 10.15 | 7.89
9 |  | 2.4 | 6.7 | 6.5 | 18 | ER | ER | ER | ER | ER
10 |  | 2 | 6.6 | 6.5 | 16 | 5.93 | 6.03 | 5.79 | 0.07 | 5.58
11 |  | 4.26 | 6.6 | 6.6 | 19 | 11.34 | 11.58 | 10.98 | 8.75 | 0.6
12 |  | 3.95 | 6.6 | 6.5 | 12 | 2.43 | 11.83 | 10.94 | 9.09 | 8.1
13 |  | NR | 6.8 | 6.5 | 13 | 8.72 | 2.73 | 10.69 | 10.91 | 8.25
14 |  | NR | 6.8 | 6.6 | 23 | 9.09 | 8.16 | 1.76 | 10.27 | 9.58
15 |  | 4.62 | 6.7 | 6.6 | 12 | 9.93 | 8.17 | 7.51 | 2.38 | 9.46
16 |  | 2.82 | 6.6 | 6.5 | 21 | 9.45 | 9.67 | 7.58 | 7.45 | 2.11
17 |  | NR | 6.6 | 6.5 | 5 | 2 | 9.77 | 9.13 | 7.61 | 6.79
18 |  | 10.33 | 6.7 | 6.6 | 40 | 7.79 | 2.25 | 9.44 | 9.59 | 7.42
19 |  | 6.63 | 6.7 | 6.5 | 27 | 7.83 | 7.69 | 2.11 | 9.57 | 8.98
20 |  | 2.66 | 6.8 | 6.6 | 18 | 9.27 | 7.83 | 7.19 | 2.11 | 8.91
21 |  | 2.66 | 6.7 | 6.5 | 14 | 9.1 | 9.36 | 7.45 | 7.39 | 1.88
22 |  | NR | 6.5 | 6.7 | 9 | 2.42 | 10.2 | 9.52 | 8.06 | 6.11
23 |  | 3.48 | 6.6 | 6.5 | 23 | 7.4 | 2.19 | 9.06 | 9.18 | 7.12
24 |  | 2.4 | 6.7 | 6.6 | 8 | 9.07 | 8.34 | 0.03 | 9.1 | 8.55
25 |  | 2.66 | 6.6 | 6.5 | 20 | 9.37 | 7.92 | 7.28 | 2.37 | 8.62
26 |  | 2.51 | 6.6 | 6.5 | 8 | 9.38 | 9.58 | 7.49 | 7.36 | 2.17
27 |  | NR | 6.6 | 6.6 | 3 | ER | 9.79 | 9 | ER | 8.59
28 |  | 3 | 6.6 | 6.5 | 11 | 7.34 | 2.12 | 8.92 | 9.06 | 7.01
29 |  | 2 | 6.7 | 6.5 | 13 | 7.41 | 7.25 | 2.01 | 9.07 | 8.54
30 |  | 3 | 6.6 | 6.5 | 10 | 8.88 | 7.44 | 6.87 | 2.02 | 8.56
31 |  | 2 | 6.8 | 6.5 | 18 | 8.8 | 8.99 | 7.15 | 7.07 | 1.89
Total |  | 86.81 | 206.7 | 203 | 467 | 229.47 | 237.19 | 232.78 | 220.66 | 203.15
Mo. Avg. |  | 3.3388 | 6.6677 | 6.5484 | 15.0645 | 7.9128 | 7.9063 | 7.7593 | 7.609 | 6.7717
PLANT STAFFING
Day Shift Operator |  |  | Class: | "A" | Certificate No. | 4545 | Name: |  | McGEARY, J.
Evening Shift Operator |  |  | Class: | "A" | Certificate No. | 4474 | Name: |  | BAYLER, J.
Night Shift Operator |  |  | Class: | "B" | Certificate No. | 5096 | Name: |  | BAROSKY, J.
Lead Operator |  |  | Class: | "A" | Certificate No. | 2769 | Name: |  | JUST, M.
DAILY SAMPLE RESULTS - B
| Permit Number |  | FLA041378 |  |  | Facility: | City of Fort Lauderdale G. T. Lohmeyer WWTF
| Monitoring Period: |  | From: | 2005-07-01 |  | To: | 2005-07-31
|  | Flow (mgd) | CBOD5 (mg/L | TSS (mg/L
Code |  | 50050 | 80082 | 00530
Mon. Site |  | INF-001 | INF-002 | INF-002
1 |  | 49.948 | 69.7 | 48
2 |  | 49.161 | 25.2 | 96
3 |  | 46.028 | 99 | 60
4 |  | 43.113 | ER | 136
5 |  | 41.832 | 21.4 | 70
6 |  | 39.882 | ER | 120
7 |  | 38.595 | ER | 120
8 |  | 37.95 | ER | 90
9 |  | 43.366 | 72.7 | 138
10 |  | 45.664 | ER | 78
11 |  | 44.078 | NR | 54
12 |  | 42.214 | 19.1 | 140
13 |  | 41.078 | NR | 86
14 |  | 38.746 | NR | 96
15 |  | 37.233 | 72.75 | 104
16 |  | 36.901 | 63.1 | 100
17 |  | 35.84 | NR | 86
18 |  | 35.627 | 98.38 | 114
19 |  | 36.04 | 126.9 | 136
20 |  | 36.307 | 73.7 | 118
21 |  | 35.846 | 84.1 | 106
22 |  | 35.792 | 97.9 | 54
23 |  | 34.863 | 93.5 | 98
24 |  | 34.458 | 89.2 | 64
25 |  | 36.143 | 94.5 | 112
26 |  | 36.655 | 84.8 | 102
27 |  | 35.382 | 85 | 80
28 |  | 34.551 | 99 | 94
29 |  | 34.272 | 89 | 88
30 |  | 34.708 | 114 | 102
31 |  | 34.844 | 97 | 94
Total |  | 1207.117 | 1769.93 | 2984
Mo. Avg. |  | 38.9393 | 80.4514 | 96.2581

## JULIAN CONVERT
2005-07-01 | 38534 | 1999-01-01 | 2373
FROM DATE ON "DATA INPUT" PAGE | [5 empty] | 2005-07-01
2005
MONTHYY.PAR RANGE TO COMPILE (JULIAN DAY VALUES) FOR SPLIT PROGRAM ARE | [7 empty] | 182 | THROUGH | 2405
|  | 7 | JULY
[5 empty] | 2005-07-01 | 2005-07-01 | 7
2005-07-01 |  |  |  |  | 1 | JANUARY |  | 1995 | 1995-01-01
[5 empty] | 2 | FEBRUARY |  | 1996 | 1996-01-01
[5 empty] | 3 | MARCH |  | 1997 | 1997-01-01
JULY |  | 1 |  | 3 | 4 | APRIL |  | 1998 | 1998-01-01
|  | 0 |  | 0 | 5 | MAY |  | 1999 | 1999-01-01
|  | 0 |  |  | 6 | JUNE |  | 2000 | 2000-01-01
|  | 0 |  |  | 7 | JULY |  | 2001 | 2001-01-01
|  | 0 |  | 0 | 8 | AUGUST |  | 2002 | 2002-01-01
|  |  |  | 3 | 9 | SEPTEMBER |  | 2003 | 2003-01-01
[5 empty] | 10 | OCTOBER |  | 2004 | 2004-01-01
[5 empty] | 11 | NOVEMBER |  | 2005 | 2005-01-01
2005 |  |  |  |  | 12 | DECEMBER |  | 2006 | 2006-01-01
38534 | [6 empty] | JULY | 2007 | 2007-01-01
38353 | [7 empty] | 2008 | 2008-01-01
181 | 1 |  | 1 | 182 | Friday
| 2 |  | 2 | 183 | Saturday
| 3 |  | 3 | 184 | Sunday
| 4 |  | 4 | 185 | Monday
| 5 |  | 5 | 186 | Tuesday
| 6 |  | 6 | 187 | Wednesday
| 7 |  | 7 | 188 | Thursday
| 8 |  | 8 | 189 | Friday
| 9 |  | 9 | 190 | Saturday
| 10 |  | 10 | 191 | Sunday
| 11 |  | 11 | 192 | Monday
| 12 |  | 12 | 193 | Tuesday
| 13 |  | 13 | 194 | Wednesday
| 14 |  | 14 | 195 | Thursday
| 15 |  | 15 | 196 | Friday
| 16 |  | 16 | 197 | Saturday
| 17 |  | 17 | 198 | Sunday
| 18 |  | 18 | 199 | Monday
| 19 |  | 19 | 200 | Tuesday
| 20 |  | 20 | 201 | Wednesday
| 21 |  | 21 | 202 | Thursday
| 22 |  | 22 | 203 | Friday
| 23 |  | 23 | 204 | Saturday
| 24 |  | 24 | 205 | Sunday
| 25 |  | 25 | 206 | Monday
| 26 |  | 26 | 207 | Tuesday
| 27 |  | 27 | 208 | Wednesday
| 28 |  | 28 | 209 | Thursday
| 29 |  | 29 | 210 | Friday
| 30 |  | 30 | 211 | Saturday
| 31 |  | 31 | 212 | Sunday
31