## Sheet1
SGF-1 PUMP TEST
72-Hour Constant Rate
Sawgrass Floridan Test Well Construction
City of Sunrise, Florida
Date | Time | Time |  |  | Elapse Time | Elapse Time | Pump Rate | Totalizer X1000 | Volume Pumped | Trans | Depth to Water | Draw- down | Sand in Rossum |  |  | Sand Content | Comments | Conductivity | Temperature | pH | H2S | Chloride | Turbidity | Sulfate | SDI
|  | hr | min | sec | min | hr | gpm | gallons | gallons |  | ft bgl |  | mL |  |  | ppm | [8 empty] | 15 min
2012-11-26 |  | 0 | 0 | 0 | 0 | 0 |  | 47046 | 0 | 138.6 | -38.6 | 0 | 0 |  |  |  | open valve
2012-11-26 |  | 0 | 2 | 30 | 2.5 | 0.041667 | [10 empty] | Begin Rossum Testing
2012-11-26 | 8:57 | 0 | 3 | 0 | 3 | 0.05 | 1391 | [9 empty] | Increase Rate
2012-11-26 |  | 0 | 4 | 30 | 4.5 | 0.075 | 1460 | [7 empty] | 0 | 0 | Start Rossum Sand Testing
2012-11-26 |  | 0 | 6 | 0 | 6 | 0.1 | 1444 | 47054 | 8000 | 108.5 | -8.5 | 30.1 | few grains | 0.0001 | 1.5 | 0.035223
2012-11-26 |  | 0 | 9 | 0 | 9 | 0.15 | 1430 | 47059 | 13000
2012-11-26 |  | 0 | 9 | 30 | 9.5 | 0.15833 | [10 empty] | Increase Rate; Begin SDI Test
2012-11-26 | 9:05 | 0 | 11 | 0 | 11 | 0.18333 | 1464 | 47062 | 16000 | 106 | -6 | 32.6 | few grains | 0.0001 | 6.5 | 0.0081284 | Complete increasing rate
2012-11-26 |  | 0 | 15 | 0 | 15 | 0.25 | 1451 | 47067 | 21000 | 105.5 | -5.5 | 33.1 | <0.01 | 0.005 | 10.5 | 0.25159
2012-11-26 |  | 0 | 20 | 0 | 20 | 0.33333 | 1445 | 47074 | 28000 | 104.5 | -4.5 | 34.1 |  |  |  |  | Increase rate to 1,458 gpm
2012-11-26 |  | 0 | 27 | 0 | 27 | 0.45 | [10 empty] | SDI: 2.4(5min), 2.3(10min), 2.0 (15 min)
2012-11-26 | 9:24 | 0 | 30 | 0 | 30 | 0.5 | 1457 | 47089 |  | 102.9 | -2.9 | 35.7 | 0.02 | 0.02 | 25.5 | 0.41439 | Was 1,445 gpm, Increase R.
2012-11-26 | 9:34 | 0 | 40 | 0 | 40 | 0.66667 | 1458 | 47103 |  | 101.7 | -1.7 | 36.9 | 0.04 | 0.04 | 35.5 | 0.59532
2012-11-26 | 9:47 | 0 | 53 | 0 | 53 | 0.88333 | 1445 | 47122 | 76000 | 100.6 | -0.6 | 38 | 0.05 | 0.05 | 48.5 | 0.54469
2012-11-26 |  | 1 | 15 | 0 | 75 | 1.25 | 1443 | 47154 |  | 99.3 | 0.7 | 39.3 | 0.07 | 0.07 | 70.5 | 0.5246
2012-11-26 | 10:30 | 1 | 36 | 0 | 96 | 1.6 | 1453 | 47189 |  | 98.138 | 1.862 | 40.462 | 0.07 | 0.07 | 91.5 | 0.4042
2012-11-26 |  | 1 | 45 | 0 | 105 | 1.75 | 1456 | 47198 |  | 97.8 | 2.2 | 40.8 | 0.11 | 0.11 | 100.5 | 0.57829
2012-11-26 | 11:03 | 2 | 10 | 0 | 130 | 2.1667 | 1448 | 47234 | 188000 | 97.16 | 2.84 | 41.44 | 0.12 | 0.12 | 125.5 | 0.50519
2012-11-26 | 11:30 | 2 | 33 | 0 | 153 | 2.55 | 1455 | 47269 | 223000 | 96.136 | 3.864 | 42.464 | 0.13 | 0.13 | 148.5
2012-11-26 | 12:30 | 3 | 31 | 0 | 211 | 3.5167 | 1452 | 47353 | 307000 | 95.123 | 4.877 | 43.477 | 0.2 | 0.2 | 206.5 | 0.51172
2012-11-26 | 13:14 | 4 | 20 | 0 | 260 | 4.3333 | 1448 | 47423 | 377000 | 94.3 | 5.7 | 44.3 | 0.21 | 0.21 | 255.5 | 0.43426
2012-11-26 | 13:30 | 4 | 34 | 0 | 274 | 4.5667 | 1465 | 47445 | 399000 | 94.215 | 5.785 | 44.385 | 0.22 | 0.22 | 269.5 | 0.4313
2012-11-26 | 14:30 | 5 | 37 | 0 | 337 | 5.6167 | 1460 | 47534 | 488000 | 93.865 | 6.135 | 44.735 | 0.3 | 0.3 | 332.5 | 0.4767
2012-11-26 | 15:26 | 6 | 33 | 0 | 393 | 6.55 | 1462 | 47616 | 570000 | 92.4 | 7.6 | 46.2 | 0.34 | 0.34 | 388.5 | 0.46239
2012-11-26 | 16:30 | 7 | 35 | 0 | 455 | 7.5833 | 1458 | 47709 | 663000 | 91.725 | 8.275 | 46.875 | 0.4 | 0.4 | 450.5 | 0.46912
2012-11-26 | 17:30 | 8 | 33 | 0 | 513 | 8.55 | 1452 | 47793 | 747000 | 91.321 | 8.679 | 47.279 | 0.5 | 0.5 | 508.5
2012-11-26 | 18:30 | 9 | 30 | 0 | 570 | 9.5 | 1450 | 47875 | 829000 | 90.956 | 9.044 | 47.644 | 0.5 | 0.5 | 565.5 | 0.46715
2012-11-26 | 19:30 | 10 | 34 | 0 | 634 | 10.5667 | 1451 | 47968 | 922000 | 90.669 | 9.331 | 47.931 | 0.5 | 0.5 | 629.5 |  | Increase Rate
2012-11-26 | 20:30 | 11 | 34 | 0 | 694 | 11.5667 | 1450 | 48054 | 1008000 | 90.102 | 9.898 | 48.498 | 0.5 | 0.5 | 689.5
2012-11-26 | 21:30 | 12 | 34 | 0 | 754 | 12.5667 | 1451 | 48412 | 1366000 | 89.69 | 10.31 | 48.91 | 0.6 | 0.6 | 749.5 | 0.42296
2012-11-26 | 22:30 | 13 | 34 | 0 | 814 | 13.5667 | 1449 | 48228 | 1182000 | 89.639 | 10.361 | 48.961 | 0.6 | 0.6 | 809.5 | 0.39161 | Increase Rate
2012-11-26 | 23:30 | 14 | 34 | 0 | 874 | 14.5667 | 1450 | 48315 | 1269000 | 89.226 | 10.774 | 49.374 | 0.6 | 0.6 | 869.5 | 0.36459
2012-11-27 | 0:30 | 15 | 34 | 0 | 934 | 15.5667 | 1450 | 48404 | 1358000 | 88.981 | 11.019 | 49.619 | 0.7 | 0.7 | 929.5 | 0.39789
2012-11-27 | 1:30 | 16 | 34 | 0 | 994 | 16.5667 | 1450 | 48489 | 1443000 | 88.649 | 11.351 | 49.951 | 0.7 | 0.7 | 989.5 | 0.37377 | Increase Rate
2012-11-27 | 2:30 | 17 | 34 | 0 | 1054 | 17.5667 | 1451 | 48575 | 1529000 | 88.455 | 11.545 | 50.145 | 0.8 | 0.8 | 1049.5 | 0.40274
2012-11-27 | 3:30 | 18 | 34 | 0 | 1114 | 18.5667 | 1450 | 48662 | 1616000 | 88.454 | 11.546 | 50.146 | 0.9 | 0.9 | 1109.5 | 0.42858 | Increase Rate
2012-11-27 | 4:30 | 19 | 34 | 0 | 1174 | 19.5667 | 1451 | 48749 | 1703000 | 88.065 | 11.935 | 50.535 | 0.9 | 0.9 | 1169.5 | 0.40659
2012-11-27 | 5:30 | 20 | 34 | 0 | 1234 | 20.5667 | 1450 | 48836 | 1790000 | 88.013 | 11.987 | 50.587 | 1 | 1 | 1229.5 | 0.42972 | Increase Rate
2012-11-27 | 6:30 | 21 | 34 | 0 | 1294 | 21.5667 | 1449 | 48924 | 1878000 | 87.26 | 12.74 | 51.34 | 1.1 | 1.1 | 1289.5 | 0.4507 | Increase Rate
2012-11-27 | 7:30 | 22 | 28 | 0 | 1348 | 22.4667 | 1450 | 49003 | 1957000 | 87.25 | 12.75 | 51.35 | 1.2 | 1.2 | 1343.5
2012-11-27 | 8:30 | 23 | 35 | 0 | 1415 | 23.5833 | 1448 | 49101 | 2055000 | 87.241 | 12.759 | 51.359 | 1.2 | 1.2 | 1410.5 |  | Increase Rate
2012-11-27 | 9:30 | 24 | 35 | 0 | 1475 | 24.5833 | 1450 | 49180 | 2134000 | 86.825 | 13.175 | 51.775 | 1.4 | 1.4 | 1470.5 | 0.50302 | [9 empty] | 24 | 0 | 24
2012-11-27 | 10:30 | 25 | 33 | 0 | 1533 | 25.55 | 1452 | 49270 | 2224000 | 86.908 | 13.092 | 51.692 | 1.4 | 1.4 | 1528.5 | 0.48393 | [10 empty] | 1 | 25
2012-11-27 | 11:30 | 26 | 41 | 0 | 1601 | 26.6833 | 1454 | 49369 | 2323000 | 86.675 | 13.325 | 51.925 | 1.5 | 1.5 | 1596.5 | 0.49641 | [10 empty] | 2 | 26
2012-11-27 | 12:30 | 27 | 29 | 0 | 1649 | 27.4833 | 1464 | 49439 | 2393000 | 85.906 | 14.094 | 52.694 | 1.5 | 1.5 | 1644.5 | 0.48192 | Decrease Rate | [9 empty] | 3 | 27
2012-11-27 | 13:30 | 28 | 36 | 0 | 1716 | 28.6 | 1451 | 49537 | 2491000 | 86.282 | 13.718 | 52.318 | 1.5 | 1.5 | 1711.5 | 0.46306 | [10 empty] | 4 | 28
2012-11-27 | 14:30 | 29 | 29 | 0 | 1769 | 29.4833 | 1448 | 49614 | 2568000 | 86.304 | 13.696 | 52.296 | 1.6 | 1.6 | 1764.5 | 0.47909 | [10 empty] | 5 | 29
2012-11-27 | 15:30 | 30 | 36 | 0 | 1836 | 30.6 | 1446 | 49711 | 2665000 | 86.726 | 13.274 | 51.874 | 1.7 | 1.7 | 1831.5 | 0.49041 | Increase Rate | [9 empty] | 6 | 30
2012-11-27 | 16:30 | 31 | 34 | 0 | 1894 | 31.5667 | 1452 | 49793 | 2747000 | 86.203 | 13.797 | 52.397 | 1.6 | 1.6 | 1889.5 | 0.4474 | [10 empty] | 7 | 31
2012-11-27 | 17:30 | 32 | 29 | 0 | 1949 | 32.4833 | 1450 | 49874 | 2828000 | 86.114 | 13.886 | 52.486 | 1.8 | 1.8 | 1944.5 | 0.48908 | [10 empty] | 8 | 32
2012-11-27 | 18:30 | 33 | 32 | 0 | 2012 | 33.5333 | 1450 | 49866 | 2820000 | 85.813 | 14.187 | 52.787 | 1.9 | 1.9 | 2007.5 | 0.50005 | [10 empty] | 9 | 33
2012-11-27 | 19:30 | 34 | 34 | 0 | 2074 | 34.5667 | 1451 | 50055 | 3009000 | 85.418 | 14.582 | 53.182 | 1.9 | 1.9 | 2069.5 | 0.48507 | [10 empty] | 10 | 34
2012-11-27 | 20:30 | 35 | 34 | 0 | 2134 | 35.5667 | 1452 | 50143 | 3097000 | 85.274 | 14.726 | 53.326 | 1.9 | 1.9 | 2129.5 | 0.47141 | [10 empty] | 11 | 35
2012-11-27 | 21:30 | 36 | 34 | 0 | 2194 | 36.5667 | 1453 | 50230 | 3184000 | 85.27 | 14.73 | 53.33 | 2 | 2 | 2189.5 | 0.48262 | [10 empty] | 12 | 36
2012-11-27 | 22:30 | 37 | 34 | 0 | 2254 | 37.5667 | 1451 | 50311 | 3265000 | 85.023 | 14.977 | 53.577 | 2 | 2 | 2249.5 | 0.46975 | [10 empty] | 13 | 37
2012-11-27 | 23:30 | 38 | 34 | 0 | 2314 | 38.5667 | 1451 | 50405 | 3359000 | 85.053 | 14.947 | 53.547 | 2.1 | 2.1 | 2309.5 | 0.48042 | [10 empty] | 14 | 38
2012-11-28 | 0:30 | 39 | 34 | 0 | 2374 | 39.5667 | 1449 | 50492 | 3446000 | 85.005 | 14.995 | 53.595 | 2.1 | 2.1 | 2369.5 | 0.46825 | [10 empty] | 15 | 39
2012-11-28 | 1:30 | 40 | 34 | 0 | 2434 | 40.5667 | 1448 | 50578 | 3532000 | 84.925 | 15.075 | 53.675 | 2.2 | 2.2 | 2429.5 | 0.47844 | Increase Rate | [9 empty] | 16 | 40
2012-11-28 | 2:30 | 41 | 34 | 0 | 2494 | 41.5667 | 1450 | 50664 | 3618000 | 84.771 | 15.229 | 53.829 | 2.2 | 2.2 | 2489.5 | 0.46691 | [10 empty] | 17 | 41
2012-11-28 | 3:30 | 42 | 34 | 0 | 2554 | 42.5667 | 1450 | 50752 | 3706000 | 84.811 | 15.189 | 53.789 | 2.3 | 2.3 | 2549.5 | 0.47664 | [10 empty] | 18 | 42
2012-11-28 | 4:30 | 43 | 34 | 0 | 2614 | 43.5667 | 1449 | 50841 | 3795000 | 84.838 | 15.162 | 53.762 | 2.4 | 2.4 | 2609.5 | 0.48593 | [10 empty] | 19 | 43
2012-11-28 | 5:30 | 44 | 34 | 0 | 2674 | 44.5667 | 1447 | 50925 | 3879000 | 84.962 | 15.038 | 53.638 | 2.4 | 2.4 | 2669.5 | 0.47501 | [10 empty] | 20 | 44
2012-11-28 | 6:30 | 45 | 34 | 0 | 2734 | 45.5667 | 1452 | 51012 | 3966000 | 84.375 | 15.625 | 54.225 | 2.5 | 2.5 | 2729.5 | 0.48392 | [10 empty] | 21 | 45
2012-11-28 | 7:30 | 46 | 29 | 0 | 2789 | 46.4833 | 1449 | 51093 | 4047000 | 84.361 | 15.639 | 54.239 | 2.5 | 2.5 | 2784.5 | 0.47436 | [10 empty] | 22 | 46
2012-11-28 | 8:30 | 47 | 38 | 0 | 2858 | 47.6333 | 1451 | 51193 | 4147000 | 84.116 | 15.884 | 54.484 | 2.5 | 2.5 | 2853.5 | 0.46289 | [10 empty] | 23 | 47
2012-11-28 | 9:30 | 48 | 34 | 0 | 2914 | 48.5667 | 1450 | 51274 | 4228000 | 84.376 | 15.624 | 54.224 | 2.5 | 2.5 | 2909.5 | 0.45398
2012-11-28 | 10:30 | 49 | 41 | 0 | 2981 | 49.6833 | 1448 | 51371 | 4325000 | 84.427 | 15.573 | 54.173 | 2.6 | 2.6 | 2976.5 | 0.46152
2012-11-28 | 11:30 | 50 | 34 | 0 | 3034 | 50.5667 | 1449 | 51447 | 4401000 | 84.306 | 15.694 | 54.294 | 2.6 | 2.6 | 3029.5 | 0.45344
2012-11-28 | 12:30 | 51 | 36 | 0 | 3096 | 51.6 | 1450 | 51537 | 4491000 | 84.109 | 15.891 | 54.491 | 2.6 | 2.6 | 3091.5 | 0.44435
2012-11-28 | 13:30 | 52 | 35 | 0 | 3155 | 52.5833 | 1451 | 51623 | 4577000 | 84.16 | 15.84 | 54.44 | 2.6 | 2.6 | 3150.5 | 0.43603
2012-11-28 | 14:36 | 53 | 39 | 0 | 3219 | 53.65 | 1449 | 51717 | 4671000 | 83.755 | 16.245 | 54.845 | 2.7 | 2.7 | 3214.5 | 0.44378
2012-11-28 | 15:30 | 54 | 34 | 0 | 3274 | 54.5667 | 1447 | 51796 | 4750000 | 83.841 | 16.159 | 54.759 | 2.7 | 2.7 | 3269.5 | 0.43632
2012-11-28 | 16:30 | 55 | 35 | 0 | 3335 | 55.5833 | 1448 | 51884 | 4838000 | 84.425 | 15.575 | 54.175 | 2.7 | 2.7 | 3330.5 | 0.42832 | Increase Rate
2012-11-28 | 17:30 | 56 | 36 | 0 | 3396 | 56.6 | 1455 | 51975 | 4929000 | 83.656 | 16.344 | 54.944 | 2.8 | 2.8 | 3391.5 | 0.4362
2012-11-28 | 18:30 | 57 | 34 | 0 | 3454 | 57.5667 | 1455 | 52058 | 5012000 | 83.439 | 16.561 | 55.161 | 2.9 | 2.9 | 3449.5 | 0.44418
2012-11-28 | 19:30 | 58 | 34 | 0 | 3514 | 58.5667 | 1456 | 52144 | 5098000 | 83.198 | 16.802 | 55.402 | 3 | 3 | 3509.5 | 0.45164
2012-11-28 | 20:30 | 59 | 34 | 0 | 3574 | 59.5667 | 1454 | 52232 | 5186000 | 83.048 | 16.952 | 55.552 | 3 | 3 | 3569.5 | 0.44405
2012-11-28 | 21:30 | 60 | 34 | 0 | 3634 | 60.5667 | 1453 | 52319 | 5273000 | 83.152 | 16.848 | 55.448 | 3 | 3 | 3629.5 | 0.43671
2012-11-28 | 22:30 | 61 | 34 | 0 | 3694 | 61.5667 | 1451 | 52406 | 5360000 | 83.243 | 16.757 | 55.357 | 3.1 | 3.1 | 3689.5 | 0.44393
2012-11-28 | 23:30 | 62 | 34 | 0 | 3754 | 62.5667 | 1450 | 52494 | 5448000 | 83.004 | 16.996 | 55.596 | 3.1 | 3.1 | 3749.5 | 0.43682
2012-11-29 | 0:30 | 63 | 34 | 0 | 3814 | 63.5667 | 1450 | 52580 | 5534000 | 83.945 | 16.055 | 54.655 | 3.1 | 3.1 | 3809.5 | 0.42994
2012-11-29 | 1:30 | 64 | 34 | 0 | 3874 | 64.5667 | 1451 | 52672 | 5626000 | 83.123 | 16.877 | 55.477 | 3.1 | 3.1 | 3869.5 | 0.42328
2012-11-29 | 2:30 | 65 | 34 | 0 | 3934 | 65.5667 | 1447 | 52154 | 5108000 | 82.851 | 17.149 | 55.749 | 3.1 | 3.1 | 3929.5 | 0.41681 | Increase Rate
2012-11-29 | 3:30 | 66 | 34 | 0 | 3994 | 66.5667 | 1448 | 52842 | 5796000 | 82.006 | 17.994 | 56.594 | 3.3 | 3.3 | 3989.5 | 0.43703 | Increase Rate
2012-11-29 | 4:30 | 67 | 34 | 0 | 4054 | 67.5667 | 1449 | 52928 | 5882000 | 82.771 | 17.229 | 55.829 | 3.7 | 3.7 | 4049.5 | 0.48275
2012-11-29 | 5:30 | 68 | 34 | 0 | 4114 | 68.5667 | 1450 | 53015 | 5969000 | 82.868 | 17.132 | 55.732 | 3.9 | 3.9 | 4109.5 | 0.50141
2012-11-29 | 6:30 | 69 | 34 | 0 | 4174 | 69.5667 | 1450 | 53101 | 6055000 | 82.519 | 17.481 | 56.081 | 4 | 4 | 4169.5 | 0.50687
2012-11-29 | 7:06 | 70 | 10 | 0 | 4210 | 70.1667 | 1447 | 53154 | 6108000 | 82.73 | 17.27 | 55.87 | 4 | 4 | 4205.5 | 0.50253
2012-11-29 | 7:30 | 71 | 38 | 0 | 4298 | 71.6333 | 1448 |  |  | 82.553 | 17.447 | 56.047 | 4 | 4 | 4293.5 | 0.49223
2012-11-29 | 8:30 | 72 | 34 | 0 | 4354 | 72.5667 | 1452 | 53275 |  | 82.594 | 17.406 | 56.006 | 4.1 | 4.1 | 4349.5 | 0.49804