TABLE 3-4	AQUIFER PERFORMANCE TEST ANAYSIS SUMMARY

|  | TRANSMISSIVITY (T) (GPD/FT) | STORAGE COEFFICIENT (Sc) | LEAKANCE (L) (GPD/FT3) |
| --- | --- | --- | --- |
| APT 1, Theis, Drawdown, MW-C | 25,500 | 7.7 x 10-5 | 1.2 x 10-4 |
| APT 1, Cooper-Jacob, Drawdown, MW-C | 25,150 | 6.6 x 10-5 | ND |
| APT 1, Theis, Recovery, MW-C | 25,900 | ND | ND |
| APT 2, Theis, Drawdown, MW-C | 23,800 | 5.7 x 10-5 | ND |
| APT 2, Cooper-Jacob, Drawdown, MW-C | 25,500 | 4.9 x 10-5 | ND |
| APT 2, Theis, Drawdown, MW-A | 13,200 | 2.3 x 10-4 | ND |
| APT 2, Cooper-Jacob, Drawdown, MW-A | 14,200 | 1.7 x 10-4 | ND |
| Average, All Analyses MW-C MW-A | 25,200 13,700 | 6.2 x 10-5 2.0 x 10-4 | 1.2 x 10-4 gpd/ft |

TABLE 3-3	AQUIFER PARAMETER ESTIMATES

PROJECT PHASES I AND II

| Aquifer/Zone | Interval (ft) below land surface | Net Thickness (ft) | Est. Transmissivity (gpd/ft) | Estimated Horizontal Hydraulic Conductivity (gpd/ft2) |
| --- | --- | --- | --- | --- |
| ASR Exploration Well Data |  |  |  |  |
| Mid Hawthorn Zone I | 336-404 | 61 | 10,000 | 170 |
| Mid Hawthorn Zone II | 428-515 | 85 | 4,000 | 45 |
| Lower Hawthorn Zone I | 524-589 | 60 | 4,000 | 50 |
| Suwannee* | Partial Penetration (34 of an estimated 240 feet) | -- | 96,000 | -- |
| Monitor Wells MW-B and MW-C Data |  |  |  |  |
| Mid Hawthorn Zone I | 330-400 | 70 | 20,000-27,000 | 285-385 |
| Mid Hawthorn Zone II | 452-504 | 52 | 900-1,200 | 17-23 |

*Also includes basal portion of Lower Hawthorn (693 to 744 feet) with which it is in contact

TABLE 5-1	EMERGENCY WITHDRAWAL ANALYSIS

| WITHDRAWAL RATE (Q) (gpm)* | FORMATION DRAWDOWN ALL WELLS (FEET) | FORMATION DRAWDOWN TYPICAL ASR WELL (FEET) | FORMATION PLUS WELL LOSS (FEET) | INTERFERENCE DRAWDOWN AT TYPICAL ASR WELL (FEET) | TOTAL DRAWDOWN (FEET) | TOTAL YIELD, ALL WELLS (MGD) |
| --- | --- | --- | --- | --- | --- | --- |
| 275 | 91 | 39 | 66 | 52 | 118 | 3.96 |
| 300 | 102 | 42 | 72 | 60 | 132 | 4.32 |
| 325 | 108 | 45 | 81 | 63 | 144 | 4.68 |
| 350 | 115 | 48 | 89 | 67 | 156 | 5.04 |
| 375 | 127 | 51 | 98 | 76 | 174 | 5.40 |

*Reflects constant per well withdrawal for 14 day period.

TABLE 6-2	SUMMARY OF ANTICIPATED BLENDED WATER QUALITY

CORKSCREW WTP - ASR PILOT PROJECT

| CONSISTENT | BLENDED WATER1 CONCENTRATION | DRINKING WATER STANDARDS |
| --- | --- | --- |
| Hardness | 85-105 mg/l | 250 mg/l |
| Alkalinity | 60-90 mg/l | Not Applicable |
| TDS | 200-300 mg/l | 500 mg/l |
| Iron | 0.03-0.10 mg/l | 0.3 mg/l |
| Manganese | <0.001 | 0.5 mg/l |
| Sulfate | 20-30 mg/l | 250 mg/l |
| THM (Total) | 0.01-0.06 mg/l | 0.10 mg/l |
| Gross Alpha | 1-4 pCi/l | 15 pCi/l |
| Color | 6-8 color units | 15 color units |
| pH | 7-8 | 6.5-8.5 |

Notes

1 Blended water concentrations is based on a recovered water flow rate between 1 to 3 mgd, mixing with a flow rate of 5 to 10 mgd from the Corkscrew WTP meeting established water quality goals.

TABLE 6-5	CORKSCREW WTP - ASR PILOT PROJECT

ASR SYSTEM OPERATING COST

3.0 MGD ASR SYSTEM

| COST COMPONENT | ANNUAL OPERATING COSTS (DOLLARS) | COST PER 1000 GALLONS (DOLLARS) |
| --- | --- | --- |
| Injection Pressure Energy | $16,000 | 0.060 |
| Recovery Pressure Energy | $17,200 | 0.063 |
| Well Maintenance Costs | $24,000 | 0.086 |
| TOTAL MAINTENANCE COST: | $57,200 | $0.22 |

Note:  Total costs based on operations of a 270 million gallon annual storage recovery and 300 million gallons injected.  Energy costs based on $0.08 per kw/hour.

TABLE 6-6	COMPARISON OF SYSTEM REQUIREMENTS

ASR SYSTEM AND CONVENTIONAL

WATER SUPPLY AND TREATMENT

|  | CAPITAL COSTS | OPERATIONS COSTS |
| --- | --- | --- |
| ASR | -ASR wells -injection/recovery pipeline -Well maintenance system -instrumentation & controls -chemical fee system | -injection/recovery pressure -rechlorination -distribution system pressure -system maintenance -water losses |
| Conventional Water Supply and Treatment | -additional water supply wells -treatment processes -chemical feed system -instrumentation & controls -disposal system | -distribution system pressure -treatment costs -maintenance costs -chemical feed system |

TABLE 6-6	COMPARISON OF SYSTEM REQUIREMENTS

ASR SYSTEM AND CONVENTIONAL

WATER SUPPLY AND TREATMENT

|  | CAPITAL COSTS | OPERATIONS COSTS |
| --- | --- | --- |
| ASR | -ASR wells -injection/recovery pipeline -Well maintenance system -instrumentation & controls -chemical feed system | -injection/recovery pressure -rechlorination -distribution system pressure -system maintenance -water losses and back flushing |
| Conventional Water Supply and Treatment | -additional water supply wells -treatment processes -chemical feed system -instrumentation & controls -disposal system | -distribution system pressure -treatment costs -maintenance costs -chemical feed system |

TABLE 6-7	CORKSCREW WTP ASR PILOT PROJECT

CAPITAL AND OPERATING COST

ANALYSIS FOR ASR AND CONVENTIONAL

WATER TREATMENT SYSTEM

| SYSTEM/COMPONENT | CAPITAL COSTS (DOLLARS) | OPERATING COSTS (DOLLARS/1000 GALLONS) |
| --- | --- | --- |
| ASR System Wells & Appurtenances Pipeline and Appurtenances Storage Zone Establishment | 1,300,000 1,400,000 66,000 | 0.12 0.10 |
| TOTAL COSTS: | $2,766,000 | $0.22 |
| Conventional Water Treatment System/Reverse Osmosis Wellfield Treatment Plant Reject Disposal Well | 580,000 4,500,000 2,800,000 | 0.30 1.00 0.05 |
| TOTAL COSTS: | $7,880,000 | $1.35 |
| Conventional Water Treatment System/Lime Softening Wellfield Treatment Plant Backwash Recovery Ponds | 1,400,000 3,900,000 300,000 | 0.18 0.55 0.04 |
| TOTAL COSTS: | $5,600,000 | $0.77 |

TABLE 6-1	ASR PILOT PROJECT CORKSCREW WATER TREATMENT PLANT

WATER BLENDING ANALYSIS

Suspended Solids	Turbidity

(mg/l)	   (NTU)

Native Water	Not detected	0.21

Not detected	0.18

Injected Water

Sample 12	0.15	0.40

Sample 23	0.18	0.37

10: 801

Sample 1	0.17	0.36

Sample 2	0.34	0.38

40: 60

Sample 1	0.15	0.35

Sample 2	0.10	0.30

60: 40

Sample 1	0.14	0.26

Sample 2	0.05	0.28

80: 20

Sample 1	Not detected	0.24

Sample 2	Not detected	0.24

1	% Native water/% Injected water ratio.

2	Sample 1 was incubated for 24 hours.

3	Sample 2 was incubated for 7 days.